## Generation Interconnection
CPUC TRANSMISSION PROJECTS -- SCE TERRITORY
Generation Interconnection Projects - Third Quarter 2016
NO. | PROJECT NAME | LOCATION | PROJECT DESCRIPTION | RATING | ID | APPROVAL STATUS |  |  | CONSTRUCTION STATUS (1) | PLANNED IN SERVICE DATE (2) | PURPOSE & BENEFIT
[6 empty] | UTILITY | ISO | CPUC
18.13 | Mountain View IV | Riverside County | Interconnect a 49 MW Wind Generating Facility via a new 115kV substation; upgrade line protection at SCE's Garnet Substation; upgrade telecommunication facilities and RTU at SCE's Devers Substation. | 49 MW 115kV | WDT213 | Yes | Yes | Phase 1 Exemption (f) & Phase 2 Exemption (g) | Operational | Int. Facilities: In Service Network Upgrades: In Service | Generation Interconnection
18.18 | Manzana Wind | Kern County | Interconnect a 300 MW Wind Generating Facility to SCE's Whirlwind 220kV Substation; terminate the Manzana Wind 220kV gentie line in a new position at Whirlwind Substation. Install telecommunications facilities to support line protection; install RTU. TRTP network upgrades apply. | 300 MW 220kV | TOT108 | Yes | Yes | "Substation Modification" as defined in GO 131-D, Section III.B. Not subject to PTC requirements. | Construction | Int. Facilities: In Service Network Upgrades: TBD -under review | Generation Interconnection
18.2 | Dracker Project | Riverside County | Interconnect a 485 MW Solar Generating Facility to SCE's expanded Colorado River 500/220kV Substation; Expand the Colorado River 500kV Substation to include a new 220kV switchayard and transformation; terminate the Dracker Project 220kV gentie line at Colorado River Substation; loop the proposed Devers-Colorado River line into the proposed Red Bluff 500/220kV Substation; upgrade MIra Loma-Vista 220kV line drop at Vista Substation; install special protection system; upgrade the four (4) West of Devers 220kV lines. Install telecommunications facilities at Colorado River Sustation to support line protection and special protection system; install RTU. | 485 MW 220kV | TOT276 | Yes | Yes | Yes-PTC | Operational | SCE Int. Facilities: In Service Network Upgrades: August 2021 | Generation Interconnection
18.21 | Palen Solar II (Almasol) | Riverside County | Interconnect a 500 MW Solar Generating Facility to SCE's proposed Red Bluff 500/220kV Substation; terminate the Palen Solar II 220kV gentie line at Red Bluff Substation; loop the proposed Devers-Colorado River line into the proposed Red Bluff 500/220kV Substation; expand the Colorado River 500kV Substation to include a new 220kV switchayard and transformation; upgrade MIra Loma-Vista 220kV line drop at Vista Substation; install special protection system; upgrade the four (4) West of Devers 220kV lines. Install telecommunications facilities at Red Bluff Sustation to support line protection and special protection system; install RTU. | 500 MW 220kV | TOT321 | Yes | Yes | Yes-PTC | Construction | SCE Int. Facilities: Ready for Service (pending the Interconnection Customer's readiness) Network Upgrades: August 2021 LGIA Amendment in progress to update Interconnection Customer's in-service date and Project name | Generation Interconnection
18.23 | AV Solar I | Kern County | Interconnect a 250 MW Solar Generating Facility to SCE's Whirlwind 220kV Substation; terminate the AV Solar I 220kV gentie line in a new position at Whirlwind Substation. Install special protection system; replace/upgrade 500kV circuit breakers at Vincent Substation. Install telecommunications facilities to support line protection and special protection system; install RTU. Install 2nd and 3rd AA transformers at Whirlwind Substation. TRTP network upgrades apply. | 250 MW 220kV | TOT345 | Yes | Yes | Exempt - Section III.A | Construction | Int. Facilities: In Service Network Upgrades: TBD-under review | Generation Interconnection
18.25 | Genesis McCoy Solar Project | Riverside County | Interconnect a 500 MW Solar Generating Facility to SCE's expanded Colorado River 500/220kV Substation; Expand the Colorado River 500kV Substation to include a new 220kV switchayard and transformation; terminate the two Genesis and McCoy 220kV gentie lines at Colorado River Substation; loop the proposed Devers-Colorado River line into the proposed Red Bluff 500/220kV Substation; upgrade MIra Loma-Vista 220kV line drop at Vista Substation; install special protection system; upgrade the four (4) West of Devers 220kV lines. Install telecommunications facilities at Colorado River Sustation to support line protection and special protection system; install RTU; install the Interim West of Devers Project consisting of temporary installation of line reactors on the existing four 220kV lines west of Devers substation and SPS. | 500 MW 230kV | TOT223 | Yes | Yes | Yes for Colorado River Substation Expansion; Interim West of Devers Upgrade is Exempt. | Operational | Phase I (250 MW) Int. Facilities: In Service Phase II (250 MW) Int. Facilities: In Service Interim West of Devers Project: In Service Network Upgrades: August 2021 | Generation Interconnection
18.26 | Desert Stateline | San Bernardino County | Interconnect a 300 MW Solar Generating Facility to SCE's Ivanpah 220kV Substation; terminate the Desert Stateline 220kV gentie line at Ivanpah Substation; Install special protection system; Install telecommunications facilities to support line protection and special protection system; install RTU. Construct a new SCE-owned Eldorado 220kV Switchyard adjacent to the existing jointly-owned Eldorado Substation (part of the cluster network upgrades) | 300 MW 220kV | TOT211 | Yes | Yes | Exempt - Section III.A | Operational | Int. Facilities: In Service Network Upgrades: In Service with the exception of the the Lugo-Victorville RAS, which is expected to be in service by 12/31/2019 8/15/2016 | Generation Interconnection
18.27 | Silver State South | Clark County | Interconnect a 250 MW Solar Generating Facility to a new SCE Primm 220kV Substation. Loop one or both of the Eldorado-Ivanpah 220kV lines into the new Primm Substation; terminate the Silver State South 220kV gentie line at the new Primm Substation; Install special protection system; Install telecommunications facilities to support line protection and special protection system; install RTU. Construct a new SCE-owned Eldorado 220kV Switchyard adjacent to the existing jointly-owned Eldorado Substation. | 250 MW 220kV | TOT381 | Yes | Yes | Exempt per CEQA Guideline 15277 | Operational | Int. Facilities: In Service Network Upgrades: In Service with the exception of the the Lugo-Victorville RAS, which is expected to be in service by 12/31/2019 8/15/2016 | Generation Interconnection
18.28 | Pacific Wind Project | Kern County | Interconnect a 250 MW Wind Generating Facility to SCE's Whirlwind 220kV Substation; terminate the Pacific Wind 220kV gentie line in a new position at Whirlwind Substation. Install special protection system; Install telecommunications facilities to support line protection and special protection system; install RTU. TRTP network upgrades apply. | 250 MW 220kV | TOT148 | Yes | Yes | Exempt - Section III.A | Construction | Int. Facilities: In Service Network Upgrades: TBD-under review | Generation Interconnection
18.29 | Suncreek & Alta 6 (formally Alta 2012) | Kern County | Interconnect a 720 MW Wind Generating Facility to SCE's Windhub 220kV Substation; terminate the Alta 2012 220kV gentie line in a new position at Windhub Substation. Install telecommunications facilities to support line protection; install RTU. TRTP network upgrades apply. | 720 MW 220kV | TOT161 TOT173 | Yes | Yes | Exempt - Section III.A | Construction | Int. Facilities: In Service Network Upgrades: TBD-under review | Generation Interconnection
18.31 | Antelope Valley Solar PV 1 | Kern County | Interconnect a 310 MW Solar Generating Facility to SCE's Whirlwind 220kV Substation; terminate the Antelope Valley Solar PV 1 220kV gentie line in a new position at Whirlwind Substation. Install special protection system; replace/upgrade 500kV circuit breakers at Vincent Substation. Install telecommunications facilities to support line protection and special protection system; install RTU. Install 2nd and 3rd AA transformers at Whirlwind Substation. TRTP network upgrades apply. | 310 MW 220kV Project capacity downsized from 325 MW to 310 MW | TOT340 | Yes | Yes | Exempt - Section III.A | Construction | Int. Facilities: In Service Network Upgrades: TBD-under review | Generation Interconnection
18.32 | Antelope Valley Solar PV 2 | Kern County | Interconnect a 276 MW Solar Generating Facility to SCE's Whirlwind 220kV Substation; terminate the Antelope Valley Solar PV 2 220kV gentie line in a new position at Whirlwind Substation. Install special protection system; replace/upgrade 500kV circuit breakers at Vincent Substation. Install telecommunications facilities to support line protection and special protection system; install RTU. Install 2nd and 3rd AA transformers at Whirlwind Substation. TRTP network upgrades apply. | 276 MW 220kV Project capacity downsized from 325 MW to 276 MW | TOT341 | Yes | Yes | Exempt - Section III.A | Construction | Int. Facilities: In Service Network Upgrades: TBD-under review | Generation Interconnection
18.33 | Soleil Solar Project (Formerly Catalina Solar Project) | Kern County | Interconnect a 150 MW Solar Generating Facility to SCE's Whirlwind 220kV Substation via the proposed, Pacific Wind-owned, PacificWind-Whirlwind 220kV gentie line and line position at Whirlwind Substation. Install special protection system; replace/upgrade 500kV circuit breakers at Vincent Substation and 220kV circuit breakers at lugo Substation; replace 500kV wave traps at Lugo and Vincent Substations. Install telecommunications facilities to support line protection and special protection system; install RTU. Install 4th AA transformer at Whirlwind Substation. | 150 MW 220kV | TOT455 | Yes | Yes | "Substation Modification" as defined in GO 131-D, Section III.B. Not subject to PTC requirements. | Construction | Int. Facilities: In Service Network Upgrades: TBD-under review | Generation Interconnection
18.4 | NRG El Segundo Energy Center 2 | Los Angeles County | Interconnect a 435 MW Combined Cycle Generating Facility to line positions 3 & 4 within SCE's El Segundo 220kV Substation. Terminate the customer-owned El Segundo Units 9-10 and El Segundo Units 11-12 Generation Tie-Lines at El Segundo Substation. Install conductors, metering equipment, disconnects and circuit breakers in line positions 3 & 4. Upgrade four 500kV circuit breakers at Vincent Substation; upgrade six 220kV circuit breakers at Colorado River Substation; replace one 220kV circuit breaker at Antelope Substation. Install communication equipment and line protection relays and upgrade the RTU at El Segundo Substation. | 435 MW 220kV | TOT560 | Yes | Yes | TBD | Engineering & Design | 2017-10-01 | Generation Interconnection
18.41 | LEAPS Generating Facility | Riverside County | Interconnect a 500 MW Hydro Pumped Storage Generating Facility to SCE's proposed Alberhill Substation. Terminate the customer-owned Alberhill-LEAPS 500kV Generation Tie-Line at Alberhill Substation; equip a new 500kV line position at Alberhill Substation; install telecommunications facilities to support line protection, RTU and SPS; install RTU at the generating facility; Upgrade the Serrano-Valley 500kV line protection at Serrano and Valley Substations; replace the wave trap on the Vsta 220kV line position at Etiwanda Generating Station; replace twenty-four 63kA 220kV circuit breakers with 80 kA rated circuit breakers and upgrade the Etiwanda 220kV switchyard to 80 kA rating. | 500 MW 500kV | TOT132 | Yes | Yes | CPCN Planned | Engineering & Design | TBD | Generation Interconnection
18.46 | Avalon Hybrid Project | Kern County | Interconnect a 100 MW Solar Photovoltaic Generating Facility to SCE's Whirlwind 220kV Substation; terminate the Avalon Hybrid-Whirlwind 220kV gentie line in a new 220kV line position at Whirlwind Substation. Install telecommunications facilities to support line protection; install RTU at the Generating Facility. | 100 MW 220 kV | TOT151 | Yes | Yes | TBD | Engineering & Design | 12/1/2019 LGIA Amendment in progress to change project size and in- service date. | Generation Interconnection
18.47 | Palmdale Power Plant | Los Angeles County | Interconnect a 570 MW Combined Cycle Gas-fired Generating Facility to SCE's Vincent 220kV Substation; terminate the Palmdale power Plant-Vincent 220kV gentie line in a new 220kV line position at Vincent Substation (requires approx 6 spans of conductor and 5 structures). Install telecommunications facilities to support line protection; install RTU at the Generating Facility. Interconnection Customer has suspended the project pursuant to the LGIA effective 9-30-2014. | 570 MW 220kV | TOT154 | Yes | Yes | TBD | Suspended | TBD after the suspension has ended | Generation Interconnection
18.48 | Kingbird Solar A | Los Angeles County | Interconnect a 20 MW Solar Generating Facility to SCE's Whirlwind 220kV Substation via the existing shared Solar Ranch-Whirlwind 220kV gentie line. Install telecommunications facilities to support line protection; install RTU at the Generating Facility. | 20 MW 220kV | TOT544 | Yes | Yes |  | Operational | In Service | Generation Interconnection
18.49 | Kingbird Solar B | Los Angeles County | Interconnect a 20 MW Solar Generating Facility to SCE's Whirlwind 220kV Substation via the existing shared Solar Ranch-Whirlwind 220kV gentie line. Install telecommunications facilities to support line protection; install RTU at the Generating Facility. | 20 MW 220kV | TOT545 | Yes | Yes |  | Operational | In Service | Generation Interconnection
18.5 | RE Astoria | Kern County | Interconnect a 175 MW Solar Generating Facility to SCE's Whirlwind 220kV Substation; terminate the Desert Star-Whirlwind 220kV gentie line in a new 220kV line position at Whirlwind Substation. Install telecommunications facilities to support line protection and SPS; install RTU at the Generating Facility; expand Whirlwind AA Bank SPS; expand Northern Area 500kV SPS; install 500kV 150MVAR capacitor bank at Whirlwind Substation; upgrade 500kV circuit breakers at Vincent Substation and Colordao River Substation. | 175 MW 220kV | TOT573 | Yes | Yes | Exempt - Section III.A | Operational | In Service | Generation Interconnection
18.52 | SP Antelope DSR Big Sky Solar | Los Angeles County | Interconnect a 330 MW Solar Photovoltaic Generating Facility to SCE's Antelope 220kV Substation; terminate the Big Sky Solar SP Antelope DSR 220kV gentie line in a new 220kV line position at Antelope Substation. Install telecommunications facilities to support line protection and SPS; install RTU at the Generating Facility; Upgrade RTUs at Antelope Substation; expand the Northern Area SPS; upgrade 500kV curcuit breakers at Vincent Substation | 330 MW 220kV | TOT585 | Yes | Yes |  | Operational Construction | 10/31/2016 In Service | Generation Interconnection
18.54 | CMS2 | Clark County, Nevada | SCE, as an Affected System resulting from the interconnection of the CMS2 project to SDG&E's Merchant Substation, will install telecomunications facilities at Eldorado Substation; install an RTU at the CMS2 project site; and modify the existing East of Pisgah Area SPS. | 155 MW 220kV | TOT404 | Yes | Yes | TBD | Engineering & Design | 2016-08-01 | Generation Interconnection
18.55 | Sonoran Project | Riverside County | Interconnect a 570 MW Combined Cycle Generating Facility to SCE's Colorado River 500/220kV Substation; terminate the Sonoran 500kV gentie line in a new 500kV line position at Colorado River Substation; install special protection system and telecommunications to support line protection and the special protection system; install RTU at the Generating Facility and expand the RTU at Colorado River Substation. LGIA Amendment in progress to postpone the estimated in service date. | 570 MW 500kV | TOT079 & TOT237 | Yes | Yes | TBD | Engineering & Design | 2017-03-01 | Generation Interconnection
18.56 | Sandstorm Wind Power | Riverside County | Interconnect a 150 MW Wind Power Generating Facility to SCE's proposed Glimmer 220kV Substation; Construct a new 220kV Glimmer Substation; terminate the Sandstorm 220kV gentie line at Glimmer Substation; loop the existing Devers-Vista No.1 220kV line into the proposed Glimmer Substation; install telecommunications facilities to support line protection; install RTU at the Generating Facility and Glimmer Substation. | 150 MW 220kV | TOT185 | Yes | Yes | TBD | Engineering & Design | 2020-08-31 | Generation Interconnection
18.57 | Alta Q175 | Kern County | Interconnection Agreement Terminated |  | TOT215 |  |  |  | Interconnection Agreement Terminated
18.58 | SGS Antelope Valley Development Rosamond West Solar | Kern County | Interconnect a 300 MW Solar Photovoltaic Generating Facility to SCE's Whirlwind 220kV Substation; terminate the TeddySGS Antelope Valley-Whirlwind 220kV gentie line in a new 220kV line position at Whirlwind Substation; install telecommunications facilities to support line protection and SPS; install RTU at the Generating Facility and expand RTU at Whirlwind Substation; expand the Northern Area 500kV SPS (loss of 500kV lines); expand the Whirlwind Substation SPS (loss of transformer bank). | 300 MW 220kV | TOT411 | Yes | Yes | TBD | Engineering & Design | 2016-11-01 | Generation Interconnection
18.59 | Desert Harvest | Riverside County | Interconnect a 150 MW Solar Photovoltaic Generating Facility to SCE's Red Bluff 500/220kV Substation; terminate the Desert Harvest 220kV gentie line in a new line 220kV position at Red Bluff Substation; install telecommunications facilities to support line protection and SPS; install RTU at the Generating Facility and expand RTU at Red Bluff Substation; expand the Red Bluff SPS (loss of transformer bank); expand the Colorado River Corridor SPS (loss of 500kV lines); install TRV capacitors on four 500kV circuit breakers at Vincent Substation. | 150 MW 220kV | TOT486 | Yes | Yes | TBD | Engineering & Design | 2019-08-01 | Generation Interconnection
18.6 | North Rosamond Solar | Kern County | Interconnect a 153 MW Solar Photovoltaic Generating Facility to SCE's Whirlwind 220kV Substation; terminate the Rattlesnake-Whirlwind 220kV gentie line in a new 220kV line position at Whirlwind Substation; install telecommunications facilities to support line protection and SPS; install RTU at the Generating Facility and expand RTU at Whirlwind Substation; expand the Northern Area 500kV SPS (loss of 500kV lines); expand the Whirlwind Substation SPS (loss of transformer bank); install new 500kV 150 MVAR capacitor bank on existing 500kV bus at Whirlwind Substation; install TRV capacitors on four 500kV circuit breakers at Vincent Substation. | 153 MW 220kV | TOT497 | Yes | Yes | TBD | Engineering & Design | 2016-11-01 | Generation Interconnection
18.61 | Copper Mountain Solar 4 (CMS4) | Clark County, Nevada | SCE, as an Affected System resulting from the interconnection of the CMS4 project to SDG&E's Merchant Substation, will install telecomunications facilities at Eldorado Substation; install an RTU at the CMS4 project site; and modify the existing East of Pisgah Area SPS; replace four 500kV circuit breakers and upgrade three 500kV circuit breakers at Vincent Substation. | 92 MW 220kV | TOT581 | Yes | Yes | TBD | Engineering & Design | 2016-10-29 | Generation Interconnection
18.62 | Willow Springs 2 | Kern County | Interconnect a 100 MW Solar Photovoltaic Generating Facility to SCE's Whirlwind 220kV Substation; terminate the Desert Flower-Whirlwind 220kV gentie line in a new 220kV line position at Whirlwind Substation; install telecommunications facilities to support line protection and SPS; install RTU at the Generating Facility and expand RTU at Whirlwind Substation; expand the Northern Area 500kV SPS (loss of 500kV lines); expand the Whirlwind Substation SPS (loss of transformer bank); install new 500kV 150 MVAR capacitor bank on existing 500kV bus at Whirlwind Substation; install TRV capacitors on four 500kV circuit breakers at Vincent Substation. | 100 MW 220kV | TOT494 | Yes | Yes | TBD | Engineering & Design | 2016-11-01 | Generation Interconnection
18.63 | Sun Valley | Riverside County | Interconnect a 507 MW Simple Cycle Combustion Turbine Generating Facility to SCE's Valley 115kV Substation; construct the generation tie line between the Sun Valley generating facility and Valley Substation comprised of two circuits on double circuit structures: relocate existing line position at Valley Substation to accommodate one of the two gentie circuits; terminate the two Sun Valley 115V gentie circuits in separate line positions at Valley Substation; install special protection system (SPS) and telecommunications to support line protection and the SPS; install two diverse fiber optic telecommunications path between the generating facility and Valley Subsatation; install RTU at the Generating Facility; install two RTUs at Valley Substation to support the SPS; install SPS relays, satellite clock, and channel equipment at Aberhill, Serrano, and Valley Substations; Upgrade the Aberhill 500kV line position terminal equipment at Serrano Substation. LGIA Terminated | 507 MW 115kV | WDT182 | Yes | Yes | TBD | Planning Interconnection Agreement Terminated | 2018-12-31 | Generation Interconnection
18.64 | Tehachapi Wind Energy Storage | Kern County | Interconnect a 8 MW Lithium-ion Battery Sorage Generating Facility to SCE's Monolith 66kV Substation; install 66kV line position (circuit breaker, disconnects, voltage transformers, conductor, dead-end structure, and tubular steel pole) at Monolith Substation; install one (1) 66/12kV, 28MVA three-phase transformer and surge arresters; install cable from transformer to Monolith Substation transfer bus; install one (1) 12kV 3500A circuit breaker with cts; install cable from transformer to 12kV circuit breaker; install two (2) sets of 12kV 3500A disconnect switches; install three sets of 12kV 400A disconnect switches; install one (1) 12kV/480V 300kVA pad-mounted transformer; install relay racks with protection and telecommunication equipment; install revenue metering; install RTU; install six (6) sets of TRV voltage capacitors on four circuitbreakers at Vincent 500kV Substation;. | 8 MW 66kV | WDT1096TOC | Yes | Yes | TBD | Engineering & Design | 2023-03-01 | Generation Interconnection
18.65 | RE Garland | Kern County | Interconnect a 200 MW Solar PV Generating Facility to SCE's Whirlwind 220kV Substation via the ; shared Desert Star-Whirlwind 220kV gentie line. Install telecommunications facilities to support line protection and SPS; install RTU at the Generating Facility; expand Whirlwind AA Bank SPS; expand Northern Area 500kV SPS. | 200 MW 220kV | TOT672 | Yes | Yes | Exempt | Construction Operational | 4/1/2016 In Service | Generation Interconnection
18.66 | Blythe Mesa Solar | Riverside County | Interconnect a 224 MW Solar PV Generating Facility to SCE's Colorado River 220kV Substation; terminate the Blythe Mesa 220kV gentie line in a new 220kV line position at Colorado River Substation; install special protection system and telecommunications to support line protection and the special protection system; install RTU at the Generating Facility; install RTUs at Red Bluff substation; expand the RTU at Colorado River Substation. | 224 MW 220kV | TOT446 | Yes | Yes | TBD | Engineering & Design | 2017-11-01 | Generation Interconnection
18.67 | Sorrel I Solar | San Bernardino County | Interconnect a 200 MW Solar Photovoltaic Generating Facility to SCE's Calcite 220kV Substation; terminate the Calcite-Sorrel 220kV gentie line in a new line 220kV position at Calcite Substation; install telecommunications facilities to support line protection and SPS; install RTU at the Generating Facility and expand RTU at Calcite Substation; expand the Calcite SPS (loss of Lugo-Pisgah 220kV transmission line) to include the Sorrel I Solar project; expand the HDPP SPS (loss of Lugo 500/220kV transformer banks) to include the Sorrel Solar project. | 200 MW 220kV | TOT640 | Yes | Yes | TBD | Engineering & Design | 2021-03-01 | Generation Interconnection
18.68 | Ord Mountain | San Bernardino County | Interconnect a 60 MW Solar Photovoltaic Generating Facility to SCE's Calcite 220kV Substation; terminate the Calcite-Ord Mountain 220kV gentie line in a new line 220kV position at Calcite Substation; install telecommunications facilities to support line protection and SPS; install RTU at the Generating Facility and expand RTU at Calcite Substation; expand the Calcite SPS to include the Ord Mountain project; expand the HDPP SPS to include the Ord Mountain project. | 60 MW 220kV | TOT438 | Yes | Yes | TBD | Engineering & Design | 2020-08-01 | Generation Interconnection
18.69 | SP Blythe 1 | Riverside County | Interconnect a 221 MW Solar PV Generating Facility to SCE's Colorado River 220kV Substation; terminate the SP Blythe 220kV gentie line in a new 220kV line position at Colorado River Substation; install special protection system and telecommunications to support line protection and the special protection system; install RTU at the Generating Facility; expand the RTU at Colorado River Substation; replace four (4) 500kV circuit breakers at Vincent Substation and perform ground grid analysis. | 221 MW 220kV | TOT528 | Yes | Yes | TBD | Engineering & Design | 2018-09-01 | Generation Interconnection
18.7 | Gaskell West | Kern County | Interconnect a 131 MW Solar PV and 125 MW Battery Storage Generating Facility to SCE's Whirlwind 220kV Substation via a shared gentie line and shared interconnection facilities already constructed and placed in service (shared with CAISO Q#746); total MW output from the Generating Facility is limited to 128 MW. Install telecommunications facilities to support the SPS; install RTU at the Generating Facility; add points to existing RTU at Whirlwind Substation; expand Whirlwind AA Bank SPS; expand Northern Area 500kV SPS; upgrade 220kV circuit breakers at Vista Substation and perform ground grid study. | 128 MW 220kV | TOT727 | Yes | Yes | TBD | Engineering & Design | 2018-07-01 | Generation Interconnection
Report Applicability: Generation Projects which have executed an interconnection agreement, require Network Upgrades on the ISO Grid, and are not yet in serivce.
Notes:
(1) Reflects the construction status of the SCE facilities.
(2) Date reflects the estimated date as provided for in the applicable interconnection agreement (including any amendments thereto), unless otherwise updated by SCE's Major Project Organization (MPO).
(3) Costs are interconnection study level estimates (i.e., Facilities Study or Phase II Study) as provided in the initial interconnection agreement, or subsequent amendment if applicable, and do not reflect final engineering.
(4) Unless otherwise noted, financing of Network Upgrades is initially provided by the generator prior to construction, and refunded to the generator after its project has achieved commercial operation in accordance with FERC Order 2003.