PACIFIC GAS AND ELECTRIC COMPANY

2018 ANNUAL ELECTRIC RELIABILITY REPORT

(Per Decision16-01-008)

July 15, 2019

Table of Contents

Executive Summary	6

How PG&E Measures Reliability	8

Introduction	10

1.	System Indices for the Last Ten Years	12

a.	System Indices (2009-2018)	12

i.	Distribution System Indices	13

ii.	Transmission System Indices	13

b.	Separate System Charts of SAIDI, SAIFI, MAIFI, and CAIDI for the past 10 years with linear trend line (MED Excluded)	14

i.	SAIDI Performance Results (MED Excluded)	14

ii.	SAIFI Performance Results (MED Excluded)	16

iii.	MAIFI Performance Results (MED Excluded)	18

iv.	CAIDI Performance Results (MED Excluded)	19

2.	Division Reliability Indices for the past 10 years including and excluding MED	21

a.	Division Reliability Indices for the past 10 years excluding ISO and planned outages and including Major Event Days	21

b.	Division Reliability Indices for the past 10 years excluding planned outages, ISO outages and Major Event Days	26

c.	Charts for Division Reliability Indices for the past 10 years	31

i.	Charts for Division Reliability Indices for the past 10 years with linear trend line excluding ISO and planned outages and including MED	31

1.	AIDI Performance Results (MED Included)	31

2.	AIFI Performance Results (MED Included)	41

3.	MAIFI Performance Results (MED Included)	51

4.	CAIDI Performance Results (MED Included)	61

ii.	Charts for Division Reliability Indices for the past 10 years with linear trend line excluding ISO, planned outages and MED	71

1.	AIDI Performance Results (MED Excluded)	71

2.	AIFI Performance Results (MED Excluded)	81

3.	MAIFI Performance Results (MED Excluded)	91

4.	CAIDI Performance Results (MED Excluded)	101

d.	Division and System Reliability Indices Performance Variances (Five-Year Average)	111

i.	System and Division Performance Assessment	118

1.	System Performance Assessment	118

2.	Central Coast Division Performance Assessment	119

3.	De Anza Division Performance Assessment	122

4.	Diablo Division Performance Assessment	123

5.	East Bay Division Performance Assessment	124

6.	Humboldt Division Performance Assessment	125

7.	Kern Division Performance Assessment	126

8.	Los Padres Division Performance Assessment	127

9.	North Valley Division Performance Assessment	129

10.	Sacramento Division Performance Assessment	133

11.	San Francisco Division Performance Assessment	135

12.	San Jose Division Performance Assessment	136

13.	Sierra Division Performance Assessment	139

14.	Sonoma Division Performance Assessment	140

15.	Stockton Division Performance Assessment	141

16.	Yosemite Division Performance Assessment	143

ii.	2018 Excludable Major Event Day (MED) CAIDI Performance	145

1.	March 16, 2018 Major Event Day	146

1.1	Fresno CAIDI Assessment	146

1.2	Los Padres CAIDI Assessment	147

1.2	San Jose CAIDI Assessment	148

1.3	Stockton CAIDI Assessment	148

2.	July 28, 2018 Major Event Day	149

2.1	San Jose CAIDI Assessment	150

2.2	Stockton Division CAIDI Assessment	151

2.3	Yosemite Division CAIDI Assessment	152

3.	October 14, 2018 Major Event Day	152

3.1	System CAIDI Assessment	153

3.2	East Bay Division CAIDI Assessment	155

3.3	Fresno Division CAIDI Assessment	155

3.4	Humboldt Division CAIDI Assessment	156

3.5	Mission Division CAIDI Assessment	157

3.6	North Bay Division CAIDI Assessment	157

3.7	North Valley Division CAIDI Assessment	158

3.8	Sierra Division CAIDI Assessment	159

3.9	Stockton Division CAIDI Assessment	160

4.	November 8, 2018 Major Event Day	161

4.1	System CAIDI Assessment	162

4.2	Kern Division CAIDI Assessment	162

4.3	North Valley Division CAIDI Assessment	163

4.4	San Francisco Division CAIDI Assessment	164

5.	November 21, 2018 Major Event Day	165

5.1	Sacramento Division CAIDI Assessment	166

5.2	Stockton Division CAIDI Assessment	167

6.	November 29, 2018 Major Event Day	168

6.1	Diablo CAIDI Assessment	169

6.2	Mission CAIDI Assessment	169

6.3	Sacramento CAIDI Assessment	170

3. System and Division Indices Based on IEEE 1366 for the past 10 years including Planned Outages and including and excluding MED	171

a.	System and Division Indices Based on IEEE 1366 for the past ten years including Planned Outages and including MED, and excluding ISO Outages	172

b.	System and Division Indices Based on IEEE 1366 for the past 10 years including Planned Outages and excluding ISO, and MED	177

c.	Charts for System and Division Indices Based on IEEE 1366 for the past 10 years including Planned Outages and including and excluding MED	182

i.	Charts for System and Division Reliability Indices based on IEEE 1366 for the past 10 years with linear trend line, and including planned outages and excluding ISO, and MED	182

1.	SAIDI Performance Results (MED Excluded)	182

2.	SAIFI Performance Results (MED Excluded)	192

3.	MAIFI Performance Results (MED Excluded)	202

4.	CAIDI Performance Results (MED Excluded)	212

ii.	Charts for System and Division Reliability Indices based on IEEE 1366 for the past 10 years including planned outages and including MED	222

1.	SAIDI Performance Results (MED Included)	222

2.	SAIFI Performance Results (MED Included)	232

3.	MAIFI Performance Results (MED Included)	242

4.	CAIDI Performance Results (MED Included)	252

d.	The number of planned outages, date, and location of planned outages in each division on an annual basis.	262

4.	Service Territory Map	263

5.	Top 1% of Worst Performing Circuits (WPC) excluding Major Event Day (MED)	264

6.	Top 10 major unplanned power outage events of 2018	284

7.	Summary List of Major Event Day (MED) per IEEE 1366	285

7.1	Major Event Day (MED) Discussions:	286

March 16, 2018 Major Event Day	286

July 28, 2018 Major Event Day	287

October 14, 2018 Major Event Day	288

November 8, 2018 Major Event Day	289

November 21 Major Event Day	290

November 29 Major Event Day	291

8.	Historical Ten Largest Unplanned Outage Events for 2008-2017	292

9.	The Number of Customer Inquiries on Reliability Data and the Number of Days per Response	302

10.	Appendix A – Definitions, Acronyms & Abbreviations	303

# Executive Summary

PG&E’s electric service reliability performance in 2018 was challenged by several weather events, including severe winter storms, extreme summer heat waves and widespread Northern California wildfires.  As a result, PG&E’s reliability declined compared to 2017.

Electric utilities measure reliability in many ways: duration of customer outages, frequency of customer outages, average restoration time, counting only unplanned outages, counting planned outages, excluding unusual events such as major storms (typically referred to as Major Event Days or “MED”), including or excluding certain types of outages, among other distinctions.  This report explains the various different measures and includes the various metrics required by CPUC Decision 16-01-008.  For purposes of this Executive Summary, PG&E is focusing on metrics that include planned outages but exclude major event days.  These metrics are found in Section 3.  PG&E believes these metrics best reflect the typical customer’s experience and are common benchmark metrics across the electric utility industry.

Compared to 10 years ago, PG&E has reduced the average annual amount of time customers experienced a sustained outage from 158.0 minutes in 2009 to 126.3 minutes in 2018.  This is a 20 percent improvement. In the same period, PG&E also reduced the average number of times customers experienced a sustained outage in a given year from 1.173 to 1.079, an 8 percent improvement.  Table 1 below displays improvement in electric reliability from 2009 through 2018.

Table 1 – Combined Transmission and Distribution System Indices (2009-2018)

(Excludes MED and Independent System Operator (ISO) outages, and includes planned outages)

Chart A below shows the reduction in duration of the amount of time the average PG&E customer experienced a sustained outage or outages each year in graphical form and includes a linear trend line:

2009-2018 Transmission & Distribution System SAIDI Performance Results

Chart A

(Includes Planned Outages, Excludes Major Event Days and ISO Outages)

Not surprisingly, similar trends are mirrored at the division level. Reliability improved in most of PG&E’s 19 divisions in 2018 compared to 2009, as shown in the additional 10-year division charts included later in this report.

## How PG&E Measures Reliability

PG&E uses four metrics commonly utilized in the electric utility industry to measure reliability for both unplanned and planned outages: the System Average Interruption Duration Index (SAIDI), the System Average Interruption Frequency Index (SAIFI), the Momentary Average Interruption Frequency Index (MAIFI), and the Customer Average Interruption Duration Index (CAIDI).

- SAIDI is the amount of time the average PG&E customer experiences a sustained outage or outages (being without power for more than five minutes) in a given year. In 2018, PG&E's SAIDI was 126.3 minutes per customer and representing a 20 percent improvement over the last 10 years.

- SAIFI is the number of times the average PG&E customer experiences a sustained outage in a given year. In 2018, PG&E's SAIFI was 1.079 for the year and representing an 8 percent improvement over the last 10 years.

- MAIFI is the number of times the average customer is interrupted by momentary outages each year. Momentary outages are outages lasting 5 minutes or less. In 2018, PG&E's MAIFI was 1.479 which is higher than 2014 but an improvement from the 2017 MAIFI results.

- CAIDI is the average duration of sustained outages. It is determined by taking the total outage minutes for all customer outages (SAIDI) and dividing it by the total number of customer outages (SAIFI). In 2018, PG&E's CAIDI was 117.0 minutes and represents a 13 percent improvement over the past 10 years.

What follows is the 2018 Electric Reliability Report for Pacific Gas and Electric Company as required by Decision 16-01-008.  This report includes system reliability data based on the Institute of Electrical and Electronic Engineers (IEEE) Standard 1366 methodology, as required by D.16-01-008. The report includes very specific details, including reliability numbers for each of PG&E’s 19 divisions. It also includes a list of worst performing circuits in Section 5.

# Introduction

This is the 2018 Electric Reliability Report for Pacific Gas and Electric Company as required by Decision 16-01-008.  This report includes system reliability data based on the Institute of Electrical and Electronic Engineers (IEEE) Standard 1366 methodology.  This report consists of the following:

| Section | Description |
| --- | --- |
| 1. | System Indices for the Last 10 Years (2009-2018) |
| 2. | Division Reliability Indices (2009-2018) Including and Excluding Major Event Days (MED) |
| 3. | System and Division Indices Based on IEEE 1366 (2009-2018) Including Planned Outages and Including and Excluding MED |
| 4. | Service Territory Map including Divisions |
| 5. | Top 1% of Worst Performing Circuits (WPC) excluding MED |
| 6. | Top 10 Major Unplanned Power Outage Events in 2018 |
| 7. | Summary List of MED per IEEE 1366 |
| 8. | Historical Ten Largest Unplanned Outage Events (2009-2018) |
| 9. | The Number of Customer Inquiries on Reliability Data and the Number of Days per Response |
| 10. | Appendix A – Definitions, Acronyms and Abbreviations |

As noted in previous reports, PG&E implemented a new outage reporting system that included the data conversion of its legacy (DART/OUTAGE) database.  This new system consists of two main components that are typically referred to as PG&E’s Integrated Logging and Information System (ILIS) and its Operations Database (ODB), also called ILIS-ODB for short.  ILIS models the actual electric switching operations reported during the circuit restoration process (which is useful for determining accurate customer outage minutes for calculating SAIDI and CAIDI).  PG&E maintains account specific information for customers affected by outages that are recorded and stored in PG&E’s ODB.  This system tracks outages at various levels (generation, transmission, substation, primary distribution, and individual transformers) and the most current outage data was used to compile the information contained in this report.

Distribution operators log outage information in PG&E’s ILIS tool, which uses minutes as the smallest time increment to record the outage start, switching operations, and outage end times.  Smart Meters measure outage duration in seconds and are used to automatically report momentary outages beyond non-SCADA auto-reclosing devices.  Momentary outages for SCADA related and other events are logged by distribution operators using the ILIS tool, which does not have the benefit of measuring the outage duration in seconds.  Consequently, and although infrequent, it is possible that an outage duration is recorded as 5 minutes when the actual outage duration was up to 5 minutes and 59 seconds.  In 2015, PG&E updated its reporting tools and process to help minimize this occurrence and allow the operator in these situations to log this event as a 6-minute sustained outage.

We have added a list of Definitions, Acronyms and Abbreviations at the end as Appendix A to help the reader who is not familiar with the jargon used in reliability reporting.

# System Indices for the Last Ten Years

## System Indices (2009-2018)

Table 2 lists the required SAIDI, SAIFI, MAIFI, and CAIDI with MED Included and Excluded as directed in Appendix B of D.16-01-008:

Table 2 – Combine Transmission and Distribution System Indices (2009-2018)

(Excludes planned and ISO outages)

Note: Includes Generation, Transmission, Substation, and Distribution related outages

### Distribution System Indices

Table 3 – Distribution System Indices (2009-2018)

(Excludes planned outages, transmission, substation, and generation related outages)

Note: PG&E defines its distribution system as line voltage less than 60 kilovolts (KV)

The MAIFI information is not included in Table 3 and Table 4 since non-SCADA automatic recording devices (EON or Smart Meters) do not distinguish between transmission system outages or distribution system outages.

### Transmission System Indices

Table 4 – Transmission System Indices (2009-2018)

(Excludes planned outages, distribution, and generation related outages)

(Includes substation outages)

Note: PG&E defines its transmission system as line voltage 60 kilovolts (KV) and above

## Separate System Charts of SAIDI, SAIFI, MAIFI, and CAIDI for the past 10 years with linear trend line (MED Excluded)

### SAIDI Performance Results (MED Excluded)

Chart 1: Transmission & Distribution System SAIDI Indices

Chart 2: Distribution System SAIDI Indices

Chart 3: Transmission System SAIDI Indices

(Includes substation outages)

### SAIFI Performance Results (MED Excluded)

Chart 4: Transmission & Distribution System SAIFI Indices

Chart 5: Distribution System SAIFI Indices

Chart 6: Transmission System SAIFI Indices

(Includes substation outages)

### MAIFI Performance Results (MED Excluded)

Chart 7: Transmission & Distribution System MAIFI Indices

### CAIDI Performance Results (MED Excluded)

Chart 8: Transmission & Distribution System CAIDI Indices

Chart 9: Distribution System CAIDI Indices

Chart 10: Transmission System CAIDI Indices

(Includes substation outages)

# Division Reliability Indices for the past 10 years including and excluding MED

## Division Reliability Indices for the past 10 years excluding ISO and planned outages and including Major Event Days

Table 5: Division Reliability Indices

## Division Reliability Indices for the past 10 years excluding planned outages, ISO outages and Major Event Days

Table 6: Division reliability Indices

## Charts for Division Reliability Indices for the past 10 years

### Charts for Division Reliability Indices for the past 10 years with linear trend line excluding ISO and planned outages and including MED

### AIDI Performance Results (MED Included)

Chart 11: Division Reliability - AIDI Indices

Chart 12: Division Reliability - AIDI Indices

Chart 13: Division Reliability - AIDI Indices

Chart 14: Division Reliability - AIDI Indices

Chart 15: Division Reliability - AIDI Indices

Chart 16: Division Reliability - AIDI Indices

Chart 17: Division Reliability - AIDI Indices

Chart 18: Division Reliability - AIDI Indices

Chart 19: Division Reliability - AIDI Indices

Chart 20: Division Reliability – AIDI Indices

Chart 21: Division Reliability - AIDI Indices

Chart 22: Division Reliability - AIDI Indices

Chart 23: Division Reliability - AIDI Indices

Chart 24: Division Reliability - AIDI Indices

Chart 25: Division Reliability - AIDI Indices

Chart 26: Division Reliability – AIDI Indices

Chart 27: Division Reliability – AIDI Indices

Chart 28: Division Reliability - AIDI Indices

Chart 29: Division Reliability - AIDI Indices

### AIFI Performance Results (MED Included)

Chart 30: Division Reliability - AIFI Indices

Chart 31: Division Reliability - AIFI Indices

Chart 32: Division Reliability - AIFI Indices

Chart 33: Division Reliability - AIFI Indices

Chart 34: Division Reliability - AIFI Indices

Chart 35: Division Reliability - AIFI Indices

Chart 36: Division Reliability - AIFI Indices

Chart 37: Division Reliability - AIFI Indices

Chart 38: Division Reliability - AIFI Indices

Chart 39: Division Reliability - AIFI Indices

Chart 40: Division Reliability - AIFI Indices

Chart 41: Division Reliability - AIFI Indices

Chart 42: Division Reliability - AIFI Indices

Chart 43: Division Reliability - AIFI Indices

Chart 44: Division Reliability - AIFI Indices

Chart 45: Division Reliability - AIFI Indices

Chart 46: Division Reliability - AIFI Indices

Chart 47: Division Reliability - AIFI Indices

Chart 48: Division Reliability - AIFI Indices

### MAIFI Performance Results (MED Included)

Chart 49: Division Reliability - MAIFI Indices

Chart 50: Division Reliability - MAIFI Indices

Chart 51: Division Reliability - MAIFI Indices

Chart 52: Division Reliability - MAIFI Indices

Chart 53: Division Reliability - MAIFI Indices

Chart 54: Division Reliability - MAIFI Indices

Chart 55: Division Reliability - MAIFI Indices

Chart 56: Division Reliability - MAIFI Indices

Chart 57: Division Reliability - MAIFI Indices

Chart 58: Division Reliability - MAIFI Indices

Chart 59: Division Reliability - MAIFI Indices

Chart 60: Division Reliability - MAIFI Indices

Chart 61: Division Reliability - MAIFI Indices

Chart 62: Division Reliability - MAIFI Indices

Chart 63: Division Reliability - MAIFI Indices

Chart 64: Division Reliability - MAIFI Indices

Chart 65: Division Reliability - MAIFI Indices

Chart 66: Division Reliability - MAIFI Indices

Chart 67: Division Reliability - MAIFI Indices

### CAIDI Performance Results (MED Included)

Chart 68: Division Reliability - CAIDI Indices

Chart 69: Division Reliability - CAIDI Indices

Chart 70: Division Reliability - CAIDI Indices

Chart 71: Division Reliability - CAIDI Indices

Chart 72: Division Reliability - CAIDI Indices

Chart 73: Division Reliability - CAIDI Indices

Chart 74: Division Reliability - CAIDI Indices

Chart 75: Division Reliability - CAIDI Indices

Chart 76: Division Reliability - CAIDI Indices

Chart 77: Division Reliability - CAIDI Indices

Chart 78: Division Reliability - CAIDI Indices

Chart 79: Division Reliability - CAIDI Indices

Chart 80: Division Reliability - CAIDI Indices

Chart 81: Division Reliability - CAIDI Indices

Chart 82: Division Reliability - CAIDI Indices

Chart 83: Division Reliability - CAIDI Indices

Chart 84: Division Reliability - CAIDI Indices

Chart 85: Division Reliability - CAIDI Indices

Chart 86: Division Reliability - CAIDI Indices

### Charts for Division Reliability Indices for the past 10 years with linear trend line excluding ISO, planned outages and MED

### AIDI Performance Results (MED Excluded)

Chart 87: Division Reliability - AIDI Indices

Chart 88: Division Reliability - AIDI Indices

Chart 89: Division Reliability - AIDI Indices

Chart 90: Division Reliability - AIDI Indices

Chart 91: Division Reliability - AIDI Indices

Chart 92: Division Reliability - AIDI Indices

Chart 93: Division Reliability - AIDI Indices

Chart 94: Division Reliability - AIDI Indices

Chart 95: Division Reliability - AIDI Indices

Chart 96: Division Reliability - AIDI Indices

Chart 97: Division Reliability - AIDI Indices

Chart 98: Division Reliability - AIDI Indices

Chart 99: Division Reliability - AIDI Indices

Chart 100: Division Reliability - AIDI Indices

Chart 101: Division Reliability - AIDI Indices

Chart 102: Division Reliability - AIDI Indices

Chart 103: Division Reliability - AIDI Indices

Chart 104: Division Reliability - AIDI Indices

Chart 105: Division Reliability - AIDI Indices

### AIFI Performance Results (MED Excluded)

Chart 106: Division Reliability - AIFI Indices

Chart 107: Division Reliability - AIFI Indices

Chart 108: Division Reliability - AIFI Indices

Chart 109: Division Reliability - AIFI Indices

Chart 110: Division Reliability - AIFI Indices

Chart 111: Division Reliability - AIFI Indices

Chart 112: Division Reliability - AIFI Indices

Chart 113: Division Reliability - AIFI Indices

Chart 114: Division Reliability - AIFI Indices

Chart 115: Division Reliability - AIFI Indices

Chart 116: Division Reliability - AIFI Indices

Chart 117: Division Reliability - AIFI Indices

Chart 118: Division Reliability - AIFI Indices

Chart 119: Division Reliability - AIFI Indices

Chart 120: Division Reliability - AIFI Indices

Chart 121: Division Reliability - AIFI Indices

Chart 122: Division Reliability - AIFI Indices

Chart 123: Division Reliability - AIFI Indices

Chart 124: Division Reliability - AIFI Indices

### MAIFI Performance Results (MED Excluded)

Chart 125: Division Reliability - MAIFI Indices

Chart 126: Division Reliability - MAIFI Indices

Chart 127: Division Reliability - MAIFI Indices

Chart 128: Division Reliability - MAIFI Indices

Chart 129: Division Reliability - MAIFI Indices

Chart 130: Division Reliability - MAIFI Indices

Chart 131: Division Reliability - MAIFI Indices

Chart 132: Division Reliability - MAIFI Indices

Chart 133: Division Reliability - MAIFI Indices

Chart 134: Division Reliability - MAIFI Indices

Chart 135: Division Reliability - MAIFI Indices

Chart 136: Division Reliability - MAIFI Indices

Chart 137: Division Reliability - MAIFI Indices

Chart 138: Division Reliability - MAIFI Indices

Chart 139: Division Reliability - MAIFI Indices

Chart 140: Division Reliability - MAIFI Indices

Chart 141: Division Reliability - MAIFI Indices

Chart 142: Division Reliability - MAIFI Indices

Chart 143: Division Reliability - MAIFI Indices

### CAIDI Performance Results (MED Excluded)

Chart 144: Division Reliability - CAIDI Indices

Chart 145: Division Reliability - CAIDI Indices

Chart 146: Division Reliability - CAIDI Indices

Chart 147: Division Reliability - CAIDI Indices

Chart 148: Division Reliability - CAIDI Indices

Chart 149: Division Reliability - CAIDI Indices

Chart 150: Division Reliability - CAIDI Indices

Chart 151: Division Reliability - CAIDI Indices

Chart 152: Division Reliability - CAIDI Indices

Chart 153: Division Reliability - CAIDI Indices

Chart 154: Division Reliability - CAIDI Indices

Chart 155: Division Reliability - CAIDI Indices

Chart 156: Division Reliability - CAIDI Indices

Chart 157: Division Reliability - CAIDI Indices

Chart 158: Division Reliability - CAIDI Indices

Chart 159: Division Reliability - CAIDI Indices

Chart 160: Division Reliability - CAIDI Indices

Chart 161: Division Reliability - CAIDI Indices

Chart 162: Division Reliability - CAIDI Indices

## Division and System Reliability Indices Performance Variances (Five-Year Average)

This section contains additional division reliability information, as required by Decision 04-10-034, and Decision 16-01-008, Appendix B, footnote 6. This section explains threshold variations (unplanned outages only) in division and/or system reliability indices relative to the prior five-year averages (excluding major events, as defined per the IEEE 1366 methodology). This section also highlights the large outage events in each division that exceeded the reporting threshold.

Table 7 summarizes the 2018 division indices that meet the reporting requirement thresholds of 10 percent or more for the division, and 5 percent or more at the system level worse than the five year rolling average of reliability performance per D. 04-10-034.  An “X” indicates that the 2018 Division and system index exceeded the 10 percent and 5 percent threshold, respectively, and is thus discussed in detail in this section.

Table 7 – 2018 Indices excluding Major Events

(Meeting the Reporting Requirement Thresholds)

Table 8:  Division and System Reliability Indices Performance Variances (Excluding MED)

Division Reliability Indices

2013-2018

(Excluding MED)

Division Reliability Indices

2013-2018

(Excluding MED)

Division Reliability Indices

2013-2018

(Excluding MED)

Division Reliability Indices

2013-2018

(Excluding MED)

## System and Division Performance Assessment

### System Performance Assessment

Table 9: System Performance

System SAIDI Performance

The system’s 2018 SAIDI performance of 99.6 was 7.9 customer-minutes (or 8.6%) higher than the previous 5-year average of 91.7 as shown in the table above and illustrated in the figure below.

Chart 163 – System SAIDI Performance

The higher than average 2018 system SAIDI was attributed to the following:

- The March 1st and 2nd storm event contributed 3.0 customer-minutes to the system’s SAIDI.

- The December 31st storm event contributed 1.2 customer-minutes to the system’s SAIDI.

System SAIFI Performance

The system’s 2018 SAIFI performance of 0.959 was 0.068 customer-interruptions (or 7.6%) higher than the previous 5-year average of 0.891 as shown in the table above and illustrated in the figure below.

Chart 164 – System SAIFI Performance

The higher than average 2018 system SAIFI was attributed to the following:

- The March 1st and 2nd storm brought heavy rain and snow throughout the system and contributed 0.019 customer-interruptions to the system SAIFI.

- The December 31st storm brought strong winds and rain across the system and contributed 0.010 customer-interruptions to the system’s SAIFI.

### 2.	Central Coast Division Performance Assessment

Central Coast Division Performance

Table 10: Central Coast Performance

Central Coast Division SAIDI Performance

Central Coast Division’s 2018 SAIDI performance of 162.4 minutes was 31.2 customer-minutes (or 23.8%) higher than the previous 5-year average of 131.2 as shown in the table above and illustrated in the figure below.

Chart 165 – Central Coast Division SAIDI Performance

The higher than average 2018 Central Coast division SAIDI was attributed to the following:

- The March 20-22 storm event brought strong winds and rain through the area and contributed 7.0 customer-minutes to the division’s SAIDI.

- Several strong December storms impacted the divisions performance; those on the 16th, 17th, 25th and 31st.   These storms contributed 12.6 customer-minutes to the division’s SAIDI.

Central Coast Division SAIFI Performance

Central Coast Division’s 2018 SAIFI performance of 1.447 was 0.249 customer-interruptions (or 20.8%) higher than the previous 5-year average of 1.198 as shown in the table above and illustrated in the figure below.

Chart 166 – Central Coast Division SAIFI Performance

The higher than average 2018 Central Coast SAIFI was attributed to the following:

- The March 1st storm brought heavy rains into the area and contributed 0.045 customer-interruptions to the division’s SAIFI.

- The storm event of March 20th-22nd brought heavy rains into the area and contributed 0.032 customer-interruptions to the division’s SAIFI.

- Several strong December storms impacted the divisions performance; those on the 16th, 17th, 25th and 31st.   These storms contributed 0.089 customer-minutes to the division’s SAIFI.

Central Coast Division MAIFI Performance

Central Coast Division’s 2018 MAIFI performance of 2.480 was 0.292 customer-interruptions (or 13.3%) higher than the previous 5-year average of 2.188 as shown in the table above and illustrated in the figure below.

Chart 167 – Central Coast Division MAIFI Performance

The higher than average 2018 Central Coast MAIFI was attributed to the following:

- The division experienced several momentary outages during the March 20th-22nd storm event.  These outages contributed 0.070 customer-interruptions to the division’s MAIFI.

- Several momentary outages were experienced during the various December storms, particularly those on the 16th, 17th, 25th and 31st.  These outages contributed 0.147 customer-interruptions to the division’s MAIFI.

### De Anza Division Performance Assessment

De Anza Division Performance

Table 11: De Anza Division Performance

De Anza Division MAIFI Performance

De Anza Division’s 2018 MAIFI performance of 1.528 was 0.287 (or 23.1%) customer-interruptions higher than the previous 5-year average of 1.241 as shown in the table above and illustrated in the figure below.

Chart 168 – De Anza Division MAIFI Performance

The higher than average 2018 De Anza Division MAIFI was attributed to the following:

- On April 13th, a momentary outage at Britton Substation of “unknown cause” contributed 0.088 customer-interruptions to the division’s MAIFI.

- On May 21st, two momentary events caused by a breaker malfunction impacted El Patio Substation.  These events contributed 0.087 customer-interruptions to the division’s MAIFI.

- The March 22nd storm event produced several momentary outages that contributed 0.019 customer-interruptions to the division’s MAIFI.

### Diablo Division Performance Assessment

Diablo Division Performance

Table 12: Diablo Division Performance

Diablo Division MAIFI Performance

Diablo Division’s 2018 MAIFI performance of 1.846 was 0.332 customer-interruptions (or 21.9%) higher than the previous 5-year average of 1.514 as shown in the table above and illustrated in the figure below.

Chart 169 – Diablo Division MAIFI Performance

The higher than average 2018 Diablo Division MAIFI was attributed to the following:

- On July 8th, a failed bus-tie switch at Tidewater substation produced momentary outages to the Tidewater 2106 and 2110 circuits contributed 0.083 customer-interruptions to the division’s MAIFI.

- On October 17th, birds caused momentary outages on the Willow Pass 2102 prior to resulting in a sustained outage.  These momentary outages contributed 0.116 customer-interruptions to the division’s MAIFI.

### East Bay Division Performance Assessment

East Bay Division Performance

Table 13: East Bay Division Performance

East Bay Division SAIDI Performance

East Bay Division’s 2018 SAIDI performance of 78.8 was 9.2 customer-minutes (or 13.3%) higher than the previous 5-year average of 69.6 as shown in the table above and illustrated in the figure below.

Chart 170 – East Bay Division SAIDI Performance

The higher than average 2018 SAIDI performance was due to the following:

- The December 24th storm event brought strong winds and rain causing several outages that contributed 4.7 customer-minutes to the division’s SAIDI performance.

### Humboldt Division Performance Assessment

Humboldt Division Performance

Table 14: Humboldt Division Performance

Humboldt Division SAIFI Performance

Humboldt Division’s 2018 SAIFI performance of 1.734 is 0.364 customer-interruptions (or 26.5%) higher than the previous 5-year average of 1.734 as shown in the table above and illustrated below.

Chart 171 – Humboldt Division SAIFI Performance

The higher than average 2018 SAIFI performance is due to the following outage events:

- Of the various December storm events, those of the 14th, 16th and 24th were the most impactful.  The storms contributed 0.115 customer-interruptions to the division’s SAIFI performance.

- The July 29th Mendocino wildfire contributed 0.190 customer-interruptions to the division’s SAIFI performance.

### Kern Division Performance Assessment

Kern Division Performance

Table 15: Kern Division Performance

Kern Division MAIFI Performance

Kern Division’s 2018 MAIFI performance of 1.901 customer-interruptions is 0.255 customer-interruptions (or 15.5%) higher than the previous 5-year average of 1.646 as shown in the table above and illustrated below.

Chart 172 – Kern Division MAIFI Performance

The higher than average 2018 MAIFI performance is due the January 9th storm event that contributed 0.142 customer-interruptions to the division’s MAIFI performance.

### Los Padres Division Performance Assessment

Los Padres Division Performance

Table 16: Los Padres Division Performance

Los Padres Division SAIDI Performance

Los Padres Division’s 2018 SAIDI performance of 130.5 was 35.9 customer-minutes (or 38.0%) higher than the previous 5-year average of 94.6 as shown in the table above and illustrated in the figure below.

Chart 173 – Los Padres Division SAIDI Performance

The higher than average 2018 Los Padres Division SAIDI was attributed to the following:

Storms:

- The storm events of January 4th, 8th, and 9th brought heavy rains that contributed 5.1 customer-minutes to the division’s SAIDI performance.

- The February 26th storm contributed 3.4 customer-minutes to the division’s SAIDI performance.

- The March 1st and 22nd storms combined for 5.3 customer-minutes contribution to the division’s SAIDI performance.

Other:

- On July 14th a car struck a transmission pole causing an outage to the Purisima Substation.  This outage contributed 3.1 customer-minutes to the division’s SAIDI performance.

- On October 18th a failed transmission switch caused an outage to the Santa Ynez Substation.  This outage contributed 8.9 customer-minutes to the division’s SAIDI.

- On December 18th a failed jumper on the Oceano 1105 circuit contributed 4.6 customer-minutes to the division’s SAIDI performance.

Los Padres Division SAIFI Performance

Los Padres Division’s 2018 SAIFI performance of 1.195 was 0.285 customer-interruptions (or 31.4%) higher than the previous 5-year average of 0.909 as shown in the table above and illustrated in the figure below.

Chart 174 – Los Padres Division SAIFI Performance

The higher than average 2018 Los Padres Division SAIFI was attributed to the following:

Storms:

- The storm events of January 4th, 8th, and 9th brought heavy rains that contributed 0.040 customer-interruptions to the division’s SAIFI performance.

- The February 26th storm contributed 0.027 customer-interruptions to the division’s SAIFI performance.

- The March 1st and 22nd storms combined for 0.026 customer-interruptions contribution to the division’s SAIFI performance.

Other:

- On July 14th a car struck a transmission pole causing an outage to the Purisima Substation.  This outage contributed 0.015 customer-interruptions to the division’s SAIFI performance.

- On October 18th a failed transmission switch caused an outage to the Santa Ynez Substation.  This outage contributed 0.067 customer-interruptions to the division’s SAIFI.

- On December 18th a failed jumper on the Oceano 1105 circuit contributed 0.031 customer-interruptions to the division’s SAIFI performance.

### North Valley Division Performance Assessment

North Valley Division Performance

Table 17: North Valley Division Performance

North Valley Division SAIDI Performance

North Valley Division’s 2018 SAIDI performance of 187.3 was 63.0 customer-minutes (or 50.7%) higher than the previous 5-year average of 124.3 as shown in the table above and illustrated in the figure below.

Chart 175 – North Valley Division SAIDI Performance

The higher than average 2018 North Valley Division SAIDI was attributed to the following outage events:

Storms:

- The February 19th and 26th storm events brought heavy rain and wind into the area.  These storms contributed 5.8 customer-minutes to the division’s SAIDI performance.

- The March 1st storm brought heavy rain and wind into the area.  This storm contributed 9.4 customer-minutes to the division’s SAIDI performance.

- The March 15th and 22nd storm events brought heavy rain into the area.  These storms contributed 2.9 customer-minutes to the division’s SAIDI performance.

- The November 22nd storm brought heavy rain and wind into the area.  This storm contributed 3.7 customer-minutes to the division’s SAIDI performance.

- The December 14th and 17th storm events brought heavy rain into the area.  These storms contributed 5.7 customer-minutes to the division’s SAIDI performance.

Other:

- A grass fire on June 23rd in the Red Bluff area contributed 3.8 customer-minutes to the division’s SAIDI performance.

- On July 26th, the Carr fire contributed 12.3 customer-minutes to the division SAIDI performance.

- On September 24th, an outage on the De Sabla-Centerville 60 kV line caused by a bear climbing into the line contributed 11.8 customer-minutes to the division’s SAIDI performance.

North Valley Division SAIFI Performance

North Valley Division’s 2018 SAIFI performance of 1.366 was 0.355 customer-interruptions (or 35.1%) higher than the previous 5-year average of 1.011 as shown in the table above and illustrated in the figure below.

Chart 176 – North Valley Division SAIFI Performance

The higher than average 2018 North Valley Division SAIFI was attributed to the following outage events:

Storms:

- The February 19th and 26th storm events brought heavy rain and wind into the area.  These storms contributed 0.051 customer-interruptions to the division’s SAIFI performance.

- The March 1st storm brought heavy rain and wind into the area.  This storm contributed 0.028 customer-interruptions to the division’s SAIFI performance.

- The March 15th and 22nd storm events brought heavy rain into the area.  These storms contributed 0.018 customer-interruptions to the division’s SAIFI performance.

- The November 22nd storm brought heavy rain and wind into the area.  This storm contributed 0.008 customer-interruptions to the division’s SAIFI performance.

- The December 14th and 17th storm events brought heavy rain into the area.  These storms contributed 0.008 customer-interruptions to the division’s SAIFI performance.

Other:

- A grass fire on June 23rd in the Red Bluff area contributed 0.060 customer-interruptions to the division’s SAIFI performance.

- On July 26th, the Carr fire contributed 0.024 customer-interruptions to the division SAIFI performance.

- On July 18th the transmission line serving Corning Substation was de-energized at the request of the fire department due to a structure fire.  This outage contributed 0.044 customer-interruptions to the division’s SAIFI performance.

- On September 24th, an outage on the De Sabla-Centerville 60 kV line caused by a bear climbing into the line contributed 0.022 customer-interruptions to the division’s SAIFI performance.

North Valley Division CAIDI Performance

North Valley Division’s 2018 CAIDI performance of 137.1 was 14.2 minutes (or 11.5%) higher than the previous 5-year average of 122.9 as shown in the table above and illustrated in the figure below.

Chart 177 – North Valley Division CAIDI Performance

The higher than average 2018 North Valley Division CAIDI was attributed to the following outage events:

Most impactful storm events to the CAIDI performance:

- The February 19th and 26th.

- The March 1st storm.

- The March 15th and 22nd storm events.

- The November 22nd storm.

- The December 14th and 17th storm events.

These outages combined contributed 9.7 minutes to the division’s CAIDI performance.

Other:

- On July 18th the transmission line serving Corning Substation was de-energized at the request of the fire department due to a structure fire.  This outage contributed an additional 7.2 minutes to the division’s CAIDI performance.

### Sacramento Division Performance Assessment

Sacramento Division Performance

Table 18: Sacramento Division Performance

Sacramento Division SAIFI Performance

Sacramento Division’s 2018 SAIFI performance of 1.021 was 0.110 customer-interruptions (or 12.0%) higher than the previous 5-year average of 0.911 as shown in the table above and illustrated in the figure below.

Chart 178 – Sacramento Division SAIFI Performance

The higher than average 2018 Sacramento Division SAIFI was attributed to the March 1st storm that brought heavy winds and rain into the area.  This storm contributed 0.024 customer-interruptions to the division’s SAIFI performance.

Sacramento Division MAIFI Performance

Sacramento Division’s 2018 MAIFI performance of 1.887 was 0.348 customer-interruptions (or 22.7%) higher than the previous 5-year average of 1.538 as shown in the table above and illustrated in the figure below.

Chart 179 – Sacramento Division MAIFI Performance

The higher than average 2018 Sacramento Division MAIFI was attributed to the following:

- On February 20th, a momentary outage of unknown cause was experienced on the Cortina #3 transmission line that contributed 0.023 customer-interruptions to the division’s MAIFI performance.

- On February 24th, a momentary outage of unknown cause was experienced on the Davis 1106 circuit that contributed 0.017 customer-interruptions to the division’s MAIFI performance.

- The storm event of January 4th caused several momentary outages that contributed 0.018 customer-interruptions to the division’s MAIFI performance.

- The storm event of March 1st caused several momentary outages that contributed 0.096 customer-interruptions to the division’s MAIFI performance.

- Many of the December storm events (December 22, 23, and 27-30) caused several momentary outages that contributed 0.080 customer-interruptions to the division’s MAIFI performance.

### San Francisco Division Performance Assessment

San Francisco Division Performance

Table 19: San Francisco Division Performance

San Francisco Division CAIDI Performance

San Francisco Division’s 2018 CAIDI performance of 93.0 was 14.2 minutes (or 18.0%) higher than the previous 5-year average of 78.8 as shown in the table above and illustrated in the figure below.

Chart 180 – San Francisco Division CAIDI Performance

The higher than average 2018 San Francisco Division CAIDI was attributed to the following:

- A failed jumper on the K-404 circuit and a failed underground switch on the A-1109 on February 13th.

- A failed underground cable on the Y-1102 circuit on April 7th.

- An outage caused by a metallic balloon on the E-1105 circuit on April 14th.

These four outages contributed 15.1 minutes.

### San Jose Division Performance Assessment

San Jose Division Performance

Table 20: San Jose Division Performance

San Jose Division SAIDI Performance

San Jose Division’s 2018 SAIDI performance of 85.0 was 9.7 customer-minutes (or 12.9%) higher than the previous 5-year average of 75.3 as shown in the table above and illustrated in the figure below.

Chart 181 – San Jose Division SAIDI Performance

The higher than average 2018 San Jose Division SAIDI was attributed to the December 31st storm event which contributed 5.2 customer-minutes to the division’s SAIDI performance.

San Jose Division SAIFI Performance

San Jose Division’s 2018 SAIFI performance of 0.858 was 0.102 customer-interruptions (or 13.5%) higher than the previous 5-year average of 0.756 as shown in the table above and illustrated in the figure below.

Chart 182 – San Jose Division SAIFI Performance

The higher than average 2018 San Jose Division SAIFI was attributed to the December 31st storm event which contributed 0.056 customer-interruptions to the division’s SAIFI performance.

San Jose Division MAIFI Performance

San Jose Division’s 2018 MAIFI performance of 1.494 was 0.407 customer-interruptions (or 37.4%) higher than the previous 5-year average of 1.087 as shown in the table above and illustrated in the figure below.

Chart 183 – San Jose Division MAIFI Performance

The higher than average 2018 San Jose Division MAIFI was attributed to the following:

- On February 6th, a failed overhead conductor on the Evergreen 2103 circuit caused a momentary outage prior to becoming a sustained outage.  This outage contributed 0.026 customer-interruptions to the division’s MAIFI.

- On February 27th, a momentary outage of unknown cause on the Piercy 2109 circuit contributed 0.025 customer-interruptions to the division’s MAIFI performance.

- On May 12th, two underground transformer failures on the Milpitas 2110 circuit produced momentary outages prior to becoming a sustained outage.  These outages contributed 0.016 customer-interruptions.  In addition, a momentary outage of unknown cause occurred on the McKee 1112 circuit and another momentary outage occurred on the Hicks 1113 due to a failed secondary wire prior to becoming a sustained outage.  These two outages contributed 0.012 customer-interruptions to the division’s MAIFI.

- On June 3rd, a failed underground switch on the Montague 2104 circuit produced a momentary outage prior to becoming a sustained outage contributing 0.012 customer interruptions.  In addition, a momentary outage of unknown cause on the Hicks 2111 contributed 0.043 customer-interruptions to the division’s MAIFI.

- On July 7th, momentary outages of unknown cause were experienced on the Mabury 1101 and 1105 circuits, the Edenvale 2107 and Almaden substations.  These outages contributed 0.062 customer-interruptions to the division’s MAIFI.

- On July 21st, a momentary outage was experienced on the Evergreen 2103 circuit (unknown cause) and another momentary outage on the Morgan Hill 2105 circuit due to birds prior to becoming a sustained outage.

- The following two momentary outages were experienced on August 2nd: (1) the San Jose B 1112 circuit due to a car-pole incident prior to becoming a sustained outage and (2) the Hicks 1111 circuit due to a failed substation switch prior to becoming a sustained outage.  The outages contributed 0.049 customer-interruptions to the division’s MAIFI.

- On December 20th, a momentary outage of unknown cause was experienced on the transmission line impacting Mabury substation. This momentary outage contributed 0.032 customer-interruptions to the division’s MAIFI.

### Sierra Division Performance Assessment

Sierra Division Performance

Table 21: Sierra Division Performance

Sierra Division SAIDI Performance

Sierra Division’s 2018 SAIDI performance of 152.9 was 22.5 customer-minutes (or 17.3%) higher than the previous 5-year average of 130.4 as shown in the table above and illustrated in the figure below.

Chart 184 – Sierra Division SAIDI Performance

The higher than average 2018 Sierra Division SAIDI was attributed to the March 2nd storm event that contributed 12.8 customer-minutes to the division’s SAIDI performance.

Sierra Division CAIDI Performance

Sierra Division’s 2018 CAIDI performance of 123.2 was 11.3 minutes (or 10.1%) higher than the previous 5-year average of 111.9 as shown in the table above and illustrated in the figure below.

Chart 185 – Sierra Division CAIDI Performance

The higher than average 2018 Sierra Division CAIDI was attributed to the March 2nd storm event that contributed 7.0 customer-minutes to the division’s CAIDI performance.

### Sonoma Division Performance Assessment

Sonoma Division Performance

Table 22: Sonoma Division Performance

Sonoma Division SAIFI Performance

Sonoma Division’s 2018 SAIFI performance of 0.956 was 0.137 customer-interruptions (or 16.7%) higher than the previous 5-year average of 0.819 as shown in the table above and illustrated in the figure below.

Chart 186 – Sonoma Division SAIFI Performance

The higher than average 2018 Sonoma Division SAIFI was attributed to a July 1st outage caused when a bird flew into a transmission switch impacting the Petaluma A and Petaluma C substations.  This outage contributed 0.085 customer-interruptions to the division’s SAIFI performance.

### Stockton Division Performance Assessment

Stockton Division Performance

Table 23: Stockton Division Performance

Stockton Division SAIDI Performance

Stockton Division’s 2018 SAIDI performance of 107.7 was 12.3 customer-minutes (or 12.8%) higher than the previous 5-year average of 95.4 as shown in the table above and illustrated in the figure below.

Chart 187 – Stockton Division SAIDI Performance

The higher than average 2018 Stockton Division SAIDI was attributed to the March 17th storm event that contributed 13.5 customer-minutes to the division’s SAIDI performance.

Stockton Division MAIFI Performance

Stockton Division’s 2018 MAIFI performance of 1.890 was 0.246 customer-interruptions (or 15.0%) higher than the previous 5-year average of 1.644 as shown in the table above and illustrated in the figure below.

Chart 188 – Stockton Division MAIFI Performance

The higher than average 2018 Stockton Division MAIFI was attributed to the March 22nd storm event that contributed 0.136 customer-interruptions to the division’s MAIFI performance.

### Yosemite Division Performance Assessment

Yosemite Division Performance

Table 24: Yosemite Division Performance

Yosemite Division SAIDI Performance

Yosemite Division’s 2018 SAIDI performance of 158.3 was 23.5 customer-minutes (or 17.4%) higher than the previous 5-year average of 134.8 as shown in the table above and illustrated in the figure below.

Chart 189 – Yosemite Division SAIDI Performance

The higher than average 2018 Yosemite Division SAIDI was attributed to the March 2nd storm event that contributed 16.8 customer-minutes to the division’s SAIDI performance.

Yosemite Division SAIFI Performance

Yosemite Division’s 2018 SAIFI performance of 1.355 was 0.174 customer-interruptions (or 14.7%) higher than the previous 5-year average of 1.181 as shown in the table above and illustrated in the figure below.

Chart 190 – Yosemite Division SAIFI Performance

The higher than average 2018 Yosemite Division SAIFI was attributed to the March 22nd storm event that contributed 0.064 customer-interruptions to the division’s SAIFI performance.

## 2018 Excludable Major Event Day (MED) CAIDI Performance

Excludable Major Event Days (MED) In 2018

This section contains PG&E’s report on weather related excludable major event days (MED) for each division in which CAIDI varied by 25 percent or more in the division benchmark, as required by Decision 04-10-034 and Decision 16-01-008, Appendix B, footnote 6.  Per D.04-10-034, the division benchmark is calculated from the rolling average of the prior 10 weather-related excludable major events.  PG&E is also required by D.04-10-034 to provide such a report for the system, where the system performance varies by more than 10 percent from the rolling average of the prior 10 weather-related system-wide excludable major event days, whichever yields more event days.

There were six weather-related Major Event Days in 2018.

Table 25 – Summary MED days

NOTE: May 17th was not a weather-related MED.

The first major event day of the year, March 16, 2018, involved a winter storm system that moved into PG&E’s service territory producing rain, gusty winds, and mountain snow at lower elevations.

Table 26 summarizes the system and division CAIDI performances during this event and the average of the prior ten weather related major events.

(March 16, 2018 vs. Prior 10 MED)

Table 26 – March 16, 2018 CAIDI Performance

### March 16, 2018 Major Event Day

### 1.1	Fresno CAIDI Assessment

Table 27 – Fresno Historical Performance

As indicated in Table 27, the Fresno Division CAIDI value of 308.1 minutes for the March 16th major event was 97.9% higher than the 155.7-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher division CAIDI value was a car pole incident on the Kingsburg 1111 circuit.  This outage contributed 204.6 minutes to the overall March 16th CAIDI performance.

### 1.2	Los Padres CAIDI Assessment

Table 28 – Los Padres Historical Performance

As indicated in Table 28, the Los Padres Division CAIDI value of 815.1 minutes for the March 16th major event was 82.1% higher than the 447.7-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher division CAIDI value was a car pole incident on the Mesa 1101 circuit.  This outage contributed 343.3 minutes to the overall March 16th CAIDI performance

### 1.2	San Jose CAIDI Assessment

Table 29 – San Jose Historical Performance

As indicated in Table 29, the San Jose Division CAIDI value of 680.0 minutes for the March 16th major event was 152.8% higher than the 269.0-minute average of the prior 10 weather-related excludable major events.

This was due to an outage of unknown cause on the Llagas 2107 circuit.

### 1.3	Stockton CAIDI Assessment

Table 30 – Stockton Historical Performance

As indicated in Table 30, the Stockton Division CAIDI value of 556.6 minutes for the March 16th major event was 229.4% higher than the 169.0-minute average of the prior 10 weather-related excludable major events.

The cause of the high CAIDI value was attributed to the low snow elevations which made roads inaccessible.

### July 28, 2018 Major Event Day

The second major event was on July 28, 2018, which was driven by the Carr fire.

Table 31 summarizes the system and division CAIDI performances during this event and the average of the prior ten weather related major events.

(July 28, 2018 vs. Prior 10 MED)

Table 31 – July 28, 2018 CAIDI Performance

### 2.1	San Jose CAIDI Assessment

Table 32 – San Jose Historical Performance

As indicated in Table 32, the San Jose Division CAIDI value of 534.8 minutes for the July 28, 2018 major event day was 98.8% higher than the 269.0-minute average of the prior 10 weather-related excludable major events.

The higher CAIDI value was due to a car-pole incident on the Piercy 2110 circuit.  This outage contributed 457.8 minutes to the overall July 28, 2018 CAIDI performance.

### 2.2	Stockton Division CAIDI Assessment

Table 33 – Stockton Division Historical Performance

As indicated in Table 33, the Stockton Division CAIDI value of 838.9 minutes for the July 28, 2018 major event day was 396.5% higher than the 169.0-minute average of the prior 10 weather-related excludable major events.

The following three outages were the top contributing factors to the higher CAIDI value:

- Salt Springs 2101 circuit - due to a failed primary riser.

- Alpine 1101 circuit – due to the Salt Springs 2101 outage.

- Alpine 1102 circuit – due to the Salt Springs 2101 outage.

Note:  Salt Springs 2101 serves the two Alpine circuits via two step-down transformers.

These three outages contributed 661.0 minutes to the overall July 28, 2018 CAIDI performance.

### 2.3	Yosemite Division CAIDI Assessment

Table 34 – Yosemite Division Historical Performance

As indicated in Table 34, the Yosemite Division CAIDI value of 691.8 minutes for the July 28, 2018 major event day was 192.2% higher than the 236.7 minute-average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was an underground cable failure on the Riverbank 1715 circuit.  This outage contributed 525.8 minutes to the overall July 28, 2018 CAIDI performance.

### October 14, 2018 Major Event Day

The third major event was for October 14, 2018 caused by an offshore wind event across the northern two thirds of the territory that produced Extreme-Plus fire danger resulting in execution of the Power Safety Power Shut-off (PSPS) program.  Table 35 summarizes the system and division CAIDI performances during this event and the average of the prior ten weather related major events.

(October 14, 2018 vs. Prior 10 MED)

Table 35 – October 14, 2018 CAIDI Performance

### 3.1	System CAIDI Assessment

Table 36 – System Historical Performance

As indicated in Table 36, the system CAIDI value of 1,468.1 minutes for the October 14, 2018 major event day was 151.4% higher than the 584.1-minute average of the prior 10 weather-related excludable major events.

The following five outage events were the top contributing factors to the higher CAIDI value:

- Execution of PSPS in two-third of the service area.  Of the 164 outages experienced, 113 were PSPS related.

- Bangor 1101 circuit – due to an outage of unknown cause (the line was patrolled, and nothing was found).

- West Point 1102 circuit – due to a tree falling into the line.

- Pinegrove 1102 circuit – due to (1) a broken cross-arm and (2) a tree falling into the line.

These five outages contributed 1,020.5 minutes to the October 14, 2018 overall CAIDI performance.

### 3.2	East Bay Division CAIDI Assessment

Table 37 – East Bay Division Historical Performance

As indicated in Table 37, the East Bay Division CAIDI value of 562.1 minutes for the October 14, 2018 major event day was 107.9% higher than the 270.3-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was an underground cable failure on the Hollywood 401 circuit.  This outage contributed 514.8 minutes to the October 14, 2018 overall CAIDI performance.

### 3.3	Fresno Division CAIDI Assessment

Table 38 – Fresno Division Historical Performance

As indicated in Table 38, the Fresno Division CAIDI value of 471.8 minutes for the October 14, 2018 major event day was 203.1% higher than the 155.7-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was a car-pole incident on the McCall 1102 circuit.  This outage contributed 422.1 minutes to the October 14, 2018 overall CAIDI performance.

### 3.4	Humboldt Division CAIDI Assessment

Table 39 – Humboldt Division Historical Performance

As indicated in Table 39, the Humboldt Division CAIDI value of 1,341.4 minutes for the October 14, 2018 major event day was 101.1% higher than the 667.2-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was the execution of PSPS, which contributed 1,176.4 minutes to the October 14, 2018 overall CAIDI performance.

### 3.5	Mission Division CAIDI Assessment

Table 40 – Mission Division Historical Performance

As indicated in Table 40, the Mission Division CAIDI value of 292.4 minutes for the October 14, 2018 major event day was 43.5% higher than the 203.8-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was a tree that fell into the San Ramon 2108 circuit.  This outage contributed 192.4 minutes to the October 14, 2018 overall CAIDI performance.

### 3.6	North Bay Division CAIDI Assessment

Table 41 – North Bay Division Historical Performance

As indicated in Table 41, the North Bay Division CAIDI value of 1,618.6 minutes for the October 14, 2018 major event day was 30.5% higher than the 1,239.9-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was the execution of PSPS, which contributed 1,107.6 minutes to the October 14, 2018 overall CAIDI performance.

### 3.7	North Valley Division CAIDI Assessment

Table 42 – North Valley Division Historical Performance

As indicated in Table 42, the North Valley Division CAIDI value of 815.7 minutes for the October 14, 2018 major event day was 155.5% higher than the 319.3-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was an outage on the Bangor 1101 circuit of unknown cause (the line was patrolled, but nothing was found).  This outage contributed 653.2 minutes to the October 14, 2018 overall CAIDI performance.

### 3.8	Sierra Division CAIDI Assessment

Table 43 – Sierra Division Historical Performance

As indicated in Table 43, the Sierra Division CAIDI value of 1,450.8 minutes for the October 14, 2018 major event day was 185.9% higher than the 507.4-minute average of the prior 10 weather-related excludable major events.

The following were the top contributing factors to the higher CAIDI value:

- Execution of PSPS.  Of the 30 outages experienced, 21 were PSPS related.

- Mountain Quarries 2101 circuit – an outage of unknown cause (the line was patrolled, but nothing was found).

These outages contributed 1,271.9 minutes to the October 14, 2018 overall CAIDI performance.

### 3.9	Stockton Division CAIDI Assessment

Table 44 – Stockton Division Historical Performance

As indicated in Table 44, the Stockton Division CAIDI value of 2,178.8 minutes for the October 14, 2018 major event day was 1,189.4% higher than the 169.0-minute average of the prior 10 weather-related excludable major events.

The following outages were the top contributing factors to the higher CAIDI value:

- Execution of PSPS.  Of the 61 outages experienced, 55 were PSPS related.

- West Point 1102 circuit – due to (1) a tree falling into the line and (2) a broken cross-arm.

- Oleta 1101 circuit – due to two outages of unknown cause (the lines were patrolled, but nothing was found)

- Pine Grove 1102 circuit – due to (1) a broken cross-arm and (2) a tree falling into the line.

These outages contributed 2,178.8 minutes to the October 14, 2018 overall CAIDI performance.

### November 8, 2018 Major Event Day

The fourth major event was for November 8, 2018 caused by the Camp fire.  Table 45 summarizes the system and division CAIDI performances during this event and the average of the prior ten weather related major events.

(November 8, 2018 vs. Prior 10 MED)

Table 45 – November 8, 2018 CAIDI Performance

### 4.1	System CAIDI Assessment

Table 46 – System Historical Performance

As indicated in Table 46, the System CAIDI value of 12,188.2 minutes for the November 8, 2018 major event day was 1,986.8% higher than the 584.1-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was due to the Camp fire.

This wildfire outage contributed 1,1991.3 minutes to the November 8, 2018 overall CAIDI performance.

### 4.2	Kern Division CAIDI Assessment

Table 47 – Kern Division Historical Performance

As indicated in Table 47, the Kern Division CAIDI value of 291.1 minutes for the November 8, 2018 major event day was 73.6% higher than the 167.7-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was due to a failed overhead conductor on the Ganso 1103 circuit.  This outage contributed 105.9 minutes to the November 8, 2018 overall CAIDI performance.

### 4.3	North Valley Division CAIDI Assessment

Table 48 – North Valley Division Historical Performance

As indicated in Table 48, the North Valley Division CAIDI value of 21,991.5 minutes for the November 8, 2018 major event day was 6,788.47% higher than the 319.3-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was due to the Camp fire.

This wildfire outage event contributed 21,862.5 minutes to the November 8, 2018 overall CAIDI performance.

### 4.4	San Francisco Division CAIDI Assessment

Table 49 – San Francisco Division Historical Performance

As indicated in Table 49, the San Francisco Division CAIDI value of 316.0 minutes for the November 8, 2018 major event day was 247.8% higher than the 103.8-minute average of the prior 10 weather-related excludable major events.

The following two outages were the top contributing factors to the higher CAIDI value:

- Randolph 403 circuit – due to (1) a failed overhead conductor and (2) a tree going into the line.

These two outages contributed 361.0 minutes to the November 8, 2018 overall CAIDI performance.

### November 21, 2018 Major Event Day

The fifth major event was for November 21, 2018 caused by an early winter storm that brought heavy rain and gusty southerly winds through the service area.  Table 50 summarizes the system and division CAIDI performances during this event and the average of the prior ten weather related major events.

(November 21, 2018 vs. Prior 10 MED)

Table 50 – November 21, 2018 CAIDI Performance

### 5.1	Sacramento Division CAIDI Assessment

Table 51 – Sacramento Division Historical Performance

As indicated in Table 51, the Sacramento Division CAIDI value of 202.2 minutes for the November 21, 2018 major event day was 49.3% higher than the 135.4-minute average of the prior 10 weather-related excludable major events.

The following two outages were the top contributing factors to the higher CAIDI value:

- Dobbins 1105 circuit – due to a pole fire.

- Vacaville 1108 circuit – due to a broken pole.

These two outages contributed 91.2 minutes to the November 21, 2018 overall CAIDI performance.

### Stockton Division CAIDI Assessment

Table 52 – Stockton Division Historical Performance

As indicated in Table 52, the Stockton Division CAIDI value of 234.6 minutes for the November 21, 2018 major event day was 38.8% higher than the 169.0-minute average of the prior 10 weather-related excludable major events.

The following two outages were the top contributing factors to the higher CAIDI value:

- Ripon 1704 circuit – due to a pole fire.

- Middle River 1101 circuit – due to a bird.

These two outages contributed 118.6 minutes to the November 21, 2018 overall CAIDI performance.

### November 29, 2018 Major Event Day

The sixth major event was from November 29, 2018 caused by a dynamic winter storm system that brought heavy rain and strong southerly winds through the service area.  Table 53 summarizes the system and division CAIDI performances during this event and the average of the prior ten weather related major events.

(November 29, 2018 vs. Prior 10 MED)

Table 53 – November 29, 2018 CAIDI Performance

### 6.1	Diablo CAIDI Assessment

Table 54 – Diablo Division Historical Performance

As indicated in Table 54, the Diablo division CAIDI value of 298.1 minutes for the November 29, 2018 major event day was 36.6% higher than the 218.3-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was due to a failed elbow on the Lakewood 2110 circuit.  This outage contributed 111.2 minutes to the November 29, 2018 overall CAIDI performance.

### 6.2	Mission CAIDI Assessment

Table 55 – Mission Historical Performance

As indicated in Table 55, the Mission division CAIDI value of 474.5 minutes for the November 29, 2018 major event day was 132.9% higher than the 203.8-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was due to a failed underground cable on the Vineyard 2108 circuit.  This outage contributed 289.9 minutes to the November 29, 2018 overall CAIDI performance.

### 6.3	Sacramento CAIDI Assessment

Table 56 – Sacramento Historical Performance

As indicated in Table 56, the Sacramento division CAIDI value of 269.7 minutes for the November 29, 2018 major event day was 99.1% higher than the 135.4-minute average of the prior 10 weather-related excludable major events.

The top contributing factor to the higher CAIDI value was due to a malfunctioning line recloser on the Zamora 1105 circuit.  This outage contributed 106.5 minutes to the November 29, 2018 overall CAIDI performance.

# 3. System and Division Indices Based on IEEE 1366 for the past 10 years including Planned Outages and including and excluding MED

The seven-year trend (2009-2015) of continuous improved reliability did not continue in 2016-2018 in terms of the total duration of sustained outages per customer for the entire year (including planned outages but excluding major events). However, PG&E has reduced the total duration of power outages per customer from 158.0 minutes in 2009 to 126.3 minutes in 2018, a 20 percent improvement, as shown in Table 57 below.

Table 57: Combined Transmission and Distribution System Indices with Planned Outages

## System and Division Indices Based on IEEE 1366 for the past ten years including Planned Outages and including MED, and excluding ISO Outages

Table 58:

## System and Division Indices Based on IEEE 1366 for the past 10 years including Planned Outages and excluding ISO, and MED

Table 59:

## Charts for System and Division Indices Based on IEEE 1366 for the past 10 years including Planned Outages and including and excluding MED

### Charts for System and Division Reliability Indices based on IEEE 1366 for the past 10 years with linear trend line, and including planned outages and excluding ISO, and MED

### SAIDI Performance Results (MED Excluded)

Chart 191: Division Reliability – AIDI Indices

Chart 192: Division Reliability – AIDI Indices

Chart 193: Division Reliability – AIDI Indices

Chart 194: Division Reliability – AIDI Indices

Chart 195: Division Reliability – AIDI Indices

Chart 196: Division Reliability – AIDI Indices

Chart 197: Division Reliability – AIDI Indices

Chart 198: Division Reliability – AIDI Indices

Chart 199: Division Reliability – AIDI Indices

Chart 200: Division Reliability – AIDI Indices

Chart 201: Division Reliability – AIDI Indices

Chart 202: Division Reliability – AIDI Indices

Chart 203: Division Reliability – AIDI Indices

Chart 204: Division Reliability – AIDI Indices

Chart 205: Division Reliability – AIDI Indices

Chart 206: Division Reliability – AIDI Indices

Chart 207: Division Reliability – AIDI Indices

Chart 208: Division Reliability – AIDI Indices

Chart 209: Division Reliability – AIDI Indices

Chart 210: System Reliability – SAIDI Indices

### SAIFI Performance Results (MED Excluded)

Chart 211: Division Reliability – AIFI Indices

Chart 212: Division Reliability – AIFI Indices

Chart 213: Division Reliability – AIFI Indices

Chart 214: Division Reliability – AIFI Indices

Chart 215: Division Reliability – AIFI Indices

Chart 216: Division Reliability – AIFI Indices

Chart 217: Division Reliability – AIFI Indices

Chart 218: Division Reliability – AIFI Indices

Chart 219: Division Reliability – AIFI Indices

Chart 220: Division Reliability – AIFI Indices

Chart 221: Division Reliability – AIFI Indices

Chart 222: Division Reliability – AIFI Indices

Chart 223: Division Reliability – AIFI Indices

Chart 224: Division Reliability – AIFI Indices

Chart 225: Division Reliability – AIFI Indices

Chart 226: Division Reliability – AIFI Indices

Chart 227: Division Reliability – AIFI Indices

Chart 228: Division Reliability – AIFI Indices

Chart 229: Division Reliability – AIFI Indices

Chart 230: System Reliability – SAIFI Indices

### MAIFI Performance Results (MED Excluded)

Chart 231: Division Reliability – MAIFI Indices

Chart 232: Division Reliability – MAIFI Indices

Chart 233: Division Reliability – MAIFI Indices

Chart 234: Division Reliability – MAIFI Indices

Chart 235: Division Reliability – MAIFI Indices

Chart 236: Division Reliability – MAIFI Indices

Chart 237: Division Reliability – MAIFI Indices

Chart 238: Division Reliability – MAIFI Indices

Chart 239: Division Reliability – MAIFI Indices

Chart 240: Division Reliability – MAIFI Indices

Chart 241: Division Reliability – MAIFI Indices

Chart 242: Division Reliability – MAIFI Indices

Chart 243: Division Reliability – MAIFI Indices

Chart 244: Division Reliability – MAIFI Indices

Chart 245: Division Reliability – MAIFI Indices

Chart 246: Division Reliability – MAIFI Indices

Chart 247: Division Reliability – MAIFI Indices

Chart 248: Division Reliability – MAIFI Indices

Chart 249: Division Reliability – MAIFI Indices

Chart 250: Division Reliability – MAIFI Indices

### CAIDI Performance Results (MED Excluded)

Chart 251: Division Reliability – CAIDI Indices

Chart 252: Division Reliability – CAIDI Indices

Chart 253: Division Reliability – CAIDI Indices

Chart 254: Division Reliability – CAIDI Indices

Chart 255: Division Reliability – CAIDI Indices

Chart 256: Division Reliability – CAIDI Indices

Chart 257: Division Reliability – CAIDI Indices

Chart 258: Division Reliability – CAIDI Indices

Chart 259: Division Reliability – CAIDI Indices

Chart 260: Division Reliability – CAIDI Indices

Chart 261: Division Reliability – CAIDI Indices

Chart 262: Division Reliability – CAIDI Indices

Chart 263: Division Reliability – CAIDI Indices

Chart 264: Division Reliability – CAIDI Indices

Chart 265: Division Reliability – CAIDI Indices

Chart 266: Division Reliability – CAIDI Indices

Chart 267: Division Reliability – CAIDI Indices

Chart 268: Division Reliability – CAIDI Indices

Chart 269: Division Reliability – CAIDI Indices

Chart 270: Division Reliability – CAIDI Indices

### Charts for System and Division Reliability Indices based on IEEE 1366 for the past 10 years including planned outages and including MED

### SAIDI Performance Results (MED Included)

Chart 271: Division Reliability – AIDI Indices

Chart 272: Division Reliability – AIDI Indices

Chart 273: Division Reliability – AIDI Indices

Chart 274: Division Reliability – AIDI Indices

Chart 275: Division Reliability – AIDI Indices

Chart 276: Division Reliability – AIDI Indices

Chart 277: Division Reliability – AIDI Indices

Chart 278: Division Reliability – AIDI Indices

Chart 279: Division Reliability – AIDI Indices

Chart 280: Division Reliability – AIDI Indices

Chart 281: Division Reliability – AIDI Indices

Chart 282: Division Reliability – AIDI Indices

Chart 283: Division Reliability – AIDI Indices

Chart 284: Division Reliability – AIDI Indices

Chart 285: Division Reliability – AIDI Indices

Chart 286: Division Reliability – AIDI Indices

Chart 287: Division Reliability – AIDI Indices

Chart 288: Division Reliability – AIDI Indices

Chart 289: Division Reliability – AIDI Indices

Chart 290: System Reliability – SAIDI Indices

### SAIFI Performance Results (MED Included)

Chart 291: Division Reliability – AIFI Indices

Chart 292: Division Reliability – AIFI Indices

Chart 293: Division Reliability – AIFI Indices

Chart 294: Division Reliability – AIFI Indices

Chart 295: Division Reliability – AIFI Indices

Chart 296: Division Reliability – AIFI Indices

Chart 297: Division Reliability – AIFI Indices

Chart 298: Division Reliability – AIFI Indices

Chart 299: Division Reliability – AIFI Indices

Chart 300: Division Reliability – AIFI Indices

Chart 301: Division Reliability – AIFI Indices

Chart 302: Division Reliability – AIFI Indices

Chart 303: Division Reliability – AIFI Indices

Chart 304: Division Reliability – AIFI Indices

Chart 305: Division Reliability – AIFI Indices

Chart 306: Division Reliability – AIFI Indices

Chart 307: Division Reliability – AIFI Indices

Chart 308: Division Reliability – AIFI Indices

Chart 309: Division Reliability – AIFI Indices

Chart 310: System Reliability – SAIFI Indices

### MAIFI Performance Results (MED Included)

Chart 311: Division Reliability – MAIFI Indices

Chart 312: Division Reliability – MAIFI Indices

Chart 313: Division Reliability – MAIFI Indices

Chart 314: Division Reliability – MAIFI Indices

Chart 315: Division Reliability – MAIFI Indices

Chart 316: Division Reliability – MAIFI Indices

Chart 317: Division Reliability – MAIFI Indices

Chart 318: Division Reliability – MAIFI Indices

Chart 319: Division Reliability – MAIFI Indices

Chart 320: Division Reliability – MAIFI Indices

Chart 321: Division Reliability – MAIFI Indices

Chart 322: Division Reliability – MAIFI Indices

Chart 323: Division Reliability – MAIFI Indices

Chart 324: Division Reliability – MAIFI Indices

Chart 325: Division Reliability – MAIFI Indices

Chart 326: Division Reliability – MAIFI Indices

Chart 327: Division Reliability – MAIFI Indices

Chart 328: Division Reliability – MAIFI Indices

Chart 329: Division Reliability – MAIFI Indices

Chart 330: System Reliability – MAIFI Indices

### CAIDI Performance Results (MED Included)

Chart 331: Division Reliability – CAIDI Indices

Chart 332: Division Reliability – CAIDI Indices

Chart 333: Division Reliability – CAIDI Indices

Chart 334: Division Reliability – CAIDI Indices

Chart 335: Division Reliability – CAIDI Indices

Chart 336: Division Reliability – CAIDI Indices

Chart 337: Division Reliability – CAIDI Indices

Chart 338: Division Reliability – CAIDI Indices

Chart 339: Division Reliability – CAIDI Indices

Chart 340: Division Reliability – CAIDI Indices

Chart 341: Division Reliability – CAIDI Indices

Chart 342: Division Reliability – CAIDI Indices

Chart 343: Division Reliability – CAIDI Indices

Chart 344: Division Reliability – CAIDI Indices

Chart 345: Division Reliability – CAIDI Indices

Chart 346: Division Reliability – CAIDI Indices

Chart 347: Division Reliability – CAIDI Indices

Chart 348: Division Reliability – CAIDI Indices

Chart 349: Division Reliability – CAIDI Indices

Chart 350: System Reliability – CAIDI Indices

## The number of planned outages, date, and location of planned outages in each division on an annual basis.

PG&E is submitting detailed planned outage information on a confidential basis under seal as required by Appendix B of Decision 16-01-008, at footnote 7.  Listed below is a summary of planned outages by year from 2009 through 2018:

Table 60: Ten Years Planned Outage Summary (2009-2018)

# Service Territory Map

PG&E Service Territory

# Top 1% of Worst Performing Circuits (WPC) excluding Major Event Day (MED)

PG&E’s selection of its worst performing circuits is comprised of two lists.  List #1 (see Table 61 below) is ranked by the highest number of sustained outages the average customer on the circuit experienced on a three-year average annual basis (AIFI).  List #2 (see Table 62 below) is ranked by the highest total number of sustained outage minutes that the average customer on the circuit experienced on a three-year average annual basis (AIDI).  PG&E recognizes that a given circuit may appear on both the AIDI and AIFI lists of worst performing circuits based on outage characteristics.  In consideration of this overlap, PG&E identified 18 circuits on each list with three circuits appearing on both lists. The net total of 33 individual circuits represents one percent of the total number of circuits in PG&E’s distribution system.

For purposes of this reliability report, PG&E’s focus in developing the worst performing circuit lists has been on the outage impacts to the average customer on the circuit.  This approach is different than adopting a focus on a circuit’s contribution to PG&E’s overall system reliability performance.  For example, a circuit serving 50 customers who experience a three-year average of five sustained outages (a total of 250 sustained customer outages per year) would have a higher ranking than a circuit serving 1,000 customers where each customer experienced a three-year average of three sustained outages (a total of 3,000 sustained customer outages per year).  For purposes of the worst performing circuit list, the fact that the average customer on the smaller circuit experienced five sustained outages caused that circuit to rank as performing worse than a circuit where the average customer only experienced three sustained outages.

Consistent with the direction provided in Decision 16-01-008, PG&E used three years (2016 - 2018) of outage data in developing the worst performing circuit lists. PG&E has excluded outage data involving planned outages, CAISO outages and major event days.  PG&E has also limited its review to mainline circuit outages only (in other words, only outages involving a circuit breaker, a line recloser, or an interrupter).  Finally, PG&E has excluded those outages which occurred when the circuit was temporarily switched into an abnormal configuration.  An abnormal circuit configuration may occur when customers are temporarily added to or transferred from a circuit to support construction or maintenance work performed on an adjacent circuit.  Analysis has shown that outages associated with abnormal circuit configurations would disproportionately skew the results of the worst performing circuit lists.  PG&E believes that this approach best defines a worst performing circuit.

Table 61 lists the worst performing circuits by outage frequency and indicates the worst AIFI circuit was the Garberville 1101 circuit.  The average customer on the Garberville 1101 circuit experienced 4.99 sustained mainline outages per year from 2016-2018 (resulting from the operation of a circuit breaker or an automatic recloser).

Table 62 focuses on the duration of the sustained outages.  Here, the Echo Summit 1101 circuit was identified as the worst AIDI performing circuit.  For this circuit, the average customer on the circuit experienced 1,400 sustained mainline outage minutes per year from 2016-2018 (resulting from the operation of a circuit breaker or an automatic recloser).

Three circuits (Garberville 1102, Tulare Lake 2108, and Otter 1102) appear on both lists.  These three circuits are highlighted in red within Tables 61 and 62.  Additionally, sixteen circuits marked with an asterisk (*) indicates that they are “deficient”.  A “deficient” circuit is defined as a circuit that has appeared consecutively on the WPC lists for the previous two years (see the “Deficient” Worst Performing Section below for further details).

Table 61: AIFI Worst Performing Circuit for 2018

Table 62: AIDI Worst Performing Circuit for 2018

Cost Effective Reliability Remediation:

The Targeted Circuit Program has been PG&E’s primary reliability improvement program to cost effectively remediate PG&E’s worst performing circuits.  Under the Targeted Circuit Program, PG&E’s distribution engineers analyzed the causes and characteristics of historical outages as well as reviewed the current circuit design to cost effectively identify work that would improve the circuit’s reliability performance.  The typical targeted circuit work included, as appropriate for the circuit, installing new protection equipment, replacing overhead and underground conductors, installing new fault indicators, reframing poles to increase phase separation, installing animal/bird guards, repairing or replacing deteriorated equipment, completing pending reliability related maintenance work, performing infrared inspections, and trimming trees.  The goal of each targeted circuit improvement project was to achieve a 25 percent reliability improvement from its 3-year historical AIFI and AIDI average performance.  The typical timeline for a targeted circuit project to be initiated, engineered, and constructed was three years.

Over a 10-year period, the Targeted Circuit Program successfully completed work on 485 targeted circuits.  The 2018 AIFI and AIDI actual performance results observed for a targeted circuit on average had shown a 31% and 39% improvement respectively in comparison to its respective three-year historical average.  Although historical reliability metric results have shown the Targeted Circuit Program to be effective in remediating worst performing circuit performance, PG&E has suspended funding for the Targeted Circuit Program in the 2020 General Rate Case (GRC) in order to focus on overhead system hardening and wildfire risk reductions efforts.

As reported in the Wildfire Mitigation Plan (Rulemaking (R.) 18-10-007), PG&E submitted a Wildfire Safety Plan to minimize the risk of catastrophic wildfires.  A key component in the Wildfire Safety Plan submittal is the System Hardening Program.  Under the System Hardening Program, PG&E’s distribution engineers evaluate a rebuild of overhead distribution circuits in the High Fire Threat District (HFTD) areas.  The typical system hardening work included, as appropriate for the circuit, replacing bare wire with insulated conductor, increasing strength requirements for poles, installing new system automation and protection equipment, and targeted conversion of overhead equipment to underground equipment.  The anticipated goal of each system hardened circuit is to minimize the risk of an asset failure that could result in a fire ignition.  The anticipated reliability improvement of each system hardened circuit is to minimize vegetation, equipment failure, third party, animal, and other (unknown) caused outages that could result in a fire ignition.  As forecasted in PG&E’s Wildfire Safety Plan, PG&E intends to begin the System Hardening Program in 2019 by completing 150 circuit miles of system hardening work in HFTD areas. In 2020-2022, PG&E forecasts completing 600 circuit miles per year during this period. At the end of the System Hardening Program, PG&E intends to complete 7,100 circuit miles of system hardening work.

Another key component of the Wildfire Safety Plan is the Enhanced Vegetation Management (EVM) Program.  Under the EVM Program, PG&E will aggressively expand its vegetation management around its assets in the HFTD areas.  The typical EVM work included, as appropriate for the circuit, clearing overhang, targeted trimming/removal of specific tree species, and performing “ground to conductor” vegetative fuel reduction.  The anticipated goal of each EVM circuit is to minimize the risk of a fire ignition due to vegetation-conductor contact.  The anticipated reliability improvement of each EMV circuit is to minimize vegetation caused outages.  As forecasted in PG&E’s Wildfire Safety Plan, PG&E intends to perform EVM work on approximately 2,450 circuit miles in HFTD areas in 2019.  The program will be a multi-year effort to address the approximately 25,200 distribution circuit miles in the HFTD areas.

Despite reductions in some reliability programs, PG&E teams continue to perform internal reviews of unplanned outages on a regular basis through the company’s Outage Review Team (ORT) Process.  The objective of the ORT process is to identify and minimize chronic reliability issues that affect smaller number of customers.  Cost effective remediation work that addresses those circuits identified from the ORT process are incorporated into PG&E’s base reliability work.

As identified in Tables 60 and 61, 10 and 15 of PG&E’s worst performing AIFI and AIDI circuits respectively are in Tiers 2 or 3 HFTD areas.  As a result, these worst performing circuits have or would be incorporated into the Wildfire Safety Plan.  For the worst performing circuits located in Tier 1 HFTD area, PG&E will evaluate what remedial action, if any, as appropriate through the ORT process.  This includes determining whether any cost-effective remedial action will be performed through PG&E’s base reliability improvement work.  Any future funding requests for PG&E’s Targeted Circuit Program would be submitted in the 2023 General Rate Case.

“Deficient” Worst Performing Circuits:

The circuits listed below are “deficient” (WPC) circuits in response to section 5b of CPUC D 16-008-001, Appendix B:

1. GARBERVILLE 1101

  - An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIFI score of 4.98

    - Three-year (2015-2017) average AIFI score of 4.95

    - Three-year (2016-2018) average AIFI score of 4.99

  - A historical record of the metric:

    - AIFI 2014 = 3.90

    - AIFI 2015 = 2.27

    - AIFI 2016 = 8.76

    - AIFI 2017 = 3.81

    - AIFI 2018 = 2.49

  - An explanation of why it was on the deficiency list again:

The Garberville 1101 circuit provides electric service to approximately 1,239 customers in Southern Humboldt and Northern Mendocino Counties through 166 circuit-miles of primarily overhead conductor.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 2 (Elevated Risk).  The Garberville 1101 circuit is comprised of three main branches.  The eastern branch serves approximately 272 customers through a 22 circuit-mile line section that travels through remote, mountainous terrain including zones with intermediate and heavy snow loading.  The western branch serves approximately 171 customers through a 12 circuit-mile line section that traverses through coastal mountains to the community of Whitethorn.  The southern branch serves approximately 745 customers through a 28 circuit-mile line section that follows the Hwy 101 corridor between Garberville and Leggett.  The southern branch also runs along the South Fork of the Eel River and crosses several State Parks including Richardson’s Grove, Smith Redwoods, and Standish Hickey Recreation Area.  The major factors driving the Garberville 1101 reliability performance are the remote mountainous service territory with increased vegetation caused outage risks, overhead conductor exposure, and minimal ties to adjacent circuits for outage restoration support.

  - An explanation of what is being done to improve the circuit's future performance:

This circuit was part of the 2012 Targeted Circuit program. Specifically, the 2012 targeted circuit project upgraded 700 feet of overhead conductor, installed two overhead switches, and performed miscellaneous reliability work like pole reframing and self-protecting transformer replacement. An additional 4,400 feet of mainline conductor was successfully replaced in 2016 as part of the OH Conductor Replacement Program. A system hardening project to replace 9,000’ of OH conductor has been initiated as part of the Wildfire Safety Plan.

  - A quantitative description of the utility's expectation for that circuit's future performance:

A 13% percent increase in 2018 AIFI reliability performance compared to the three-year outage history from 2007-2009 was observed after the completion of the 2012 targeted circuit project.  This reflects the reliability performance challenges that still exist on the Garberville 1101 circuit.  Incremental reliability improvement is anticipated after completion of the system hardening project, but the anticipated reliability benefits have not been quantified.  This includes the associated reliability benefits after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tier 2 High Fire Threat District.

2. GARBERVILLE 1102

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIFI score of 3.34 and AIDI score of 726

    - Three-year (2015-2017) average AIFI score of 4.41 and AIDI score of 970

    - Three-year (2016-2018) average AIFI score of 4.01 and AIDI score of 1,083

- A historical record of the metric:

    - AIFI 2014 = 3.50

    - AIFI 2015 = 2.66

    - AIFI 2016 = 3.87

    - AIFI 2017 = 6.68

    - AIFI 2018 = 1.50

    - AIDI 2014 = 936

    - AIDI 2015 = 510

    - AIDI 2016 = 732

    - AIDI 2017 = 1,665

    - AIDI 2018 = 853

- An explanation of why it was on the deficiency list again:

The Garberville 1102 circuit provides electric service to approximately 1,239 customers in Humboldt County through 146 circuit-miles of primarily overhead conductor.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 2 (Elevated Risk).  The primary mainline section of Garberville 1102 circuit travels through a 50 mile stretch of mountainous terrain along the northern coast.  The primary mainline section also crosses an area known in the outdoor/hiking community as “The Lost Coast” and portions of the Humboldt Redwoods State Park. The primary mainline section splits near the town of Briceland, approximately 10 circuit miles northwest of Garberville.  The north branch extends 37 miles to Petrolia while the south branch extends 14 miles to the community of Whitethorn. The major factors driving the Garberville 1102 reliability performance are the remote mountainous service territory with increased vegetation caused outage risks, overhead conductor exposure, and minimal ties to adjacent circuits for outage restoration support. A 15% and 32% contribution to the 2017 AIFI and AIDI performance respectively was driven by a single vegetation caused outage that resulted in a wire down occurrence and a broken pole.

- An explanation of what is being done to improve the circuit's future performance:

This circuit was part of the 2011 Targeted Circuit program. Specifically, the 2011 targeted circuit project installed twelve fuses, three reclosers and performed miscellaneous reliability improvement work like pole reframing and self-protecting transformer replacement.  A 2013 reconductor project successfully replaced over one mile of overhead conductor with a larger conductor.  A reliability improvement project to allow a temporary generator to be interconnected at the town of Petrolia was successfully completed in 2018. This project was part of a pilot program to minimize outage restoration time. A system hardening project has been initiated to replace 4,000’ of OH conductor as part of the Wildfire Safety Plan.

- A quantitative description of the utility's expectation for that circuit's future performance:

A 66% and 45% percent improvement in 2018 AIFI and AIDI reliability performance respectively were observed after the completion of the 2011 targeted circuit project compared to the three-year outage history from 2006-2008.  Although difficult to quantify the anticipated reduction in outage restoration time after completion of a 2018 distribution generation interconnection project, AIDI improvement was observed from 2017 to 2018.  Incremental reliability improvement is also anticipated after completion of the system hardening project, but the anticipated reliability benefits have not been quantified.  This includes the associated reliability benefits after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tier 2 High Fire Threat District.

3. HOOPA 1101

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIDI score of 828

    - Three-year (2015-2017) average AIDI score of 907

    - Three-year (2016-2018) average AIDI score of 751

- A historical record of the metric:

    - AIDI 2014 = 222

    - AIDI 2015 = 1,152

    - AIDI 2016 = 1,105

    - AIDI 2017 = 459

    - AIDI 2018 = 691

- An explanation of why it was on the deficiency list again:

The Hoopa 1101 circuit provides electric service to approximately 1,985 customers in Humboldt County through 151 circuit-miles of primarily overhead conductor.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 2 (Elevated Risk).   The Hoopa 1101 circuit is comprised of two main branches.  The eastern branch serves approximately 522 customers through a 24 circuit-mile line section that traverses through remote mountainous terrain including the Six Rivers and Klamath National Forests.  The western branch is a 20 circuit-mile line section that runs along the Klamath River and follows the Hwy 169 corridor between the communities of Weitchpec and Johnsons.  The major factors driving the Hoopa 1101 reliability performance are the remote mountainous service territory with increased vegetation caused outage risks, overhead conductor exposure, and minimal ties to adjacent circuits for outage restoration support.

- An explanation of what is being done to improve the circuit's future performance:

A reliability improvement project to allow a temporary generator to be interconnected on the eastern branch at Orleans was successfully completed in 2017.  A second distribution generation interconnection project to support the circuit breaker zone is targeted for 2019-20 installation.  As of the date of this report, no system hardening project has been initiated for the Hoopa 1101 circuit.

- A quantitative description of the utility's expectation for that circuit's future performance:

Although difficult to quantify the anticipated reduction in outage restoration time after completion of the 2017 distribution generation interconnection project, AIDI improvement was observed from 2016 to 2018.  Incremental reliability improvement is also anticipated after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tier 2 High Fire Threat District.

4. CHALLENGE 1101

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIDI score of 1,017

    - Three-year (2015-2017) average AIDI score of 766

    - Three-year (2016-2018) average AIDI score of 533

- A historical record of the metric:

    - AIDI 2014 = 1,087

    - AIDI 2015 = 942

    - AIDI 2016 = 1,022

    - AIDI 2017 = 331

    - AIDI 2018 = 250

- An explanation of why it was on the deficiency list again:

The Challenge 1101 circuit provides electric service to approximately 690 customers in Yuba, Butte and Plumas Counties through 49 circuit-miles of primarily overhead conductor.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 3 (Extreme Risk).  The Challenge 1101 circuit is comprised of one main branch that travels northeast through remote, mountainous terrain including the Plumas National Forest.  The major factors driving the Challenge 1101 reliability performance are the remote mountainous service territory with increased vegetation caused outage risks, overhead conductor exposure, and minimal ties to adjacent circuits for outage restoration support.  A 71% contribution of the 2016 AIDI performance was driven by a single vegetation caused outage resulting in wire down occurrences at multiple locations.

- An explanation of what is being done to improve the circuit's future performance:

This circuit was part of the 2013 Targeted Circuit program. Specifically, the 2013 targeted circuit project installed 13 fuses, 1 recloser, 2 switches, and performed miscellaneous reliability work like pole reframing and pole replacement.  As of the date of this report, no system hardening project has been initiated for the Challenge 1101 circuit.

- A quantitative description of the utility's expectation for that circuit's future performance:

A 77% percent improvement in 2018 AIDI reliability performance was observed after the completion of the 2013 targeted circuit project compared to the three-year outage history from 2008-2010. Incremental reliability improvement is also anticipated after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tier 3 High Fire Threat District.

5. ALLEGHANY 1101

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIDI score of 711

    - Three-year (2015-2017) average AIDI score of 562

    - Three-year (2016-2018) average AIDI score of 630

- A historical record of the metric:

    - AIDI 2014 = 1,340

    - AIDI 2015 = 205

    - AIDI 2016 = 590

    - AIDI 2017 = 846

    - AIDI 2018 = 420

- An explanation of why it was on the deficiency list again:

The Alleghany 1101 circuit provides electric service to approximately 1,074 customers in Sierra County through 79 circuit-miles of primarily overhead conductor.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 3 (Extreme Risk).  The Alleghany 1101 circuit is comprised of about 45 miles of mainline with various branches that travel through a mix of rural highway and cross-country access.  Its most northern branch travels through mountainous terrain including the Plumas National Forest.  The major factors driving the Alleghany 1101 reliability performance are the remote service territory, overhead conductor exposure, and minimal ties to adjacent circuits for outage restoration support.  In a specific instance, 2014 performance was driven by two outages that resulted in over one million customer outage minutes.  Restoration in those outages was delayed due to severe weather and its remote location.

- An explanation of what is being done to improve the circuit's future performance:

This circuit was part of PG&E’s 2013 Targeted Circuit program. Specifically, the 2013 targeted circuit project replaced 2,700 feet of overhead conductor with larger wire to be more resilient to snow loading conditions. This project also upgraded 2 reclosers to provide remote operation capability.  As of the date of this report, no system hardening project has been initiated for the Alleghany 1101 circuit.

- A quantitative description of the utility's expectation for that circuit's future performance:

A 57% percent improvement in 2018 AIDI reliability performance was observed after the completion of the 2013 targeted circuit project compared to the three-year outage history from 2008-2010.  Incremental reliability improvement is also anticipated after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tier 3 High Fire Threat District.

6. WILLOW CREEK 1103

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIDI score of 558

    - Three-year (2015-2017) average AIDI score of 807

    - Three-year (2016-2018) average AIDI score of 628

- A historical record of the metric:

    - AIDI 2014 = 797

    - AIDI 2015 = 576

    - AIDI 2016 = 303

    - AIDI 2017 = 1,540

    - AIDI 2018 = 49

- An explanation of why it was on the deficiency list again:

The Willow Creek 1103 circuit provides electric service to approximately 1,529 customers in Humboldt and Trinity Counties through 87 circuit-miles of primarily overhead conductor.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 2 (Elevated Risk) and Tier 3 (Extreme Risk).  The Willow Creek 1103 circuit is comprised of two main branches that travel south and southeast through remote, mountainous terrain including the Six Rivers and Trinity National Forests.  The major factors driving the Willow Creek 1103 reliability performance are the remote mountainous service territory with increased vegetation caused outage risks, overhead conductor exposure, and minimal ties to adjacent circuits for outage restoration support.  A 63% contribution of the 2017 AIDI performance was driven by a single vegetation caused outage that resulted in a wire down occurrence.

- An explanation of what is being done to improve the circuit's future performance:

This circuit was part of the 2014 Targeted Circuit program. Specifically, the 2014 targeted circuit project replaced over 900 feet of conductor, installed 5 fuses, 6 switches, and performed miscellaneous reliability work like pole reframing and pole replacement.  A system hardening project has been initiated to replace 6,300’ of OH conductor as part of the Wildfire Safety Plan.

- A quantitative description of the utility's expectation for that circuit's future performance:

A 63% percent improvement in 2018 AIDI reliability performance was observed after the completion of the 2014 targeted circuit project compared to the three-year outage history from 2009-2011.  Incremental reliability improvement is anticipated after completion of the system hardening project, but the anticipated reliability benefits have not been quantified.  This includes the associated reliability benefits after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tiers 2 and 3 High Fire Threat Districts.

7. OTTER 1102

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIFI score of 4.29 and AIDI score of 1,224

    - Three-year (2015-2017) average AIFI score of 3.06 and AIDI score of 687

    - Three-year (2016-2018) average AIFI score of 3.84 and AIDI score of 976

- A historical record of the metric:

    - AIFI 2014 = 5.54

    - AIFI 2015 = 1.44

    - AIFI 2016 = 5.90

    - AIFI 2017 = 1.84

    - AIFI 2018 = 3.80

    - AIDI 2014 = 1,714

    - AIDI 2015 = 844

    - AIDI 2016 = 1,110

    - AIDI 2017 = 103

    - AIDI 2018 = 1,713

- An explanation of why it was on the deficiency list again:

The Otter 1102 circuit provides electric service to approximately 530 customers in Monterey County through 65 circuit-miles of primarily overhead conductor.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 2 (Elevated Risk).  The primary mainline section of Otter 1102 circuit travels south along Central California’s coastline through a 26 mile stretch of mountainous terrain including Andrew Molera and Pfeiffer Big Sur State Parks.  The major factors driving the Otter 1102 reliability performance are the remote mountainous service territory with increased vegetation caused outage risks, overhead conductor exposure with elevated corrosion conditions, and minimal ties to adjacent circuits for outage restoration support.

- An explanation of what is being done to improve the circuit's future performance:

This circuit was part of the 2014 Targeted Circuit program. Specifically, the targeted circuit project replaced 1,000 feet of overhead conductor, installed seven fuses, replaced 7 poles, reframed 14 cross arms, and installed 9 animal guards.  An additional 19,100 feet of reconductor work was completed from 2015-2016 with another 10,100 feet of reconductor work planned for 2019 completion.  As of the date of this report, no system hardening project has been initiated for the Otter 1102 circuit.

- A quantitative description of the utility's expectation for that circuit's future performance:

A 10% increase and 4% percent improvement in 2018 AIFI and AIDI reliability performance, respectively, compared to the three-year outage history from 2009-2011were observed after the completion of the 2014 targeted circuit project.  This reflects the reliability performance challenges that still exist on the Otter 1102 circuit.  Incremental reliability improvement is anticipated after completion of the overhead reconductor work in 2019 and the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tier 2 High Fire Threat District.

8. EL DORADO PH 2101

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIFI score of 3.61

    - Three-year (2015-2017) average AIFI score of 3.55

    - Three-year (2016-2018) average AIFI score of 2.99

- A historical record of the metric:

    - AIFI 2014 = 3.09

    - AIFI 2015 = 4.29

    - AIFI 2016 = 3.36

    - AIFI 2017 = 3.00

    - AIFI 2018 = 2.62

- An explanation of why it was on the deficiency list again:

The El Dorado PH 2101 circuit provides electric service to approximately 4,611 customers in El Dorado County through 170 circuit-miles of primarily overhead conductor.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 2 (Elevated Risk) and Tier 3 (Extreme Risk).  The El Dorado PH 2101 circuit is comprised of one main branch that travels east along Highway 50 through a 30 mile stretch of mountainous terrain including El Dorado National Forest.  The primary mainline section splits near the town of Polluck Pines, approximately 4 miles southeast of El Dorado PH (Power House).  The southwest branch extends 8 miles to Pleasant Valley while the south branch extends 10 miles to the community of Grizzly Flat. The major factors driving the El Dorado PH 2101 reliability performance are the remote mountainous service territory with increased vegetation caused outage risks, overhead conductor exposure, and minimal ties to adjacent circuits for outage restoration support.

- An explanation of what is being done to improve the circuit's future performance:

This circuit was part of the 2011 Targeted Circuit program.  Specifically, the targeted circuit project installed 2 fuses and reframed 13 poles.  As part of PG&E’s base reliability work, a project was initiated to install additional line reclosers, add remote operating capabilities to existing line reclosers, replace overhead conductor to increase capacity, and install automated switches with a 2019 completion timeframe.  Several system hardening projects have been initiated to replace over 102 miles of OH conductor as part of the Wildfire Safety Plan.

- A quantitative description of the utility's expectation for that circuit's future performance:

A 26% percent improvement in 2018 AIFI reliability performance was observed after the completion of the 2011 targeted circuit project compared to the three-year outage history from 2006-2008.  Incremental reliability improvement is anticipated after completion of the 2019 base reliability improvement project and system hardening projects, but the anticipated reliability benefits have not been quantified.  This includes the associated reliability benefits after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tiers 2 and 3 High Fire Threat Districts.

9. TULARE LAKE 2108

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIFI score of 3.15 and average AIDI score of 823

    - Three-years (2015-2017) average AIFI score of 3.43 and average AIDI score of 659

    - Three-year (2016-2018) average AIFI score of 4.49 and average AIDI score of 686

- A historical record of the metric:

    - AIFI 2014 = 5.57

    - AIFI 2015 = 1.99

    - AIFI 2016 = 2.68

    - AIFI 2017 = 5.57

    - AIFI 2018 = 5.21

    - AIDI 2014 = 1,506

    - AIDI 2015 = 712

    - AIDI 2016 = 473

    - AIDI 2017 = 789

    - AIDI 2018 = 805

- An explanation of why it was on the deficiency list again:

The Tulare Lake 2108 circuit provides electric service to approximately 104 customers in Kings County through 58 circuit-miles of primarily overhead conductor.  The Tulare 2108 circuit is comprised of several branches that supports a predominately agriculture community.  The major factors driving the Tulare Lake 2108 reliability performance are equipment failure and animal caused outages.

- An explanation of what is being done to improve the circuit's future performance:

A targeted circuit project has been initiated on the Tulare Lake 2108 with the work scope to be developed.  The typical installation of mainline protective devices and performing miscellaneous reliability improvement work is anticipated.  As of the date of this report, no funding for the Targeted Circuit Program has been submitted with any future funding requests to be submitted in the 2023 General Rate Case.

- A quantitative description of the utility's expectation for that circuit's future performance:

Based on results shown by other similar circuits after targeted circuit work, PG&E anticipates that the work proposed will improve reliability performance by 25 percent or more.

10. ALPINE 1102

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIFI score of 4.58

    - Three-year (2015-2017) average AIFI score of 4.00

    - Three-year (2016-2018) average AIFI score of 3.33

- A historical record of the metric:

    - AIFI 2014 = 3.00

    - AIFI 2015 = 5.99

    - AIFI 2016 = 4.00

    - AIFI 2017 = 2.00

    - AIFI 2018 = 4.00

- An explanation of why it was on the deficiency list again:

The Alpine 1102 circuit provides electric service to approximately 309 customers in Alpine County through 3 circuit-miles of entirely underground conductor.  Specifically, the Alpine 1102 circuit supports the Bear Valley community.  The Salt Springs 2101 circuit provides the primary service to the Alpine 1102 circuit through 21/12 kV voltage step down transformers. The major factor driving the Alpine 1102 reliability performance is the reliability performance of the Salt Springs 2101 circuit.  The Salt Springs 2101 circuit also serves customers located in the CPUC High Fire Threat District - Tier 2 (Elevated Risk).

- An explanation of what is being done to improve the circuit's future performance:

It is anticipated that the improvement work on the Salt Springs 2101 will improve the Alpine 1102 reliability performance.  A targeted circuit project had been initiated on the Salt Springs 2101 circuit but has since been repurposed to support the wildfire mitigation efforts.  As of the date of this report, no system hardening project has been initiated for the Salt Springs 2101 circuit.

- A quantitative description of the utility's expectation for that circuit's future performance:

Incremental reliability improvement is anticipated after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tier 2 High Fire Threat District.

11. POSO MOUNTAIN 2101

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIDI score of 1,078

    - Three-year (2015-2017) average AIDI score of 1,088

    - Three-year (2016-2018) average AIDI score of 884

- A historical record of the metric:

    - AIDI 2014 = 245

    - AIDI 2015 = 1,691

    - AIDI 2016 = 1,379

    - AIDI 2017 = 192

    - AIDI 2018 = 1,082

- An explanation of why it was on the deficiency list again:

The Poso Mountain 2101 circuit provides electric service to approximately 146 customers in Kern County through 60 circuit-miles of entirely overhead conductor.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 2 (Elevated Risk).  The Poso Mountain 2101 circuit is comprised of several branches that support a predominately unincorporated community north of Bakersfield. The major factors driving the Poso Mountain 2101 reliability performance are overhead conductor exposure, animal caused outages, and minimal ties to adjacent circuits for outage restoration support.

- An explanation of what is being done to improve the circuit's future performance:

As part of PG&E’s base reliability work, three failed reclosers were replaced with bird guard protection in 2016.  As of the date of this report, no system hardening project has been initiated for the Poso Mountain 2101 circuit.

- A quantitative description of the utility's expectation for that circuit's future performance:

Although difficult to quantify the anticipated reliability benefits after completion of the 2016 base reliability project, AIDI improvement was observed from 2016 to 2018.  Incremental reliability improvement is also anticipated after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tier 2 High Fire Threat District.

12. LOS GATOS 1106

  - An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIFI score of 2.58

    - Three-year (2015-2017) average AIFI score of 2.94

    - Three-year (2016-2018) average AIFI score of 4.51

  - A historical record of the metric:

    - AIFI 2014 = 2.51

    - AIFI 2015 = 0.82

    - AIFI 2016 = 4.42

    - AIFI 2017 = 3.58

    - AIFI 2018 = 5.54

  - An explanation of why it was on the deficiency list again:

Los Gatos is located approximately seven miles southwest of San Jose in De Anza Division. The Los Gatos 1106 circuit provides electric service to approximately 1,597 customers in Santa Clara county through 74 miles of primary overhead conductor.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 2 (Elevated Risk) and Tier 3 (Extreme Risk).  The Los Gatos 1106 circuit is comprised of one main branch that travels south along Highway 50 through a 3 mile stretch of mountainous terrain including Lexington Reservoir Park.  The primary mainline section splits into various branches near the Lexington Reservoir and extends into the Santa Cruz mountains.  The major factors driving the Los Gatos 1106 reliability performance are the mountainous service territory with increased vegetation caused outage risks, overhead conductor exposure, and minimal ties to adjacent circuits for outage restoration support.

  - An explanation of what is being done to improve the circuit's future performance:

A targeted circuit project had been initiated on the Los Gatos 1106 circuit but has since been repurposed to support the wildfire mitigation efforts.  Several system hardening projects have been initiated to replace over 30 miles of OH conductor as part of the Wildfire Safety Plan.

  - A quantitative description of the utility's expectation for that circuit's future performance:

Incremental reliability improvement is anticipated after completion of the system hardening projects, but the anticipated reliability benefits have not been quantified.  This includes the associated reliability benefits after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tiers 2 and 3 High Fire Threat Districts.

13. EIGHT MILE 2106

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIFI score of 2.50

    - Three-year (2015-2017) average AIFI score of 2.79

    - Three-year (2016-2018) average AIFI score of 2.52

- A historical record of the metric:

    - AIFI 2014 = 0.00

    - AIFI 2015 = 1.63

    - AIFI 2016 = 5.91

    - AIFI 2017 = 0.85

    - AIFI 2018 = 0.82

- An explanation of why it was on the deficiency list again:

The Eight Mile 2106 circuit provides electric service to approximately 196 customers in San Joaquin County through 31 circuit-miles of mainly overhead conductor.  The Eight Mile 2106 circuit is comprised of several branches that support a predominately King Island and Empire Tract north east of Stockton. The major factors driving the Eight Mile 2106 reliability performance are equipment failures, remote access challenges, and minimal ties to adjacent circuits for outage restoration support.

- An explanation of what is being done to improve the circuit's future performance:

A base reliability improvement project to install 1 recloser and 2 fuses has been initiated for 2020 completion.

- A quantitative description of the utility's expectation for that circuit's future performance:

Incremental reliability improvement is anticipated after completion of the 2020 base reliability improvement project, but the anticipated reliability benefits have not been quantified.  PG&E will continue to explore cost effective reliability improvement opportunities such as installing additional remotely operable devices and replacing traditional fuses with single phase reclosers.

14. TRINIDAD 1102

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIFI score of 2.98

    - Three-year (2015-2017) average AIFI score of 2.82

    - Three-year (2016-2018) average AIFI score of 2.95

- A historical record of the metric:

    - AIFI 2014 = 1.63

    - AIFI 2015 = 2.29

    - AIFI 2016 = 5.01

    - AIFI 2017 = 1.17

    - AIFI 2018 = 2.68

- An explanation of why it was on the deficiency list again:

The Trinidad 1102 circuit provides electric service to approximately 761 customers in Humboldt County through 24 circuit-miles of primarily overhead conductor. The Trinidad 1102 circuit is comprised of one main branch that travels north along Patrick’s Point Drive and paralleling Highway 101 through a 7 mile stretch of densely forested coastal mountainous terrain including Patrick’s Point State Park to the community of Big Lagoon.  The major factors driving Trinidad 1102 reliability performance are the mountainous service territory with increased vegetation caused outage risks, overhead conductor exposure, and minimal ties to adjacent circuits for outage restoration support.

- An explanation of what is being done to improve the circuit's future performance:

As of the date of this report, no targeted circuit project has been initiated for the Trinidad 1102 circuit.

- A quantitative description of the utility's expectation for that circuit's future performance:

PG&E will continue to explore cost effective reliability improvement opportunities through the Outage Review Team Process such as installing additional remotely operable devices and replacing traditional fuses with single phase reclosing devices.  This includes exploring cost effective reliability improvement opportunities to minimize wildfire ignition risks in the Tier 1 High Fire Threat District through proactive asset replacement or targeted vegetation management work.

15. ROB ROY 2105

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIFI score of 2.54

    - Three-year (2015-2017) average AIFI score of 2.66

    - Three-year (2016-2018) average AIFI score of 2.80

- A historical record of the metric:

    - AIFI 2014 = 0.23

    - AIFI 2015 = 1.80

    - AIFI 2016 = 5.61

    - AIFI 2017 = 0.59

    - AIFI 2018 = 2.29

- An explanation of why it was on the deficiency list again:

The Rob Roy 2105 circuit provides electric service to approximately 8,104 customers to the city of Aptos and Santa Cruz County through 72 circuit-miles of overhead conductor and 28 circuit-miles of underground cable.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 2 (Elevated Risk) and Tier 3 (Extreme Risk).  The Rob Roy 2105 circuit is comprised of several branches that travels along the coast line from Seacliff Beach to La Selva Beach including Nisene Marks State Park. The major factors driving Rob Roy 2105 reliability performance are equipment failures, vegetation, 3rd party (vehicle accidents), and overhead conductor exposure.

- An explanation of what is being done to improve the circuit's future performance:

A reliability improvement project for installing additional sectionalizing devices (2 UG switches) was completed in 2017.  A system hardening project to replace 2.16 miles of OH conductor was initiated for 2019 completion.  An additional system hardening project has been initiated to replace 9 miles of OH conductor as part of the Wildfire Safety Plan.  A third project has been initiated to replace 0.88 miles in the Tier 1 High Fire Threat Districts under the OH Conductor Replacement Program.

- A quantitative description of the utility's expectation for that circuit's future performance:

Incremental reliability improvement is anticipated after completion of the system hardening projects, but the anticipated reliability benefits have not been quantified.  This includes the associated reliability benefits after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tiers 2 and 3 High Fire Threat Districts.

16. BUCKS CREEK 1103

- An explanation of why it was ranked as a "deficient" circuit:

    - Three-year (2014-2016) average AIDI score of 744

    - Three-year (2015-2017) average AIDI score of 1,106

    - Three-year (2016-2018) average AIDI score of 1,175

- A historical record of the metric:

    - AIDI 2014 = 0

    - AIDI 2015 = 1,036

    - AIDI 2016 = 1,199

    - AIDI 2017 = 1,084

    - AIDI 2018 = 1,242

- An explanation of why it was on the deficiency list again:

The Bucks Creek 1103 circuit provides electric service to approximately 322 customers in Plumas County through 26 circuit-miles of OH conductor and UG cable.  This circuit also serves customers located in the CPUC High Fire Threat District - Tier 3 (Extreme Risk).  The Bucks Creek 1103 circuit is comprised of one main branch that travels east along OHV Road 9 through a 15 mile stretch of mountainous terrain including Plumas National Forest to the Bucks Lake community.  The major factors driving Bucks Creek 1103 reliability performance are the remote mountainous service territory with increased vegetation caused outage risks, overhead conductor exposure, and minimal ties to adjacent circuits for outage restoration support.

- An explanation of what is being done to improve the circuit's future performance:

As of the date of this report, no system hardening project has been initiated for the Bucks Creek 1103 circuit.

- A quantitative description of the utility's expectation for that circuit's future performance:

Incremental reliability improvement is anticipated after completion of the comprehensive Wildfire Safety Plan to minimize wildfire ignition risks in the Tier 3 High Fire Threat District.

# Top 10 major unplanned power outage events of 2018

Significant Outage Events Of 2018

Table below lists the ten largest outage events experienced during 2018.  PG&E interprets this reporting requirement as the ten events (individual days or in some cases a group of consecutive days) with a significant number of customer interruptions in the system or a portion of the system.  These events are listed in descending order of customer interruptions.

Table 63 - Ten Largest 2018 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service | CPUC Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | A trio of early winter-season storms generated a significant amount of outage activity due to gusty south winds and heavy rain with considerable flashover activity across the interior south. | 11/21/2018 – 11/23/2018 | 224,103 | 97 | 460 | Yes (11/21 only) |
| 2 | Carr Fire | 7/28/2018 – 7/30/2018 | 121,187 | 248 | 132 | Yes (7/28 only) |
| 3 | Early season low pressure system brought the first rain in months to the territory resulting in significant flashover-related outages with widespread thunderstorm activity across the interior and south on 10/3 producing over 2,000 lightning strikes. | 10/2/2018 – 10/3/2018 | 115,705 | 30 |  |  |
| 4 | A dynamic Pacific weather system delivered gusty south winds, heavy rain, scattered thunderstorms and heavy mountain snow to the territory; causing significant outage activity, especially in Central Coast division. | 11/28/2018 –11/29/2018 | 109,891 | 99 | 741 | Yes (11/29 only) |
| 5 | A strong winter storm impacted the territory with heavy rain, heavy mountain snow and gusty south winds followed by a secondary wave generating low snow and thunderstorms the next day | 3/1/2018 – 3/2/2018 | 108,654 | 100 |  |  |
| 6 | Not weather related | 5/17/2018 | 75,292 | 19 | 120 | Yes |
| 7 | An offshore wind event developed across the northern two thirds of the territory and produced Extreme-Plus fire danger resulting in execution of PSPS. | 10/14/2018 | 70,326 | 89 | 441 | Yes |
| 8 | Camp Fire | 11/8/2018 | 68,468 | 936 | 214 | Yes |
| 9 | Breezy to gusty northeast winds developed across the territory producing considerable outage activity in San Jose and Central Coast divisions | 12/31/2018 | 57,736 | 31 |  |  |
| 10 | A moist, atmospheric-river storm system delivered copious amounts of rainfall to parts of the territory with thunderstorm activity across the interior producing over 900 lightning strikes and widespread outage activity. | 3/22/2018 | 55,598 | 39 |  |  |

* Note:  Values exclude planned outages

# Summary List of Major Event Day (MED) per IEEE 1366

Major Event Day

IEEE Standard 1366 defines MED as follows:

IEEE Standard 1366-2003 uses a statistically-based method of identifying excludable events. Specifically, the IEEE standard provides for the exclusion of all outages occurring on any day where its SAIDI is greater than “TMED” where:

TMED =  e average over 5 yrs. of Ln (daily SAIDI) + 2.5 * STD DEV of 5 yrs. of Ln (daily SAIDI)

The IEEE 1366 Standard includes outage resulting from the failure of a single line transformer.

Table 64 – 2018 Major Event Day

*MED is defined as Major Events Day

### 7.1	Major Event Day (MED) Discussions:

### March 16, 2018 Major Event Day

Table 65 below indicates the number of customers without service at periodic intervals for this event (03/16/2018).  The numbers of customers noted in the table are for only those divisions impacted by this event.

Table 65 – March 16

Chart 250: March 16, 2018 MED

Note: The number of customer outages segmented by hourly restoration periods requires a level of detail not normally maintained by PG&E in its central computerized records.  The information shown here is what PG&E has been able to reconstruct from several databases and may have a margin of error of up to 5%.

### July 28, 2018 Major Event Day

Table 66 below indicates the number of customers without service at periodic intervals for this event (07/28/2018).  The numbers of customers noted in the table are for only those divisions impacted by this event.

Table 66 – July 28

Chart 251: July 28, 2018 MED

Note: The number of customer outages segmented by hourly restoration periods requires a level of detail not normally maintained by PG&E in its central computerized records.  The information shown here is what PG&E has been able to reconstruct from several databases and may have a margin of error of up to 5%.

### October 14, 2018 Major Event Day

Table 67 below indicates the number of customers without service at periodic intervals for this event (10/14/2018).  The numbers of customers noted in the table are for only those divisions impacted by this event.

Table 67 – October 14

Chart 252: October 14, 2018 MED

Note: The number of customer outages segmented by hourly restoration periods requires a level of detail not normally maintained by PG&E in its central computerized records.  The information shown here is what PG&E has been able to reconstruct from several databases and may have a margin of error of up to 5%.

### November 8, 2018 Major Event Day

Table 68 below indicates the number of customers without service at periodic intervals for this event (11/8/2018).  The numbers of customers noted in the table are for only those divisions impacted by this event.

Table 68 – November 8

Chart 253: November 8, 2018 MED

Note: The number of customer outages segmented by hourly restoration periods requires a level of detail not normally maintained by PG&E in its central computerized records.  The information shown here is what PG&E has been able to reconstruct from several databases and may have a margin of error of up to 5%.

### November 21 Major Event Day

Table 69 below indicates the number of customers without service at periodic intervals for this event (11/21/2018).  The numbers of customers noted in the table are for only those divisions impacted by this event.

Table 69 – November 21

Chart 254: November 21, 2018 MED

Note: The number of customer outages segmented by hourly restoration periods requires a level of detail not normally maintained by PG&E in its central computerized records.  The information shown here is what PG&E has been able to reconstruct from several databases and may have a margin of error of up to 5%.

### November 29 Major Event Day

Table 70 below indicates the number of customers without service at periodic intervals for this event (11/28/2018).  The numbers of customers noted in the table are for only those divisions impacted by this event.

Table 70 – November 28

Chart 255: November 28, 2018 MED

Note: The number of customer outages segmented by hourly restoration periods requires a level of detail not normally maintained by PG&E in its central computerized records.  The information shown here is what PG&E has been able to reconstruct from several databases and may have a margin of error of up to 5%.

# Historical Ten Largest Unplanned Outage Events for 2008-2017

Table 71 - Ten Largest 2017 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service | CPUC Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | A series of atmospheric river storm events impacted the territory with heavy rain and strong south winds. Extensive damage occurred on the Central Coast where Salinas Airport recorded a gust to 69 mph. This was caused by a rapidly intensifying area of low pressure, also known as ‘bombogenesis’. | 02/17/2017 – 02/22/2017 | 732,590 | 235 | 3,496 Total 3,186 PG&E 310 Mutual Assistance | Y (except Feb 19) |
| 2 | Another winter storm series comprised of three storms impacted the territory from 1/18 – 1/23 with heavy rain, mountain snow, and strong south winds. | 1/18/2017 – 1/23/2017 | 653,502 | 170 | 3,274 Total 3,151 PG&E 123 Mutual Assistance | Y |
| 3 | A vigorous storm produced significant damage across the territory on 1/8/17 due to a combination of very heavy rain and strong south winds. The heavy rain resulted in flooding along rivers, creeks, and streams. A second strong winter storm impacted the territory 1/10/2017 to 1/11/2017. | 1/8/2017 – 1/11/2017 | 560,246 | 450 | 3,357 Total 3,180 PG&E 177 Mutual Assistance | Y |
| 4 | A strong and dynamic winter storm impacted the territory 4/6 to 4/7 and produced significant outage activity. The storm was the most impactful April storm in the 22+ year PG&E outage record (back to 1995). This storm put the capstone on the wettest water year in PG&E’s history. | 4/6/2017 – 4/7/2017 | 249,024 | 328 | 1,945 | Y |
| 5 | October wildfires | 10/8/2017 – 10/9/2017 | 211,812 | 587 | 2,336 Total 2,125 PG&E 211 Mutual Assistance | Y |
| 6 | A winter storm brought heavy rain and gusty southerly winds through the northern two thirds of the service area, causing significant outage activity | 2/7/2017 | 146,210 | 127 | 2,103 | Y |
| 7 | An offshore wind event developed across the northern two thirds of the territory and produced wind gusts up to 45 mph across lower elevations. Multiple Red Flag Warnings were posted. | 12/16/2017 | 112,218 | 59 | 1,385 | Y |
| 8 | A winter storm moved in the territory and produced considerable outage activity due to rain, gusty south winds, and mountain snow | 1/3/2017 – 1/4/2017 | 102,123 | 172 | 1,227 | Y (except Jan 4) |
| 9 | This event was not weather related. Bad breaker at Larkin Sub in San Francisco. | 4/21/2017 | 93,863 | 13 | 220 | Y |
| 10 | A weather system moved into the territory from the Pacific and generated wind and rain-related outage activity | 10/20/2017 | 70,839 | 101 | 499 | Y |

* Note:  Values exclude planned outages

Table 72 - Ten Largest 2016 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service | CPUC Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | A strong winter storm passed through northern and central CA producing strong south winds of 30 - 50 mph across the lower elevations and 60+ across the exposed higher terrain, as well as moderate to heavy rain. A strong squall line nearly 200 miles long developed in the Sacramento Valley. | 3/5/2016 – 3/7/2016 | 266,173 | 87 | 2,405 | Yes (Mar 5th) |
| 2 | A series of three storms impacted northern and central CA with periods of moderate to heavy rain and gusty south winds. Some locations saw rain totals near 10 inches and gusts 50+ mph were also observed. | 10/14/2016 – 10/16/2016 | 255,680 | 59 | 1,553 | Yes (Oct 14th) |
| 3 | A dynamic weather system moved through the PG&E territory late Wednesday into Thursday with strong south winds. Wind gusts were generally 25 - 40 mph across the Sacramento and northern San Joaquin valley, but very strong gusts to 50 - 60 were observed over the Sierra foothills. | 2/17/2016 – 2/18/2016 | 166,492 | 46 | 1,292 | Yes (Feb 17th) |
| 4 | A weather system produced breezy northwest winds 25 – 35 mph with gusts to 50 mph in some locations. Thunderstorms were also reported in the Sacramento, San Joaquin Valleys and the Sierra foothills. | 4/24/2016 – 4/25/2016 | 96,897 | 24 |  | No |
| 5 | Tropical moisture interacted with a Pacific weather system and associated cold front to wring out significant rain across the PG&E territory. 4 – 7 inches of rain were observed along with wind gusts from 20 – 40+ mph. | 12/15/2016 – 12/16/2016 | 91,581 | 38 |  | No |
| 6 | Generally fair and seasonably cool weather was observed across the PG&E territory. | 6/16/2016 | 82,691 | 15 |  | No |
| 7 | A winter storm brought moderate to heavy rain showers, prompting flash flood watches for recent burn scars (e.g., Rim, King, Butte). | 1/5/2016 – 1/6/2016 | 79,600 | 44 |  | No |
| 8 | A very wet weather system produced considerable rain across central CA. 24 hours rain totals topped 6 inches in the wettest locations in the Sierra Nevada. | 12/10/2016 | 77,546 | 56 |  | No |
| 9 | A winter storm and associated cold front pushed west to east across the territory today bringing moderate to heavy rain and gusty southeast winds 25 to 35 with higher gusts over elevated and exposed terrain | 3/11/2016 | 52,342 | 47 |  | No |
| 10 | A strong storm system across southern CA produced low elevation snow in the southern Sierra down to near 2500 ft. and gusty northwest winds from 30 – 40 mph. | 1/31/2016 | 48,120 | 52 |  | No |

* Note:  Values exclude planned outages

Table 73 - Ten Largest 2015 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service | IEEE Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | A series of strong Pacific storms moved into CA producing very heavy rain and gusty south winds. South wind gusts near 50 mph were observed along the coast with gusts near 60 mph observed in the northern Sacramento Valley. Generally 4 - 8 inches of rain were observed across the elevated terrain in the northern part of the territory. Some locations topped 8 inches with Bucks Lake for example, recording 9 inches of rain during the series. | 2/6/2015 - 2/8/2015 | 389,567 |  | 2836 | Yes |
| 2 | Tropical moisture associated with former Hurricane Dolores drifted over the territory. Atmospheric instability combined with the abundant tropical moisture initiated a widespread thunderstorm outbreak across the San Joaquin Valley and Central Coast. More than 6000 cloud to ground strikes were recorded. | 7/18/2015 - 7/19/2015 | 154,459 |  | 925 | Yes |
| 3 | A strong cold front (squall line) moved into the northern part of the territory and produced strong wind gusts, a period of very heavy rainfall, and significant outage activity. The front swiftly progressed south through the remainder of the territory. Widespread wind gusts from 40 - 55 mph were observed across the Sacramento Valley and Redding recorded a gust near 60 mph. | 12/13/2015 | 142,059 |  | 364 | Yes |
| 4 | A late winter-storm moved through the territory producing moderate rain showers, gusty south winds from 30 - 40 mph, and thunderstorms. Nearly 1000 cloud to ground lighting strikes were recorded across the Sacramento and San Joaquin Valleys | 4/6/2015 - 4/7/2015 | 134,789 |  | 442 | Yes |
| 5 | A strong high pressure ridge developed over the territory and produced the first significant heat of the season. Some selected high temperature readings: Redding 107, Fresno 106, Livermore 106, Sacramento 104, Santa Rosa 99, and San Jose 91. | 6/8/2015 | 99,439 |  | 1104 | Yes |
| 6 | The first widespread rain and snow producing system of the fall/winter season passed through the territory. Thunderstorms also developed and near 500 cloud to ground lightning strikes were recorded. Wind gusts from 25 - 35 mph were observed. | 11/2/2015 | 92,777 |  | 33 | No |
| 7 | A large transmission outage in the central coast at Moss Landing occurred. No significant adverse weather was recorded. | 10/18/2015 | 69,906 |  | 1080 | No |
| 8 | A potent Pacific weather system produced wind gusts to 40 - 50 mph across the lower elevations with gusts near 60 - 70 mph across the exposed, higher terrain. Most of the adverse weather and resultant outage impacts were observed across the northern part of the PG&E service territory. | 12/10/2015 | 64,533 |  | 602 | No |
| 9 | A cold frontal system with moderate rain showers moved through the territory and was followed by gusty northwest winds primarily along the coast. Peak winds gusts from 40 - 50 mph were observed. | 11/15/2015 | 59,547 |  | 554 | No |
| 10 | An upper level weather system moved over the territory and produced rain showers, breezy winds, and thunderstorms. The PG&E lightning detection network recorded 456 lightning strikes in the territory. | 5/7/2015 | 57,241 |  | 1740 | No |

* Note:  Values exclude planned outages

Table 74 - Ten Largest 2014 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service (Major Events) ** | IEEE Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | The strongest storm event in more than 3 years slammed the territory with strong winds and heavy rain showers starting on 12/11. Rain and unsettled weather began Wednesday along the north coast and then a very strong cold front developed and intensified Wednesday evening and overnight into Thursday and very slowly progressed through the territory bringing very heavy rain and strong southerly winds. The gusty southerly winds reached up to 50 mph across the Santa Cruz mountains, near 70 mph across elevated Bay Area terrain, and near 120 mph across the Sierra Crest. Over 3 inches of rain fell across many Bay Area locations and over 2 inches for northern Central Valley by Thursday afternoon. | 12/11/2014 - 12/12/2014 | 467,394 | 77 |  | Yes |
| 2 | A strong but dry storm system originating from Western Canada dropped south through the Service Area and produced very strong north to northeast winds from Tuesday morning through early Wednesday. Gusts in excess of 60 mph were reported across the Bay Area elevated terrain and foothills across the Sierra Nevada. A strong mountain wave moved into San Jose division from the east, resulting in reported gusts above 50 mph in downtown San Jose. | 12/30/2014 – 12/31/2014 | 296,402 | 67 |  | Yes (Dec 30th) |
| 3 | A strong storm moved in from the southwest, bringing heavy rain and gusty southeast winds to many areas, especially the Central Coast and San Joaquin Valley. A secondary line of heavy showers with imbedded thundershowers developed over the San Joaquin Valley during the early afternoon hours, which caused significant outage activity. Wind gusts up to 47 mph were also observed across the lower elevations. | 2/28/2014 – 3/1/2014 | 167,137 | 55 |  | N |
| 4 | Two strong Pacific weather systems produced an impressive round of precipitation across the territory Tuesday and Wednesday. Accompanying the rain showers were breezy to gusty southerly winds that developed through the San Joaquin Valley and adjacent elevated terrain. Rainfall totals were 7 inches across the Santa Cruz Mountains and the Central Sierra and generally 2 - 4 inches across the lower elevations in the Bay Area. | 12/02/2014 – 12/04/2014 | 138,447 | 34 |  | Yes (Dec 3rd) |
| 5 | An “Atmospheric River” weather event delivered significant rain and high-elevation mountain snow to the territory. The abundant rain and gusty south winds to 40 mph at times produced a prolonged stretch of light to moderate elevated outage activity. Rain totals from the event were highest across the central Sierra and the north coast where 7 – 15 inches of rain fell during the event. | 2/7/2014 – 2/8/2014 | 102,832 | 35 |  | N |
| 6 | At 3:20 AM on Sun 8/24/2014 a magnitude 6.0 earthquake was observed in the North Bay Area near American Canyon, Ca. An earthquake summary poster from USGS can be found here: http://earthquake.usgs.gov/earthquakes/eqarchives/poster/2014/20140824.pdf | 8/24/2014 | 99,705 | 30 |  | Yes |
| 7 | A strong ridge of high pressure and lack of the marine layer and sea-breeze combined to produce hot temperatures for Bay Area interior valleys and across the interior. Maximum temperatures reached over 100 in Santa Rosa and Livermore on Sunday and up to 105 across the interior Central Valley. | 6/8/2014 – 6/9/2014 | 83,962 | 39 |  | N |
| 8 | A wet weather system delivered heavy rain across Northern California and the Sierra, along with moderate rain throughout the Bay Area. After the front moved through, thunderstorms developed and produced 331 lightning strikes within the PG&E territory. | 9/25/2014 | 61,597 | 23 |  | N |
| 9 | A weather system delivered the first widespread rain of the season south of a Salinas to Sonora line and also produced a northwest gust front down the San Joaquin Valley where gusts up to 40 mph were observed in Fresno and Bakersfield. | 10/31/2014 | 55,145 | 22 |  | N |
| 10 | The weather system with a very moist air mass slid through the Bay Area early Thursday morning and produced light showers and drizzly conditions that resulted in isolated significant outage activity in the east Bay Area. | 9/18/2014 | 39,860 | 17 |  | N |

* Note:  Values exclude planned outages.

** Note:  This data is requested only for Major Event days.

Table 75 - Ten Largest 2013 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service (Major Events) ** | CPUC Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | On 11/19 into 11/20, a weather system moved into the territory and delivered up to 2 inches of rain over elevated terrain. It was the first significant rain storm of the season. Then on 11/21 into 11/22 surface low pressure over southern California combined with developing high pressure in Nevada to deliver very strong north to northeast winds across the north half of the Service Territory. Winds were very strong over elevated terrain; wind gusts up to 65 mph were observed in the Oakland hills (Oakland North RAWS) and to 101 mph in the northern Sierra Nevada. (The wind gust at Oakland north was second only to the January 4th mega-storm gust of 71 mph). Wind speeds near 45 - 50 mph were also observed over lower elevation locations such as Oakland and Santa Rosa. | 11/19/2013 - 11/22/2013 | 385,017 | 143 |  | N |
| 2 | The marine layer surged onto the coast and delivered coastal mist and drizzle which ultimately resulted in an insulator flashover event. The event was preceded by a series of brisk wind events which may have increased salt contamination along the coast. | 6/23/2013 | 170,429 | 15 |  | N |
| 3 | Fair and dry weather was observed on 11/12/2013. An unplanned outage occurred in the Bellota substation. | 11/12/2013 | 113,266 | 10 |  | N |
| 4 | High pressure built over California and maximum temperatures from 99 - 107 were observed along the Central Valley. Temperature maximums near the coast were in the 60s to 70s with 70s - 90s for coastal to intermediate valleys. Most customers were impacted by trouble on the Transmission system. | 7/19/2013 | 99,738 | 18 |  | N |
| 5 | Overnight Sunday into the early morning hours of Monday April 8, 2013, a strong Pacific Jet Stream drove a small but intense cold front with very gusty northwest winds into the California coast and Bay Area. Gusts along the coast reached generally into the 50 - 60 mph range with the peak gust of 75 mph recorded at a station on the west edge of San Francisco County. | 4/8/2013 | 93,200 | 42 |  | N |
| 6 | A strong ridge of high pressure built over California bringing extreme heat to all locations except the coast and immediate coastal valleys. High temperatures on 7/1 near the coast ranged from the 70s - 80s with 90s - low 100s for coastal Valleys. Temperatures were extreme in the interior with maximum temperatures up to 111 in the Central Valley. The heat intensified on 7/2 where maximum soared again into the 100s, with Redding observing a 116-degree maximum. | 7/1/2013-7/2/2013 | 93,194 | 29 |  | N |
| 7 | On Sunday a weak area of low pressure moved west to east through the Territory bringing increasing clouds, light showers and snow showers over the Sierra and a few light stray showers elsewhere, primarily across the south. Most customers were impacted by a fault on a substation relay. | 3/3/2013 | 69,578 | 11 |  | N |
| 8 | A classic California October offshore wind event unfolded 10/3/2013 as surface high pressure built north of the Service Territory. Wind speeds were generally 20 – 35 mph with gusts to 40 – 55 across the Sacramento valley, northern Sierra Nevada and elevated terrain around the Bay Area. | 10/3/2013 | 56,573 | 25 |  | N |
| 9 | The ridge of high pressure dramatically amplified delivering significant heat across the Territory. Maximum temperatures across the interior valley locations reached above 105 with Red Bluff reaching 112 degrees. Overnight temperatures remained warm on the far ends of the valley, with minimum temperatures only dipping into the upper 70s in the southern San Joaquin and mid 80s in the northern Sacramento Valley. | 6/8/2013 | 52,442 | 22 |  | N |
| 10 | A cold and dynamic weather system dropped southwestward into the territory and brought cooler and very unsettled weather in the form of rain, snow and gusty winds. Winds were strongest over elevated terrain of the Bay Area – Altamont pass gusted to 69 mph. | 10/27/2013 | 49,692 | 36 |  | N |

* Note:  Values exclude planned outages.

** Note:  This data is requested only for Major Event days.

Table 76 - Ten Largest 2012 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service (Major Events) ** | CPUC Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | The final and strongest storm of an ‘Atmospheric River’ series moved through the territory on 12/02/2012 delivering widespread gusts of 50-70 mph in the northern Sacramento Valley. The strongest wind observed was in Plumas National Forest where a gust of 102 mph was recorded. This system also brought heavy amounts of rain across northern California where localized flooding and mudslides were reported in numerous locations. Precipitation totals from the entire series (See Rank #3) topped 20 inches in the wettest locations in the north. | 12/02/2012 | 298,393 | 80 |  | N |
| 2 | A series of moderate to strong storms impacted the Service Area delivering rain, wind, thunderstorms and several feet of snow across the northern mountains and Sierra. The second storm in the series moved onto the Humboldt coast during the evening of 12/21 and then progressed south and east through the territory overnight into 12/22. The third and strongest storm of the series developed just off the coast and pushed a vigorous cold front through the Service Area on 12/23. Gusts up to 80 mph were observed over elevated terrain. Yet another round of heavy mountain snow fell across the north and the Sierra. Up to 6 feet of snow fell in some locations across the north during the series making restoration difficult. | 12/21/2012 – 12/23/2012 | 195,099 | 172 |  | N |
| 3 | The first storm of the ‘Atmospheric River’ series moved into the territory on 11/28 and delivered strong south winds up to 50-60 mph and heavy rains. The second and stronger system impacted the Territory 11/29 through 11/30. This system brought significant rainfall totals across the north half of the Territory with up to 10” observed in the wettest locations across elevated terrain. After a brief break on 12/1 the final and strongest storm of the series moved through on 12/2 (see Rank 1). | 11/28/2012 – 11/30/2012 | 183,145 | 71 |  | N |
| 4 | On 1/20 a strong Pacific weather system with an associated well-organized frontal band pushed north to south through the territory. This system delivered heavy rains and gusty southerly winds to most locations and was the first rain in a month or more for many locations across the south half of the territory. | 1/20/2012 – 1/21/2012 | 168,496 | 40 |  | N |
| 5 | On 3/16 a system impacted Northern Region and the Bay Area with heavy showers, gusty southerly winds, and a few lightning strikes. On 3/17 this system progressed south through Central Coast and Central Valley Divisions bringing heavy rains, thunderstorms and gusty winds. On 3/18, snow levels fell as cold air filtered in resulting in low snow outage activity from Grass Valley south into Fresno division. | 3/16/2012 – 3/18/2012 | 146,602 | 63 |  | N |
| 6 | Overnight Sunday, 10/21/2012 into Monday, 10/22/2012 a cold front associated with a unusually cold, early-season storm swept west to east across the PG&E Service Area bringing a variety of adverse weather including rain, wind, thunderstorms and low snow. Two tornados also formed in the eastern Sacramento Valley and Sierra foothills. | 10/22/2012 | 129,801 | 22 |  | N |
| 7 | A vigorous late season weather system swept through the Service Area on 6/4 – 6/5 and brought a variety of adverse weather conditions. This system delivered over 700 lightning strikes across the Service Territory with the majority occurring in the northern Sacramento Valley. Winds gusting to 40 mph came up abruptly in the San Joaquin causing numerous wind related outages. | 6/4/2012 – 6/5/2012 | 93,735 | 22 |  | N |
| 8 | On 12/17 a weakening front moved through the Service Area bringing rain showers and breezy southerly winds up to 35-40 mph across the Sacramento Valley. Showers progressed into the southern San Joaquin overnight into 12/18. Post-frontal northwest winds then developed across the San Joaquin Valley, with gusts up to 35 mph observed at Fresno. | 12/17/2012 – 12/18/2012 | 83,063 | 18 |  | N |
| 9 | A Pacific storm system and associated cold front and swept through the north half of the PG&E Service Area. The front brought brisk south winds of 30 to 40 mph, with higher gusts over elevated terrain. During the afternoon, thunderstorms formed along the north coast and northern Sacramento Valley in the post-frontal environment. | 3/31/2012 | 68,165 | 21 |  | N |
| 10 | Non-weather-related event. | 7/21/2012 | 47,182 | 30 |  | N |

* Note:  Values exclude planned outages.       ** Note:  This data is requested only for Major Event days.

Table 77 - Ten Largest 2011 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service (Major Events) ** | CPUC Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | A series of cold and powerful storms moved through the Service Area with the majority of outages resulting from low snow and gusty winds. The bulk of outage activity occurred overnight Sat 19th to Sun 20th as strong southeasterly wind gusts were observed in many locations (SF Apt 45 mph, Stockton 44 mph, Redding 45 mph, Bakersfield 40 mph). Excessive low elevation snowfall caused significant outage activity. Yosemite Division was hard hit with low snow (snow totals - 38” reported at 4200’ above Oakhurst) | Mar 17 -22 | 581,949 | 256 | 1,839*** | Y-Partial (See Table 4) |
| 2 | After a short respite from inclement weather, another strong and cold storm moved into the Service Area on March 24th. Once again, strong southerly wind gusts were observed (SF Apt 38 mph, Oakland 37 mph). Low elevation snow was the main adverse weather issue with Sierra, North Valley, Stockton, and Yosemite Divisions hard hit with low snow. (snow totals - 13” in Shingletown, 25” at 3700’ along Highway 88, 34” at the 4200’ above Oakhurst) | Mar 24 – 27 | 464,767 | 504 | 1,839*** | Y-Partial (See Table 4) |
| 3 | A series of cold storms moved across the Service Area starting Valentine’s day until Feb 19. On the 17th very cold air filtered into the region lowering snow levels enough to create low snow related outages across the Coast Ranges of Humboldt Divisions, and down the entire Sierra Nevada foothills. The hardest hit divisions were Humboldt, Yosemite, and Sierra. (Snow totals - 14” in Shingletown, 38” at 3700’ on Highway 88, 12” at 2600’ in Humboldt County). Snow recorded down to 500 feet in Humboldt. | Feb 15 – 19 | 357,802 | 151 |  | N |
| 4 | High pressure in the Great Basin and low pressure off the southern California coast set the stage for strongest northeast wind event to hit the Service Area in the last 20 years. Gusts up to 50 mph were common in the Sierra with the highest gust of 94 mph recorded on Mt. Elizabeth in the Yosemite division. Winds were quite strong in the Valley as well (Stockton 52 mph, Redding 40 mph, Fresno 36 mph) | Nov 30 – Dec 1 | 325,942 | 131 |  | N |
| 5 | A strong and cold storm affected the entire Service Area with low snow falling in the Northern Region and gusty southerly winds and heavy rains further east and south. The hardest hit divisions were Humboldt, North Valley, and Sierra. (Snow totals – 18” in Shingletown, 20” in Susanville, 19” in Grass Valley). Snow recorded down to 500 feet in Humboldt. | Feb 24 - 25 | 187,851 | 152 |  | N |
| 6 | An early season storm moved through the Service Area bringing moderate southerly winds and heavy precipitation rates. In Ukiah, more than a half inch of rain fell within one hour in the early morning. The Central Valley Region experienced the most outages. These were mainly pole fires/flashover caused by the first rain to fall in the area after months of prolonged dry weather. | Oct 5 | 100,357 | 24 |  | N |
| 7 | Widespread thunderstorm activity broke out across the southern part of the Service Area early in the morning with the biggest impacts in Fresno and Kern divisions. The Bakersfield area in Kern was hit particularly hard by lightning, with Kern Division recording 3833 lightning strikes for the day. | Sept 10 | 77,443 | 69 |  | N |
| 8 | A late season cold storm moved through the Service Area with low snow outage conditions across divisions in the Sierra Nevada, especially the Sierra Division. (8” of snow at 3700’ along Highway 88) Thunderstorms and associated lightning also broke out across the Central Valley. Impacts were minimal in the Bay Area and Central Coast Regions. | May 15 | 62,863 | 30 |  | N |
| 9 | A non-weather-related outage day with maximum temperatures along the Central Valley in the mid-80s. The outage count was only slightly above average for a June day; however, a large number of customers in the East Bay were affected by two distribution substation outages. | Jun 12 | 50,028 | 15 |  | N |
| 10 | The first warm day of the spring was observed in many areas. San Jose had a high of 84. This could have contributed to the above average outage total. No other adverse weather was reported. The largest impacts were recorded in the San Francisco and San Jose Divisions. | Apr 1 | 44,177 | 6 |  | N |

* Note:  Values exclude single distribution line transformer and planned outages.        ** Note:  This data is requested only for Major Event days.

*** Note: During the course of the March 17-27, 2011 storms, approximately 1,839 PG&E Operations, Maintenance and Construction (OM&C) employees responded.  These employees included electric and gas construction crews, troublemen, meter technicians, clerical staff, gas and electric estimators and meter readers.  Resources were dispatched and moved from lesser impacted areas to the more heavily impacted areas.  In addition to PG&E personnel, 110 vegetation crews, 10 contract crews (approximately 200 individuals), and 36 mutual aid crews (approximately 175 individuals) were utilized to supplement existing resources.

Table 78 - Ten Largest 2010 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service (Major Events) ** | CPUC Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | A strong jet stream developed over the Eastern Pacific, which spawned a series of outage producing weather events that included: - Three impulses of strong winds; gust above 50 mph each day (Jan 18, 19, 20) - Periods of moderate to heavy rainfall (Jan 18, 19, 20, 21) - Bands of thundershower activity (several thousand strikes Jan 18-21) - Heavy snowfall at low elevations of the Sierra Nevada (Jan 21, 22) | Jan 18-24 | 1,169,513 | 497 | 3,830 *** | Y |
| 2 | A strong storm system with several impulses moved through the entire Service Area during the Dec 17 – 20 period bringing gusty winds and heavy rain. Wind gusts during the period: 43 mph at Stockton, 43 mph at Salinas, 46 mph at SFO, 43 at Red Bluff. | Dec 17-20 | 215,116 | 120 |  | N |
| 3 | A series of cold storms brought significant snow to low elevations in the Sierra Nevada foothills. The snow came early in the season, when deciduous trees still retained most of their leaves. Excessive snow loading occurred on trees causing large limbs to break off and fall onto power lines. Snowfall amounts ranged from near 1 foot at the 3000’ elevation, to several feet above 5000’. This storm produced the most low elevations snow in November in the last 15 years. | Nov 20-21 | 215,245 | 186 |  | N |
| 4 | Storm system with strong south winds on Dec 28 (gusts to 47 mph at Marysville, 41mph at Stockton, 46 mph SFO) followed by strong northwest winds on Dec 29 (gusts to 46 mph at San Jose, 41 mph at Stockton, 43 at Bakersfield, 46 mph at SFO). | Dec 28-29 | 180,370 | 47 |  | N |
| 5 | A late season storm brought rain, thunderstorms, and wind. Over 500 lightning strikes were recorded. The storm was particularly strong along the Central Coast and in the southern San Joaquin Valley. Reported wind gusts: 45 mph at Salinas, 46 mph at Santa Maria, 46 mph at Bakersfield 46. | Apr 11-12 | 122,050 | 73 |  | N |
| 6 | Early season storm brought thunderstorms to Northern Region (over 1000 strikes recorded) along with rain to other parts of the Service Area. In many cases, this was the first rain of the season causing flashover outages. | Sep 8-10 | 114,402 | 60 |  | N |
| 7 | An early season storm brought high winds and heavy rain to primarily the Northern Region. Redding recorded a peak wind gust of 49 mph. Santa Rosa recorded 4.75” of rainfall. | Oct 24 | 111,522 | 43 |  | N |
| 8 | Storm system swept across the Service Area bringing rain and gusty winds. Reported wind gusts: 41 mph at Salinas, 41 mph at Bakersfield. | Dec 4-5 | 98,041 | 21 |  | N |
| 9 | Heat wave conditions resulted in the hottest two days of the summer. Maximum temperatures exceeded 110 in portions of the Central Valley (111 at Bakersfield on 8/25). Maximum temperatures between 100 and 110 were reported both days at many coastal valley areas (109 at Ukiah on 8/25, 107 at Santa Rosa on 8/24, 105 at Livermore on 8/25). | Aug 24-25 | 97,616 | 82 |  | N |
| 10 | Heat wave affected the service area, on both days Central Valley maximum temperatures ranged between 100 and 110; maximum temperatures above 100 were reported in coastal valleys on 6/27. | Jun 27-28 | 87,751 | 38 |  | N |

* Note:  Values exclude single distribution line transformer and planned outages.

*** Note:  This data is requested only for Major Event days.

*** Note: During the course of the January 18, 2010 Storm approximately 3,830 PG&E Operations, Maintenance and Construction (OM&C) employees responded.  These employees included electric and gas construction crews, troublemen, gas service representatives, meter technicians, clerical staff, gas and electric estimators and meter readers.  Resources were dispatched and moved from lesser areas to the more heavily impacted areas.  In addition to PG&E personnel, 1000 vegetation workers and 60 contract crews (approximately 360 individuals) were utilized to supplement existing resources.

impacted areas to the more heavily impacted areas.  In addition to PG&E personnel, 1000 vegetation workers and 60 contract crews (approximately 360 individuals) were utilized to supplement existing resources.

Table 79 - Ten Largest 2009 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service (Major Events) ** | CPUC Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | A strong early season storm affected the entire service area with many stations reporting wind gusts over 50 mph (57 mph at Ft. Funston (SF), 56 mph at Fairfield, 55 mph at Oroville, 51 mph at Monterey). Single day rainfall totals ranged between two and five inches at many locations (4.54 in. at Watsonville, 4.27 in. at Fairfield, and 3.66 in. at Napa). National Weather Service records indicate this storm was the strongest October rain and wind event since 1962. | 10/13–10/14 | 617,589 | 244*** | 4,400 **** | Y |
| 2 | A strong cold front produced significant snowfall on Feb. 13 in the 1500-3000 ft. range of the northern and central Sierra foothills (up to 2 feet of snow at 3000 ft. and @ 1 foot at 2000 ft.). A second storm followed on Feb.15 producing widespread heavy rain and strong wind gusts to the entire Service Area (67 mph at Valley Ford, 59 mph at Oroville, 50 mph at Redding, and Ft. Funston (SF), 47 mph at Salinas, 43 mph at San Luis Obispo. A third storm on Feb 16 delivered additional rainfall and wind gusts in the 30 to 40 mph range at several locations. | 2/13-2/17 | 340,582 | 107 |  | N |
| 3 | A large cluster of thunderstorms produced widespread lightning activity in the Bay Area and Sacramento Valley on Sep. 12. The lightning activity was followed by a weak weather front the next day that produced the first light rain of the season over much Northern California resulting in flashover related outages. | 9/12-9/14 | 190,671 | 92 |  | N |
| 4 | A strong cold front produced significant snowfall at the 1000-3000 ft. range of the Sierra foothills (up to 2 feet of snow was observed at 3000 ft., @ 1 foot at 1500 ft.) Light snow was reported at locations in the Central Valley. | 12/7 | 147,630 | 113 |  | N |
| 5 | Strong northerly winds developed across the entire Service Area with the gusts in the 45 to 55 mph range in the Bay Area and Sacramento Valley (52 mph at Fairfield, 49 mph at Sacramento, 45 mph at Red Bluff) | 11/28 | 119,504 | 84 |  | N |
| 6 | Strong north to northwest winds in the 40 to 60 mph range followed the passage of a weak weather front through the service area (58 mph at Ft. Funston (SF), 58 mph at SF Airport, 50 mph at San Carlos, 46 mph at Stockton) | 4/14 | 116,406 | 45 |  | N |
| 7 | An area of low pressure produced a large outbreak of thunderstorms with widespread lightning overnight on Jun. 3, continuing into the morning of June 4. | 6/3-6/4 | 98.187 | 38 |  | N |
| 8 | Strong north to northwest winds in the 45 to 55 mph range were recorded throughout the Sacramento and San Joaquin Valleys following the passage of a weak weather front (52 mph at Merced, 49 mph at Stockton, 47 mph at Modesto and Madera, 46 mph at Red Bluff, 45 mph at Fresno). | 10/27 | 70,901 | 20 |  | N |
| 9 | A winter storm accompanied by periods of moderate to heavy rainfall and scattered thundershower activity crossed the service area. Rainfall totals of up to 2 inches were reported. | 12/12 | 54,111 | 41 |  | N |
| 10 | Widespread thunderstorm activity resulted in several hundred lightning strikes in Areas 4, 5, 6 and 7. | 5/28 | 52,705 | 22 |  | N |

* Note: Values exclude single distribution line transformer and planned outages.

** Note: This data is requested only for Major Event days.

*** Note: This duration was due to the lack of access caused by flooding in the Stockton area.  Access was granted after waters receded.  Work was the completed and service was restored to the six customers remaining out of service.

**** Note: Approximately 4,400 PG&E Operations, Maintenance & Construction (OM&C) employees responded. In addition to PG&E personnel, 400 vegetation workers and 42 contract crews (approximately 210 individuals) were utilized to supplement existing resources.

Table 80 - Ten Largest 2008 Outage Events

| Rank | Description | Date | Number of Customers Affected * | Longest Customer Interruption (Hours) | # of People Used To Restore Service (Major Events) ** | CPUC Major Event? |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Strongest storm system since December 1995 affected the entire service area on Jan 4. Wind gusts exceeded 65 mph at many low elevation sites throughout the service area (Redding 70 mph, Beale AFB 69 mph, Sacramento Apt. 66 mph, Pt. San Pablo 83 mph), with some coastal hills and foothill sites gusting to over 80 mph (Los Gatos, elev. 2000 ft. 105 mph, Big Rock Marin Co. elev. 1500 ft. 83 mph). Rainfall totals on Jan 4 ranged up to 4 inches with storm totals above 6 inches in the North Bay counties. Multiple lightning strikes were reported on Jan 4 and 5. | 1/3 – 1/6 | 1,631,765 | 290 | 7,130 *** | Y |
| 2 | A series of cold winter storms crossed the state. The first system (Jan 24-25) delivered gusty winds (generally in the 30 to 50 mph range), up to 2 inches of rain and snow below 2000 ft. A second system focused on the southern half of the service territory brought additional rain and thundershower activity along with even gustier winds (Santa Maria 67 mph, Bakersfield 49 mph). | 1/24 – 1/27 | 303,168 | 172 |  | N |
| 3 | A storm system with wind gusts in the 25 to 40 mph range crossed the state. Most locations reported under one inch of rain with a few coastal stations reaching two inches total. | 10/31 – 11/1 | 189,811 | 50 |  | N |
| 4 | The first rains of the winter season were accompanied by winds generally gusting from 25 to 35 mph (Red Bluff 44 mph). A large number of flashover incidents were likely triggered by the combination of light rain and power lines heavily sooted after the widespread summer season wildfires. | 10/3 – 10/4 | 147,703 | 65 |  | N |
| 5 | Gusty winds with periods of moderate rain accompanied a weather system that crossed the state. Wind gusts were generally in the 30 to 50 mph range (SF Airport 47 mph, Stockton 47 mph, Merced 45 mph). | 2/2 – 2/3 | 121,865 | 65 |  | N |
| 6 | Gusty winds from this storm were strongest in the southern half of the service area. Gusts between 50 and 55 mph were reported at SF Airport, Salinas, Santa Maria, Red Bluff and Bakersfield. | 2/23 – 2/24 | 113,086 | 101 |  | N |
| 7 | A weather front brought gusty winds and periods of moderate to heavy rain to the state. Post-frontal west to northwest wind gusts were strongest in the Bay Area (SF Apt 54 mph, Hayward 63 mph, Oakland 47 mph, Salinas 51 mph) | 12/25 | 111,134 | 102 |  | N |
| 8 | Gusty north winds generally in the 25 to 35 mph range were reported in the north. San Joaquin and Central Coast winds gusted from 30 to over 50 mph (Santa Maria 41 mph, Stockton 45 mph, Madera 52 mph, Merced 47 mph) | 5/22 | 105, 635 | 102 |  | N |
| 9 | Gusty north winds developed on the evening of Feb 13 and continued through Feb 14. Winds were generally in the 30 to 45 mph range, with strongest gusts in the Central Valley (Redding 48 mph, Marysville 48 mph, Sacramento 47 mph) | 2/13 – 2/14 | 98,788 | 47 |  | N |
| 10 | Gusty north winds between 20 and 35 mph resulted in a record breaking early season heat wave. Bay Area and Central Valley temperatures ranged from 100 to 105F | 5/15 | 84,659 | 28 |  | N |

* Note: Values exclude single distribution line transformer and planned outages.

** Note:  This data is requested only for Major Event days.

*** Note: Approximately 6,000 PG&E Operations, Maintenance & Construction (OM&C) employees responded. In addition to PG&E personnel, 300-350 vegetation crews (approximately 700 individuals), 70 contract crews (approximately 450 individuals) and 28 mutual assistance crews (approximately 170 individuals) from Southern California Edison (SCE), San Diego Gas and Electric (SDG&E), City of Gridley, City of Redding, and Sierra Pacific Power were utilized to supplement existing resources

# The Number of Customer Inquiries on Reliability Data and the Number of Days per Response

The following table provides the total number of customer inquiries, and PG&E response times for the year 2018.

Note: ESR = Electric Service Reliability (Recurring Outages).  This Includes ESR cases created on or after January 1, 2018 and closed as of December 31, 2018.

# Appendix A – Definitions, Acronyms & Abbreviations

AIDI – Average Interruption Duration Indices

AIFI – Average Interruption Frequency Indices for sustained outages only

Customer: A metered electrical service point for which an active bill account is established at a specific location.

CAIDI: Customer Average Interruption Duration Index - The Customer Average Interruption Duration Index (CAIDI) represents the average time required to restore service.

CESO:  A term that counts the number of Customers Experiencing Sustained Outages.

DART – Distribution Asset Reconciliation Tools – a distribution asset database used by PG&E.

Distribution system: That portion of an electric system that delivers electric energy from transformation points on the transmission system to the customer.  PG&E defines its distribution system as line voltage less than 60 kilovolts (KV).  The distribution system is generally considered to be anything from the distribution substation fence to the transformer prior to stepping down the voltage to the customer premise.

EON:  EON stands for Enhanced Outage Notification, now retired, that was used to identify and record momentary outages.  Customers agreed to put EON devices in their homes and the device would send PG&E information when the customer experienced and outages.  The EON project was used prior to the availability of Smart Meter data.

IEEE – Institute of Electrical and Electronics Engineers, Inc.

ILIS – Integrated Logging and Information System – The tool PG&E’s distribution operators use to log electric outages.

ISO:   The California Independent System Operator.  The ISO operates the transmission system throughout most of the State of California, including throughout PG&E’s service territory.

Major Event: Designates an event that exceeds reasonable design and or operational limits of the electric power system. A Major Event includes at least one Major Event Day. See also: Major Event Day.

Major Event Day (MED): A day in which the daily system, System Average Interruption Duration Index (SAIDI) exceeds a Major Event Day threshold value. For the purposes of calculating daily system SAIDI, any interruption that spans multiple calendar days is accrued to the day on which the interruption began.

MAIFI: Momentary Average Interruption Frequency Index

The Momentary Average Interruption Frequency Index (MAIFI) indicates the average frequency of momentary interruptions.  PG&E’s momentary outage reporting tools were originally designed to track momentary outages based on D96-09-045.  As provided in D.16-01-008, the provided MAIFI metric is the same as what PG&E has used in its prior annual reliability reports and corresponds to the MAIFIE definition contained in the IEEE Guide for Electric Power Distribution Reliability Indices (IEEE 1366 standard), which counts multiple outage interruptions that occur close to each other in time as a single momentary outage event.  This metric is equal to the total number of customer momentary interruption events divided by the total number of customers served and does not include the events immediately preceding a sustained interruption.

Momentary interruption: The brief (five minutes or less) loss of power delivery to one or more customers caused by the opening and closing operation of an interrupting device.

Non-Restorable Outage Process – PG&E utilizes a non-restorable outage designation and process for unique outage events involving requests by customers or agencies requiring that facilities be de-energized, access not permitted, and/or restoration be delayed due to circumstances not initiated or controlled by PG&E.  This process includes adjusting the outage minutes to accurately reflect these situations and to measure PG&E’s actual true performance.

ODB – Operations Database - ODB is the outage database for PG&E

Planned outage: The intentional disabling of a component’s capability to deliver power, done at a preselected time, usually for the purposes of construction, preventative maintenance, or repair.

SAIDI: System Average Interruption Duration Index

The System Average Interruption Duration Index (SAIDI) indicates the total duration of interruption for the average customer during a predefined period of time. It is commonly measured in minutes or hours of interruption.

SAIFI: System Average Interruption Frequency Index

The System Average Interruption Frequency Index (SAIFI) indicates how often the average customer experiences a sustained interruption over a predefined period of time.

SCADA:  Supervisory Control and Data Acquisition – an online database for distribution operators to remotely gather information and control the distribution system.

Sustained interruption: Any interruption not classified as a part of a momentary event. That is, any interruption that lasts more than five minutes.

Unplanned interruption: The loss of electric power to one or more customers that does not result from a planned outage.

See Table 57 as shown in Section 3.

PG&E’s outage reporting tools were originally designed to track momentary outages as defined in D96-09-045.  Under D.16-01-008, this method of tracking momentary outages corresponds to the MAIFIE definition contained in the IEEE Guide for Electric Power Distribution Reliability Indices (IEEE 1366 standard), which counts multiple outage interruptions that occur close to each other in time as a single momentary outage event.  This metric is equal to the total number of customer momentary interruption events divided by the total number of customers served and does not include the events immediately preceding a sustained interruption.

Measures sustained outage events and excludes momentary outage events.

On November 18, 2011 the EON recording system was removed from service.  Momentary outage data is now being collected from SCADA devices and through the use of Smart Meters.  Data collection from the Smart Meters is more effective than the previous EON system since Smart Meters don’t rely on customer volunteers having EON devices connected inside their buildings.   The increased frequency of momentary outages recorded does not necessarily indicate an actual increase in momentary outages in 2012 and after (as compared to prior years) but is a result of this improved method for recording momentary outages.

See footnote 4.

As in prior reports, PG&E does not interpret this reporting requirement as applying to those indices where 2018 reliability was better than the prior five-year average.

Per Decision 16-01-008, Appendix B footnote 6, Decision 04-10-034 only applies to PG&E:

Investigate and report on all weather-related excludable major events for each division in which CAIDI varies by 25 percent or more from the division benchmark.  The division benchmarks are calculated from the rolling average of the prior 10 weather-related excludable events as defined by IEEE 1366.

A major event is defined in the IEEE Standard 1366.  As in prior reports, PG&E is using the “prior ten weather related excludable major events” prior to the calendar year that is the subject of the report.

May 17th was a non-weather-related MED (outage due to a vehicle hitting a 230 kV tower).

See footnote 4.

See footnote 4 above.

The three-year average AIFI values are determined by the three-year average of the customers that experienced a sustained outage divided by the three-year average of the total customers served by that circuit.  The three-year average AIDI values are determined by the three-year average of the customer-outage minutes divided by the three-year average of the total customers served by that circuit.  These calculations are slightly different than determining the three-year average of just the actual recorded metric values for each of the three years.

The circuit mileage data in this report is determined through the use of PG&E’s Electric Distribution Geographic Information System (EDGIS).  PG&E recently expanded the use of its EDGIS technology to map and analyze assets across its system and provide more accurate information about the expanse of its system and the mileage of particular circuits.  As a result of using this more accurate technology, mileages for particular circuits may vary from prior reports.