## Readme
This is the workbook for translating a Loss of Load study to the Slice of Day framework. Here's a step-by-step description of the process: 1. Input 1-2 managed load. 2. Obtain the storage values from SERVM. In the storage tab, calculate the energy using this formula: nameplate MW * duration = 8035.54 * 4 = 32,138 MWh. 3. The Jun_profiles tab has the NQC values by unit category and the profile for each resource type, with solar and wind profiles based on the exceedance values. The PSH and DR shapes and counting are based on RA rules. The import is capped at 4000MW across 24 hours. 4. The final output tab calculates the MW by hour based on the profiles by unit category. 5. The Dashboard tab reflects the MW values of each unit category as well as managed load and supply with and without storage. 6. The PRM_setting tab calculates the PRM using a solver by looking for the minimum PRM across 24 hours without storage, then optimizing by adding storage to this lowest PRM while not allocating more than 8035.54 MW in a given hour and ensuring the total allocation does not exceed 32,138 MWh, also making sure there is enough energy to charge the batteries.

## PRM_Setting
Hour | Load | Supply No batteries (MW) | Excess Capacity | Cumlative Excess | Battery Allocation | Battery SOC Day 1 (MWh) | Battery SOC Day 2 (MWh) | Adjusted Supply | adjusted PRM | Mean PRM - PRM | Min PRM | battery Limits
1 | 36389.74 | 41066.13 | -0.0019065 | -0.0019065 | 3282.0086 | 51141.4714 | 10503.7677 | 44348.1386 | 21.87% | 0.14747 | 16.92% | 54423.48
2 | 35081.74 | 41017.13 | 810.3907 | -3050.7979 | 0.0019065 | 51141.4695 | 10503.7658 | 41017.1319 | 16.92% | 0.19699 |  | 13605.87 | MW (Total)
3 | 34198.74 | 40795.13 | 562.264 | -2488.5361 | 8.2808e-05 | 51141.4694 | 10503.7657 | 40795.1301 | 19.29% | 0.17329 | Objective
4 | 34116.74 | 40451.13 | -504.6294 | -2993.1656 | 5.9179e-05 | 51141.4693 | 10503.7656 | 40451.1301 | 18.57% | 0.18051 | 1.1002
5 | 34801.74 | 40185.13 | -2261.2376 | -5254.4032 | 2489.8211 | 48651.6482 | 8013.9445 | 42674.9511 | 22.62% | 0.13994
6 | 36034.74 | 39870.13 | -2118.4712 | -10302.0757 | 4093.2413 | 44558.4069 | 3920.7032 | 43963.3713 | 22% | 0.14615
7 | 36325.74 | 40353.13 | 5137.0318 | -9980.6219 | 3920.7032 | 40637.7037 | -3.1755e-06 | 44273.8332 | 21.88% | 0.14737
8 | 35861.74 | 47066.13 | 14023.3829 | -569.831 | 0 | 52202.6932 | 11564.9895 | 47066.13 | 31.24% | 0.053741
9 | 34730.74 | 54630.13 | 17851.6773 | 17281.8464 | 0 | 54423.48 | 23129.979 | 54630.13 | 57.3% | -0.20679
10 | 33357.74 | 56853.13 | 19373.6615 | 36655.5079 | 0 | 54423.48 | 34694.9685 | 56853.13 | 70.43% | -0.33817
11 | 32636.74 | 57532.13 | 19259.9602 | 55915.4681 | 0 | 54423.48 | 46259.958 | 57532.13 | 76.28% | -0.39663
12 | 32782.74 | 57589.13 | 18590.5468 | 74506.0149 | 0 | 54423.48 | 54423.48 | 57589.13 | 75.67% | -0.39052
13 | 33541.74 | 57807.13 | 16904.4216 | 91410.4365 | 0 | 54423.48 | 54423.48 | 57807.13 | 72.34% | -0.35726
14 | 34913.74 | 57725.13 | 14688.0163 | 106098.4528 | 0 | 54423.48 | 54423.48 | 57725.13 | 65.34% | -0.28719
15 | 36925.74 | 57861.13 | 12037.3512 | 118135.804 | 0 | 54423.48 | 54423.48 | 57861.13 | 56.7% | -0.20079
16 | 38974.74 | 57606.13 | 8170.355 | 126306.159 | 0 | 54423.48 | 54423.48 | 57606.13 | 47.8% | -0.11186
17 | 41551.74 | 56752.13 | 5122.3817 | 131428.5406 | 0 | 54423.48 | 54423.48 | 56752.13 | 36.58% | 0.00035524
18 | 43590.74 | 56088.13 | -4064.491 | 127364.0496 | 0.0024094 | 54423.4776 | 54423.4776 | 56088.1324 | 28.67% | 0.079475
19 | 44399.74 | 47847.13 | -8514.2518 | 118849.7949 | 4754.7059 | 49668.7717 | 49668.7717 | 52601.8359 | 18.47% | 0.18144
20 | 44238.74 | 43209.13 | -7255.3355 | 106000.6877 | 9241.5185 | 40427.2532 | 40427.2532 | 52450.6485 | 18.56% | 0.18055
21 | 43015.74 | 43038.13 | -5189.9067 | 89938.4063 | 8170.6474 | 32256.6059 | 32256.6059 | 51208.7774 | 19.05% | 0.17571
22 | 41192.74 | 42972.13 | -5329.8325 | 74996.0475 | 6393.179 | 25863.4269 | 25863.4269 | 49365.309 | 19.84% | 0.16778
23 | 39708.74 | 41097.13 | -3799.6411 | 63675.0194 | 6740.6213 | 19122.8055 | 19122.8055 | 47837.7513 | 20.47% | 0.16146
24 | 38442.74 | 41147.13 | 0 | 55744.8767 | 5337.0293 | 13785.7763 | 13785.7763 | 46484.1593 | 20.92% | 0.15699
|  |  |  | Min: | 0 | -3.1755e-06
|  |  |  | Max: | 9241.5185 | 54423.48
|  |  |  | Sum: | 54423.48 | 1847664.3731
|  |  |  | Cumulative Check: | 1321.3967

## Dashboard
| Resource Portfolio | Resource Portfolio | [10 empty] | Hour
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
|  | Biogas | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202
|  | Biomass/Wood | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378
|  | CC | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217
|  | Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Cogen | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843
|  | CT | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017
|  | DR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016 | 2062 | 1989 | 1931 | 1788 | 0 | 0
|  | ICE | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
|  | Geothermal | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242
Legend |  | Hydro | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889
User Input |  | Interchange | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
Imputed Input |  | Nuclear | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280
Obj Function Elements |  | PSH | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457
Decision Variable |  | Storage | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606
Constraint |  | Solar Fixed_Norcal | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 410 | 1062 | 1391 | 1544 | 1607 | 1659 | 1627 | 1622 | 1551 | 1394 | 1062 | 430 | 25 | 0 | 0 | 0 | 0
|  | Solar Fixed_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 1261 | 2543 | 3200 | 3497 | 3634 | 3644 | 3590 | 3518 | 3210 | 2769 | 1873 | 486 | 11 | 0 | 0 | 0 | 0
|  | Solar Thermal_Norcal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Solar Thermal_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 494 | 725 | 775 | 778 | 781 | 751 | 709 | 701 | 672 | 604 | 285 | 34 | 0 | 0 | 0 | 0
|  | Solar Tracking_Norcal | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 1511 | 3336 | 3756 | 3783 | 3694 | 3816 | 3762 | 3778 | 3771 | 3611 | 3266 | 1494 | 68 | 0 | 0 | 0 | 0
|  | Solar Tracking_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 4466 | 8113 | 8733 | 8938 | 8957 | 8965 | 8946 | 8916 | 8529 | 8034 | 6569 | 2159 | 52 | 0 | 0 | 0 | 0
|  | Wind_Norcal | 770 | 750 | 670 | 585 | 521 | 459 | 404 | 345 | 266 | 258 | 235 | 185 | 183 | 202 | 237 | 308 | 417 | 522 | 604 | 615 | 704 | 721 | 741 | 791
|  | Wind_Socal | 2016 | 1987 | 1845 | 1586 | 1384 | 1131 | 975 | 719 | 536 | 510 | 480 | 454 | 479 | 567 | 801 | 1256 | 1575 | 1896 | 2047 | 2135 | 2123 | 2183 | 2076 | 2076
|  | Total Supply With Storage (MW) | 54672 | 54623 | 54401 | 54057 | 53791 | 53476 | 53959 | 60672 | 68236 | 70459 | 71138 | 71195 | 71413 | 71331 | 71467 | 71212 | 70358 | 69694 | 61453 | 56815 | 56644 | 56578 | 54703 | 54753
|  | Total Supply Without Storage (MW) | 41066.13 | 41017.13 | 40795.13 | 40451.13 | 40185.13 | 39870.13 | 40353.13 | 47066.13 | 54630.13 | 56853.13 | 57532.13 | 57589.13 | 57807.13 | 57725.13 | 57861.13 | 57606.13 | 56752.13 | 56088.13 | 47847.13 | 43209.13 | 43038.13 | 42972.13 | 41097.13 | 41147.13
|  | Load | 36389.74 | 35081.74 | 34198.74 | 34116.74 | 34801.74 | 36034.74 | 36325.74 | 35861.74 | 34730.74 | 33357.74 | 32636.74 | 32782.74 | 33541.74 | 34913.74 | 36925.74 | 38974.74 | 41551.74 | 43590.74 | 44399.74 | 44238.74 | 43015.74 | 41192.74 | 39708.74 | 38442.74

## Final_Output
Hour Ending | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Biogas | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202
Biomass/Wood | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378
CC | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217 | 17217
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cogen | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843
CT | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017 | 8017
DR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016 | 2062 | 1989 | 1931 | 1788 | 0 | 0
ICE | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
Geothermal | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242 | 1242
Hydro | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889 | 2889
Interchange | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
Nuclear | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280
PSH | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457
Storage | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606 | 13606
Solar Fixed_Norcal | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 410 | 1062 | 1391 | 1544 | 1607 | 1659 | 1627 | 1622 | 1551 | 1394 | 1062 | 430 | 25 | 0 | 0 | 0 | 0
Solar Fixed_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 1261 | 2543 | 3200 | 3497 | 3634 | 3644 | 3590 | 3518 | 3210 | 2769 | 1873 | 486 | 11 | 0 | 0 | 0 | 0
Solar Thermal_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 494 | 725 | 775 | 778 | 781 | 751 | 709 | 701 | 672 | 604 | 285 | 34 | 0 | 0 | 0 | 0
Solar Tracking_Norcal | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 1511 | 3336 | 3756 | 3783 | 3694 | 3816 | 3762 | 3778 | 3771 | 3611 | 3266 | 1494 | 68 | 0 | 0 | 0 | 0
Solar Tracking_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 4466 | 8113 | 8733 | 8938 | 8957 | 8965 | 8946 | 8916 | 8529 | 8034 | 6569 | 2159 | 52 | 0 | 0 | 0 | 0
Wind_Norcal | 770 | 750 | 670 | 585 | 521 | 459 | 404 | 345 | 266 | 258 | 235 | 185 | 183 | 202 | 237 | 308 | 417 | 522 | 604 | 615 | 704 | 721 | 741 | 791
Wind_Socal | 2016 | 1987 | 1845 | 1586 | 1384 | 1131 | 975 | 719 | 536 | 510 | 480 | 454 | 479 | 567 | 801 | 1256 | 1575 | 1896 | 2047 | 2135 | 2123 | 2183 | 2076 | 2076

## Output
Hour Ending | Biogas | Biomass/Wood | CC | Coal | Cogen | CT | DR | ICE | Geothermal | Hydro | Interchange | Nuclear | PSH | Storage | Solar Fixed_Norcal | Solar Fixed_Socal | Solar Thermal_Norcal | Solar Thermal_Socal | Solar Tracking_Norcal | Solar Tracking_Socal | Wind_Norcal | Wind_Socal
1 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 0 | -8.3277e-05 | 0 | 0 | 0 | 0 | 769.8212 | 2015.752 | 54672.2648
2 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 0 | -0.0024959 | 0 | 0 | 0 | 0 | 749.682 | 1986.9913 | 54623.3624
3 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 0 | -0.0041188 | 0 | 0 | 0 | 0 | 670.3484 | 1844.7108 | 54401.7467
4 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 0 | -0.0055383 | 0 | 0 | 0 | 0 | 584.7916 | 1586.0752 | 54057.553
5 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 0 | -0.0060683 | 0 | 0 | 0 | 0 | 520.8901 | 1383.5156 | 53791.0913
6 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 0 | 0.012133 | 0 | 0 | 0 | 0 | 459.3342 | 1130.9437 | 53476.9817
7 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 20.5358 | 154.2406 | 0 | 0 | 69.2134 | 450.0787 | 403.5517 | 974.5713 | 53958.8831
8 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 409.6524 | 1261.3569 | 0 | 74.4816 | 1511.4279 | 4466.2821 | 344.8866 | 718.6754 | 60673.4546
9 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 1061.7414 | 2542.8421 | 0 | 493.8018 | 3336.3346 | 8113.4043 | 265.8362 | 535.5385 | 68236.1906
10 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 1390.5942 | 3199.9308 | 0 | 724.8898 | 3755.6275 | 8732.9367 | 257.8561 | 509.737 | 70458.2638
11 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 1543.9803 | 3496.6925 | 0 | 775.0151 | 3782.9523 | 8937.7131 | 234.9087 | 480.4676 | 71138.4213
12 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 1606.8559 | 3634.4034 | 0 | 778.2753 | 3693.8364 | 8956.7199 | 185.2896 | 454.1204 | 71196.1925
13 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 1659.2829 | 3644.3862 | 0 | 780.8135 | 3815.6721 | 8964.8834 | 182.7358 | 478.8067 | 71413.2722
14 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 1627.0926 | 3589.8002 | 0 | 751.2288 | 3761.5804 | 8946.396 | 201.6374 | 566.6353 | 71331.0624
15 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 1622.4864 | 3518.4969 | 0 | 708.6957 | 3777.6546 | 8915.5838 | 236.9393 | 800.6714 | 71467.2198
16 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 1550.6946 | 3210.2812 | 0 | 700.7829 | 3770.907 | 8529.2179 | 307.6214 | 1256.2563 | 71212.4529
17 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 1394.0577 | 2769.4589 | 0 | 671.7586 | 3610.9958 | 8033.9105 | 416.7732 | 1574.849 | 70358.4955
18 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 2015.8261 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 1061.5869 | 1872.5306 | 0 | 603.6199 | 3265.6941 | 6569.3369 | 522.1081 | 1895.8094 | 69693.2037
19 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 2061.9487 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 429.5084 | 485.7291 | 0 | 284.7669 | 1493.7573 | 2158.6629 | 604.0116 | 2046.5716 | 61451.6482
20 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 1989.2466 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 24.7032 | 10.7566 | 0 | 34.422 | 67.9558 | 51.8545 | 614.9961 | 2135.3639 | 56815.9904
21 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 1931.3648 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 0 | 0.039374 | 0 | 0 | 0 | 0 | 704.2628 | 2122.8517 | 56645.2103
22 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 1788.1389 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 0 | 0.019951 | 0 | 0 | 0 | 0 | 721.1152 | 2183.2202 | 56579.1859
23 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 0 | 0.012768 | 0 | 0 | 0 | 0 | 740.7118 | 2075.7369 | 54703.1532
24 | 202.4036 | 377.5456 | 17217.45 | 0 | 1843.2379 | 8017.33 | 0 | 254.7 | 1242.209 | 2888.8655 | 2500 | 2280 | 1457.08 | 13605.87 | 0 | 0.0052753 | 0 | 0 | 0 | 0 | 790.8062 | 2075.8163 | 54753.3195

## Apr_Profiles
Hour Ending | Biogas | Biomass/Wood | CC | Coal | Cogen | CT | DR | ICE | Geothermal | Hydro | Interchange | Nuclear | PSH | Storage | Solar Fixed_Norcal | Solar Fixed_Socal | Solar Thermal_Norcal | Solar Thermal_Socal | Solar Tracking_Norcal | Solar Tracking_Socal | Wind_Norcal | Wind_Socal | Unit Category | NQC
1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | -1.9626e-08 | 0 | 0 | 0 | 0 | 0.40132 | 0.34685 | Biogas | 202.4036
2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | -5.8821e-07 | 0 | 0 | 0 | 0 | 0.39082 | 0.3419 | Biomass/Wood | 377.5456
3 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | -9.7067e-07 | 0 | 0 | 0 | 0 | 0.34947 | 0.31741 | CC | 17217.45
4 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | -1.3052e-06 | 0 | 0 | 0 | 0 | 0.30486 | 0.27291 | Coal | 0
5 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | -1.4301e-06 | 0 | 0 | 0 | 0 | 0.27155 | 0.23806 | Cogen | 1843.2379
6 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2.8593e-06 | 0 | 0 | 0 | 0 | 0.23946 | 0.1946 | CT | 8017.33
7 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.010091 | 0.036349 | 0 | 0 | 0.013537 | 0.04148 | 0.21038 | 0.16769 | DR | 2376.71
8 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.20129 | 0.29726 | 0 | 0.074706 | 0.29561 | 0.41162 | 0.1798 | 0.12366 | Geothermal | 1242.209
9 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5217 | 0.59926 | 0 | 0.49529 | 0.65252 | 0.74774 | 0.13859 | 0.092149 | Hydro | 2888.8655
10 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.68329 | 0.75412 | 0 | 0.72707 | 0.73453 | 0.80483 | 0.13443 | 0.087709 | ICE | 254.7
11 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.75866 | 0.82406 | 0 | 0.77735 | 0.73987 | 0.82371 | 0.12246 | 0.082673 | Interchange | 2500
12 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.78956 | 0.85651 | 0 | 0.78062 | 0.72244 | 0.82546 | 0.096595 | 0.078139 | Nuclear | 2280
13 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.81532 | 0.85886 | 0 | 0.78316 | 0.74627 | 0.82621 | 0.095264 | 0.082387 | PSH | 1457.08
14 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7995 | 0.846 | 0 | 0.75349 | 0.73569 | 0.82451 | 0.10512 | 0.0975 | Storage | 13605.87
15 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.79724 | 0.82919 | 0 | 0.71083 | 0.73884 | 0.82167 | 0.12352 | 0.13777 | Solar Fixed_Norcal | 2035.14
16 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.76196 | 0.75656 | 0 | 0.70289 | 0.73752 | 0.78606 | 0.16037 | 0.21616 | Solar Fixed_Socal | 4243.27
17 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.68499 | 0.65267 | 0 | 0.67378 | 0.70624 | 0.74041 | 0.21727 | 0.27098 | Solar Thermal_Norcal | 0
18 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84816 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.52163 | 0.44129 | 0 | 0.60544 | 0.63871 | 0.60544 | 0.27219 | 0.32621 | Solar Thermal_Socal | 997
19 | 1 | 1 | 1 | 1 | 1 | 1 | 0.86756 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.21105 | 0.11447 | 0 | 0.28562 | 0.29215 | 0.19894 | 0.31488 | 0.35215 | Solar Tracking_Norcal | 5112.97
20 | 1 | 1 | 1 | 1 | 1 | 1 | 0.83697 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.012138 | 0.002535 | 0 | 0.034526 | 0.013291 | 0.004779 | 0.32061 | 0.36743 | Solar Tracking_Socal | 10850.5933
21 | 1 | 1 | 1 | 1 | 1 | 1 | 0.81262 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 9.2791e-06 | 0 | 0 | 0 | 0 | 0.36715 | 0.36527 | Wind_Norcal | 1918.21
22 | 1 | 1 | 1 | 1 | 1 | 1 | 0.75236 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 4.7018e-06 | 0 | 0 | 0 | 0 | 0.37593 | 0.37566 | Wind_Socal | 5811.67
23 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 3.0091e-06 | 0 | 0 | 0 | 0 | 0.38615 | 0.35717 | Total | 85232.255
24 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1.2432e-06 | 0 | 0 | 0 | 0 | 0.41226 | 0.35718

## Storage
Pndcap | Total Energy
54423.48 | 54423.48

## Managed_load
HOUR | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
MANAGED_NET_LOAD | 23678 | 22370 | 21487 | 21405 | 22090 | 23323 | 23614 | 23150 | 22019 | 20646 | 19925 | 20071 | 20830 | 22202 | 24214 | 26263 | 28840 | 30879 | 31688 | 31527 | 30304 | 28481 | 26997 | 25731
NOU | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74 | 12711.74
Total | 36389.74 | 35081.74 | 34198.74 | 34116.74 | 34801.74 | 36034.74 | 36325.74 | 35861.74 | 34730.74 | 33357.74 | 32636.74 | 32782.74 | 33541.74 | 34913.74 | 36925.74 | 38974.74 | 41551.74 | 43590.74 | 44399.74 | 44238.74 | 43015.74 | 41192.74 | 39708.74 | 38442.74