## CPUC TPR PUBLIC
[71 empty] | 1514894.0462 | 1514894.0462 | 1514894.0462 | 1514894.0462 | 1514894.0462 | 1514894.0462 | 1514894.0462 | 1514894.0462 | 1514894.0462 | 1514894.0462
| Project Description | [37 empty] | Utility/CAISO Approval and FERC Rate Cases | [9 empty] | CPUC Permit Status | [9 empty] | Project Status | [7 empty] | Costs | [30 empty] | Notes
1 | 2 | 3a | 3b | 4 | 5 | 6 | 7 | 7 | 8 | 9 | 10 | 11 | 11 | 12 | 13 | 14 | 15a | 15b | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 |  |  |  |  | 26 | 27 |  |  | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40a | 40b | 41a | 41b | 42a | 42b | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 52 | 53 | 54 | 55 | 56 |  | 57 |  | 57 | 57 | 57 | 57 | 58 | 58 | 58 | 58 | 59 | 60 | 61 | 62 | 63 | 63 | 63 | 63 | 63 | 63 | 64 | 65 | 65 | 66 | 67 | 68 | 69 | 70
Row/Line No. | Project Name(s) | Latitude | Longitude | Location2 | Project Description | Project Description - What | Project Description - Action Taken | Project Description - Action Taken (2) | Project Dependencies | Primary Purpose | Secondary Purpose | NERC/WECC/CAISO Standard/Requirement/Contingency | NERC/WECC/CAISO Standard/Requirement/Contingency (2) | Last Inspection | Age of Asset | Types of Analyses | Alternative Solutions and Costs - Solutions | Alternative Solutions and Costs - Costs | CPUC Fire Threat Zone/Rating | Wildfire Related | RAMP | Other Environmental Factors | Project Manager | Transmission Project Size (length in miles) | Substation Project Footprint (acres) | Transmission Voltage Level (kV) | Substation or Transformer Capacity (MVA and/or kV) | Utility Prioritization Ranking - RIBA | Utility Prioritization Ranking - Loading Order | Utility Prioritization Ranking - Circuit Based Plan Rank | Utility Prioritization Ranking - RBPPF | Utility Prioritization Ranking - Integrated Grid Planning | Utility Unique ID #1 (Most Specific) | Utility Unique ID #2 (Less Specific) | Utility Unique ID #2 (Less Specific) - T.Dot Name | Utility Unique ID #2 (Less Specific) - Planning Orders per T.Dot | Utility Unique ID #3 (Least Specific) | Changes in Unique IDs | Utility Approval | Year of Internal Utility Approval | Process(es) for Utility Approval | Long term Transmission Investment Plan Inclusion | CAISO Year | TPP Phase 3 | Year(s) when considered in CAISO TPP | Year when expected to be considered in CAISO TPP | Link to TPP where project has been considered, approved, and/or expected to be considered | GIDAP-Related | CEQA Status | CEQA Status - Date | CEQA Document Type | NEPA Document Type | CEQA Lead Agency | NEPA Lead Agency | CPUC Filing Type | CPUC Date Filed | CPUC Status | CPUC Status - Year | Project Status | AACE Class | Construction Start Date | Original Planned In-Service Date | Current Projected or Actual In-Service Date | Reason for Change in In-Service Date | Reason for Change in In-Service Date (2) | In-Flight Projects | Original Projected Cost or Cost Range ($000) | Cost Cap ($000) | Inception to Date ($000) | Current Projected Total or Actual Final Cost ($000) | Actual Capital Expenditures 2021 ($000) | Actual Capital Expenditures 2022 ($000) | Actual Capital Expenditures 2023 ($000) | Actual Capital Expenditures 2024 ($000) | Actual Capital Expenditures 2025 ($000) | Actual and Forecast Capital Expenditures 2026 ($000) | Projected Capital Expenditures 2027 ($000) | Projected Capital Expenditures 2028 ($000) | Projected Capital Expenditures 2029 ($000) | Projected Capital Expenditures 2030 ($000) | Construction Work in Progress ($000) | Accrued Overhead ($000) | Accrued AFUDC ($000) | FERC: Year(s) | Dollars Put into FERC Rate Base 2021 ($000) | Dollars Put into FERC Rate Base 2022 ($000) | Dollars Put into FERC Rate Base 2023 ($000) | Dollars Put into FERC Rate Base 2024 ($000) | Dollars Put into FERC Rate Base 2025 ($000) | Dollars Put into FERC Rate Base 2026 ($000) | Percentage of Bid | Percentage and Value ($000) of Work Requested by Others Passed onto Ratepayers | Load Facility Type | Cost-Benefit Analysis | FERC Incentives | Percentage of Cost in High Voltage TAC | Percentage of Cost in Low Voltage TAC | Notes
1 | Purch Tools & Equip - TLINE |  |  | NA | Bucket for purchasing tools and equipment for T-Line. | Other | New | NA | NA | Other [See Notes] | Tools | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 758 | 9. Reliability (Low Safety Risk) | NA | 1.0001 | Non-IGP | 5501201 | NA | NA | NA | 5 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 44256.9648 | 50485.5224 | 684.0502 | 656.3976 | 1029.9009 | 1075.4614 | 454.6848 | 527.1986 | 1024.1588 | 1024.1588 | 1045.06 | 1045.06 | 43729.7662 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 836.9211 | 807.019 | 480.8762 | 1759.4661 | 454.6848 | 227.5818 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
2 | Sub Constr Capital Tools |  |  | NA | Bucket for capital tools for Construction. | Other | New | NA | NA | Other [See Notes] | Tools | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 31 | 9. Reliability (Low Safety Risk) | NA | 1.0001 | Non-IGP | 5512939 | NA | NA | NA | 5 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 16179.9992 | 25043.0198 | 1266.1546 | 1758.3253 | 764.5146 | 1223.6629 | 2760.7195 | 499.1981 | 1457.3423 | 1457.3423 | 1487.084 | 1487.084 | 15680.8011 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 1556.5436 | 1804.188 | 24.6751 | 1982.9732 | 2760.7195 | 499.198 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
3 | Sub Maint Capital Tools |  |  | NA | Bucket for capital tools for Maintenance work. | Other | New | NA | NA | Other [See Notes] | Tools | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 247 | 9. Reliability (Low Safety Risk) | NA | 1.0001 | Non-IGP | 5512940 | NA | NA | NA | 5 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 16085.0389 | 24948.0595 | 1607.6566 | 1300.7367 | 1106.4488 | 1549.7199 | 1077.1362 | 31.3824 | 1457.3423 | 1457.3423 | 1487.084 | 1487.084 | 16053.6565 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 1719.5281 | 1426.5166 | 415.246 | 1725.9797 | 1077.1362 | 31.3824 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
4 | Trans Sub Test Capital Tools |  |  | NA | Bucket for capital tools for testing. | Other | New | NA | NA | Other [See Notes] | Tools | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 594 | 9. Reliability (Low Safety Risk) | NA | 1.0001 | Non-IGP | 5512941 | NA | NA | NA | 5 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 18505.0552 | 34467.5462 | 1801.9134 | 1473.7188 | 1149.2063 | 1370.2859 | 1194.7483 | 0 | 3384.845 | 3796.526 | 3002.186 | 3038.453 | 18505.0552 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 2733.9993 | 1473.7188 | 1149.2063 | 1370.2859 | 1194.7483 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
5 | Env Cap Improvements (Tran) |  |  | NA | Bucket for SPCC (Spill Prevention Containment Control) actions such as installation of concrete ponds and drainage to control the run-off of spills at Electric Transmission sites. | Other - Environmental | New | NA | NA | Other [See Notes] | Environmental | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5515080 | NA | NA | NA | 12 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1688.4408 | 1696.4408 | 46.4235 | 1.9621 | 1.8272 | 0.9347 | 0 | 8 | 0 | 0 | 0 | 0 | 1688.4408 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 383.3207 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
6 | ETrans - Treated Wood Transport&Disposal |  |  | NA | Bucket for costs associated with the transport and disposal of transmission wood poles after they have been removed from service and are being disposed. | Other - Environmental | Removal | NA | NA | Other [See Notes] | Environmental | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5515081 | NA | NA | NA | 12 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 3201.9445 | 3525.9445 | 363.4932 | 201.794 | 188.2452 | 414.9364 | 392.4075 | 326.0862 | 0 | 0 | 0 | 0 | 3199.8583 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
7 | FIXED WING - CAMERAS |  |  | NA | Purchase and attach two MX-15 cameras to the aircraft. The addition of MX-15 cameras would enable the fixed wing fleet to support some Public Safety Power Shut-off -related patrol activities (that are traditionally performed by helicopters) in a much safer capacity and with improved asset inspection quality. Improved camera assets can provide support for external agencies (e.g., fire patrol, geological assessments) • Adds capability to perform circuit patrols at night, reducing customer outage time • Adds capability to perform fixed wing Electric Transmission Tower patrol • Imagery and video recording improves permanent records keeping | Other - Operations Tech | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5790210 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2020-09-30 | NA | NA | FALSE | NA | NA ¦ NA | 2713.0252 | 2713.0252 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2713.0252 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 75 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
8 | 2021-2022 Replace Eureka T-line Trailer |  |  | Eureka, Humboldt | Procure a trailer in Eureka area due to a T-WRFR decision. | Other | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5546477 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2023-04-06 | NA | NA | FALSE | NA | NA ¦ NA | 1407.7785 | 1407.7785 | 388.9056 | 464.7503 | 444.6448 | 109.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 1407.7785 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 835.7013 | 0 | 0 | 358.8785 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
9 | misc. contracts |  |  | NA | Forecast placeholder for misc. contacts in support of ET capital work | Other | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | 5547779 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8292 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 2073 | 2073 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 | 0 | 100.1475 | 701.0774 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
10 | Transmission As-Build Process Improvement |  |  | NA | Forecast placeholder for t-line As Build Process Improvement | Other | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | Ex112888 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 3500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 1000 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
11 | Transmission/Substation As-Built Process Improvement |  |  | NA | Forecast placeholder for substation As Build Process Improvement | Other | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | Ex112889 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 3500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 1000 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
12 | PLS-CADD Model - Operability Assessmnt |  |  | NA | Bucket for PLS-CADD modeling project creating detailed electronic models of ~48,000 PG&E Transmission Tower and Pole assets in the Tier 2/3 HFTD. PLS-CADD models refine the baseline of each structure’s design basis in the Risk Model to more accurately predict structural failure under wind load cases to better inform PSPS decision making and asset investment strategy. Models provide an accurate 3D representation of assets in the field (the ‘digital twin’ concept) and unify various PG&E data sources (SDS, Construction Drawings, Photos, LiDAR). PLS-CADD: • Industry-standard overhead power line design software produced by Power Line Systems®. • Supports computer-aided modeling of an entire transmission line • Sophisticated 3-D engineering model including terrain, structures, and wires. • Uses Finite Element Analysis (FEA) to combine a system of structures as a single model (accounts for effect of load on adjacent structures) • The analysis output reports the effect of pre-defined load cases for every structural element of the model (actual stress / allowed stress) | Other | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | 5538644 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 18621.0481 | 18621.0481 | 5625.4095 | 4719.9569 | 1357.242 | 0 | 0 | 0 | 0 | 0 | 2000.0001 | 2000.0001 | 18621.0481 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 5625.4095 | 4719.9569 | 1357.242 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
13 | TG 2021 Holding Order - Transmission |  |  | NA | Bucket for Temporary Generation Transmission work | Other | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5545721 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1802.6981 | 1802.6981 | 1593.4087 | 90.4894 | 118.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1802.6981 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
14 | Copperleaf capital T |  |  | NA | Bucket for an Asset Investment Planning Management (AIPM) tool called Copperleaf to enable more informed asset investment decisions and improve the effectiveness of risk-based asset investment plans. Copperleaf will enable Electric Operations to develop risk and benefit models and incorporate different models into a common scale, thereby allowing for more equivalent comparisons of risk reduction or investment value across different types of assets. The tool also provides scenario planning capabilities that enable continuous, automated optimization of investment plans over time based on different constraints or changing conditions. | Other | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | 5546960 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 3590.5024 | 3590.5024 | 1002.1423 | 2404.6257 | 183.7345 | 0 | 0 | 0 | 0 | 0 | 350 | 350 | 3590.5024 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 3590.5025 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
15 | Transmission CIRT Capital |  |  | NA | CIRT is centralized inspection review team and they would come in once the inspection has been complete and review the findings to determine if we repair or replace the asset which will trigger creating notification under maintenance program or other programs which manage the replace of asset which is typically capital. | Other | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5551452 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1203.0016 | 1203.0016 | 0 | 1203.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1203.0016 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 1203.0016 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
16 | Risk Model-Transmission (Exponent) HFTD |  |  | NA | Wildfire Transmission Risk Model (WTRM) is a Composite model framework integrating useful life for all 47 components that have a potential ignition risk upon their failure. The model calculates a probability of failure for each component group under specific threats\hazards which is joined with different types of consequence data to calculate various types of risk. (Wildfire, Public Safety etc.) | Other | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | 5551539 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 13313.9794 | 13313.9794 | 0 | 5495.5692 | 3205.9291 | 1913.115 | 2480.15 | 219.2162 | 2000 | 2000 | 2000 | 2000 | 13094.7632 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 5495.5692 | 3150.3945 | 1832.9575 | 2401.5378 | 231.684 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
17 | ET Federal Land Authorizations |  |  | NA | Bucket for renewal for a 30-50 year period, authorizations from the U.S. Forest Service (USFS) and the Bureau of Land Management (BLM) for transmission lines that currently have expired authorizations. | Other | Replace | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 25 | NA | NA | NA | Non-IGP | 5721938 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2013 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 9328.2762 | 9328.2762 | 544.6578 | 174.3423 | 145.4313 | -429.5879 | -5 | 0 | 0 | 0 | 0 | 0 | 9328.2762 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 1242.476 | 174.3423 | 145.4313 | -429.5879 | -5 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
18 | AutoCAD License (AutoDesk Inc) |  |  | NA | Licensing of AutoCAD software to support substation and transmission design workflows. Enables engineers to create, modify, and validate electrical schematics and layouts critical to infrastructure planning and execution. | Other | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | Ex123623 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2162.152 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1054.708 | 0 | 0 | 1107.444 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
19 | Substation Design Suite License (SBS Inc) |  |  | NA | Acquisition of SBS Inc’s Substation Design Suite to enhance design automation and standardization across substation projects. Supports compliance with engineering standards and improves design cycle efficiency. | Other | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | Ex123624 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1582.063 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 1582.063 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
20 | IGP Cap Tx PO |  |  | NA | Implementation and development of SNAP (System Needs Analysis Platform) which integrates electric grid asset data from numerous sources into the Palantir Foundry platform for analysis to provide an aggregated view of electric system risk and need across various dimensions. The aggregated grid needs are exported to Copperleaf for portfolio-level prioritization and optimization. | Other | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | 5556008 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 6080.1966 | 6080.1966 | 0 | 0 | 0 | 1357.4026 | 3759.5212 | 963.2729 | 0 | 0 | 0 | 0 | 5116.9237 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 6080.1967 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
21 | Data Products Tool Development Tx |  |  | NA | SNAP-AFO--TSAM Release 2 (System Needs Analysis Platform -- Transmission Substation Asset Management -- Asset Family Owners) Improve TSAM AFOs efficiency and accuracy, while simultaneously incurring cost savings by enhancing the reliability of PG&E’s substation and transmission systems, data pipelines, and reporting tools, as well as through supplemental enhancements to the System Needs Analysis Platform (SNAP). Build a Scalable Standardized Dashboard: Integrate AIC, APM, TCM, TOA, SAP, & GIS data for critical assets with visibility and workflow consistency into a user-friendly dashboard for TSAM personnel. Automate Processes: Expose risk model insights & define data collection workflows.Provide Training: Train users. Monitor Performance: Regularly update the system, conduct biannual evaluations & optimize dashboards. GIS Apps Develop ESRI based Experience Builder tools that connect disparate data sources across the enterprise to replace exist functionality from legacy systems WiRE – Foundry Use Case Create a single repository for WMP data in Foundry that serves as PG&E’s single record of evidence for WMP reporting Asset Failures, Predictions, and Reliability Suite Develop a Foundry based platform that centralizes critical asset failure data allowing for trend analysis to inform asset management decision-making. Foundry Ontology – for SNAP Create trusted pipelines and ontology datasets that can be relied upon and leveraged across the enterprise | Other | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | 5816019 | NA | NA | NA | 21 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1373.6109 | 1373.6109 | 0 | 0 | 0 | 0 | 1314.8757 | 58.7352 | 0 | 0 | 0 | 0 | 1314.8757 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1314.8757 | 58.7352 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
22 | Olivehurst TLine Yard-Property Purchase |  |  | Olivehurst CDP, Yuba | Purchased 5.5 acre parcel including 4.17 acre fenced and partially graveled yard with the following structures: 5,100 SF Warehouse, 5,100 SF Office Building, 960 SF modular trailer, 3,000 SF metal shed. TLINE M&C is occupying this location. | Other | New | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-02-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5811779 | NA | NA | NA | 23 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2024-12-20 | 2024-12-20 | NA | NA | FALSE | 5600 | NA ¦ NA | 4725.2571 | 4725.2571 | 0 | 0 | 0 | 4732.0694 | -6.8123 | 0 | 0 | 0 | 0 | 0 | 4725.2571 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 4732.0694 | -6.8123 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
23 | Oroville T-Line Warehouse - Bldg Purch |  |  | Oroville, Butte | Ground lease for 11 acres + building purchase 55,000 sqft (office and warehouse) in the city of Oroville. Support T-Line operations with potential for use by Vegetation Management and others as space allows. | Other | New | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5812916 | NA | NA | NA | 23 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2024-12-25 | 2024-12-25 | NA | NA | FALSE | 4800 | NA ¦ NA | 3903.8408 | 3903.8408 | 0 | 0 | 0 | 3915.9508 | -12.11 | 0 | 0 | 0 | 0 | 0 | 3903.8408 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 3903.8408 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
24 | Sacramento Area - T-Line Fab Shop |  |  | West Sacramento, Yolo | The existing Fab shop is outdated and not up to current CRESS standards. The existing T-Line Fab shop is 70 years old and does not meet space nor functionality requirements. This project will improve safety and compliance-based deficiencies that exist. | Other | New | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-02-17 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5787644 | NA | NA | NA | 23 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2021-09-01 | OAI | NA | NA | FALSE | 13500 | NA ¦ NA | 14067.2889 | 14067.2889 | 11128.7662 | 72.9017 | 204.2721 | 646.8115 | 2.0773 | 0 | 0 | 0 | 0 | 0 | 14067.2889 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 12623.7861 | 69.9371 | 195.8767 | 620.2282 | 1.9919 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
25 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | T.0006261 | Other [See Notes] | System Operations | NA | NA | NA | 14 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5788603 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 23 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-01 | 2022-12-29 | 2022-12-30 | NA | NA | FALSE | 182000 | NA ¦ NA | 54981.1439 | 54981.1439 | 9283.225 | 39446.7859 | 5355.8274 | 526.3084 | 2.2281 | 0 | 0 | 0 | 0 | 0 | 54981.1439 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 49096.78 | 4207.4589 | 1674.6769 | 2.2281 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
26 | Livermore Substation Training Fac. (TO) |  |  | Livermore, Alameda | The purpose of the Livermore Substation Training Facility project is to build a best-in-class training venue at the Livermore Substation Training Facility to provide training on Electric Transmission substation operations and maintenance. | Substation - Other Equipment | New | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-04-01 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.60395 | NA | NA | 361 | NA | NA | NA | Non-IGP | 5782941 | T.0002104 | Livermore Substation Training Facility | 2 | 23 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-11-15 | 2018-11-30 | 2018-11-30 | NA | NA | FALSE | 63000 | NA ¦ NA | 13811.6068 | 13811.6068 | -216.8398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13811.6068 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -216.8398 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
27 | Livermore Substation Training Facility |  |  | Livermore, Alameda | The purpose of the Livermore Substation Training Facility project is to build a best-in-class training venue at the Livermore Substation Training Facility to provide training on Electric Transmission substation operations and maintenance. | Substation - Other Equipment | New | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-04-01 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.60395 | NA | NA | 361 | NA | NA | NA | Non-IGP | 5771658 | T.0002104 | Livermore Substation Training Facility | 2 | 23 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-12-22 | 2018-11-30 | 2021-12-29 | Scope Change | NA | FALSE | 63000 | NA ¦ NA | 38.3226 | 38.3226 | 958.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.3226 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 38.3226 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
28 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5816828 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Cybersecurity [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
29 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | New | NA | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5794224 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2023-07-30 | NA | NA | FALSE | 1296 | NA ¦ NA | 2517.7191 | 2517.7191 | 1266.0529 | 584.7268 | 433.7428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2517.7191 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1274.7981 | 327.338 | 915.583 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
30 | TO lifecycle 2024 |  |  | NA | Replace End of life ODN TO devices that support transmission operations. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5554576 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | 2024-10-18 | NA | OAI | NA | NA | FALSE | 950 | NA ¦ NA | 1642.953 | 1642.953 | 0 | 0 | 0 | 640.9949 | 990.4223 | 11.5357 | 0 | 0 | 0 | 0 | 1631.4173 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 640.9949 | 0.29275 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
31 | CS - SAP Unifer Ariba Integration TO (C) |  |  | NA | SAP Unifier and Ariba Integration: The key objective of this phase of Unifier EPM Tools is to build integrations between standard enterprise applications and establish repositories of high quality data that can be used to improve project management, and to provide an appealing, efficient end user experience through automation. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5796838 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2022-12-07 | NA | NA | FALSE | NA | NA ¦ NA | 3239.5236 | 3239.5236 | 610.7503 | 2628.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3239.5236 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 3239.5236 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
32 | N20_Foundational MW Transition TO ( C ) |  |  | NA | This Project is to support the microwave radio upgrade of legacy and bandwidth limited microwave radio equipment on the Hogback Mtn to Pit 6 PH (D239) and Hogback Mtn to Pit 7 PH (D240) microwave radio paths. Upgrading microwave radio equipment will improve network reliability and provide better functionality (e.g, Native TDM, Native Ethernet Transport, Remote Login, Telenium Monitoring, etc.) to these critical facilities. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5816699 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2022-01-01 | NA | 2026-06-01 | NA | NA | TRUE | NA | NA ¦ NA | 6924.4471 | 11997.3501 | 0 | 0 | 0 | 3607.0565 | 3168.7608 | 5104.3065 | 0 | 0 | 0 | 0 | 6893.0436 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 5247.2426 | 0.9939 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
33 | N20_Foundational Fiber TO (C ) |  |  | NA | Objective: To enable the Utility network to meet increased client bandwidth and reliability demands resulting from the deployment of new automation technologies that support Los Banos Substation. Additionally, to establish diverse optical connectivity to Panoche Substation and Padre Flat Switching Station at a comparatively low incremental cost. Scope: Addressing Bandwidth and Reliability Demands: Install a diverse optical connection and associated active equipment to support Los Banos Substation. Establish diverse optical connectivity to Panoche Substation and Padre Flat Switching Station. Collaboration and Infrastructure Installation: The Padre Flat-Panoche Sub 230 kV #1 Reconductoring Project will procure and install the physical fiber cable infrastructure. A parallel IT project will cover the fiber cable hardware and installation costs, terminate the fiber cable, and perform final acceptance testing. The IT project will install new ROADM network elements and degrees to establish a diverse ROADM degree into Los Banos Substation. The IT project will unfold SONET connectivity via new optical fiber routes between Panoche Substation and Padre Flat Switching Station, and between Los Banos Substation and Panoche Substation. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5816719 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2021-08-30 | NA | 2026-07-15 | NA | NA | TRUE | NA | NA ¦ NA | 14970.208 | 16315.361 | 58.0621 | 225.1478 | 2323.9263 | 8325.0753 | 3414.5543 | 1528.4246 | 0 | 0 | 0 | 0 | 14786.9364 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 9913.7346 | 70.6213 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
34 | Foundry Capitalization 2025 5YR ET_C |  |  | NA | This is a prepaid license/maintenance costs for Palantir Foundry. It is a software license agreement that allows us to use the technology to build other technology solutions and deliver new capabilities to existing technology solutions. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5811798 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | OAI | NA | NA | FALSE | 10000 | NA ¦ NA | 10000 | 10000 | 0 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 10000 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
35 | Inspect inspect correct ET (Non-WF) |  |  | NA | Delivers new capabilities for detailed inspections and correctives in the Inspect for ED/ET Non-WF | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5816686 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-03-13 | NA | 2026-12-15 | NA | NA | TRUE | NA | NA ¦ NA | 56.9462 | 1209.2604 | 0 | 0 | 0 | 0 | 0 | 1209.2604 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
36 | PSPS 5.0_TO_C _2026_HFTD |  |  | NA | The first main objective is to improve scoping granularity to target specific areas of wildfire risk and reduce the number of customers impacted and the length of de-energization. We are doing this by enabling a range a granularity for decision making based on real time observations, reducing the time to operationalize de-energization and restoration, and reducing field crews needed by operating SCADA devices. The second objective is to enable notification automation at this granular scope. To enable this, we will automate staging, QA/QC and execution of Customer and Agency notifications and updates to PSPS Portal and Emergency website, so that these communications align with the granular scope enhancements. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5818659 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-02-26 | NA | 2026-12-15 | NA | NA | TRUE | NA | NA ¦ NA | 452.9586 | 3295.4966 | 0 | 0 | 0 | 0 | 0 | 3295.4966 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] PSPS [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
37 | Bentley-SAP IntegrationCAP-ET Phase 3 |  |  | NA | Build interface between the Bentley Substation design tool and SAP to facilitate automated material ordering.The SAP and Bentley data will be automatically synchronized; the Fresno Materials Team will be able to perform their work in SAP without manually reconciling data across legacy data bases. Automatically populating the Bill of Materials (BoM) into the components screen in the SAP work management PM order, manual process will be minimized and eventually eliminated. The materials populated in the components screen will also be reflected in the Clarity functionality now used by Electric Transmission. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5773912 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2019-06-15 | 2021-12-06 | Project Design | NA | FALSE | 1200 | NA ¦ NA | 2579.8412 | 2579.8412 | 809.7275 | 9.3796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2579.8412 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 2570.4616 | 9.3796 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
38 | Copperleaf 5 Year Capitalization TO_C |  |  | NA | The Electric Investment Planning organization currently uses Copperleaf Portfolio software to help prioritize investments in PG&E’s electric grid. The results obtained from Copperleaf portfolio, although helpful, have not fully met expectations for better matching investments in the grid with PG&E enterprise objectives around safety, reliability, and adequate customer capacity. Reasons identified for this shortfall include: Insufficient detail to operationalize some investment recommendations Difficulty visualizing the impact of the recommendations on particular sections of the grid Lack of robust reporting capabilities for both Investment Planning use and justifying investments to the CPUC and FERC. The Investment Planning team have identified opportunities to improve ease of use and provide more granularity to results by implementing three additional Copperleaf modules under the Copperleaf Portfolio umbrella. Implementing these modules will require assistance from Copperleaf and PG&E IT. Objective: improve recommendations for investments in the electric grid by enhancing the current Investment Planning Copperleaf Portfolio application:. Scope – 2023 Complete the implementation of the RBPPF Value Model for investment valuation where program specific Value Models haven’t been created. Support the IP team with optimizations they would like to perform in 2023. Scope – 2024 Conduct workshops to review and update Investment Planning’s existing Value Framework. This includes the design and updates of existing Value Frameworks. Final loads of asset data. IP has identified a set of 24 Program codes that require review. Review the Foundry data being used by IGP and create a summary report of current Foundry data and data that would be beneficial to add to Foundry for IP’s use cases. Configure ten asset classes in the updated IP Portfolio application. Asset Aware will be expanded for IP to cover asset types not covered by the IGP project. Deliver a documented procedure to export from the target system to automatically convert to Copperleaf’s spreadsheet importer format. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5813348 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2024-11-01 | 2024-12-20 | NA | NA | FALSE | 2889.377 | NA ¦ NA | 2889.3768 | 2889.3768 | 0 | 0 | 22.171 | 2867.2059 | 0 | 0 | 0 | 0 | 0 | 0 | 2889.3768 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 162.9706 | 2726.4062 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
39 | Substation_5 Year_C |  |  | NA | The current substation design process at PG&E relies on the Bentley OUS platform, which has proven to be inefficient and inadequate in meeting the needs of both internal design teams and external contractors. Bentley OUS suffers from frequent errors and its dependence on Citrix/VDI has caused significant disruptions for external contractors, leading to inconsistent design workflows, delayed project timelines, and increased costs. This legacy system has become a bottleneck, limiting the overall efficiency of PG&E's substation design processes. The frequent downtime and difficulties in accessing the system have also introduced potential risks, including safety issues and increased design errors. As a result, design resources are not being fully utilized, leading to lost productivity and value. To address these challenges, PG&E is initiating a transition to AutoCAD and the Substation Design Suite (SDS) from Spatial Business Systems, which will be deployed across all 110 internal substation engineers and approximately 200 external contractors. This project also includes the adoption of ProjectWise in the cloud as the central repository for project documentation. Standardizing AutoCAD SDS as the key design software will align substation design processes with other business units, ensuring consistency, reducing errors, and eliminating the reliance on Citrix/VDI for contractors. This shift is expected to significantly improve design accuracy, reduce downtime, enhance collaboration, and support more efficient project execution, ultimately leading to considerable cost savings and improved safety performance. • Replace Bentley OUS with AutoCAD SDS: Transition from the outdated Bentley OUS system to the more robust AutoCAD Substation Design Suite (SDS) combination, which will be implemented across all internal and external substation design teams. This change will enhance the efficiency and accuracy of the substation design process by eliminating the reliance on Citrix/VDI and reducing design errors. • Implement ProjectWise for Centralized Documentation: Adopt ProjectWise in the cloud as the central repository for managing and storing all project-related documentation. This will streamline document control, ensure consistency in project documentation, and support enhanced collaboration between internal teams and external contractors. • Standardize AutoCAD Across Business Units: Align substation design processes with other lines of business by standardizing on AutoCAD as the core design tool. This standardization will simplify workflows, increase operational efficiency, and reduce software complexity across the organization. • Integrate GridSearch for Material Tracking: Deploy GridSearch to enhance material tracking and project status visibility. This integration will support better control over Bill of Materials (BOM) submissions, enabling more accurate and timely procurement of materials required for substation projects. • Integrate with SAP for BOM Management: Set up secure API connections through MuleSoft to integrate with SAP, enabling automatic approval of Bill of Materials (BOM) when submitted to SAP, and fulfillment through the SUBMAT application. This will streamline the ordering process and ensure that long-lead items are available when needed. • Migrate Data to AutoCAD SDS: Migrate existing substation asset drawings and models from Bentley OUS into AutoCAD SDS. This data migration will ensure the continuity of design workflows and enable future projects to leverage the latest design tools. • Change Management and User Training: Execute a comprehensive change management plan that includes updating documentation, creating training materials, and providing training sessions for both internal and external users. This will ensure a smooth transition to the new system and high user adoption rates. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5813400 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2025-03-28 | 2025-03-28 | NA | NA | FALSE | 2774.024 | NA ¦ NA | 2774.024 | 2774.024 | 0 | 0 | 0 | 2774.024 | 0 | 0 | 0 | 0 | 0 | 0 | 2774.024 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 2774.024 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
40 | Microwave Radio Capacity Increase (TO) |  |  | NA | FT - Las Yeguas - Midway (D145) Microwave Upgrade Project/Work Description: Replace 1 link across 2 sites (D145) | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5778490 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-08-13 | 2024-07-05 | 2025-12-01 | Project Design | NA | FALSE | NA | NA ¦ NA | 1185.1841 | 1185.1841 | 0 | 0 | 0 | 997.0094 | 150.8736 | 0 | 0 | 0 | 0 | 0 | 1185.1841 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1185.1841 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
41 | N20_Foundational Multiplexing TO (C ) |  |  | NA | SONET equipment serving these facilities are beyond lifecycle and in need of replacement to maintain safe and reliable operations of the Power Plants, Gas facilities and substations. The SONET Replacements were prioritized by the network 20/20 team by facility served, condition of equipment, and link congestion. Replace 24 SONET nodes across 22 sites (SFGONOC, SFGORASB, SFGOVOC, San Francisco SC, Martin Sub TF, Martin Sub, San Mateo 115 kV Sub, San Mateo 60 kV Sub, Embarcadero Sub, SFJ, Redwood City Sub, Jefferson Sub, Sneath Lane Sub, Serramonte Sub, Daly City Sub, Martin SC, Midway Control Room, La Paloma PP Sub, Sunrise PP, Midway 500 kV Sub, Midway TF, Midway 230 kV Sub) | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5816720 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-01 | 2023-12-15 | 2026-01-31 | Workforce | NA | TRUE | 2950 | NA ¦ NA | 10617.2607 | 17430.7847 | 0 | 0 | 1821.5367 | 2312.7605 | 6254.3281 | 7089.3233 | 0 | 0 | 0 | 0 | 10341.4614 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 5874.3197 | 2424.7356 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
42 | Aerial Inspect Sherlock_WF ET 2025_C |  |  | NA | PG&E developed an enhanced inspection program as part of the Community Wildfire Safety Program, known as the Wildfire Safety Inspection Program ("WSIP"). The WSIP implemented enhanced inspections to be completed on an accelerated schedule for PG&E to inspect its electric facilities in Tier 2 and Tier 3 HTFD areas and address any high priority repairs identified before the 2019 fire season. Under WSIP, the accelerated inspections focus on conditions that could lead to potential fire ignitions, known as the Failure Modes and Effects Analysis ("FMEA"), and supplement PG&E's baseline inspection and maintenance procedures. Through the FMEA, PG&E has identified single points of failure of electric system components that could lead to fire ignition. The identification of these failure points will aid in the development of inspection methods that can most appropriately identify the condition of such components, which are designed in accordance with GOs 95, 165, and 174 requirements. As part of the Wildfire Safety Inspection Program, PG&E has committed to inspecting 50,000 Tier 1 and Tier 2 Transmission Structures with a combined total of over two million images. In order to handle this magnitude of images that need to be inspected individually, a visualization tool and backend system needs to be developed that will allow for receipt of images and an intuitive interface to allow inspectors to review images and identify any possible irregularities. This effort also presents an opportunity to implement computer vision API, where computer vision models are trained to identify problems in an automated fashion (Waldo). By implementing such models, PG&E will be able to position itself for future inspections where problems can be identified in real time and brought to inspectors attention and/or can be used for predictions. Product Suite includes currently: Sherlock, SAP, BW, BOBJ, MPMT, MRAD, ARAD 1. ED/ET Checklist update* 2. ED/ET Prioritization user interface to allow business control over work assignment instead of urgent developer updates to the system* o Holding structures/groups of structures o Individual structure prioritization o PSPS prioritization 3. ED/ET Inspection record correction workflow * 4. ED/ET Deprecate ARAD and move images and PDF records to alternate storage location * 5. ED automation for additional notification types: ECV Vegetation Management, Third Party Utility and Non Utility, Idle Investigation* o Additional BW report required 6. ED/ET Tech debt* 7. ET 2.0 Phase 2 - mandatory items follow up to MVP* 8. ED/ET SAP enhancements* o EC notif rule enhancements for pending notification reviews o Need ET reoccurring MPs * o Need ET/ED LC/EC notifications linked to inspections - impacts to WMP reporting* 9. ED/ET Adapt to annual yearly standard, procedure changes from Asset Strategy | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5811481 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2025-06-23 | 2025-12-31 | 2026-12-31 | Project Design | NA | TRUE | NA | NA ¦ NA | 887.789 | 2429.2178 | 0 | 0 | 0 | 0 | 576.6916 | 1852.5262 | 0 | 0 | 0 | 0 | 576.6916 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 576.6916 | -3.7174 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
43 | Waldo Computer Vision Models (TO) HFTD |  |  | NA | Platform for development & deployment of computer vision models that extract data from raw drone and helicopter images. Used by Asset Strategy for collecting asset registry data used for proactive and reactive maintenance planning, risk mitigation. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Non-Wires | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5809168 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-10-25 | 2024-12-15 | 2025-12-01 | Project Design | NA | TRUE | 6090 | NA ¦ NA | 4808.887 | 5931.8298 | 0 | 0 | 0 | 2725.949 | 1822.5956 | 1383.2852 | 0 | 0 | 0 | 0 | 4548.5446 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 2725.949 | 1822.5956 | 157.5378 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
44 | IO-Kings Craine Microwave Capacity TO_C |  |  | NA | This project is to provide a redundant Telecom Transmission route for the Helms Power Generation Plant. A new microwave radio path, using the existing company technology since 2011, from the FOC to Bear Mtn, Bear Mtn to Balch PH (via a Passive Reflector) while upgrading the Balch PH to Haas PH microwave radios. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5794223 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-12-04 | 2022-12-15 | 2022-12-07 | NA | NA | FALSE | NA | NA ¦ NA | 2146.309 | 2146.309 | 839.0042 | 460.618 | 147.6403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2146.309 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 1998.6687 | 147.6403 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
45 | FT FiberPGE-Stockton_to_Weber_Rep(TO)_C |  |  | NA | FT - Stockton A to Weber MW Replacement Replace D003 and D250 with a new, diverse dark fiber SONET connection between Stockton Station A and Weber Sub. Improves reliability of core business electric protection, GDN, RAS, EMS, and SCADA circuits. AHI = 1.70 | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5798158 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2023-05-15 | NA | NA | FALSE | 1330 | NA ¦ NA | 1544.3614 | 1544.3614 | 531.7431 | 487.9839 | 476.3273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1544.3614 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 1544.3614 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
46 | Joint Pole Accelerated Collections (C) |  |  | NA | Item 1: Merge the SAP EES and Joint Pole billing tables Item 2: SAP rule to recognize that a blue bill has been printed and not allow an SAP blue bill to be emailed Item 3: Update reports to include the blue bill number Item 4: Transmission pole intents within TEMACC will pass data to SAP Joint Pole. Item 5: Provide additional enhancements for Form 2 process Implement versioning. Currently, when a revision is made to a Form 2 intent, there is no way to reset the clock and re-send the new version to the Other Utility. This causes process delays and re-work. Assume this is a revision after the Form 2 has already been sent, and than an unlimited number of revisions and re-sends is required. Enhancement to JPORDER email functionality. Item 6: Provide additional enhancements for Form 7 process – Provide the ability to manually set an intent to “F7 Received”. Item 7: Provide additional enhancements for Intent process – Provide ta limited ability to reverse intent statuses to allow for corrections and intent cleanup. Sent to Construction status enhancements. Currently, no changes to any intent can be made from this status. Item 8: Provide additional enhancements for Form 48 and 44 process – There is a gap in our tool that does not provide for a Draft Final Form 48 to be sent to OU for review. Currently, the application directs a completed Form 48 directly to Billing Form 48 process is currently not working. Analysis and cause to be determined. Form 44 process for Final Billing and Payment not working. Analysis and cause will need to be determined. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5804920 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2023-09-13 | 2023-10-02 | NA | NA | FALSE | 1300 | NA ¦ NA | 1284.0858 | 1284.0858 | 0 | 0 | 1246.0725 | 38.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 1284.0858 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 1246.0725 | 38.0133 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
47 | FT - 2023 Network Lifecycle (TO) |  |  | NA | Replace End of life network gear that supports transmission operations | Other - IT | Replace | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5803335 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-12-08 | NA | 2024-03-18 | NA | NA | FALSE | 1950 | NA ¦ NA | 1728.8477 | 1728.8477 | 0 | 1.8072 | 1293.2681 | 433.7724 | 0 | 0 | 0 | 0 | 0 | 0 | 1728.8477 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 1728.8477 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
48 | IGP IT ET (TO)_C |  |  | NA | Objective: use detailed data about the PG&E electric grid, from substation to distribution, to: 1) lower costs for annual grid projects and maintenance; and 2) increase how well the annual grid investments promote key PG&E goals. SCOPE FOR PHASE 1 Develop a high level design, identify data sources, and complete initial data population of the IGP applications. Develop and test the initial IGP Benefits model. Complete Asset, Portfolio, and Investment workshops.Configure investment types, portfolios, and users. Final loads of asset data and creation of the 2025 integrated grid investment recommendations/plan. SCHEDULE FOR PHASE 1 Release: 9/27/2024 go live for investment planning to recommend investments for all addressable Capital Pole Management and Maintenance Tag work: about 38% of the addressable Electric investment portfolio. Compare where feasible to Bain 2025 rrecommendations. Stabilization Complete: 10/31/2024. SCOPE – 2025 Complete Value Framework workshops and create initial Value Model designs. Develop an automated interface from data sources to the application SaaS databases. Deliver training to the teams doing investment planning and go live, including delivery of 2026 IGP plan. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5807158 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2025-03-28 | NA | NA | FALSE | 1603.831 | NA ¦ NA | 1615.4083 | 1615.4083 | 0 | 0 | 190.2326 | 1199.9374 | 219.8363 | 0 | 0 | 0 | 0 | 0 | 1615.4083 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1055.12 | 560.2883 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
49 | Inspect ET System Inspections_Non-WF_C |  |  | NA | Each year System Inspections Electric OH Ground/Climb has changes to update the checklist to capture required information based on a variety of different drivers. Objectives/Scope: Update checklist yearly. Checklist must be changed to meet ever changing compliance obligations and asset strategy needs for our electric system to remain compliant and ensure we are capturing the right level of information yearly. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5807038 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2025-04-02 | 2025-06-30 | NA | NA | FALSE | 5530 | NA ¦ NA | 1208.8484 | 1208.8484 | 0 | 0 | 0 | 771.827 | 413.8351 | 0 | 0 | 0 | 0 | 0 | 1208.8484 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1208.8484 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
50 | Sherlock System Inspct New Cap_TO_C HFTD |  |  | NA | PG&E developed an enhanced inspection program as part of the Community Wildfire Safety Program, known as the Wildfire Safety Inspection Program ("WSIP"). The WSIP implemented enhanced inspections to be completed on an accelerated schedule for PG&E to inspect its electric facilities in Tier 2 and Tier 3 HTFD areas and address any high priority repairs identified before the 2019 fire season. Under WSIP, the accelerated inspections focus on conditions that could lead to potential fire ignitions, known as the Failure Modes and Effects Analysis ("FMEA"), and supplement PG&E's baseline inspection and maintenance procedures. Through the FMEA, PG&E has identified single points of failure of electric system components that could lead to fire ignition. The identification of these failure points will aid in the development of inspection methods that can most appropriately identify the condition of such components, which are designed in accordance with GOs 95, 165, and 174 requirements. Sherlock is a tool for performing multiple roles associated with remote desktop inspection of aerial imagery of Transmission and Distribution structures. The software also serves as an image viewer utilized by other departments. As of 2024 Transmission is on version 1 while Distribution was released in version 2. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5807003 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-03-11 | 2025-08-25 | 2025-10-29 | NA | NA | FALSE | 3584.376 | NA ¦ NA | 3546.1318 | 3546.1318 | 0 | 0 | 0 | 1845.4118 | 1680.8383 | 0 | 0 | 0 | 0 | 0 | 3546.1318 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 3546.1318 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
51 | PSPS 5.0_TO_C HFTD |  |  | NA | Scope includes two dashboards, one focused on de-energization and re-energization execution for incident commanders and the other focused on communication completion and compliance, to support real-time operations and situational awareness throughout a PSPS event. Dashboards support objective of minimized and more targeted PSPS events, specifically to reduce number of customers and duration of impact | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5807775 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-06-28 | 2027-12-31 | 2025-12-31 | NA | NA | FALSE | 20580 | NA ¦ NA | 1757.6502 | 1757.6502 | 0 | 0 | 150.9067 | 544.6472 | 1062.0962 | 0 | 0 | 0 | 0 | 0 | 1757.6502 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2027 | 0 | 0 | 0 | 695.554 | 1062.0962 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
52 | PSPS Smart Comm (TO)_C |  |  | NA | Leverage the existing Foundry SmartComms application and expand to include PSPS event communications. Ensuring customers receive outage information promptly to keep them informed about the status and expected duration of the outage.Efficiently managing communications during PSPS events to minimize inconvenience and ensure customer safety. All outage journey programs like Unplanned, Planned outage transitioning to Smartcomms.. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5815258 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2026-06-15 | 2026-01-28 | NA | NA | FALSE | 4740 | NA ¦ NA | 2979.3616 | 2979.3616 | 0 | 0 | 0 | 0 | 3017.3532 | 4.5835 | 0 | 0 | 0 | 0 | 2974.7781 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 2979.3616 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
53 | EGI Transmission_C |  |  | NA | Develop a new generational EGI project life cycle tool that would encompass Substation and Transmission Line design Review WEB Based tools in the PG&E Cloud Based Center Of Excellence Work with Infrastructure team to determine usability of Planisware scheduling and resource planning tool Tie EGI project drawings into the ProjectWise system Link Project Data sources (EGI to PLS CADD & Substation) Develop Drawing Comparison tools and workflows to improve design file quality Open up the EGI work process to enterprise level to gain visibility on new projects and new customers and their potential delay | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5807027 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | 2026-12-30 | NA | NA | TRUE | 1694.704 | NA ¦ NA | 1920.0002 | 3919.3752 | 0 | 0 | 0 | 140.2255 | 1210.3255 | 2557.9038 | 0 | 0 | 0 | 0 | 1361.4714 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1361.4714 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
54 | N20_Foundational CF Transition TO (C ) |  |  | NA | Bucket planning order for Network 2020 CF projects transitioning to Foundational Common Facilities. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5816718 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2023-07-24 | 2025-12-31 | OAI | NA | NA | TRUE | 13200 | NA ¦ NA | 2911.0326 | 3204.8046 | 0 | 0 | 0 | 1670.3836 | 1093.1728 | 386.1345 | 0 | 0 | 0 | 0 | 2818.6701 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1878.0604 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
55 | San Leandro J UG Fiber Build |  |  | San Leandro, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-05 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2372 | NA | NA | NA | NA | NA | NA | Non-IGP | 5540640 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E ¦ AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020 ¦ 2022 | Operational | 1 | NA | 2015-03-01 | 2022-01-30 | Prioritization | NA | FALSE | $15,000 ¦ $30,000 | NA ¦ NA | 14.789 | 14.789 | 2.9575 | 8.5001 | 0.248 | 0.646 | 0.8915 | 0 | 0 | 0 | 0 | 0 | 14.789 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil
56 | ET Substation Asset Registry - (CAP) |  |  | NA | Develop a source of records for Electric Transmission and Substation asset facilities ratings by integrating multiple data sources; develop a process for easily identifying a customer’s pricing node and be able to provide the information for requesting party. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NERC FAC Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5779318 | K.0000044 | ET Asset Registry | 1 | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2023-09-25 | 2023-09-25 | NA | NA | FALSE | 5556 | NA ¦ NA | 6628.4864 | 6628.4864 | 2224.1194 | 1554.4618 | 476.5969 | 0 | 4.0765 | 0 | 0 | 0 | 0 | 0 | 6628.4864 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2023 ¦ 2026 | 2818.9845 | 0 | 3127.3142 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC FAC 8, CPUC D.15-11-042, WECC Audit Findings [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
57 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5788501 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2021-03-26 | NA | NA | FALSE | NA | NA ¦ NA | 2103.2871 | 2103.2871 | 646.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2103.2871 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 2103.2871 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Cybersecurity [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
58 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | New | NA | NA | Other [See Notes] | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5785784 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2020-10-30 | 2020-10-20 | NA | NA | FALSE | 2917 | NA ¦ NA | 5039.2335 | 5039.2335 | 91.5472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5039.2335 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 91.5472 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 2 & 7 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
59 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | New | NA | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5784618 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA ¦ 5775788 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2024-09-26 | OAI | NA | NA | TRUE | 41311 | NA ¦ NA | 50042.1594 | 56618.0035 | 5005.9013 | 6366.0866 | 7459.1769 | 6236.4472 | 7031.1872 | 7300 | 21.1135 | 0 | 0 | 0 | 49296.89 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 1616.6757 | 8832.7137 | 9769.2497 | 9280.6842 | 4149.8764 | 1574.9704 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Cybersecurity [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
60 | WSIP: TSS Phase 2 (C) TO |  |  | NA | Objectives of this project include a greater understanding of failure modes, establishment of a common repository of data gathered, and effectively updating workflows of key asset systems to align with new data strategies. The project is a series of enhancements to the current TSS application, with no new infrastructure or application software required. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5795571 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2015-01-01 | 2021-08-16 | 2022-01-28 | NA | NA | FALSE | 985 | NA ¦ NA | 1709.4561 | 1709.4561 | 1549.5107 | 159.9454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1709.4561 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 1709.4561 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
61 | ET Operability Assessment (C) |  |  | NA | Enable enhancements made to the (Operability Assessment) OA model as directed by Electric Transmission Line Asset Strategy. IT's scope is to host the model, where the algorithm is developed by T-line Asset Strategy. Develop v3 PAF models as additional data are made available that improve the quality of asset health predictions. PAF models are developed by Data Scientists in Data & Analytics. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5795497 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2023-05-25 | 2023-05-25 | NA | NA | FALSE | 4528 | NA ¦ NA | 4528.2268 | 4528.2268 | 1599.2183 | 2106.3478 | 822.6607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4528.2268 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 2789.5304 | 1738.6964 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
62 | OH Asset Info Collection_TO_C HFTD |  |  | NA | Define critical components of Electric Transmission towers and other structures in High Fire Threat District areas that require recording of foundational asset information, including asset age. Execute processes as part of the Foundational Asset Knowledge collection effort / phase. Update systems of record component age information using completed data collection template | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5797621 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2023-12-28 | 2023-12-28 | NA | NA | FALSE | 1862 | NA ¦ NA | 1861.9989 | 1861.9989 | 145.8631 | 855.9638 | 864.3709 | -4.1989 | 0 | 0 | 0 | 0 | 0 | 0 | 1861.9989 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 1866.1978 | -4.1989 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
63 | Radio System Expansion_TO_C |  |  | NA | FT - SCADA Radio Capacity and Reliability Improvements (TO) 2022 Project/Work Description: This project migrates SCADA RTUs at substations that are on the ODN and migrated away from DSO leases or private 4 Wire circuits. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5750578 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-15 | 2023-07-01 | 2025-02-28 | Material | NA | FALSE | 1070 | NA ¦ NA | 7901.4246 | 7901.4246 | 251.3299 | 529.7729 | 540.9517 | 383.8004 | 50.0967 | 0 | 0 | 0 | 0 | 0 | 7901.4246 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2025 ¦ 2026 | 973.047 | 0 | 0 | 0 | 1528.6628 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
64 | Inspect and Engage 1.0 ET (CAP) |  |  | NA | Implement new features and capabilities for the Electric Transmission Patrol & Inspection applications. New features include completing development of digital assignment, documentation, approval and reporting of Electric Transmission patrol and inspection data, and designing and developing an emergency mode to facilitate the assessment and documentation of corrective work for routine and major emergency conditions. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5784142 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2019-12-31 | 2020-10-30 | Project Design | NA | FALSE | 6000 | NA ¦ NA | 6714.807 | 6714.807 | 51.1479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6714.807 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 51.1479 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
65 | ElecOps - Bentley SAP Integratn P3 (C) |  |  | NA | Upgrade the existing Substation Product from Substation v8i to Substation Connect. Build interfaces to and from Substation Connect and SAP for Materials and Job Orders which is currently a manual process. In addition, replace the Engineering Materials Database and TSM&C which are Access databases to support end-to-end integrations. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5773843 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-01-14 | 2019-06-15 | 2021-03-31 | Scope Change | NA | FALSE | 6390 | NA ¦ NA | 6404.4845 | 6404.4845 | 773.8639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6404.4845 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 6404.4845 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
66 | Inspect and Engage 2.0 ET (CAP) |  |  | NA | Continue to implement new features and capabilities for the Electric Transmission Patrol & Inspection applications. New features include refining maintenance plans, improving regulatory reporting, and allowing field supervisors to view work progress, and assign / prioritize work geo-spatially. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5785399 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2021-11-26 | NA | NA | FALSE | NA | NA ¦ NA | 2462.8234 | 2462.8234 | 2028.7816 | -14.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2462.8234 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 2477.4134 | -14.59 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
67 | ElecOps - Substa Rcrd-RcrdKeep 2019 TO C |  |  | NA | Build and deploy a software technology solution that will enable a more automated approach to the substation record keeping process. The current software in place does not address these requirements without a significant upgrade to add new functionality. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5773844 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2023-05-31 | 2023-07-24 | NA | NA | FALSE | 3584 | NA ¦ NA | 8028.021 | 8028.021 | 79.4316 | 476.8573 | 390.6386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8028.021 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 946.9275 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
68 | GWD for Substation AutoCAD_TO_C |  |  | NA | The current substation design process at PG&E relies on the Bentley OUS platform, which has proven to be inefficient and inadequate in meeting the needs of both internal design teams and external contractors. Bentley OUS suffers from frequent errors and its dependence on Citrix/VDI has caused significant disruptions for external contractors, leading to inconsistent design workflows, delayed project timelines, and increased costs. This legacy system has become a bottleneck, limiting the overall efficiency of PG&E's substation design processes. The frequent downtime and difficulties in accessing the system have also introduced potential risks, including safety issues and increased design errors. As a result, design resources are not being fully utilized, leading to lost productivity and value. To address these challenges, PG&E is initiating a transition to AutoCAD and the Substation Design Suite (SDS) from Spatial Business Systems, which will be deployed across all 110 internal substation engineers and approximately 200 external contractors. This project also includes the adoption of ProjectWise in the cloud as the central repository for project documentation. Standardizing AutoCAD SDS as the key design software will align substation design processes with other business units, ensuring consistency, reducing errors, and eliminating the reliance on Citrix/VDI for contractors. This shift is expected to significantly improve design accuracy, reduce downtime, enhance collaboration, and support more efficient project execution, ultimately leading to considerable cost savings and improved safety performance. • Replace Bentley OUS with AutoCAD SDS: Transition from the outdated Bentley OUS system to the more robust AutoCAD Substation Design Suite (SDS) combination, which will be implemented across all internal and external substation design teams. This change will enhance the efficiency and accuracy of the substation design process by eliminating the reliance on Citrix/VDI and reducing design errors. • Implement ProjectWise for Centralized Documentation: Adopt ProjectWise in the cloud as the central repository for managing and storing all project-related documentation. This will streamline document control, ensure consistency in project documentation, and support enhanced collaboration between internal teams and external contractors. • Standardize AutoCAD Across Business Units: Align substation design processes with other lines of business by standardizing on AutoCAD as the core design tool. This standardization will simplify workflows, increase operational efficiency, and reduce software complexity across the organization. • Integrate GridSearch for Material Tracking: Deploy GridSearch to enhance material tracking and project status visibility. This integration will support better control over Bill of Materials (BOM) submissions, enabling more accurate and timely procurement of materials required for substation projects. • Integrate with SAP for BOM Management: Set up secure API connections through MuleSoft to integrate with SAP, enabling automatic approval of Bill of Materials (BOM) when submitted to SAP, and fulfillment through the SUBMAT application. This will streamline the ordering process and ensure that long-lead items are available when needed. • Migrate Data to AutoCAD SDS: Migrate existing substation asset drawings and models from Bentley OUS into AutoCAD SDS. This data migration will ensure the continuity of design workflows and enable future projects to leverage the latest design tools. • Change Management and User Training: Execute a comprehensive change management plan that includes updating documentation, creating training materials, and providing training sessions for both internal and external users. This will ensure a smooth transition to the new system and high user adoption rates. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5811158 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2025-03-28 | 2025-12-11 | Project Design | NA | FALSE | 4412 | NA ¦ NA | 4380.9285 | 4380.9285 | 0 | 0 | 0 | 914.0636 | 3446.1059 | 3.433 | 0 | 0 | 0 | 0 | 4377.4955 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 4377.4956 | 3.433 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
69 | OEIS_DPPI_TO_C HFTD |  |  | NA | As part of the Wildfire Mitigation Plan (WMP), Energy Safety (OEIS) released a complex GIS Data Standard that requires quarterly submission of a broad set of Asset, Initiative, PSPS, and Risk data in a specified data schema containing over 1000 fields, equating to millions of records (Q1 2022 submission included ~15M records). PG&E lacks a consolidated, readily accessible view of much of this data and its data is not organized to meet compliance requirements. This results in significant inefficiencies in producing the data and WMP compliance risks in producing incomplete submissions. OEIS has established an expectation for quarterly improvements. PG&E has reached a threshold for which process improvements can improve the report and incorporated technology (Foundry) in 2021-2022 to meet compliance requirements and reduce manual labor requirements. This work needs to continue through 2025 to meet 2025 WMP quarterly reporting compliance while progressing Electric Ontology. In addition, OEIS uses this data to inform their own inspections of PG&E assets and initiative work. Where field or data level deficiencies are found, OEIS can file Notices of Violation / Notices of Defect. Continue to build a wildfire data foundation through Foundry in order to progress WMP data compliance requirements and contribute to EO Ontology objectives and enabling data access for risk/analytics use cases Scope includes ingestion and transformation of wildfire critical data via Foundry to create a single, accessible, trusted set of data to meet reporting requirements and accelerate other EO wildfire mitigation efforts. In addition PG&E assets, PSPS, and risk data, there are 39 critical wildfire mitigation programs needed to fully comply. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5807595 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | 2026-12-15 | 2026-12-15 | NA | NA | TRUE | 1548 | NA ¦ NA | 776.3502 | 1395.039 | 0 | 0 | 0 | 197.5899 | 542.9575 | 654.4916 | 0 | 0 | 0 | 0 | 740.5474 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 197.5899 | 542.9575 | -20.0714 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
70 | STAR for Transmission Line CAP |  |  | NA | STAR is currently part of the Asset Data Foundation (ADF) program as PG&E’s first-of-its-kind unified Transmission & Distribution Asset data set where attributes are defined, sources are known, and data pipelines are established and governed. Planning Order 5784102 contains costs associated with Electric Transmission work only. By linking multiple utility systems of record into one data warehouse using the AWS cloud platform, STAR’s mission is to operationalize electric asset intelligence at lower cost and greater repeatability with more trustworthy analytical results for wildfire risk reduction. Two primary data products that PG&E is currently developing that leverage STAR include the Electric Transmission Operability Assessment (OA) Tool and Probability of Asset Failure (PAF). OA is an engineering model that calculates Electric Transmission structure fragility and aids in the determination of Electric Transmission lines within scope during PSPS events. PAF is an Electric Transmission Asset tool that will help Asset Strategy prioritize maintenance and replacement of assets such as conductors, insulators, structures and switches. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5784102 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-02-07 | 2019-06-15 | 2021-06-30 | Project Design | NA | FALSE | 4694 | NA ¦ NA | 6411.3272 | 6411.3272 | 1366.5961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6411.3272 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 2363.8628 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
71 | Sys-Insp WF-Mitigation-ET (C) |  |  | NA | The System Inspections organization in Wildfire Risk has an annual workplan that requires a technology suite of applications to appropriately document the detailed overhead inspection of Electric Transmission and Distribution structures. This is accomplished using Inspect Mobile, Engage Web, Maintenance Plan Management Tool, and SAP/BW applications. The current System Inspections program requires annual updates to the detailed overhead inspection checklist, modifications to the data collected, updates to the process, data clean-up and data requests. The proposed scope ensures that PG&E continues to enhance the applications for the multitude of needs in the system inspection process. This technology is directly supporting the Wilfire Mitigation program | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5798268 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2021-10-30 | 2021-11-30 | NA | NA | FALSE | 2500 | NA ¦ NA | 1057.5714 | 1057.5714 | 1057.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1057.5714 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 1057.5714 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
72 | E Trans Underbuild Transmission (C) |  |  | NA | Approximately 60,000 transmission structures have distribution underbuilds. These ~60,000 assets are shared by distribution and transmission but currently show up as separate assets in SAP, ETGIS and EDGIS, without an indication they are the same structure. This allows for inconsistencies with distribution and transmission potentially working on the same asset without knowledge of the other. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5800227 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2022-09-21 | NA | NA | FALSE | 1080 | NA ¦ NA | 1080.4708 | 1080.4708 | 0 | 1080.4708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080.4708 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 1080.4708 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
73 | Smart Connect Phase 2 (CAP) |  |  | NA | Improve the existing Your Projects portal for all New Business applications by: - Simplifying application creation for customers and contractors - Adding dashboards and reporting. - Allowing user self-scheduling of PG&E work. 2)Integrate the Electric Engineering Assessment Tool (i.e., Calculator) and the DGST with SAP and the Portal for automating and streamlining impact analysis. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5800519 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2022-12-10 | 2022-12-10 | NA | NA | FALSE | 5556 | NA ¦ NA | 5555.5254 | 5555.5254 | 0 | 5246.6184 | 308.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5555.5254 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 5246.6184 | 308.907 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
74 | UO-AMR-ETGIS (C) |  |  | NA | PG&E has implemented ETGIS Editor on Esri and Schneider Electric ArcFM 10.2.1 and ETViewer using ArcGIS JS API on operating systems window 2008 R2 and RDBMS 11g, which provides Electric Transmission data capture on ET Editor and viewing asset on the web browser. The technology and infrastructure being used in ETGIS is no longer supported by the product vendor and it is in extended support. Also, the legacy systems are not capable enough to meet future needs and can cause performance issues or even outage of systems, potentially impacting the ability of PG&E employees to perform work. The objective of this program is to upgrade and re-architect the operating system, database, and GIS software by adopting upgraded versions of Esri and Schneider suites of products to improve user experiences. - Build new infrastructure to migrate existing ETGIS - Install Windows OS 2016 (or 2019 is available) - Install ArcGIS, ArcFM, and FME software on new infrastructure - Migrate all ETGIS related databases to new environment - Business functionality for Editor and Viewer will remain the same - Test ArcGIS | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5797622 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2022-12-19 | 2022-12-29 | NA | NA | FALSE | 4487 | NA ¦ NA | 4486.5451 | 4486.5451 | 1777.4 | 2721.6812 | -12.5361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4486.5451 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 4499.0812 | -12.5361 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
75 | ET Composite Model - CAP |  |  | NA | Wildfire Risk Composite Models that Electric Operations has committed to the Federal Monitor and the CPUC. PO 5797825 represents the development of composite models to understand the fire ignition risk from Electric Transmission Assets. Multiple groups are developing sub-models which act as inputs to the composite model. Each sub-model accesses specific threat data. As of mid-2021, some sub-models exist and require some to little refinement. Once refined, these sub-models need to be composited into one comprehensive model for risk ranking of Electric Tansmission assets to make inspection priority decisions. Develop 3 sub-models for the Electric Wildfire Risk Composite Models: - Bird - 3rd Party - Animal (non-bird) Each sub-model will predict the probability of an outage being caused by the specific threat for a discrete portion of the system. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5797825 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2023-05-25 | 2023-05-25 | NA | NA | FALSE | 2128 | NA ¦ NA | 2128.0683 | 2128.0683 | 713.8071 | 1133.8875 | 280.3736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2128.0683 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 879.8182 | 1248.2501 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
76 | PLS-CADD Integration (CAP) |  |  | NA | T-Line Engineering & Estimating has migrated to PLS CADD to perform design and estimating work. However, this tool is not currently integrated with SAP. The proposed solution is to integrate PLS CADD with SAP to streamline material ordering, cost estimating, and settlement rule generation. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5797224 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2023-05-31 | 2023-05-31 | NA | NA | FALSE | 4567 | NA ¦ NA | 4566.752 | 4566.752 | 726.0323 | 2947.0232 | 893.6966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4566.752 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 4566.752 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
77 | PLS CADD Ph2_TO_C |  |  | NA | PLS-CADD Ph2 continues the improvements and integration for Transmission projects delivered in Phase 1. The major areas of improvement are: 1. Integrating with additional applications, including Joint POle SAP, Job Force, and other work management and imaging applkications 2. Further support compliance activities (FERC and CPUC) 3. Deliver a new set of Capital Accounting cost allocations 4. Retire FFE and spreadsheets used by Transmission engineers | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5806061 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2023-12-22 | 2023-12-22 | NA | NA | FALSE | 2497 | NA ¦ NA | 2497.0375 | 2497.0375 | 0 | 0 | 1994.2331 | 502.8044 | 0 | 0 | 0 | 0 | 0 | 0 | 2497.0375 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 1994.2331 | 502.8044 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
78 | Sherlock Tool _TO_(WSIP)_C HFTD |  |  | NA | Following the catastrophic California wildfires in November 2018, PG&E captured more than 2 million images of our field equipment in high fire-risk areas. We developed a technology solution called “Sherlock” that enables the automation of otherwise manual inspections using industry-leading artificial intelligence (AI) techniques to reduce cost, increase quality, and enable PG&E to have in-depth knowledge of the state of our equipment. The Sherlock Suite allows desktop inspectors to markup potential equipment problems on high-resolution images, further training computer-vision models to automatically detect potential issues and adding metadata to enable searchability of these images across the enterprise. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5783781 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2019-06-15 | 2023-12-29 | Project Design | NA | FALSE | 4509 | NA ¦ NA | 13586.6677 | 13586.6677 | 2936.7566 | 2856.4889 | 2320.6765 | 255.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 13586.6677 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 5029.6664 | 3091.8485 | 3743.6332 | 255.6687 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
79 | Electric GIS 2023 Enhancements_C |  |  | NA | Complete at least one release each quarter to deploy GIS enhancements and address production defects | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5804307 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2024-03-05 | 2024-03-05 | NA | NA | FALSE | 1073 | NA ¦ NA | 1073.43 | 1073.43 | 0 | 0 | 1037.5348 | 35.8952 | 0 | 0 | 0 | 0 | 0 | 0 | 1073.43 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 1073.43 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
80 | M&C Tower Unit Material Tracking_TO_C |  |  | NA | Migrate existing unsupported ShopList Access database to a new centralized, managed database platform | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5806062 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2024-03-19 | 2024-03-19 | NA | NA | FALSE | 1550 | NA ¦ NA | 1550.102 | 1550.102 | 0 | 0 | 1064.7363 | 485.3657 | 0 | 0 | 0 | 0 | 0 | 0 | 1550.102 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 1550.102 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
81 | UO-FWM-Inspect ET (C) |  |  | NA | Data Collection Tool - System Inspections (non-Wildfire) (pge.com).The current Inspect, Engage, MPMT applications have released a minimal viable product (MVP) in 2020. The current System Inspections program requires annual updates to the detailed overhead inspection checklist, including impacts to Inspect Mobile application, Engage Web Portal, MPMT, SAP and BW. The proposed scope ensures that PG&E continues to better the applications for the multitude of needs in the system inspection process with special focus on: 1) The ability to quickly identify and efficiently assign work; 2) Quicker completion and data throughput; 3) Making planning easier and reducing human error with better detective controls. This technology is not in support of the Wildfire Mitigation program. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5798041 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2024-03-29 | NA | NA | FALSE | 1740.417 | NA ¦ NA | 5056.8822 | 5056.8822 | 650.3224 | 1926.7697 | 2019.0856 | 460.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 5056.8822 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 3051.1187 | 2005.7635 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
82 | Sys-Insp-WF-Mitigation 21-22 ET (C) HFTD |  |  | NA | The System Inspections Wildfire Mitigation Program Carryover project supports the Wildfire Mitigation Program.. The current Inspect, Engage, MPMT applications have released an MVP in 2020. The current System Inspections program requires annual updates to the detailed overhead inspection checklist including impacts to Inspect Mobile application, Engage Web Portal, MPMT, SAP and BW. The proposed scope ensures that we are continuing to better the applications for the multitude of needs in the system inspection process with special focus on 1) The ability to quickly identify and efficiently assign work, 2) Quicker completion and data throughput, 3) Making planning easier and reducing human error with better detective controls. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5798270 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-08-30 | 2023-01-15 | 2024-03-30 | Project Design | NA | FALSE | 2500 | NA ¦ NA | 3637.12 | 3637.12 | 630.1012 | 1692.4567 | 1023.9163 | 290.6457 | 0 | 0 | 0 | 0 | 0 | 0 | 3637.12 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 2525.6596 | 1111.4604 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
83 | FT-Micro_Radio_CapIncreReliab_Imp_TO_C |  |  | NA | FT - SCADA Radio Capacity and Reliability Improvements (TO) 2022 Project Description: This project migrates SCADA RTUs at substations that are on the ODN and migrated away from DSO leases or private 4 Wire circuits The scope of PO 5794363 is as follows: 1) Install a Tait repeater station at Gato Ridge and a spread spectrum microwave radio link from Gato Ridge to Red Rock. The station is necessary to fill gaps and improve mobile radio coverage in Santa Barbara County and surrounding areas. 2) Provide a diverse fiber optical connection along Electric Transmission 60kV line between Stockton Station A and Weber Substation for resiliency and increased bandwidth. Circuits will be migrated off of the existing microwave path onto the new fiber network. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5794363 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2015 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-25 | 2024-10-30 | 2024-06-27 | NA | NA | FALSE | NA | NA ¦ NA | 3362.9964 | 3362.9964 | 382.196 | 1095.3502 | 416.4676 | 442.1472 | 5.0811 | 0 | 0 | 0 | 0 | 0 | 3362.9964 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 3357.8995 | 5.0811 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
84 | Pole Test & Treat ET 2023 CAP |  |  | NA | Development of a mobile enabled inspection application for Electric Transmission Pole Test & Treat processes. This application would mitigate pole safety and compliance risks that exist with the current process.” | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5804306 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2024-06-30 | 2025-02-28 | Scope Change | NA | FALSE | 2260 | NA ¦ NA | 1977.4685 | 1977.4685 | 0 | 0 | 772.7733 | 1145.9154 | 18.5125 | 0 | 0 | 0 | 0 | 0 | 1977.4685 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1977.4684 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
85 | UO-AMR-Remote Sensing Data-TO_C HFTD |  |  | NA | This project seeks a centralized, ESRI compatible platform that acts as a centralized coordinator of the various data sets, allowing for greater data access and minimizing duplication of remote sensing data capture. In addition, chosen platform would require an open API architecture, allowing for greater collaboration with external partners (labs, universities, vendors). Engineers will customize | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5797623 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2024-08-15 | 2025-12-30 | Project Design | NA | TRUE | 9423 | NA ¦ NA | 1824.3025 | 1986.9577 | 148.1489 | 595.4254 | 405.9755 | 346.7089 | 259.8559 | 221.614 | 0 | 0 | 0 | 0 | 1765.3437 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 1379.4268 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
86 | Risk Model_APS_TO_C HFTD |  |  | NA | Wildfire Transmission Model Dashboards in PowerBI with data connected from Foundry to predict the failure of transmission asset so that annual inspection and work can be planned. Operability Assessment Dashboard: Predict the failure of transmission asset at given wind speed so that transmission asset health specialist can help with PSPS. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5807621 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | 2026-10-15 | 2026-10-15 | NA | NA | TRUE | 3176 | NA ¦ NA | 4045.6446 | 5850.6187 | 0 | 0 | 0 | 1418.4501 | 2259.1625 | 2170.5422 | 0 | 0 | 0 | 0 | 3680.0765 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1395.6447 | 2007.9332 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
87 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | Replace | NA | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5541386 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | OAI | NA | NA | FALSE | 2646 | NA ¦ NA | 5842.8154 | 5842.8154 | 2333.8457 | 1438.5655 | 768.7398 | 136.5927 | 5.2573 | 2.0205 | 0 | 0 | 0 | 0 | 5840.7949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 3491.6397 | 1438.5655 | 768.7398 | 136.5927 | 0.05449 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Cybersecurity [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
88 | 63-SCADA Electric Trans - SCADA MS LC_C |  |  | NA | Bucket for ongoing ET&S Work Management System configuration changes and enhancements- Systems scope includes P6, Clarity, Click, SAP WM components (including tables and forms), EPPM, AMS, ET GIS, and Unit Based Planning used in Capital and Expense Work Mgmt Implement system enhancements and configuration changes to maintain alignment between work management systems and related business processes; This is critical to keeping the work management systems and tools aligned to business needs. | Other - IT | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5508146 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 23698.734 | 23698.734 | 1376.3086 | 168.1435 | 83.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23698.734 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1860.3721 | -1.115 | 2579.152 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
89 | 63-SCADA Electric Trans - SCADA Comm_C |  |  | NA | Bucket to construct a redundant Telecom Transmission path from Helms PGP to Fresno Operations Center by constructing new microwave radio paths and overbuild of a fiber cable. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5508145 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 55717.3709 | 55717.3709 | 622.0181 | 22.9919 | 10.8986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55717.3709 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 2462.8564 | 696.7822 | 338.2225 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
90 | TRANSMISSION SCADA B/R (Break/Replace) |  |  | NA | Bucket for a web- or cloud-based relational database that would house all historical T-line and substation outage and relevant asset data so that users could easily perform custom queries to help with analyses related to improving grid reliability. The tables contained in this database would be designed to facilitate acquisition of specific outage data in a prescribed format required by the various regulatory agencies (e.g., CAISO, North America Transmission Forum (NATF), NERC-TADS) and for several benchmarking studies.Why:Currently historical outage data for electric transmission and substation are kept in various Excel workbooks which are not effectively linked with one another. Some, but not all, of these data are updated on our share point, but much of the data reside on an individual PC hard drive. This project would enable us to comply with the Records Information Management (RIM) process. Moreover, the current process is inefficient, prone to errors and does not enable users to acquire data and/or generate reports easily or automatically. The proposed system brings efficiency by automating data acquisition, minimizing errors associated with manual data entry and enabling many more users to gather data specific to their needs, including but not limited to report generation for both internal (executive leadership reliability meetings, RIBA score calculation, corrective action committees) and external (e.g., CAISO, NATF, NERC-TADS and various benchmarking studies) use. Note: This outage database is first phase of Transmission Data Management System, eventually this will house non outage related information as well. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | Non-IGP | 5509119 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 3728.7879 | 3732.7879 | 35.3488 | 9.8842 | 32.1659 | 53.6919 | 18.402 | 8.8214 | 0 | 0 | 0 | 0 | 3723.9665 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 6.0699 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
91 | FT - Teleprotection (TO)_Multi-sites_C |  |  | NA | FT - Teleprotection (TO) Replace manufacturer discontinued Electric Protection Relays at third party Cogens. Ensuring continued safe and reliable operation of the electric lines. Approximately 4 sites. Risk: Working with 3rd parties can cause delays. Determine if this can be done in one year or needs to be done over two years and reallocate budget appropriately. | Other - IT | Replace | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5541385 | NA | NA | NA | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2025-07-01 | 2026-03-20 | 2026-11-20 | Scope Change | NA | TRUE | 1500 | NA ¦ NA | 2921.6406 | 3197.6336 | 194.4057 | 279.9285 | 636.156 | 474.5233 | 877.5843 | 333.1466 | 0 | 0 | 0 | 0 | 2864.487 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1986.9026 | 0.03253 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
92 | FT- FiberMaint/Replace Metcalf-Eden_TO_C |  |  | San Jose, Santa Clara ¦ Santa Clara | The purpose of this project is to replace all spans of the Metcalf -Edenvale 115kV and IBM Harry Road 115kV Tap non-track resistant ADSS fiber optic cable route that are within an excessively high E-fields with new 72 count OPGW fiber optic cable. The previously installed ADSS fiber optic cable on Metcalf-Edenvale #2 115 kV between Metcalf Sub and Edenvale Sub and the IBM Harry Road 115 kV Tap are non-track resistant. A span of that cable route failed and fell to the ground. Forensic investigation revealed that the cable had failed due to induced current on the cable jacket (tracking). Subsequently, E-field analysis was performed on the entire ADSS route. The analysis indicated that the ADSS on all spans must be removed and replaced with OPGW. In order to keep the enterprise operational during the transmission line outage, diverse paths with lease lines need to be established, and are included in the scope of this project. Associated lease line costs will be estimated once routes are designed. | Other - IT | Replace | NA | NA | Other [See Notes] | System Operations | NA | NA | 2025-06-04 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5791976 | T.0006243 | IO - Fiber Optic Maintenance and Replace | 2 | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-29 | 2022-08-31 | 2026-01-09 | Permitting | Project Design | TRUE | 3738 | NA ¦ NA | 2187.7717 | 2556.4865 | -27.8757 | 708.8953 | 175.141 | 198.939 | 864.8706 | 464.2797 | 0 | 0 | 0 | 0 | 2092.2068 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -74.8948 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
93 | Oakland J UG Fiber Build |  |  | Oakland, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Other - IT | New | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-02-09 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.5059 | NA | NA | NA | NA | NA | NA | Non-IGP | 5540639 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 2F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E ¦ AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020 ¦ 2022 | Operational | 1 | NA | 2015-03-01 | 2022-01-30 | Prioritization | NA | FALSE | $15,000 ¦ $30,000 | NA ¦ NA | 45.2283 | 45.2283 | 23.3855 | 11.7479 | 2.4077 | 1.8812 | 1.3953 | 0.5 | 0 | 0 | 0 | 0 | 44.7283 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil
94 | 3FA DET Plan |  |  | NA | Forecast placeholder for 500 kV relay replacements | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | False ¦ False ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | 500 kV | NA | NA | NA | 4.0111 | Non-IGP | 5555020 | NA | NA | NA | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 4500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
95 | LOS BANOS: Upgrade ML 500 KV Remote End |  |  | Monterey | This project will resolve current configuration issues and address reliability concerns. This project will rebuild Moss Landing 500kV Substation within the existing substation fence line. The project will replace the existing 500kV breakers and switches in a BAAH configuration, and upgrade the protection schemes. This will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-10 | 34 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 41.3213 | NA | 500 kV | 321 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5760484 | T.0000678 | MOSS LANDING 500KV Upgrade | 6 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-02-03 | 2020-03-31 | 2020-06-22 | NA | NA | FALSE | 46400 | NA ¦ NA | 3033.8794 | 3033.8794 | 45.1713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3033.8794 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 39.7381 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
96 | MOSS LANDING: Inst 500 KV Ctrl Building |  |  | Monterey | This project will resolve current configuration issues and address reliability concerns. This project will rebuild Moss Landing 500kV Substation within the existing substation fence line. The project will replace the existing 500kV breakers and switches in a BAAH configuration, and upgrade the protection schemes. This will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-10 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 41.3213 | NA | 500 kV | 321 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5760568 | T.0000678 | MOSS LANDING 500KV Upgrade | 6 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-05-17 | 2020-03-31 | 2020-06-22 | NA | NA | FALSE | 46400 | NA ¦ NA | 14301.5367 | 14301.5367 | 1121.5607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14301.5367 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 1108.3708 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
97 | METCALF: Upgrade ML 500 KV Remote End |  |  | Santa Clara | This project will resolve current configuration issues and address reliability concerns. This project will rebuild Moss Landing 500kV Substation within the existing substation fence line. The project will replace the existing 500kV breakers and switches in a BAAH configuration, and upgrade the protection schemes. This will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-05 | 34 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 500 kV | 321 | 5a.Mitigates System Wide Failure Risk | NA | 3.003 | Non-IGP | 5769038 | T.0000678 | MOSS LANDING 500KV Upgrade | 6 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-02-03 | 2020-03-31 | 2020-06-29 | NA | NA | FALSE | 46400 | NA ¦ NA | 6072.8171 | 6072.8171 | -86.2355 | 13.1268 | 0 | 204.9099 | 61.4471 | -7.5 | 0 | 0 | 0 | 0 | 6080.3171 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 ¦ 2025 ¦ 2026 | -75.6837 | -162.5017 | 0 | 173.4701 | 52.0191 | -6.3493 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
98 | MIDWAY: REPL BANK 11 AND VINCENT RELAYS |  |  | Buttonwillow CDP, Kern | The scope of the replacement includes installing new microprocessor relays following new 500/230 kV standard on Midway Bank 11. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-03 | 12 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 ¦ 230 kV | 245 | 5a.Mitigates System Wide Failure Risk | NA | 3.003 | Non-IGP | 5773128 | T.0002454 | Midway Bank 11 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-01-03 | 2022-08-31 | 2025-07-18 | Bundling Dependencies | NA | TRUE | 5876 | NA ¦ NA | 18139.9404 | 17804.3976 | 383.0356 | 1521.738 | 9492.7167 | 2270.6762 | 3950.3622 | 15.6911 | 0 | 0 | 0 | 0 | 18138.7065 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 17582.9379 | 1.1907 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
99 | Midway Bank 13 Relay Project |  |  | Buttonwillow CDP, Kern | The scope of the replacement includes installing new microprocessor relays following new 500/230 kV standard on Midway Bank 13. | Substation - Protection Relay | Replace | NA | T.0002454 ¦ T.0004292 ¦ T.0006402 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-03 | 23 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 ¦ 230 kV | 245 | 5a.Mitigates System Wide Failure Risk | NA | 3.003 | Non-IGP | 5773129 | T.0002455 | Midway Bank 13 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-07-01 | 2022-08-31 | 2025-12-20 | Bundling Dependencies | NA | TRUE | 7500 | NA ¦ NA | 11832.7863 | 11832.7863 | 506.9821 | 2370.3979 | 910.6538 | 4897.1109 | 2485.7111 | 90.2413 | 0 | 0 | 0 | 0 | 11742.545 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 11402.0133 | 87.1864 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
100 | ROUND MOUNTAIN: Repl 500 KV RM-TM RLY 2 |  |  | Round Mountain CDP, Shasta | The scope of this project is to replace the line relays on the Round Mountain – Table Mountain #2 500kV Line at Round Mtn.as well as upgrade the operator interface (Install associated network architecture necessary to incorporate this line in existing HMI). The newly installed relaying package will include two sets of line protection relays, (SEL-411L’s and GE L90’s), and breaker failure relays, (SEL 451’s). | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-09 | 34 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 500 kV | 978 | 3. Emergency Preparedness | NA | 3.003 | Non-IGP | 5773132 | T.0002458 | RM:ROUND MTN - TABLE MTN #2 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-12-16 | 2020-12-31 | 2021-04-25 | NA | NA | FALSE | 3630 | NA ¦ NA | 2119.9808 | 2119.9808 | 1187.4596 | 11.9394 | 4.5855 | 16.4001 | 15.0561 | 0 | 0 | 0 | 0 | 0 | 2119.9808 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 1719.3296 | 9.8279 | 3.7745 | 13.4996 | 12.3933 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
101 | TABLE MOUNTAIN: Repl 500 KV TM-RM RLY 2 |  |  | Butte | The scope of this project is to replace the line relays at Table Mtn. on the Round Mountain – Table Mountain #2 500kV Line as well as upgrade the operator interface (Install associated network architecture necessary to incorporate this line in existing HMI at both Round Mountain and Table Mountain). The newly installed relaying package will include two sets of line protection relays, (SEL-411L’s and GE L90’s), and breaker failure relays, (SEL 451’s). | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-20 | 18 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 47.516 | NA | 500 kV | 978 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5773133 | T.0002459 | TM:ROUND MTN - TABLE MTN #2 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-12-14 | 2021-05-06 | 2021-04-25 | NA | NA | FALSE | 3840 | NA ¦ NA | 3089.9712 | 3089.9712 | 1654.4045 | 52.677 | 3.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.9712 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 2542.4197 | 43.7656 | 2.8658 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
102 | TABLE MOUNTAIN: Repl Cap BK 6 Relays |  |  | Butte | Replace Table Mountain Cap Bank 6 | Substation - Protection Relay | Replace | NA | T.0003940 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-20 | 34 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 47.516 | NA | 500 kV | NA | NA | NA | 3.0022 | Non-IGP | 5779902 | T.0003939 | Table Mountain Cap 6 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-12-31 | NA | 2027-03-02 | NA | NA | TRUE | NA | NA ¦ NA | 3.8125 | 3932.8864 | 0 | 0 | 0 | 0 | 4 | 179.0739 | 1000 | 2000 | 750 | 0 | 3.8125 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
103 | Table Mountain Cap 5 Relay Project |  |  | Butte | Replace Table Mountain Cap Bank 5 | Substation - Protection Relay | Replace | NA | T.0003939 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-20 | 34 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 47.516 | NA | 500 kV | NA | NA | NA | 3.0022 | Non-IGP | 5779903 | T.0003940 | Table Mountain Cap 5 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-12-31 | NA | 2027-03-02 | NA | NA | TRUE | NA | NA ¦ NA | 5.6106 | 3933.4036 | 0 | 0 | 0 | 0 | 6 | 177.793 | 1000 | 2000 | 750 | 0 | 5.6106 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
104 | Midway: Repl Building |  |  | Buttonwillow CDP, Kern | The existing 500kV control building at Midway has deficiencies that prevent completion of in-flight and future projects. These deficiencies include wire trays that are filled to twice the allowable capacity in some locations, and overly congested outdoor-to-indoor building wiring egress points . PG&E project management, substation engineering, and the construction departments have met on-site on several occasions to review a variety of possible solutions and have determined that these deficiencies cannot be mitigated in a safe and reliable manner in the existing building. The recommended course of action is to implement future protection and control projects in a new modular building. The problem identification and solution is similar to Moss Landing (New modular building design is nearly complete)•The new building(s) will be designed to address single point vulnerabilities. The “System A” and “System B” relaying be placed in different buildings, or different rooms within the same building. •The building(s) will be sized for the ultimate substation plan with predetermined locations for equipment (Layout). •Use the Moss Landing 500 kV control building design as the go-by.•The dual battery system is not needed at this time (it’s not the acute issue that we are solving now), but the two buildings should be set-up to allow easy future implementation of a dual battery system (Reference Moss Landing DWG: 4131039)•Procure buildings that are ready for populating with protection and control racks. Unlike Moss Landing where the building will be delivered fully populated with Protection and Control equipment, each independent Midway project will fund and install the required bay protection and control racks within the new building by following a preplanned layout. | Substation - Modular Protection and Automation Control Building | Replace | NA | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-03 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 kV | 707 | 5a.Mitigates System Wide Failure Risk | NA | 3.003 | Non-IGP | 5782198 | T.0004292 | Midway: Repl 500k Building | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-10 | 2022-02-15 | 2023-03-15 | Workforce | NA | TRUE | 7400 | NA ¦ NA | 20300.9311 | 20953.7801 | 2165.5461 | 11921.4298 | 3651.2437 | 1553.1264 | 319.4665 | 653.2354 | 0 | 0 | 0 | 0 | 20300.5447 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 18427.9518 | 1553.1264 | 319.4665 | 0.38643 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
105 | MIDWAY: REP VINCENT AND LB RELAYS |  |  | Buttonwillow CDP, Kern | The scope of this project is to replace the line relays on the Midway-Vincent #2 500kV Line and Los Banos-Midway #2 500kV Line at Midway substation only. The scope includes the upgrade of the operator interface on the Midway terminal of the Midway-Vincent 500kV line #2, consisting of installation of associated network architecture necessary to incorporate this line in existing HMI. | Substation - Protection Relay | Replace | NA | T.0002454 ¦ T.0002455 ¦ T.0004292 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-03 | 34 | Lifecycle Replacement Analysis | Other - Status Quo | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 kV | NA | 5a. Mitigates System Wide Failure Risk | NA | 3.003 | Non-IGP | 5792705 | T.0006402 | MIDWAY: REP VINCENT AND LB RELAYS | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-07-08 | 2026-06-20 | 2027-02-10 | Clearances | NA | TRUE | 17800 | NA ¦ NA | 12164.539 | 18913.9816 | 0 | 183.7951 | 555.2989 | 3945.1099 | 6284.2079 | 6463.4005 | 1482.1693 | 0 | 0 | 0 | 10968.4118 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
106 | Midway Los Banos #2 Relay Upgrade |  |  | Merced | The scope of this project is to replace the line relays on the Midway-Vincent #2 500kV Line and Los Banos-Midway #2 500kV Line at Midway substation only. The scope includes the upgrade of the operator interface on the Midway terminal of the Midway-Vincent 500kV line #2, consisting of installation of associated network architecture necessary to incorporate this line in existing HMI. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0002454 ¦ T.0002455 ¦ T.0004292 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-06 | 13 | Lifecycle Replacement Analysis | Other - Status Quo | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 53.2803 | NA | 500 kV | NA | NA | NA | 3.003 | Non-IGP | 5802726 | T.0006402 | MIDWAY: REP VINCENT AND LB RELAYS | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-10-02 | 2026-06-20 | 2026-10-30 | NA | NA | TRUE | 17800 | NA ¦ NA | 408.974 | 967.5987 | 0 | 0 | 167.6902 | 105.541 | 130.4176 | 263.0679 | 115.5467 | 25.686 | 0 | 0 | 403.6488 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
107 | MIDWAY: REP 525kV Bay 1 |  |  | Buttonwillow CDP, Kern | The scope of this project is to replace the line relays and breaker failure relays in Midawy Bay 1 | Substation - Protection Relay | Replace | NA | EX139362 ¦ EX139364 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-03 | 12 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 kV | NA | NA | NA | 4.0111 | Non-IGP | EX130457 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1000 | 3500 | 3000 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
108 | Table Mountain: 525 kV Bus Diff |  |  | Butte | Reaplce Table Mountain 525 kV Bus Diff | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-20 | 39 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 47.516 | NA | 500 kV | NA | NA | NA | 3.0021 | Non-IGP | EX139361 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-12-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1500 | 2000 | 3000 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
109 | DC: REPL DIABLO CANYON - MIDWAY #2 |  |  | Avila Beach CDP, San Luis Obispo ¦ Buttonwillow CDP, Kern ¦ Kern ¦ San Luis Obispo | Upgrade Diablo Canyon relay for work at Midway | Substation - Protection Relay | Replace | NA | EX130457 ¦ EX139364 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-04-03 | 12 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 kV | NA | NA | NA | 4.0111 | Non-IGP | EX139362 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-02-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 500 | 1000 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
110 | Gates: Midway - Gates |  |  | Fresno | Upgrade Gates relay for work at Midway | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-12 | 12 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 77.6619 | NA | 500 kV | NA | NA | NA | 4.0111 | Non-IGP | EX139363 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-02-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 500 | 1000 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
111 | MIDWAY: REP 525kV Bay 4 |  |  | Buttonwillow CDP, Kern | The scope of this project is to replace the line relays and breaker failure relays in Midawy Bay 4 | Substation - Protection Relay | Replace | NA | EX139362 ¦ EX130457 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | NA | 2026-03-03 | 12 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 kV | NA | NA | NA | 4.0111 | Non-IGP | EX139364 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-12-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 1000 | 3500 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
112 | 3FB DET Plan |  |  | NA | Forecast placeholder for 230/115/70/60 kV Relay Replacement | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | False ¦ False ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | 230 ¦ 115 ¦ 70 ¦ 60 kV | NA | NA | NA | 3.0022 | Non-IGP | 5555021 | NA | NA | NA | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 24188.027 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 7434.983 | 0 | 1301.713 | 3069.705 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
113 | DRUM PH 1: Repl SPS Relay Scheme |  |  | Placer | Replace the relays associated with the existing Drum SPS | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-12 | 34 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.2491 | NA | 115 ¦ 60 kV | NA | NA | NA | 3.0021 | Non-IGP | 5758495 | T.0000060 | Drum #1 PH SPS Relays_CB10 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-05-11 | NA | 2027-08-04 | NA | NA | TRUE | NA | NA ¦ NA | 149.1536 | 1173.338 | 15 | 14 | 10 | 11 | 97.5 | 75.7206 | 335.1968 | 600 | 50 | 0 | 147.6174 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
114 | LAS POSITAS: INSTALL 230KV & 60KV RELAY |  |  | Livermore, Alameda | This planned project will replace Las Positas Substation’s failed CKT SW 286 and Motor Operated Air Switch (MOAS) 289 with four (4) 230 kV circuit breakers (CBs) that will be interconnected in a “Ring” bus configuration, install one (1) new control building to be installed near the 60 kV yard, install new relays on all new 230 kV CBs (Nos. 222, 232, 262, 272). This planned project is needed to maintain safe and reliable power to the East Bay area and will support PG&E top-level initiatives such as improved service reliability, improved operational flexibility, and reducing operating costs. | Substation - Protection Relay | New | NA | NA | Asset Condition | Relay Upgrades | NA | NA | 2026-04-02 | 27 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.2184 | NA | 230 kV | NA | NA | NA | NA | Non-IGP | 5791153 | T.0000185 | Las Positas:Convert 230kV Bus & Repl Rly | 5 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-01 | 2023-06-30 | 2023-06-30 | NA | NA | FALSE | 7851 | NA ¦ NA | 5449.8718 | 5449.8718 | 1456.6548 | 4251.3101 | 1263.0746 | 53.1001 | -1924.3206 | 0.8124 | 0 | 0 | 0 | 0 | 5449.0594 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 7320.2799 | 53.1002 | -1924.3206 | 0.81237 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
115 | LAS POSITAS: 230KV & 60KV RELAY Phase 2 |  |  | Livermore, Alameda | This planned project will replace Las Positas Substation’s failed CKT SW 286 and Motor Operated Air Switch (MOAS) 289 with four (4) 230 kV circuit breakers (CBs) that will be interconnected in a “Ring” bus configuration, install one (1) new control building to be installed near the 60 kV yard, install new relays on all new 230 kV CBs (Nos. 222, 232, 262, 272). This planned project is needed to maintain safe and reliable power to the East Bay area and will support PG&E top-level initiatives such as improved service reliability, improved operational flexibility, and reducing operating costs. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-04-02 | 26 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.22 | NA | 230 ¦ 60 kV | NA | NA | NA | 3.0021 | Non-IGP | 5798814 | T.0000185 | Las Positas:Convert 230kV Bus & Repl Rly | 5 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-01 | 2023-06-30 | 2024-06-18 | Project Design | NA | TRUE | 7851 | NA ¦ NA | 3005.264 | 3005.264 | 0 | 2.7948 | -0.8016 | 934.5338 | 2068.7371 | 0 | 0 | 0 | 0 | 0 | 3005.264 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 844.2082 | 2161.0558 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
116 | Monta Vista 115kV Bus Diff Project |  |  | Cupertino, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-03 | 16 | Lifecycle Replacement Analysis | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.8314 | NA | 115 kV | 472 | NA | NA | NA | NA | 5775238 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-06-18 | 2020-08-07 | 2018-12-17 | NA | NA | FALSE | 39600 | NA ¦ NA | 2125.0158 | 2125.0158 | 15.1937 | 4.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2125.0158 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 15.1937 | 4.7289 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
117 | LOS ESTEROS: Repl CB 652 Line Relay |  |  | San Jose, Santa Clara | The Montague Substation Bundle and Remote End projects will replace Circuit Breaker (CB) 132, CB 142, Circuit Switcher (CSW) 176, CSW 186, replace protection relays for Bank 1, Bank 2, Bank 3, line and bus protection relays, install Distribution SCADA on CB 2100, CB 2200 and CB 2300. In addition, the line and bus protection relays at the Remote End Substations Los Esteros and Trimble will be replaced. The Montague Substation Bundle and Remote Ends are comprised of multiple projects that contribute to the betterment of the PG&E Electric System. CB132 and CB142 are being replaced as part of the Deteriorated Breakers Replacement Program to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. The replacement of the old Protection relays at Montague Substation, as well as the Remote Ends will improve system reliability, whereas installing SCADA on all the distribution equipment in Montague Substation will provide system visibility for low side devices at Montague Substation. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-09 | 20 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.1703 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5525505 | T.0000706 | MONTAGUE SUB 115 KV CB 132, 142 | 4 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-03 | 2023-02-01 | 2022-04-08 | NA | NA | FALSE | 9841 | NA ¦ NA | 1848.3513 | 1848.3513 | 292.8014 | 1093.045 | 30.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1848.3513 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 ¦ 2026 | 272.1468 | 1061.9 | 29.5646 | 0 | -5e-05 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
118 | TRIMBLE: Repl CB 312 Line Relay |  |  | San Jose, Santa Clara | The Montague Substation Bundle and Remote End projects will replace Circuit Breaker (CB) 132, CB 142, Circuit Switcher (CSW) 176, CSW 186, replace protection relays for Bank 1, Bank 2, Bank 3, line and bus protection relays, install Distribution SCADA on CB 2100, CB 2200 and CB 2300. In addition, the line and bus protection relays at the Remote End Substations Los Esteros and Trimble will be replaced. The Montague Substation Bundle and Remote Ends are comprised of multiple projects that contribute to the betterment of the PG&E Electric System. CB132 and CB142 are being replaced as part of the Deteriorated Breakers Replacement Program to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. The replacement of the old Protection relays at Montague Substation, as well as the Remote Ends will improve system reliability, whereas installing SCADA on all the distribution equipment in Montague Substation will provide system visibility for low side devices at Montague Substation. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-05 | 29 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2309 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5525504 | T.0000706 | MONTAGUE SUB 115 KV CB 132, 142 | 4 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-26 | 2023-02-01 | 2023-01-20 | NA | NA | FALSE | 9841 | NA ¦ NA | 788.6558 | 788.6558 | 97.8396 | 428.5919 | 142.3549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788.6558 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 89.5944 | 412.3599 | 136.9636 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
119 | MONTAGUE: Replace Line Relay |  |  | San Jose, Santa Clara | The Montague Substation Bundle and Remote End projects will replace Circuit Breaker (CB) 132, CB 142, Circuit Switcher (CSW) 176, CSW 186, replace protection relays for Bank 1, Bank 2, Bank 3, line and bus protection relays, install Distribution SCADA on CB 2100, CB 2200 and CB 2300. In addition, the line and bus protection relays at the Remote End Substations Los Esteros and Trimble will be replaced. The Montague Substation Bundle and Remote Ends are comprised of multiple projects that contribute to the betterment of the PG&E Electric System. CB132 and CB142 are being replaced as part of the Deteriorated Breakers Replacement Program to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. The replacement of the old Protection relays at Montague Substation, as well as the Remote Ends will improve system reliability, whereas installing SCADA on all the distribution equipment in Montague Substation will provide system visibility for low side devices at Montague Substation. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-05 | 29 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2309 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5774460 | T.0000706 | MONTAGUE SUB 115 KV CB 132, 142 | 4 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-03 | 2023-02-01 | 2023-03-20 | NA | NA | FALSE | 9841 | NA ¦ NA | 2139.4966 | 2139.4966 | 433.0661 | 941.8198 | 606.6244 | -1.4891 | 14.6457 | 0 | 0 | 0 | 0 | 0 | 2139.4966 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 2084.3248 | -1.4577 | 14.3366 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
120 | PA SW STA: Repl PA-Ravenswood Relay |  |  | Palo Alto, Santa Clara | This project will replace the electromechanical relays on Ravenswood - Palo Alto Switching Station (PASS) 115kV #1 and #2 with two levels of high speed protection in accordance with the latest microprocessor protection standards thus addressing a combination of critical problems related to the protection on the following circuit by replacing aged, unreliable, and unsafe relays with standard packages: • Ravenswood - Palo Alto Switching Station 115kV #1 and #2 By completing this project within the timeframe specified, the Company will be diligently addressing known reliability issues attributed to the existing protection equipment. This course of action directly correlates to PG&E’s vision and values through the company’s goal of improving reliability. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-06 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.0138 | NA | 115 kV | 124 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5758485 | T.0000786 | PALO ALTO LINE RELAY 74002152 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-05-01 | 2019-06-28 | 2021-09-28 | Workforce | NA | FALSE | 1000 | NA ¦ NA | 2933.3546 | 2933.3546 | 1463.9729 | 60.1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2933.3546 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 2682.0598 | 55.6999 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
121 | RAVENSWOOD: Repl 115 KV RD-PA 1-2 RLY |  |  | Menlo Park, San Mateo | System Protection recommends to replace the existing electromechanical relays and POTT over lease line with two levels of current differential protection (GE L90 and SEL311L) over redundant channels on existing PG&E’s fiber optics for the Ravenswood - Palo Alto 115 KV #1 and #2 Line Relay Replacement Project. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-05 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.3472 | NA | 115 kV | 459 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5758486 | T.0000787 | RAVENSWOOD LINE RELAY 74002153 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-05-01 | 2019-06-28 | 2021-08-22 | Workforce | NA | FALSE | 1395 | NA ¦ NA | 3083.938 | 3083.938 | 1379.0967 | 30.8996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3083.938 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 2907.4301 | 29.2638 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
122 | CARIBOU PH 1: Repl BF Project |  |  | Plumas | install a breaker failure relay to insure people safety, system reliability and asset protection in case CB 62 failed to trip under a fault condition. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-10 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.96252 | NA | 60 kV | 430 | 3. Emergency Preparedness | NA | NA | NA | 5758501 | T.0000829 | CARIBOU PH 1 BF PROJECT | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-08-03 | 2018-11-19 | 2020-10-01 | Prioritization | NA | FALSE | 989 | NA ¦ NA | 1295.1783 | 1295.1783 | 7.8863 | 2.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1295.1783 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 7.8863 | 2.123 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
123 | TRACY: REPL CB 162 & BUS TOTAL OC RELAY |  |  | Tracy, San Joaquin | Tracy CB162 has a combination of electromecahnical relays and microprocessor relay. These relays were installed in 1998 and are 19 years old. The microprocessor relay is past its lifecycle and the electromechanical relays are at their life cycle. In order to improve system reliability, System Protection proposes to replace the line relays with new SMP standard relays using 400 series SEL relays. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-31 | 51 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.7469 | NA | 115 kV | 131 | 5a.Mitigates System Wide Failure Risk | NA | 3.0011 | Non-IGP | 5778258 | T.0000887 | TRACY SUB 115 KV CB 152, 162 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2031-05-20 | NA | 2031-12-09 | NA | NA | FALSE | NA | NA ¦ NA | 42.3799 | 1267.1255 | 2.3849 | 2.5827 | 2.8403 | 1.4529 | 0 | 2.7881 | 0 | 0 | 0 | 0 | 42.3799 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
124 | EASTSHORE: REPL CB322 and CB332 Relays |  |  | Hayward, Alameda | Eastshore-Mt Eden #1 and #2 lines are short line slightly longer than 1.00 mile. For such a short line, one set of line differential relay plus another set of overcurrent relay configuration does not meet current PG&E protection standard and results in significant coordination problems when line differential protection is not available for any reason (e.g., relay or communication channel maintenance or failure). The primary relay L90 is the only relay that provides high speed fault clearance. If L90 is out of service due to relay/channel failure or scheduled maintenance, etc., the line is only protected by non-pilot phase & ground overcurrent relays, which are inherently difficult to coordinate for the short line protection in this area, and have delayed fault clearance time. This is especially TRUE for phase overcurrent protection, which have to be set above max load current. The sensitivity, selectivity and speed of the existing protection is not at the level desirable for transmission lines in this particular area. In addition, the SEL-267 is an older vintage product. It is close to the end of the useful life. Coordination problems during the time of differential protection unavailability might result in unnecessary customer loss. System Protection recommends that the backup relays at both ends be replaced with new SEL line differential relays with separate communication channel from the primary relay. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-04 | 24 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.9849 | NA | 115 kV | 177 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5760302 | T.0001220 | EASTSHORE-MT EDEN #1&#2 115KV RELAY | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-05-24 | 2023-04-12 | 2023-07-05 | NA | NA | FALSE | 4419 | NA ¦ NA | 2131.7799 | 2131.7799 | 176.3088 | 1645.7254 | 110.7066 | 116.0869 | 0 | 0 | 0 | 0 | 0 | 0 | 2131.7799 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 1849.1137 | 105.6765 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $3 Mil -$5 Mil ¦ $3 Mil -$5 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
125 | Mt Eden: REPL CB142 and CB182 Relays |  |  | Hayward, Alameda | Eastshore-Mt Eden #1 and #2 lines are short line slightly longer than 1.00 mile. For such a short line, one set of line differential relay plus another set of overcurrent relay configuration does not meet current PG&E protection standard and results in significant coordination problems when line differential protection is not available for any reason (e.g., relay or communication channel maintenance or failure). The primary relay L90 is the only relay that provides high speed fault clearance. If L90 is out of service due to relay/channel failure or scheduled maintenance, etc., the line is only protected by non-pilot phase & ground overcurrent relays, which are inherently difficult to coordinate for the short line protection in this area, and have delayed fault clearance time. This is especially TRUE for phase overcurrent protection, which have to be set above max load current. The sensitivity, selectivity and speed of the existing protection is not at the level desirable for transmission lines in this particular area. In addition, the SEL-267 is an older vintage product. It is close to the end of the useful life. Coordination problems during the time of differential protection unavailability might result in unnecessary customer loss. System Protection recommends that the backup relays at both ends be replaced with new SEL line differential relays with separate communication channel from the primary relay. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-05 | 32 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.6074 | NA | 115 kV | NA | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5785439 | T.0001220 | EASTSHORE-MT EDEN #1&#2 115KV RELAY | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-05-24 | 2023-04-12 | 2023-10-10 | Prioritization | NA | FALSE | 4419 | NA ¦ NA | 2646.2483 | 2646.2483 | 176.2458 | 1849.084 | 459.9387 | 59.6249 | 26.8185 | 0 | 0 | 0 | 0 | 0 | 2646.2483 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 2426.2533 | 56.2278 | 25.2906 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $3 Mil -$5 Mil ¦ $3 Mil -$5 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
126 | FAMOSO: Repl CB 132 & CB 152 RELAY PROJ |  |  | Kern | This project is to replace outdated protection relays with new microprocessor relays would reduce maintenance and provide event recording capability allowing for timely evaluation of line faults and proved line fault locations on our transmission lines on CB 152 and CB 132. The relays on Famoso CB 132 and 152 are GYC and JBCG GE electromechanical relays are over 50 years old and have reached end of their life cycle. The performance and functionality of electromechanical relays are not as good as the latest digital relays. They have no fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-05 | 15 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.8913 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5764419 | T.0001223 | FAMOSO CB 132 & CB 152 RELAY PROJECT | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-12-03 | 2023-12-29 | 2025-04-17 | Construction Delays | NA | TRUE | 4553 | NA ¦ NA | 4349.451 | 4408.3501 | 60.6773 | 2332.857 | 596.6483 | 803.8756 | 525.6679 | 60.4553 | 0 | 0 | 0 | 0 | 4347.8948 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 3815.3986 | 1.3398 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
127 | MARTIN: Upgrade 115 KV Differential |  |  | Brisbane, San Mateo | Install Martin 115kV Bus Section “E”, “F” and “G” SET B bus 1 & 2 differential scheme with the current Standard integrated SEL-587Z scheme. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-12 | 15 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 18.2105 | NA | 115 kV | 483 | 5a.Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5764431 | T.0001236 | MARTIN 115KV DIFFERENTIAL UPGRADE | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-17 | 2023-06-12 | 2024-10-11 | Prioritization | NA | TRUE | 8911 | NA ¦ NA | 7949.9243 | 7969.0031 | 2553.3688 | 3062.7952 | 68.819 | 1488.2494 | 478.8784 | 45.442 | 0 | 0 | 0 | 0 | 7923.5611 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 6849.7502 | 436.1672 | 24.0118 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
128 | NEWARK 115KV BUS DIFFERENTIAL |  |  | Fremont, Alameda | Newark 115kV bus is one of the most critical busses in the system as identified by Transmission Planning and Transmission Operations. If existing bus differential is cut our or fails to clear the fault, remote backup protection cannot clear the fault fast enough to maintain stability. NERC requirement for TPL (planning) standard requires the fully redundant bus protection on all the critical busses. Based on that, System Protection strongly recommends to add fully redundant bus differential protection for Newark 115kV bus sections D, E and F. This installation will significantly improve reliability of bus protection and eliminate existing deficiencies related to maintenance and clearances. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-03 | 18 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 27.7611 | NA | 115 kV | 177 | 5a.Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5764434 | T.0001238 | NEWARK 115KV BUS DIFFERENTIAL | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 3 | 2027-09-13 | NA | 2030-02-26 | NA | NA | FALSE | NA | NA ¦ NA | 320.6211 | 16188.3962 | 41.007 | 83.322 | 9.3605 | 161.9026 | 20.8924 | 188.8511 | 1000 | 1218.32 | 9000 | 4000 | 320.6211 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
129 | OAKLAND X: Upgd 115 KV Diff EDR |  |  | Oakland, Alameda | This project supports the replacement of Oakland X 115kV Bus Differential. This requires the installation of new bus protection relays. The new microprocessor relays will also be easier to maintain than the old relays. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-12 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.1294 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5764437 | T.0001244 | OAKLAND X 115KV DIFFERENTIAL UPGRADE | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-01-15 | 2019-04-11 | 2020-01-31 | Workforce | NA | FALSE | 8445 | NA ¦ NA | 5982.2437 | 5982.2437 | 94.8164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5982.2437 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 91.3941 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
130 | RADUM: Upgrade Protection |  |  | Pleasanton, Alameda | Replace the line relays to bring up to current standard for breakers 22, 72 and 82. Add CT's to breakers 22,72, 82 and add three new CCVT/PT to measure bus section E voltage. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-03 | 51 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.61928 | NA | 60 kV | 124 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5758487 | T.0001252 | RADUM PROTECTION UPGRADE | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-09-01 | 2020-12-15 | 2021-05-03 | NA | NA | FALSE | 3900 | NA ¦ NA | 3247.7101 | 3247.7101 | 1420.5532 | -0.3185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3247.7101 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 3162.8321 | -0.30964 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $2 Mil - $3 Mil ¦ $3 Mil -$5 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
131 | EVERGREEN: Upgrade 60 KV Protection |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-05 | 41 | Lifecycle Replacement Analysis | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.3776 | NA | 60 kV | 579 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5770123 | T.0001685 | Evergreen Substation Upgrade | 7 | 3F | NA ¦ 5738678 ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-05-28 | 2018-05-21 | 2020-08-03 | Prioritization | NA | FALSE | 27200 | NA ¦ NA | 3810.0224 | 3810.0224 | 98.9747 | 16.6347 | 1.1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3810.0224 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 91.5542 | 15.3876 | 1.0598 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
132 | TESLA: Repl 230 KV Bus Differential |  |  | Alameda | The Tesla 230kV Bus Differential Replacement Project will remove old equipment and install new Bus Differential relaying. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-19 | 50 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 627 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5764661 | T.0002021 | Tesla 230kV Bus Differential Replacement | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-11-20 | 2019-07-31 | 2020-11-23 | Workforce | NA | FALSE | 14900 | NA ¦ NA | 15300.9309 | 15300.9309 | 97.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15300.9309 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 97.0173 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
133 | Tesla 230kV Bus Section E - Diff Repl |  |  | Alameda | The Tesla 230kV Bus Differential Replacement Project will remove old equipment and install new Bus Differential relaying. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-19 | 51 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | NA | NA | NA | NA | NA | 5793949 | T.0002021 | Tesla 230kV Bus Differential Replacement | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-11-20 | 2019-07-31 | 2022-03-25 | Workforce | NA | FALSE | 14900 | NA ¦ NA | 2341.2525 | 2341.2525 | 1085.5946 | 1168.5466 | 30.5881 | -16.5969 | 0 | 0 | 0 | 0 | 0 | 0 | 2341.2525 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 2319.391 | 30.4822 | -16.5395 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
134 | HUMBOLDT BAY PP: Repl Generator Relays |  |  | Humboldt | Replace the existing VAMP 210 and 265 generator protection relays for each of the 10 generators at Humboldt Bay Generating Station. Due to reliability issues at other sites, the lack of breaker failure protection, and the VAMP relays not being on the list of approved PG&E relay equipment, it has been determined that the VAMP relays should be replaced with the most current PG&E approved generator relays (redundant SEL 700G) and SCADA equipment. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-03 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.2745 | NA | 60 kV | 1259 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5774820 | T.0002968 | Humboldt Bay PP Generator Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-10-22 | 2019-08-20 | 2020-01-15 | NA | NA | FALSE | 3600 | NA ¦ NA | 1692.8105 | 1692.8105 | 94.8211 | 151.8664 | 113.7299 | 58.5807 | 0 | 0 | 0 | 0 | 0 | 0 | 1692.8105 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
135 | LOS ESTEROS 115KV DIFFERENTIAL UPGRADE |  |  | San Jose, Santa Clara | Install redundant bus differential scheme Los Estero 115kV Bus. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-09 | 23 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.1703 | NA | 115 kV | 483 | 5a.Mitigates System Wide Failure Risk | NA | 3.0022 | Non-IGP | 5521171 | T.0003192 | Los Estero 115kV Differential upgrade | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2032-01-26 | NA | 2032-09-17 | NA | NA | FALSE | NA | NA ¦ NA | 98.494 | 4080.4631 | 18.7081 | 75.8084 | 3.8886 | 0.0888 | 0 | 0 | 0 | 0 | 0 | 0 | 98.494 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 12.4721 | 50.5389 | 2.5924 | 0.05922 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
136 | LAS GALLINAS_INSTALL NOKIA MUX |  |  | San Rafael, Marin | To improve the service reliability on the San Rafael area, this job proposes to replace the existing electromechanical relays described above with a primary and backup SEL 311C. This will simplify relay maintenance, improve the transmission loop reliability and provide fault location with load monitoring capabilities to the transmission lines. | Substation - Protection Relay | New | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-02 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.0126 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5801080 | T.0003262 | San Rafael CB 132 & CB 142 Relay Project | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-11 | 2023-12-31 | 2026-07-08 | Prioritization | NA | TRUE | 500 | NA ¦ NA | 65.1624 | 445.0749 | 0 | 35.0594 | 20.4098 | 1.948 | 4.3761 | 383.2818 | 0 | 0 | 0 | 0 | 61.7932 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
137 | SAN RAFAEL: Repl CB 132- 142 Relay |  |  | San Rafael, Marin | To improve the service reliability on the San Rafael area, this job proposes to replace the existing electromechanical relays described above with a primary and backup SEL 311C. This will simplify relay maintenance, improve the transmission loop reliability and provide fault location with load monitoring capabilities to the transmission lines. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-02 | 63 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2052 | NA | 115 kV | 483 | 5a. Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5775586 | T.0003262 | San Rafael CB 132 & CB 142 Relay Project | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-18 | 2023-12-31 | 2026-08-20 | Prioritization | NA | TRUE | 500 | NA ¦ NA | 839.7721 | 2248.4308 | 2.7029 | 300.8843 | 129.2391 | 25.2252 | 370.3185 | 987.1479 | 0.9967 | 0 | 0 | 0 | 828.3701 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
138 | IGNACIO_INSTALL NOKIA MUX |  |  | Novato, Marin | To improve the service reliability on the San Rafael area, this job proposes to replace the existing electromechanical relays described above with a primary and backup SEL 311C. This will simplify relay maintenance, improve the transmission loop reliability and provide fault location with load monitoring capabilities to the transmission lines. | Substation - Protection Relay | New | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-05 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.9486 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5801081 | T.0003262 | San Rafael CB 132 & CB 142 Relay Project | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-08-06 | 2023-12-31 | 2026-09-18 | Prioritization | NA | TRUE | 500 | NA ¦ NA | 93.0645 | 409.4746 | 0 | 47.792 | 32.7388 | 7.4723 | 4.144 | 316.1682 | 1.1593 | 0 | 0 | 0 | 92.147 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
139 | APM: Repl APM-Newark Relay |  |  | Sunnyvale, Santa Clara | Replace the line relays at Applied Materials Substation for the Newark-Applied Material 115kV Line. SMP relays for CB142, GPS clock, annunciator and ODN is in the scope of this project to replace and install. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-06 | 25 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.0337 | NA | 115 kV | 483 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5775588 | T.0003264 | APM: Newark- Applied Materials Relay | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-26 | 2022-08-16 | 2022-08-23 | NA | NA | FALSE | 1540 | NA ¦ NA | 1476.1501 | 1476.1501 | 291.7061 | 1155.5163 | 0.3628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1476.1501 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 1372.9969 | 0.33683 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
140 | APM: Applied Materials |  |  | Sunnyvale, Santa Clara | Line relays at Applied Materials substation were installed in 1998 and the relays include LFCB 102, SEL-321, BE1-BPR and SEL-279. Applied Materials - Britton 115kV line is 1.0 mile long with a section of underground cable; however, the line is protected by one level of high speed protection. The lines in Newark - Monta Vista corridor are mutually coupled and pose coordination challenges. LFCB relays belong to early generation microprocessor relays and do not provide backup line protection functions. Other existing relays on the line terminal are older vintage approaching end of their life which include obsolete Basler BPR and SEL-279 relays. System protection recommends upgrading the line terminal per currently approved protection standards to provide redundant line current differential protection for the line. Require upgrading remote terminal line relays at Britton substation. | Substation - Protection Relay | Replace | NA | T.0003266 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-06 | 28 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.0337 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 3.0022 | Non-IGP | 5776119 | T.0003265 | APM: APM-Britton Relay 74013112 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 5 | 2031-07-03 | NA | 2031-12-05 | NA | NA | TRUE | NA | NA ¦ NA | 60.3524 | 1022.2134 | 0 | 45.1963 | 11.2294 | 3.9267 | 0 | 3.7659 | 0 | 0 | 0 | 0 | 60.3524 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
141 | BRITTON: Repl 115 KV APM-Britton Relay |  |  | Sunnyvale, Santa Clara | Line relays at Applied Materials substation were installed in 1998 and the relays include LFCB 102, SEL-321, BE1-BPR and SEL-279. Applied Materials - Britton 115kV line is 1.0 mile long with a section of underground cable; however, the line is protected by one level of high speed protection. The lines in Newark - Monta Vista corridor are mutually coupled and pose coordination challenges. LFCB relays belong to early generation microprocessor relays and do not provide backup line protection functions. Other existing relays on the line terminal are older vintage approaching end of their life which include obsolete Basler BPR and SEL-279 relays. System protection recommends upgrading the line terminal per currently approved protection standards to provide redundant line current differential protection for the line. Require upgrading remote terminal line relays at Britton substation. | Substation - Protection Relay | Replace | NA | T.0003264 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-04 | 28 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.4779 | NA | 115 kV | 483 | 5a.Mitigates System Wide Failure Risk | NA | 3.0022 | Non-IGP | 5776120 | T.0003266 | Britton: APM-Britton Relay 74013113 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 5 | 2031-07-03 | NA | 2031-12-05 | NA | NA | TRUE | NA | NA ¦ NA | 47.6797 | 1026.8012 | 0 | 37.8564 | 6.5265 | 3.2968 | 0 | 2.9752 | 0 | 0 | 0 | 0 | 47.6797 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
142 | MCCALL: Repl BK 1 and BK 2 Relays |  |  | Fresno | Replace McCall Bank 1 and 2 relays | Substation - Protection Relay | Replace | NA | T.0009584 ¦ EX112724 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-06 | 19 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 16.2494 | NA | 230 ¦ 115 kV | NA | NA | NA | 3.0022 | Non-IGP | 5776250 | T.0003305 | McCall Cap Bank #1 and #2 BF Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-01-28 | NA | 2032-03-10 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1650 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 450 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
143 | HERDON: Repl Her-Bul-Pin #1 Relay |  |  | Fresno, Fresno ¦ Madera | Herndon-Bullard-Pinedale #1 line is part of a double circuit line that serves 2 looped stations and because of timing issues with the POTT scheme, the scheme has been cut-out for years (not sure if it was ever cut-in), and Pinedale loop is run N/O. Due to this, if we have a fault on any one line, we drop customers. With a line current differential scheme we can close the loop and ensure more reliability since the customers will not be impacted by a fault on one line. System protection recommends that Herndon-Bullard-Pinedale #1 line relays be replaced with line current differential pilot scheme relays per latest PG&E standard. Replace the following relays with dual SEL-411L Line Current Differential Scheme per latest PG&E standard: • Herndon CB 112 Device 121/167NA-112, 121/167NB-112, 150/162BF-112 and 179-112 (SEL 311C, SEL 321, GE F60, and GE F60) o This will be a complete panel replacement. • Bullard CB 312 Device 121/167NA-1, 121/167NB-1, 150/162BF-1 and 179-1 (SEL 311C, SEL 321, Basler BE1 BPR, and SEL 279) o This will be a complete panel replacement. • Pinedale CB 412 Device 121/167NA-1, 121/167NB-1, 150/162BF-1 and 179-1 (SEL 311C, SEL 321, SEL 351, and SEL 279) o This will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | T.0003307 ¦ T.0003310 ¦ T.0003309 ¦ T.0004347 ¦ T.0003311 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2025-08-08 | 25 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | NA | 115 kV | NA | NA | NA | 3.0022 | Non-IGP | 5776244 | T.0003306 | Herdon: Her-Bul-Pin #1 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-07-01 | NA | 2030-07-30 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
144 | BULLARD: Repl Her-Bul-Pin #1 Relay |  |  | Fresno, Fresno ¦ Madera | Herndon-Bullard-Pinedale #1 line is part of a double circuit line that serves 2 looped stations and because of timing issues with the POTT scheme, the scheme has been cut-out for years (not sure if it was ever cut-in), and Pinedale loop is run N/O. Due to this, if we have a fault on any one line, we drop customers. With a line current differential scheme we can close the loop and ensure more reliability since the customers will not be impacted by a fault on one line. System protection recommends that Herndon-Bullard-Pinedale #1 line relays be replaced with line current differential pilot scheme relays per latest PG&E standard. Replace the following relays with dual SEL-411L Line Current Differential Scheme per latest PG&E standard: • Herndon CB 112 Device 121/167NA-112, 121/167NB-112, 150/162BF-112 and 179-112 (SEL 311C, SEL 321, GE F60, and GE F60) o This will be a complete panel replacement. • Bullard CB 312 Device 121/167NA-1, 121/167NB-1, 150/162BF-1 and 179-1 (SEL 311C, SEL 321, Basler BE1 BPR, and SEL 279) o This will be a complete panel replacement. • Pinedale CB 412 Device 121/167NA-1, 121/167NB-1, 150/162BF-1 and 179-1 (SEL 311C, SEL 321, SEL 351, and SEL 279) o This will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | T.0004347 ¦ T.0003310 ¦ T.0003306 ¦ T.0003309 ¦ T.0003311 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2025-08-08 | 25 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | NA | 115 kV | NA | NA | NA | 3.0022 | Non-IGP | 5776238 | T.0003307 | Bullard: Her-Bul-Pin #1 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-03-01 | NA | 2030-03-29 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
145 | PINEDALE: Repl Her-Bul-Pin #1 Relay |  |  | Fresno, Fresno | Herndon-Bullard-Pinedale #1 line is part of a double circuit line that serves 2 looped stations and because of timing issues with the POTT scheme, the scheme has been cut-out for years (not sure if it was ever cut-in), and Pinedale loop is run N/O. Due to this, if we have a fault on any one line, we drop customers. With a line current differential scheme we can close the loop and ensure more reliability since the customers will not be impacted by a fault on one line. System protection recommends that Herndon-Bullard-Pinedale #1 line relays be replaced with line current differential pilot scheme relays per latest PG&E standard. Replace the following relays with dual SEL-411L Line Current Differential Scheme per latest PG&E standard: • Herndon CB 112 Device 121/167NA-112, 121/167NB-112, 150/162BF-112 and 179-112 (SEL 311C, SEL 321, GE F60, and GE F60) o This will be a complete panel replacement. • Bullard CB 312 Device 121/167NA-1, 121/167NB-1, 150/162BF-1 and 179-1 (SEL 311C, SEL 321, Basler BE1 BPR, and SEL 279) o This will be a complete panel replacement. • Pinedale CB 412 Device 121/167NA-1, 121/167NB-1, 150/162BF-1 and 179-1 (SEL 311C, SEL 321, SEL 351, and SEL 279) o This will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | T.0003307 ¦ T.0003310 ¦ T.0003306 ¦ T.0003309 ¦ T.0004347 ¦ T.0003311 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-10 | 25 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.2566 | NA | 115 kV | NA | NA | NA | 3.0022 | Non-IGP | 5776251 | T.0003308 | Pinedale: Her-Bul-Pin #1 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-03-15 | NA | 2030-04-11 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
146 | HERDON: Repl Her-Bul-Pin #2 Relay |  |  | Fresno, Fresno ¦ Madera | Herndon-Bullard-Pinedale #2 line is part of a double circuit line that serves 2 looped stations and because of timing issues with the POTT scheme, the scheme has been cut-out for years (not sure if it was ever cut-in), and Pinedale loop is run N/O. Due to this, if we have a fault on any one line, we drop customers. With a line current differential scheme we can close the loop and ensure more reliability since the customers will not be impacted by a fault on one line. System protection recommends that Herndon-Bullard-Pinedale #2 line relays be replaced with line current differential pilot scheme relays per latest PG&E standard. Replace the following relays with dual SEL-411L Line Current Differential Scheme per latest PG&E standard: • Herndon CB 122 Device 121/167NA-122, 121/167NB-122, 150/162BF-122 and 179-122 (SEL 311C, SEL 321, GE F60, and GE F60) o This will be a complete panel replacement. • Bullard CB 322 Device 121/167NA-3, 121/167NB-3, 150/162BF-3 and 179-3 (SEL 311C, SEL 321, Basler BE1 BPR, and SEL 279) o This will be a complete panel replacement. • Pinedale CB 422 Device 121/167NA-3, 121/167NB-3, 150/162BF-3 and 179-3 (SEL 311C, SEL 321, Basler BE1 BPR, and SEL 279) o This will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | T.0003307 ¦ T.0003310 ¦ T.0003306 ¦ T.0004347 ¦ T.0003311 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2025-07-29 | 25 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | NA | 115 kV | NA | NA | NA | 3.0022 | Non-IGP | 5776245 | T.0003309 | Herdon: Her-Bul-Pin #2 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-03-01 | NA | 2030-03-28 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
147 | BULLARD: Repl Her-Bul-Pin #2 Relay |  |  | Fresno, Fresno ¦ Madera | Herndon-Bullard-Pinedale #2 line is part of a double circuit line that serves 2 looped stations and because of timing issues with the POTT scheme, the scheme has been cut-out for years (not sure if it was ever cut-in), and Pinedale loop is run N/O. Due to this, if we have a fault on any one line, we drop customers. With a line current differential scheme we can close the loop and ensure more reliability since the customers will not be impacted by a fault on one line. System protection recommends that Herndon-Bullard-Pinedale #2 line relays be replaced with line current differential pilot scheme relays per latest PG&E standard. Replace the following relays with dual SEL-411L Line Current Differential Scheme per latest PG&E standard: • Herndon CB 122 Device 121/167NA-122, 121/167NB-122, 150/162BF-122 and 179-122 (SEL 311C, SEL 321, GE F60, and GE F60) o This will be a complete panel replacement. • Bullard CB 322 Device 121/167NA-3, 121/167NB-3, 150/162BF-3 and 179-3 (SEL 311C, SEL 321, Basler BE1 BPR, and SEL 279) o This will be a complete panel replacement. • Pinedale CB 422 Device 121/167NA-3, 121/167NB-3, 150/162BF-3 and 179-3 (SEL 311C, SEL 321, Basler BE1 BPR, and SEL 279) o This will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | T.0004347 ¦ T.0003307 ¦ T.0003306 ¦ T.0003309 ¦ T.0003311 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2025-07-29 | 25 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | NA | 115 kV | NA | NA | NA | 3.0022 | Non-IGP | 5776239 | T.0003310 | Bullard: Her-Bul-Pin #2 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-03-01 | NA | 2030-03-28 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
148 | PINEDALE: Repl Her-Bul-Pin #2 Relay |  |  | Fresno, Fresno | Herndon-Bullard-Pinedale #2 line is part of a double circuit line that serves 2 looped stations and because of timing issues with the POTT scheme, the scheme has been cut-out for years (not sure if it was ever cut-in), and Pinedale loop is run N/O. Due to this, if we have a fault on any one line, we drop customers. With a line current differential scheme we can close the loop and ensure more reliability since the customers will not be impacted by a fault on one line. System protection recommends that Herndon-Bullard-Pinedale #2 line relays be replaced with line current differential pilot scheme relays per latest PG&E standard. Replace the following relays with dual SEL-411L Line Current Differential Scheme per latest PG&E standard: • Herndon CB 122 Device 121/167NA-122, 121/167NB-122, 150/162BF-122 and 179-122 (SEL 311C, SEL 321, GE F60, and GE F60) o This will be a complete panel replacement. • Bullard CB 322 Device 121/167NA-3, 121/167NB-3, 150/162BF-3 and 179-3 (SEL 311C, SEL 321, Basler BE1 BPR, and SEL 279) o This will be a complete panel replacement. • Pinedale CB 422 Device 121/167NA-3, 121/167NB-3, 150/162BF-3 and 179-3 (SEL 311C, SEL 321, Basler BE1 BPR, and SEL 279) o This will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | T.0003307 ¦ T.0003310 ¦ T.0003306 ¦ T.0003309 ¦ T.0004347 ¦ T.0003308 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-10 | 25 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.2566 | NA | 115 kV | NA | NA | NA | 3.0022 | Non-IGP | 5776252 | T.0003311 | Pinedale: Her-Bul-Pin #2 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-03-15 | NA | 2030-04-11 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
149 | Henrietta: Repl CB 42 Relays |  |  | Kings | Replace electro-mechanical relays for Lemoore NAS 70kV Line (CB 42) and Lemoore 70kV Line (CB 52). | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-06 | 62 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.0079 | NA | 70 kV | 718 | 5a.Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5776243 | T.0003312 | Henrietta CB 42 and CB 52 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-09-03 | 2025-05-06 | 2025-05-20 | NA | NA | TRUE | 1927 | NA ¦ NA | 1891.5767 | 1922.392 | 41.5165 | 429.5952 | 61.3807 | 644.5527 | 694.548 | 47.0562 | 0 | 0 | 0 | 0 | 1875.3358 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1773.2258 | 15.3135 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
150 | SAN JOAQUIN: Repl CB 12- 22 Relay |  |  | Fresno | San Joaquin CB 22 The old EM relays were actually replaced with a USED SEL 321 – we need backup MP relay. There are coordination issues with these terminals and additional we will have to do an area study to try to coordinate. Replace San Joaquin CB 22 OC EM relays with new Phase Distance relays, SEL 411L. Relay Coordination and setting issues. San Joaquin CB 32 The old EM relays were actually replaced with a USED SEL 321 – we need backup MP relay. There are coordination issues with these terminals and additional we will have to do an area study to try to coordinate. Replace San Joaquin CB 32 OC EM relays with new Phase Distance relays, SEL 411L. Relay Coordination and setting issues. Replace the following relays with dual SEL-411L relays per latest PG&E standard: • San Joaquin CB 22 Device 167/167N-1 and 179-1 (SEL 321 and SEL 279) o This will be a complete panel replacement. • San Joaquin CB 32 Device 167/167N-3 and 179-3 (SEL 321 and SEL 279) o This will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-06 | 32 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.84207 | NA | 70 kV | NA | NA | NA | 3.0021 | Non-IGP | 5776253 | T.0003313 | San Joaquin CB 12 & CB 22 Relay | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-10-25 | NA | 2030-01-14 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1600 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 900 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
151 | MARICOPA: Repl Relay |  |  | Taft, Kern | The replacement of the Maricopa CB 42 and CB 52 Relay Project at the Maricopa Substation to develop the detailed scope and engineering. This project’s scope is to remove old electro mechanical relays and install Line Protection for CB 42, CB 52 and Bus Total OC to enhance efficiency, safety, and reliability. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-06 | 59 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.8868 | NA | 70 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5776249 | T.0003317 | Maricopa Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-07-08 | 2020-01-27 | 2019-11-05 | NA | NA | FALSE | 3900 | NA ¦ NA | 2228.1926 | 2228.1926 | 6.6131 | 1.2892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2228.1926 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 6.4586 | 1.2591 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
152 | MAGUNDEN: Repl CB 22 Relay |  |  | East Niles CDP, Kern | Magunden CB 22 has two sets of electromechanical (EM) directional OC relays, installed in 1970, protecting the 70kV line both directions – the Kern-Magunden 70kV line and the Kern Canyon-Magunden-Weedpatch 70kV line. There are coordination issues with phase distance relays. In addition, the relays are at the end of their useful life cycle. The performance and functionality are not as good as the latest digital relays. They have no fault recording capability, do not provide self-monitoring, and will not issue alarms when it fails. Due to the lack of self-monitoring, the relay needs shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Recommend replacing the EM relays with two sets of SEL 411L relays with phase distance and directional ground OC elements. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-09 | 57 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.2256 | NA | 70 kV | 718 | 5a.Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5776248 | T.0003320 | Magunden CB 22 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-06-21 | NA | 2027-10-14 | NA | NA | TRUE | NA | NA ¦ NA | 430.9519 | 2143.9509 | 47.4142 | 299.0127 | 64.854 | 16.2385 | 0 | 166.9602 | 889.061 | 568.821 | 50 | 0 | 430.9519 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
153 | PALERMO: Repl 60 KV Relay |  |  | Palermo CDP, Butte | Replace the following relays with dual SEL-411L relays per latest PG&E standard: • Palermo CB32 o Phase directional overcurrent GE-JBC53 relays o Ground directional overcurrent GE-JBCG53 relay o Westinghouse RC reclosing relay  This will be a complete panel replacement. • Palermo CB42 o Phase directional overcurrent GE-JBC53 relays o Ground directional overcurrent GE-JBCG53 relay o Westinghouse RC reclosing relay  This will be a complete panel replacement. • Palermo CB52 o Phase directional overcurrent GE-JBC53 relays o Ground directional overcurrent GE-JBCG53 relay o Westinghouse RC reclosing relay o RFL-6745 - terminal sends a DTT to Oroville cogen  This will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-13 | 77 | Lifecycle Replacement Analysis | Other - Deferral | $2 Mil - $3 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 8.0464 | NA | 60 kV | 483 | 3. Emergency Preparedness | NA | 3.0021 | Non-IGP | 5776821 | T.0003367 | Palermo 60kV Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-11-27 | 2025-02-20 | 2025-02-27 | NA | NA | TRUE | 2200 | NA ¦ NA | 1576.7601 | 1876.7601 | 0 | 9.4814 | 195.335 | 694.9499 | 671.6398 | 5.354 | 0 | 0 | 0 | 0 | 1571.4061 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1423.2928 | 4.8323 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
154 | EDENVALE: Repl 115 KV Recl & Bus Relays |  |  | San Jose, Santa Clara | Project shall replace/upgrade the following components per the latest standard: 1. Reclosing relays for sectionalizing switches 177 and 187. 2. Bus Total overcurrent scheme for Bus sections ‘D’ & ‘H’. 3. Bus protection for Bus section ‘G’. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-03 | 45 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3853 | NA | 115 kV | 177 | 5a. Mitigates System Wide Failure Risk | NA | 3.0011 | Non-IGP | 5776823 | T.0003369 | Edenvale 115kV Recloser and Bus Diff | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-08-16 | NA | 2032-09-13 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 4179.9444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 1500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
155 | Oakland L: Rep 115kV Relays |  |  | Oakland, Alameda | Replace OAKLAND L CB 312 and 412 oil circuit breakers under the 2023 transmission breakers replacement program | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-05 | 51 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.197 | NA | 230 kV | NA | 5a. Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5782012 | T.0003467 | Oakland L Sub: Repl CB 322, 422,312,412 | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2031-06-03 | NA | 2032-01-16 | NA | NA | FALSE | NA | NA ¦ NA | 185.0943 | 872.4421 | 52.2319 | 112.7572 | 15.4933 | 0 | 0 | 38.5724 | 365.9704 | 237.4169 | 50 | 0 | 180.4824 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
156 | ATLANTIC: Repl CB 52- 62 Relay |  |  | Roseville, Placer | The line and reclosing relays at Atlantic CB 52 are old relays, and they were in service for 24 years. The line and reclosing relays are no longer supported by their manufacturers and are at the end or nearing the end of their useful life. The model of the line relays are SEL 221G and SEL 221F. The reclosing relay is a Basler BE1-25/79TR. The line relays at Atlantic CB 62 are old relays, and they were in service for 25 years. The original reclosing relay Basler BE1-25/79TR failed, and it was replaced with a used SEL 279 relay on 2013. The line and reclosing relays are no longer supported by its manufacturer and are at the end or nearing the end of their useful life. The model for both the line relays is SEL 121B. The line relays will need to be replaced with new SEL relays. The standard relaying package SMP will consist of two SEL 411L and two SEL 451 relays for an integrated design. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-03 | 26 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.6984 | NA | 60 kV | NA | NA | NA | 3.0022 | Non-IGP | 5777560 | T.0003533 | Atlantic CB 52 and CB 62 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-01-04 | NA | 2027-01-25 | NA | NA | TRUE | NA | NA ¦ NA | 0.3453 | 1067.5416 | 0 | 0 | 0 | 0 | 0 | 117.1963 | 199.2605 | 600 | 50 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
157 | VACA DIXON: Repl Cap Bank Relays |  |  | Solano | In 2013, the S&C Voltage Controller (Dev 260-1) for the Vaca Dixon Step # 1 Cap Bank had failed during a 6 year relay testing. A temporary non-standard SEL-2411 relay was installed under an emergency project. In 2015, the S&C Voltage Controller (Dev 260-2) for the Vaca Dixon Step # 2 Cap Bank had failed. A temporary non-standard SEL-2411 relay was installed under an emergency project. The installations of standard relays (SEL 487V) for Shunt Capacitor application are recommended to replace the temporary relays for Dev # 260-1 and Dev # 260-2. | Substation - Protection Relay | Replace | NA | 5800102 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-25 | 32 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | NA | NA | NA | 3.0011 | Non-IGP | 5777561 | T.0003534 | Vaca Dixon Cap Bank Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-07-10 | NA | 2030-08-21 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 350 | 650 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
158 | GATES: Repl CB 32 Relay |  |  | Fresno | On Gates CB32 the existing microprocessor line relays are two SEL 321-1 and Electro Mechanical RC recloser that were installed prior 1996. The relays are close to the end of their useful life cycle. Their performance and functionality are not as good as the latest digital relays. They are no longer adequately supported by the manufacturers. In addtion, there is no breaker failure relay installed on CB 32. | Substation - Protection Relay | Replace | NA | T.00010700 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-12 | 29 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 70 kV | 764 | 5a. Mitigates System Wide Failure Risk | NA | 3.0011 | Non-IGP | 5777302 | T.0003540 | GATES: Repl CB 22, 32, 42, and 52 Relays | 4 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-03-24 | NA | 2032-05-04 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 700 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
159 | GATES: Replace CB 42 Relay |  |  | Fresno | On Gates CB42 the existing microprocessor line relays are two SEL 321-1 and Electro Mechanical RC recloser that were installed in 1996. The relays are close to the end of their useful life cycle. Their performance and functionality are not as good as the latest digital relays. They are no longer adequately supported by the manufacturers. In addtion, there is no breaker failure relay installed on CB 42. | Substation - Protection Relay | Replace | NA | T.00010700 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-12 | 29 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 70 kV | 764 | 5a. Mitigates System Wide Failure Risk | NA | 3.0011 | Non-IGP | 5777303 | T.0003540 | GATES: Repl CB 22, 32, 42, and 52 Relays | 4 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-03-24 | NA | 2032-05-04 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 700 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
160 | GATES: Repl CB 52 Relay |  |  | Fresno | On Gates CB52 the existing microprocessor line relays are two SEL 321-1 and SEL 279 that were installed in 2001. The relays are close to the end of their useful life cycle. Their performance and functionality are not as good as the latest digital relays. They are no longer adequately supported by the manufacturers. In addtion, there is no breaker failure relay installed on CB 52. | Substation - Protection Relay | Replace | NA | T.00010700 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-12 | 24 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 70 kV | 764 | 5a. Mitigates System Wide Failure Risk | NA | 3.0011 | Non-IGP | 5777304 | T.0003540 | GATES: Repl CB 22, 32, 42, and 52 Relays | 4 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-03-24 | NA | 2032-05-04 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 700 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
161 | GATES: Repl CB 22 Relay |  |  | Fresno | On Gates CB 22 the existing microprocessor line relays are two SEL 321-1 and SEL 279 that were installed in 2003. The relays are close to the end of their useful life cycle. Their performance and functionality are not as good as the latest digital relays. They are no longer adequately supported by the manufacturers. In addtion, there is no breaker failure relay installed on CB 22. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-12 | 22 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 70 kV | 764 | 5a. Mitigates System Wide Failure Risk | NA | 3.0011 | Non-IGP | 5777301 | T.0003540 | GATES: Repl CB 22, 32, 42, and 52 Relays | 4 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2034-11-03 | NA | 2034-12-19 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 700 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
162 | LOS BANOS: Repl CB 22 Relay |  |  | Merced | On Los Banos CB 22 the existing old electromechanical line relays are GE JBCG 53 and JBC 53 and Electro Mechanical RC recloser that were installed over 36 years ago. The existing radio is obsolete (RFL 6745). Recommend to replace with GARD 8000. The relays are at the end of their useful life cycle. The relays have no fault recording capability and are no longer supported by the manufacturers. System protection recommends that these relays be replaced with new line relay protection package per the latest standard | Substation - Protection Relay | Replace | NA | T.0000157 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-06 | 60 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 53.2803 | NA | 70 kV | NA | NA | NA | 3.0011 | Non-IGP | 5777308 | T.0003548 | Los Banos CB 22 Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-07-16 | NA | 2030-08-27 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 350 | 650 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
163 | Livermore: Replace 60kV Relays |  |  | Livermore, Alameda | Livermore CB 52 System protection recommends that line relays and reclosing/breaker fail relays will be replaced with two new SMP standard panels. Livermore CB 62 System protection recommends that these relays will be replaced with new line relay protection package per the latest standard with two new SMP standard panels.Livermore CB 42 System protection recommends that line relays and reclosing/breaker fail relays will be replaced with two new SMP standard panels.Livermore SW 77 System protection recommends that reclosing relay will be replaced with one new SMP standard panel.Livermore 60kV Bus Total OCSystem protection recommends that these relays will be replaced with new bus total overcurrent protection package per the latest standard with one new SMP standard panel.Livermore Bank 2 (PO 5778221 Distribution Project) System protection recommends that these relays be replaced with new distribution bank protection package per the latest standard with one new SMP standard panel. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-04-01 | 27 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.60395 | NA | 60 kV | 718 | 5a.Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5784220 | T.0003653 | Livermore Sub Replace Relays and CB 1104 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-02-09 | NA | 2027-05-18 | NA | NA | TRUE | NA | NA ¦ NA | 647.5329 | 2862.6933 | 16.785 | 257.7708 | 75.5909 | 209.9717 | 72.453 | 799.6656 | 1162.8305 | 327 | 50 | 0 | 632.5713 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
164 | EDES: Replace CB 112 Line Relays |  |  | Oakland, Alameda | Edes CEY/CEY/IBC/IBC/RC are E/M phase distance and ground overcurrent relays, whose performance and functionality are not as good as the latest digital relays. They have no fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers.Replace the following relays with dual SEL-311C per latest PG&E standard:•Edes CB 112 Device 121Z1-1, 121Z2BU-1, 167N-1, 167NBU-1, and 179-1 (CEY, CEY, IBC, IBC, RC – Electromechanical relays) installed in 1974 oThis will be a complete panel replacement.•San Leandro U CB 152 Device 121/167N-4, 121Z1-4, 121Z2BU-4, 167N-4, 167NBU-4, 150-4 and 179-4 (SEL-221H, CEY, CEY, JBCG, JBCG, PJC, RC) installed in 1971oThis will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-04 | 52 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.4009 | NA | 115 kV | 439 | 5a.Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5779608 | T.0003870 | Oakland J-San Leandro U Relay | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-07-21 | 2020-08-30 | 2026-07-27 | Bundling Dependencies | NA | FALSE | 587 | NA ¦ NA | 702.1673 | 702.1673 | 47.2609 | 24.5377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 702.1673 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
165 | SAN LEANDRO: Replace CB 152 Line Relays |  |  | San Leandro, Alameda | Edes CEY/CEY/IBC/IBC/RC are E/M phase distance and ground overcurrent relays, whose performance and functionality are not as good as the latest digital relays. They have no fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers.Replace the following relays with dual SEL-311C per latest PG&E standard:•Edes CB 112 Device 121Z1-1, 121Z2BU-1, 167N-1, 167NBU-1, and 179-1 (CEY, CEY, IBC, IBC, RC – Electromechanical relays) installed in 1974 oThis will be a complete panel replacement.•San Leandro U CB 152 Device 121/167N-4, 121Z1-4, 121Z2BU-4, 167N-4, 167NBU-4, 150-4 and 179-4 (SEL-221H, CEY, CEY, JBCG, JBCG, PJC, RC) installed in 1971oThis will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-05 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2372 | NA | 115 kV | 439 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5779580 | T.0003870 | Oakland J-San Leandro U Relay | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-12-14 | 2020-08-30 | 2021-03-01 | Bundling Dependencies | NA | FALSE | 587 | NA ¦ NA | 1050.0771 | 1050.0771 | 687.0022 | 36.9274 | 0.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050.0771 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 903.5942 | -4.9071 | 0.04122 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
166 | OAK J: Repl U Relay |  |  | Oakland, Alameda | Edes CEY/CEY/IBC/IBC/RC are E/M phase distance and ground overcurrent relays, whose performance and functionality are not as good as the latest digital relays. They have no fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers.Replace the following relays with dual SEL-311C per latest PG&E standard:•Edes CB 112 Device 121Z1-1, 121Z2BU-1, 167N-1, 167NBU-1, and 179-1 (CEY, CEY, IBC, IBC, RC – Electromechanical relays) installed in 1974 oThis will be a complete panel replacement.•San Leandro U CB 152 Device 121/167N-4, 121Z1-4, 121Z2BU-4, 167N-4, 167NBU-4, 150-4 and 179-4 (SEL-221H, CEY, CEY, JBCG, JBCG, PJC, RC) installed in 1971oThis will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-09 | 20 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.5059 | NA | 115 kV | 439 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5779658 | T.0003870 | Oakland J-San Leandro U Relay | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-02-01 | 2020-08-30 | 2021-03-25 | Bundling Dependencies | NA | FALSE | 587 | NA ¦ NA | 358.1982 | 358.1982 | 172.8936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358.1982 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 348.097 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
167 | Ames: Ames Dis # Ames 115kV line relay |  |  | Mountain View, Santa Clara | Ames Distribution – Ames 115kV line is protected by unconventional transformer differential relays (KBCH 120 and SEL-587). Existing scheme does not provide back-up protection at Ames Distribution end for 115kV bus faults at Ames substation. Existing relay package at both ends include obsolete relays, namely, BE1-50BF, BE1-BPR and SEL-279. Relays are 1998 vintage which are at the end of expected life span. Also, due to operating system upgrades on PG&E computers in recent years, technicians are no longer able to interrogate with KBCH relays which is a limitation in operating and maintaining the relays. Considering all these factors, it is recommended to upgrade line relays to conventional Line Current Differential scheme for this extremely short line. Recommended scope of work is to install (1) SEL-451 and (2) SEL-311L relays at each end of the line. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2025-08-08 | 27 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | NA | 115 kV | NA | NA | NA | 3.0022 | Non-IGP | 5779509 | T.0003872 | Ames: Ames Dis | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2031-04-08 | NA | 2031-05-23 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
168 | AMES-DIS: Repl Ames D-Ames 115 KV Relays |  |  | Mountain View, Santa Clara | Ames Distribution – Ames 115kV line is protected by unconventional transformer differential relays (KBCH 120 and SEL-587). Existing scheme does not provide back-up protection at Ames Distribution end for 115kV bus faults at Ames substation. Existing relay package at both ends include obsolete relays, namely, BE1-50BF, BE1-BPR and SEL-279. Relays are 1998 vintage which are at the end of expected life span. Also, due to operating system upgrades on PG&E computers in recent years, technicians are no longer able to interrogate with KBCH relays which is a limitation in operating and maintaining the relays. Considering all these factors, it is recommended to upgrade line relays to conventional Line Current Differential scheme for this extremely short line. Recommended scope of work is to install (1) SEL-451 and (2) SEL-311L relays at each end of the line. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2025-08-08 | 27 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | NA | 115 kV | NA | NA | NA | 3.0022 | Non-IGP | 5779510 | T.0003872 | Ames: Ames Dis | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2031-03-25 | NA | 2031-05-23 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
169 | HERDLYN: Repl 60 KV Relay |  |  | Contra Costa | This project includes the relaying upgrade for the 60kV Vasco – Herdlyn line, Herdlyn – Balfour Line, Herdlyn Bank 1, Herdlyn Bank 2 and Herdlyn – Tracy Line and the Breaker controls for HVCB 32 & HVCB 62 at Herdlyn substation. The existing relays will be upgraded with the installation of SMP relays. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-03 | 28 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.81884 | NA | 60 kV | 771 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5780244 | T.0003959 | Herdlyn 60kV Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-07-01 | 2019-09-04 | 2022-03-31 | Workforce | NA | FALSE | 4146 | NA ¦ NA | 5175.0861 | 5175.0861 | 1116.2525 | 265.1417 | 468.7647 | -79.7823 | 0 | 0 | 0 | 0 | 0 | 0 | 5175.0861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 4590.8046 | 447.1889 | -76.1101 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
170 | CHICO A: Repl CB 42 Relays |  |  | Chico, Butte | Install the emergency replacement of CB 42 RELAYSat CHICO A SUB, which failed on or around 04/23/2018 | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-05 | 33 | Lifecycle Replacement Analysis | Other - Deferral | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.90513 | NA | 60 kV | 720 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5781579 | T.0004183 | CHICO A: Repl CB 42 Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-04 | 2021-11-18 | 2021-11-18 | NA | NA | FALSE | 1038 | NA ¦ NA | 1018.4414 | 1018.4414 | 453.7885 | 93.9161 | 0.1718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.4414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 924.3535 | 93.9161 | -75.1785 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
171 | EM COLGATE REPL CB 12 AND CB 22 RELAYS |  |  | Yuba | The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no or limited fault recording capability. In addition, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. This project includes the relaying upgrade for the 60kV CB 12 & CB 22 at Colgate PH. The existing SEL-121G relays will be upgraded with the installation of SEL-311C relays. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-04 | 31 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.5839 | NA | 60 kV | 176 | 3. Emergency Preparedness | NA | NA | NA | 5781580 | T.0004184 | EM: COLGATE: Repl CB 12 and CB 22 Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-01-04 | 2021-05-03 | 2021-05-03 | NA | NA | FALSE | 2101 | NA ¦ NA | 2080.5193 | 2080.5193 | 1108.3295 | 5.4289 | 0.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2080.5193 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 2074.7818 | 4.4739 | -206.791 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
172 | DESCHUTES: REPL CB 22 AND CB 32 RELAYS |  |  | Palo Cedro CDP, Shasta | System Protection recommends the installation of distance relay protection on Deschutes CB 22 and CB 32. Deschutes CB 22 The Deschutes CB 22 relays are SEL 121G and SEL 167 that were installed in 1989. They have been in service for 29 years and the relay manufacture no longer provide support and/or parts for these relays. These relays have been showing failure and have been experiencing intermittent relay fail alarm. System protection recommends replacing these relays with the current line protection standard. Deschutes CB 32 For the single contingency of Deschutes CB 12 open, Deschutes CB 32 line relays cannot see end-of-line faults due to the absence of a system source behind the relays, with very low fault currents sourced only by the generation on the Kilarc-Deschutes 60kV line. Mitigation of this deficiency will require the installation of line relays with step distance protection which can accommodate high load currents and trip for low fault currents. The risk of not installing new relays is that for a single contingency (Deschutes CB 12 open), a portion of faults on the Volta-Deschutes 60kV line will have to be cleared by generator protection operating to trip off generators on the adjacent Kilarc-Deschutes 60kV line. Relying on primary or auxiliary generator protective functions to trip the generators offline for this fault condition will result in faults of long duration at best, and the generator protection failing to operate at worst. System Protection recommends the installation of distance relay protection on Deschutes CB 22 and CB 32. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-12 | 44 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2762 | NA | 60 kV | 720 | 3. Emergency Preparedness | NA | 3.0021 | Non-IGP | 5781581 | T.0004185 | DESCHUTES: Repl CB 22 Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-09-30 | 2019-12-01 | 2026-02-12 | Prioritization | NA | TRUE | 1221.5 | NA ¦ NA | 1392.4957 | 1456.4298 | 26.2783 | 19.5726 | 24.0998 | 32.5883 | 672.7739 | 322.8429 | 0 | 0 | 0 | 0 | 1133.587 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 1258.2881 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
173 | EM HAMILTON BRANCH REPL CB 12 RELAYS |  |  | East Shore CDP, Plumas | Hamilton Branch CB12 protects the Hamilton Branch-Chester 60kV line branch of the Caribou-Westwood 60kV line. This is the only source to Chester Sub and Collins Pine. CB12 is currently protected by two (2) existing SEL-167 relays that were both installed in 2004. These relays are nearing the life expectancy of a microprocessor relay. These relays have been showing failure and have been experiencing intermittent relay fail alarm. System protection recommends replacing these relays with the current line protection standard. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-09 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.1317 | NA | 60 kV | 720 | 3. Emergency Preparedness | NA | NA | NA | 5781587 | T.0004191 | EM: HAMILTON BRANCH: Repl CB 12 Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-01 | 2020-10-09 | 2020-10-09 | NA | NA | FALSE | 1220 | NA ¦ NA | 1200.8724 | 1200.8724 | 44.0404 | 7.4128 | 0.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200.8724 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1193.151 | 6.4683 | -103.4025 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
174 | Vaca Dixon : Rep 230kV Bus Sec E-F Relay |  |  | Solano | Replace existing Bus Diff with two levels (System A & System B) SEL487B/SEL451 (SMP design) | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-25 | 57 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 42.1076 | NA | 230 kV | NA | 5a. Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5782038 | T.0004232 | Vaca Dixon - Rep 230kV Bus Sec E-F Relay | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-08-31 | NA | 2028-01-19 | NA | NA | FALSE | NA | NA ¦ NA | 106.4868 | 10498.2377 | 0 | 86.2449 | 10.6411 | 5.5855 | 0 | 1098.7727 | 0 | 0 | 0 | 0 | 102.4715 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
175 | Ames: Repl 115 kV Bus Diff Relay |  |  | Mountain View, Santa Clara | Ames serves as a critical 115kV switching station with (4) lines to Newark, (2) lines to Ravenswood, (2) lines to Monta Vista and (2) lines to customer owned NASA Ames Research facility. (1) of the lines to Newark is looped through Ames Distribution substation and the (2) lines to Monta Vista are looped through Whisman and Mountain View substation respectively. Mountain View and Whisman substations serve 37,600 customers and 7,700 customers respectively. Google is currently planning a major expansion in the area. This year, transmission planning decided to permanently reconnect lines to Whisman and Mountain View substation(s) into Ames 115kV bus. As a result, the fault duty has increased and exceeds over 40kA. Existing bus differential scheme was originally installed in 1973 and the current selector switches are installed in an outdoor cabinet. Due to exposure to weather and lack of scheduled maintenance activity on these outdoor cabinets number of issues have surfaced system wide that could potentially affect performance of the scheme. Ames being a critical substation, system protection recommends to install redundant bus differential scheme(s) at this facility to provide safe and reliable operating conditions. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-05 | 35 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.8814 | NA | 115 kV | 131 | 5a. Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5782002 | T.0004239 | Ames- Repl 115 kV Bus Diff Relay | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-09-17 | NA | 2033-01-21 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2878.5542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
176 | Geyser 11: Repl CB 312 Relays |  |  | Sonoma | The project will replace the LFCB102 with SEL 411L relays on both Eagle Rock CB 162 and Geysers unit 11 CB 312 due to the fact PGE owns both relay terminals. The existing fiber is the communication medium and will be retained. The work will improve the dependability and reliability of the protection scheme. This will also help the voltage stability with Geysers unit 11 on line in the Mendocino Area. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | NA | 46 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.83 | NA | 115 kV | 761 | 3. Emergency Preparedness | NA | 3.0021 | NA | 5782718 | T.0004357 | Geyser 11: Repl CB 312 Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-09-21 | 2023-12-31 | 2024-02-01 | NA | NA | FALSE | 985 | NA ¦ NA | 1080.4256 | 1080.4256 | 1.1434 | 186.7624 | 765.467 | 127.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 1080.4256 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 1047.7212 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
177 | Applied Materials: Replace Bus Diff Rel |  |  | Sunnyvale, Santa Clara | Applied Materials substation is part of the transmission path between Newark and Monta Vista substation that serves number of customers at Britton, Lockheed 2 substations as well as other critical transmission customers including Lockheed Martin and Applied Materials. Existing KBCH relays used for bus protection are 1998 vintage and are at the end of their life time. KBCH relays are obsolete relays as field technicians do not have necessary software to interface with the relays for maintenance and troubleshooting purpose(s). Besides, existing scheme implementation creates challenges during relay maintenance activity as trip relays associated with bus protection scheme are also used as part of Breaker Fail scheme. Existing bus protection scheme is not redundant and redundant bus protection is deemed essential for safe and reliable transmission system per current standards. Considering these factors, system protection recommends to upgrade Bus Protection at Applied Materials substation per current standards. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-06 | 28 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.0337 | NA | 230 kV | 133 | 5a. Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5783118 | T.0004401 | Applied Materials: Replace Bus Diff Rel | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2032-12-30 | NA | 2033-05-02 | NA | NA | FALSE | NA | NA ¦ NA | 36.906 | 2626.1335 | 7.7014 | 2.2491 | 2.4735 | 1.2652 | 0 | 2.3718 | 0 | 0 | 0 | 0 | 36.906 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
178 | Cottonwood:Install 115kV Bus Diff Relay |  |  | Cottonwood CDP, Shasta | There is a single level of bus protection for 115 kV double bus single breaker at Cottonwood. We are adding a parallel breaker for 115 kV bus and upgrading protection to CB 172 and CB 192 as part of the Transmission Banks replacement. Additionally, there are plans to add two sectionalizing breakers for 115 kV bus. Proposal for Redundant Bus ProtectionNew bus protection calls for redundant bus protection for bulk electric supply. ABB is proposing Distributed Busbar Protection performed by one set of the protection relay REB500 mainly using fiber optic connections in a redundant scheme with the existing GE B90 Busbar relay. ABB proposal reduces the number of additional switch racks for bus differential from 6 to 1 inside the control room and eliminates copper wiring from yard to the control room. Elimination of copper wiring saves lot of cable trenching time in the energized yard. ABB solution consists of Central Unit installed inside the control room and bay units (REG500BU) installed outdoor in cabinets close to existing breaker cabinets. Each individual bay distributed around the station is connected to the central unit by optical fiber cables. Since this is the first installation for PG&E, we have discussed the cybersecurity concerns of distributed busbar protection and ABB addressed the concerns raised by System Automation and CIP Compliance in the revised proposal.We are also excited to use process bus technology that has lot of promise for future jobs especially where cable trenching is limiting protection upgrades.New bus protection calls for redundant bus protection for bulk electric supply. ABB is proposing Distributed Busbar Protection performed by one set of the protection relay REB500 mainly using fiber optic connections in a redundant scheme with the existing GE B90 Busbar relay. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-19 | 20 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 26.1945 | NA | 115 kV | 483 | 3. Emergency Preparedness | NA | 3.0021 | Non-IGP | 5784719 | T.0004659 | Cottonwood Install 115kV Bus Diff Relay | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2021-06-09 | 2022-03-31 | 2027-10-20 | Workforce | NA | TRUE | 9866 | NA ¦ NA | 8566.3778 | 11909.5592 | 4312.82 | 1287.0421 | 537.8953 | 827.8714 | 691.1397 | 756.5777 | 2309.2793 | 0 | 0 | 0 | 8442.6562 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
179 | Colgate: Repl 60kV Relays |  |  | Yuba | System Protection recommends replacement of relay on Colgate CB 52, CB 32, 42, 62, 72, and the 60kV Bus Differential using the latest Protection standard.these relays have exceeded their life cycle, thus a higher probability of failure. The performance and functionality are not as good as the latest digital relays. The electro-mechanical relays have no fault recording capability, do not provide self-monitoring, and will not issue alarms when fail. Due to the lack of self-monitoring, the relay needs shorter maintenance cycle. They are no longer adequately supported by the manufacturers | Substation - Protection Relay | Replace | NA | T.0005895 ¦ T.0005865 ¦ T.0005916 ¦ T.0009721 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-04 | 82 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 1.31 | NA | 60 kV | NA | NA | NA | 3.0022 | Non-IGP | 5786079 | T.0004829 | Colgate: Repl 60kV Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-06-16 | NA | 2030-01-28 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2750 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 600 | 2000 | 150 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
180 | AMES DIS: Install Redundant Bus Relay |  |  | Mountain View, Santa Clara | System Protection recommends to install redundant bus protection at this facility per current standards.Redundant bus protection is deemed necessary to provide safe and reliable operating conditions. Fault duty at this facility is 40470 A and the station serves 153 customers. Providing redundant bus protection also helps ensure coordination for the relays at the remote ends. System Protection recommends to install redundant bus protection at this facility per current standards. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-05 | 26 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.5685 | NA | 115 kV | 133 | 5a. Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5787899 | T.0005207 | AMES DIS- Install Redundant Bus Relay | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-03-08 | NA | 2032-07-07 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1192.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
181 | MILIPITAS: REPL CB 332 RELAYS |  |  | Milpitas, Santa Clara | ABB REL 301 relays belong to the early generation of microprocessor relays. These relays have not been adequately supported by the manufacturer for a number of years. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. For this reason, ABB REL-301 relays are targeted for system wide replacement. REL-301 relays have in-built test switches and hence replacement of these relays will require panel rearrangement due to addition of external FT test switches for the new relays. Other existing relays on the line terminal are older vintage approaching end of their life which include obsolete Basler BPR and SEL-279 relays. Future replacement of Basler BPR and SEL-279 will involve significant rework in terms of panel rearrangement when replaced with currently approved SEL-451 relay for breaker fail/reclosing functions. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-02 | 29 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.3452 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5799739 | T.0005211 | MILIPITAS: Install Redundant Bus Relay | 4 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2032-07-16 | NA | 2032-11-05 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 992.7973 | 0 | 31.4178 | 2.5615 | 1.2063 | 0 | 2.2612 | 0 | 0 | 240.5361 | 750 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
182 | SWIFT: REPL CB 132 RELAYS |  |  | San Jose, Santa Clara | Replace remote terminal relays at Swift (CB 132) substation as the relays are 1997 vintage including obsolete relays (Basler BPR and SEL-279). It also makes sense from clearance standpoint to replace relays at Swift end while Milpitas end relays are being replaced. From project execution standpoint, Swift CB 132 relays can be combined with Swift CB 142 relay replacement to gain efficiencies from design and construction standpoint. Also, this will help us enable us implement POTT scheme for Milpitas – Swift 115kV line using existing digital communication circuits. | Substation - Protection Relay | Replace | NA | T.0009169 ¦ T.0009536 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-02-06 | 29 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.1012 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5799738 | T.0005211 | MILIPITAS: Install Redundant Bus Relay | 4 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2031-09-10 | NA | 2031-11-26 | NA | NA | FALSE | NA | NA ¦ NA | 22.8693 | 822.0738 | 0 | 20.3494 | 1.7358 | 0.784 | 0 | 1.4697 | 0 | 0 | 0 | 0 | 22.8693 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
183 | MENDOCINO: Replace CB 32 Relays |  |  | Mendocino | This project will replace the Mendocino CB 32 and 52 relays with the current SMP standard line and breaker relay packages. This upgrade will provide better protection during PSPS events and remove old relays that are at the end of their useful life. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-12 | 29 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.7328 | NA | 60 kV | NA | 3. Emergency Preparedness | NA | NA | NA | 5787917 | T.0005227 | MENDOCINO: Replace CB 32 Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-06-28 | 2021-10-21 | 2021-10-15 | NA | NA | FALSE | 1315 | NA ¦ NA | 1649.6669 | 1649.6669 | 1541.2239 | 76.1199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1649.6669 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1487.0768 | 71.8394 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
184 | SMARTVILLE: Replace CB 22 Relays |  |  | Smartsville CDP, Yuba | System protection is recommending to upgrade Smartville CB 22, CB 52, CB 62 and CB 72 terminals per currently approved protection standards | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-05 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.2017 | NA | 60 kV | NA | 3. Emergency Preparedness | NA | NA | NA | 5788719 | T.0005470 | Smartville: Repl Relays on CB 52 & CB 22 | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-03-01 | 2022-05-13 | 2022-05-13 | NA | NA | FALSE | 1700 | NA ¦ NA | 638.827 | 638.827 | 104.3828 | 495.6505 | 30.3068 | 2.6738 | 0 | 0 | 0 | 0 | 0 | 0 | 638.827 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 561.8418 | 28.076 | 2.477 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
185 | SMARTVILLE: REPL CB 52 RELAYS |  |  | Smartsville CDP, Yuba | System protection is recommending to upgrade Smartville CB 22, CB 52, CB 62 and CB 72 terminals per currently approved protection standards | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-05 | 77 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.2017 | NA | 60 kV | NA | NA | NA | NA | NA | 5798721 | T.0005470 | Smartville: Repl Relays on CB 52 & CB 22 | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-11-21 | 2022-05-13 | 2023-01-13 | Prioritization | NA | FALSE | 1700 | NA ¦ NA | 507.9685 | 507.9685 | 8.2809 | 357.8677 | 141.5396 | 0.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 507.9685 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 459.5117 | 0.25321 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
186 | VGCC: Replace PACIRAS GG1 - GG5 Relays |  |  | Solano | Existing PACIRAS equipment for Midway Gen Groups (1 through 5) consists of RFL transfer trip and RFL telemetry equipment that is in need of life cycle replacements. This equipment is located at Midway and at the Gen Group tripping locations. Analog communication circuits are used for the existing transfer trip and megawatt telemetry from the Gen Group sites to Midway. Midway is a hub where the analog equipment is connected to RFL GARD 8000 digital equipment that communicate to RFL GARD 8000 transceivers at SFGO and VGCC. This project proposes to replace all of the RFL equipment with GE N60 relays at the Gen Group tripping locations and at SFGO and VGCC, and to install digital communication circuits from SFGO and VGCC to the Gen Group tripping locations. This project is being driven by the need for life cycle replacements and deteriorated/failing equipment. Additionally, this work is tied into the relocation of RAS controllers from SFGO to Rocklin and is part of “pre-migration” work to replace RAS RFL equipment with GE N60 relays. Gen Groups 3 and 5 (to La Paloma) are the highest priority due to the frequent transducer failures for the PACIRAS megawatt telemetry. | Substation - Protection Relay | Replace | NA | T.0006190 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | NA | 36 | Lifecycle Replacement Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 kV | NA | 5a. Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5790397 | T.0006261 | Midway Sub 230kV Replace PACIRAS | 10 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-10-01 | 2023-08-31 | 2026-05-28 | Prioritization | NA | TRUE | 11400 | NA ¦ NA | 1771.5894 | 1922.1057 | 128.6389 | 154.6454 | 177.4675 | 739.193 | 524.3199 | 190.6195 | 0 | 0 | 0 | 0 | 1731.4861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
187 | MIDWAY: Replace PACIRAS 115/230kV Relays |  |  | Buttonwillow CDP, Kern | Existing PACIRAS equipment for Midway Gen Groups (1 through 5) consists of RFL transfer trip and RFL telemetry equipment that is in need of life cycle replacements. This equipment is located at Midway and at the Gen Group tripping locations. Analog communication circuits are used for the existing transfer trip and megawatt telemetry from the Gen Group sites to Midway. Midway is a hub where the analog equipment is connected to RFL GARD 8000 digital equipment that communicate to RFL GARD 8000 transceivers at SFGO and VGCC. This project proposes to replace all of the RFL equipment with GE N60 relays at the Gen Group tripping locations and at SFGO and VGCC, and to install digital communication circuits from SFGO and VGCC to the Gen Group tripping locations. This project is being driven by the need for life cycle replacements and deteriorated/failing equipment. Additionally, this work is tied into the relocation of RAS controllers from SFGO to Rocklin and is part of “pre-migration” work to replace RAS RFL equipment with GE N60 relays. Gen Groups 3 and 5 (to La Paloma) are the highest priority due to the frequent transducer failures for the PACIRAS megawatt telemetry. | Substation - Protection Relay | Replace | NA | T.0006190 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-03 | 34 | Lifecycle Replacement Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 230 kV | NA | NA | NA | 3.0021 | Non-IGP | 5790391 | T.0006261 | Midway Sub 230kV Replace PACIRAS | 10 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-01 | 2023-08-31 | 2026-05-29 | Prioritization | NA | TRUE | 11400 | NA ¦ NA | 234.9666 | 238.4911 | 94.1382 | 62.3044 | 18.6727 | 19.5995 | 28.4635 | 6.4712 | 0 | 0 | 0 | 0 | 232.0199 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
188 | KERN OIL: Replace PACIRAS GG1 Relays |  |  | Oildale CDP, Kern | Existing PACIRAS equipment for Midway Gen Groups (1 through 5) consists of RFL transfer trip and RFL telemetry equipment that is in need of life cycle replacements. This equipment is located at Midway and at the Gen Group tripping locations. Analog communication circuits are used for the existing transfer trip and megawatt telemetry from the Gen Group sites to Midway. Midway is a hub where the analog equipment is connected to RFL GARD 8000 digital equipment that communicate to RFL GARD 8000 transceivers at SFGO and VGCC. This project proposes to replace all of the RFL equipment with GE N60 relays at the Gen Group tripping locations and at SFGO and VGCC, and to install digital communication circuits from SFGO and VGCC to the Gen Group tripping locations. This project is being driven by the need for life cycle replacements and deteriorated/failing equipment. Additionally, this work is tied into the relocation of RAS controllers from SFGO to Rocklin and is part of “pre-migration” work to replace RAS RFL equipment with GE N60 relays. Gen Groups 3 and 5 (to La Paloma) are the highest priority due to the frequent transducer failures for the PACIRAS megawatt telemetry. | Substation - Protection Relay | Replace | NA | T.0006190 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-06 | 36 | Lifecycle Replacement Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.2122 | NA | 230 kV | NA | 5a. Mitigates System Wide Failure Risk | NA | 4.012 | Non-IGP | 5790388 | T.0006261 | Midway Sub 230kV Replace PACIRAS | 10 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-04 | 2023-08-31 | 2026-06-05 | Prioritization | NA | TRUE | 11400 | NA ¦ NA | 453.1013 | 852.9567 | 107.172 | 96.0616 | 56.3285 | 120.4213 | 63.5844 | 380.2159 | 27.9184 | 0 | 0 | 0 | 444.8223 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
189 | MIDSUN SW: Replace PACIRAS GG1 Relays |  |  | Kern | Existing PACIRAS equipment for Midway Gen Groups (1 through 5) consists of RFL transfer trip and RFL telemetry equipment that is in need of life cycle replacements. This equipment is located at Midway and at the Gen Group tripping locations. Analog communication circuits are used for the existing transfer trip and megawatt telemetry from the Gen Group sites to Midway. Midway is a hub where the analog equipment is connected to RFL GARD 8000 digital equipment that communicate to RFL GARD 8000 transceivers at SFGO and VGCC. This project proposes to replace all of the RFL equipment with GE N60 relays at the Gen Group tripping locations and at SFGO and VGCC, and to install digital communication circuits from SFGO and VGCC to the Gen Group tripping locations. This project is being driven by the need for life cycle replacements and deteriorated/failing equipment. Additionally, this work is tied into the relocation of RAS controllers from SFGO to Rocklin and is part of “pre-migration” work to replace RAS RFL equipment with GE N60 relays. Gen Groups 3 and 5 (to La Paloma) are the highest priority due to the frequent transducer failures for the PACIRAS megawatt telemetry. | Substation - Protection Relay | Replace | NA | T.0006190 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-06 | 36 | Lifecycle Replacement Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.41861 | NA | 230 kV | NA | 5a. Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5790390 | T.0006261 | Midway Sub 230kV Replace PACIRAS | 10 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-01 | 2023-08-31 | 2026-06-15 | Prioritization | NA | TRUE | 11400 | NA ¦ NA | 234.3372 | 239.2583 | 81.0756 | 118.5584 | 17.7629 | -16.1259 | 22.9851 | 7.8599 | 0 | 0 | 0 | 0 | 231.3984 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
190 | TAFT: Replace PACIRAS GG1 Relays |  |  | Taft, Kern | Existing PACIRAS equipment for Midway Gen Groups (1 through 5) consists of RFL transfer trip and RFL telemetry equipment that is in need of life cycle replacements. This equipment is located at Midway and at the Gen Group tripping locations. Analog communication circuits are used for the existing transfer trip and megawatt telemetry from the Gen Group sites to Midway. Midway is a hub where the analog equipment is connected to RFL GARD 8000 digital equipment that communicate to RFL GARD 8000 transceivers at SFGO and VGCC. This project proposes to replace all of the RFL equipment with GE N60 relays at the Gen Group tripping locations and at SFGO and VGCC, and to install digital communication circuits from SFGO and VGCC to the Gen Group tripping locations. This project is being driven by the need for life cycle replacements and deteriorated/failing equipment. Additionally, this work is tied into the relocation of RAS controllers from SFGO to Rocklin and is part of “pre-migration” work to replace RAS RFL equipment with GE N60 relays. Gen Groups 3 and 5 (to La Paloma) are the highest priority due to the frequent transducer failures for the PACIRAS megawatt telemetry. | Substation - Protection Relay | Replace | NA | T.0006190 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-02 | 36 | Lifecycle Replacement Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 5.2046 | NA | 230 kV | NA | 5a. Mitigates System Wide Failure Risk | NA | 4.012 | Non-IGP | 5790392 | T.0006261 | Midway Sub 230kV Replace PACIRAS | 10 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-01 | 2023-08-31 | 2026-07-07 | Prioritization | NA | TRUE | 11400 | NA ¦ NA | 391.8749 | 762.1382 | 93.4303 | 133.2063 | 48.3081 | 48.4536 | 51.427 | 367.407 | 11.2511 | 0 | 0 | 0 | 383.4801 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
191 | LA PALOMA: Repl PACIRAS GG3 & GG Relays |  |  | Buttonwillow CDP, Kern | Existing PACIRAS equipment for Midway Gen Groups (1 through 5) consists of RFL transfer trip and RFL telemetry equipment that is in need of life cycle replacements. This equipment is located at Midway and at the Gen Group tripping locations. Analog communication circuits are used for the existing transfer trip and megawatt telemetry from the Gen Group sites to Midway. Midway is a hub where the analog equipment is connected to RFL GARD 8000 digital equipment that communicate to RFL GARD 8000 transceivers at SFGO and VGCC. This project proposes to replace all of the RFL equipment with GE N60 relays at the Gen Group tripping locations and at SFGO and VGCC, and to install digital communication circuits from SFGO and VGCC to the Gen Group tripping locations. This project is being driven by the need for life cycle replacements and deteriorated/failing equipment. Additionally, this work is tied into the relocation of RAS controllers from SFGO to Rocklin and is part of “pre-migration” work to replace RAS RFL equipment with GE N60 relays. Gen Groups 3 and 5 (to La Paloma) are the highest priority due to the frequent transducer failures for the PACIRAS megawatt telemetry. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-03 | 22 | Lifecycle Replacement Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 230 kV | NA | 5a. Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5790394 | T.0006261 | Midway Sub 230kV Replace PACIRAS | 10 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-12-02 | 2023-08-31 | 2025-02-28 | Prioritization | NA | TRUE | 11400 | NA ¦ NA | 1455.5313 | 1455.5313 | 79.6653 | 205.2663 | 248.5586 | 633.1186 | 269.7989 | 0 | 0 | 0 | 0 | 0 | 1455.5313 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1408.4964 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
192 | ARCATA: REPL BUS OC RELAYS - PSPS |  |  | Arcata, Humboldt | Existing bus protection does not coordinate with remote end line relays for 60kV faults. System Protection recommends upgrade the 60kV bus protection from bus total overcurrent to bus differential protection. System Protection recommends the following: • Replace the existing SEL 501 bus TOC scheme with two (2) SEL 487B bus differential relays (1 panel of two 3-phase relays for redundancy); see Electra PH as a go-by (dwg #s 401348, 4123327, 4148424, 4148423, 432512). These relays would need to be wired to the high-side bank CTs (same CTs shared with the bank relays), and the scheme would have to be modified to enable the SW 36 pallet contact to drive the bus differential between 2 sections, and 1 overall section mode. • Upgrade the existing GE T60 bank relays for Banks 1 & 2 to firmware version 7.2x which has distance elements that include a reverse directionality option and VT fuse fail logic. Wire in 3-phase PTs from the 12kV source, and use both low-side phase distance elements and low-side ground overcurrent elements to speed up tripping for 12kV bus faults. • Install two (2) SEL 311C relays, one on the low-side of Bank 1 and one on the low-side of Bank 2. These relays are necessary to achieve redundant low-side phase distance protection which is not available in the SEL 387E relay. Wire in 3-phase PTs from the 12kV source, and use both low-side phase distance elements and low-side ground overcurrent elements to speed up tripping for 12kV bus faults. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-02 | 16 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.53072 | NA | 60 kV | NA | NA | NA | 3.0021 | Non-IGP | 5795424 | T.0007077 | ARCATA: Repl Bus & Bk Relays-PSPS | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-04-02 | NA | 2027-09-14 | NA | NA | TRUE | NA | NA ¦ NA | 789.1292 | 4026.4998 | 0 | 117.2476 | 185.693 | 390.1053 | 71.0011 | 1001.287 | 2218.1632 | 0 | 0 | 0 | 764.047 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
193 | LOS ESTEROS: Repl Bank 3 & Bank 4 Relays |  |  | San Jose, Santa Clara | Los Esteros is a critical substation serving large number of critical customers in Silicon Valley area. Los Esteros 230/115kV banks are protected by previous generation microprocessor relays including KBCH relays. KBCH relays are prone to operate during inrush conditions as we have experienced, though, some firmware upgrades have been implemented to address this issue. Test department indicated that KBCH relays are outdated and they are not able to interrogate KBCH relays to acquire data. Most other relays protecting the banks are 2002 vintage and would have served their useful time within next 2-3 years. Manufacturers have made us aware about discontinuing them with other products such as SEL-501 relays. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-09 | 23 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 230 ¦ 115 kV | NA | NA | NA | 3.0022 | Non-IGP | 5800058 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-02-01 | NA | 2028-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1400 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 450 | 900 | 50 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
194 | SAN MATEO: REPL PLC for SPS |  |  | San Mateo, San Mateo | Replace PLC for San Mateo SPS. PLCs cannot record Sequence of Events (SOE) due to hardware limitation. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-17 | 23 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 17.354 | NA | NA | NA | NA | NA | 3.0022 | Non-IGP | 5800059 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 3900 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 900 | 2000 | 1000 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
195 | METCALF: REPL PLC for SPS |  |  | Santa Clara | Metcalf SPS scheme has been implemented to avoid emergency overload of Metcalf-Moss Landing 230kV lines and to avoid voltage collapse in the event of Moss Landing-Metcalf and Tesla-Metcalf 500kV line outage. With the implementation of Metcalf SPS, generation and loads will be automatically tripped for critical continencies. Therefore pre-contingency load curtailment in the South Bay will not be needed. The existing Metcalf SPS PLCs cannot record Sequence of Events (SOE) due to hardware limitation. SOEs are critical for RAS operation analysis as required by NERC PRC-012 R5. The existing Metcalf PLCs have a number of logic issues that need to be reviewed and subsequently fixed. PG&E has been reliant upon sole-source contractor for PLC logic update and testing. Upon conclusion of this project, Metcalf SPS PLCs will be replaced with SEL RTACs and Axions which PG&E internal resources are familiar with and can fully support with programming and testing. This effort will remove the risk when the sole-source contractor becomes unavailable to PG&E and PG&E has to replace the PLCs on emergency in order to provide support. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-05 | 28 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 500 ¦ 230 kV | NA | NA | NA | 3.0022 | Non-IGP | 5800060 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 3900 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 900 | 2000 | 1000 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
196 | TESLA: REPL BANK 2 RELAYS |  |  | Alameda | The 525/230kV transformers are critical for the backbone of the system and are an extremely expensive asset. Therefore, the protection of this asset is considered a high priority. The relay replacement schedule adheres to the relay asset management replacement schedule (40 years for electromechanical and 20 years for microprocessor-based relays). The existing electromechanical relays on Tesla Bank 2 were installed at: • Dev. 87TH-2 Type HRU • Dev. 87T-2 Type IAC53B, installed in 1967 • Dev. 51-2 Type CO-9, installed in 1967 • Dev. 51T-2 Type CO-8 • Dev. 51T-2A Type CO-8 The low side distance relay, Dev. 221/267NT-2 Type SEL 421 was installed in 2016. We will also recommend its replacement to bring the full relays to the same asset year and utilize our 2018 525/230kV standard. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-19 | 59 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 69.382 | NA | 500 ¦ 230 kV | NA | NA | NA | 3.0011 | Non-IGP | 5800104 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 6000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 1500 | 3500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
197 | VACA DIXON: REPL BANK 11 RELAYS |  |  | Solano | The 525/230kV transformers are critical for the backbone of the system and are an extremely expensive asset. Therefore, the protection of this asset is considered a high priority. The relay replacement schedule adheres to the relay asset management replacement schedule (40 years for electromechanical and 20 years for microprocessor-based relays). The existing microprocessor relays on Tesla Bank #6 are as follows: • Dev. 87TA-11 • Dev. 87TB-11 • Dev. 551TA/51TT-11 • Dev. 51T-11 The low side distance relay, Dev. 221/267NT-1. We will also recommend its replacement to bring the full relay package to the same asset year and utilize our 2018 525/230kV standard. | Substation - Protection Relay | Replace | NA | 5777561 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-25 | 21 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 42.1076 | NA | 500 ¦ 230 kV | NA | NA | NA | 3.0011 | Non-IGP | 5800102 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2031-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 5000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 1500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
198 | TESLA: REPL BANK 6 RELAYS |  |  | Alameda | The 525/230kV transformers are critical for the backbone of the system and are an extremely expensive asset. Therefore, the protection of this asset is considered a high priority. The relay replacement schedule adheres to the relay asset management replacement schedule (40 years for electromechanical and 20 years for microprocessor-based relays). The existing microprocessor relays on Tesla Bank #6 are as follows: • Dev. 87TA-6 Type KBCH-130, installed 2003 • Dev. 87TB-6 Type T60, installed in 2003 • Dev. 551TA/51TT-6 Type SEL-501-2, installed in 2003 • Dev. 51T-6 Type SEL-501-2, installed in 2003 The low side distance relay, Dev. 221/267NT-6 Type SEL-421-4 was installed in 2016. We will also recommend its replacement to bring the full relay package to the same asset year and utilize our 2018 525/230kV standard. | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-19 | 23 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 69.382 | NA | 500 ¦ 230 kV | NA | NA | NA | 3.0022 | Non-IGP | 5800106 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2031-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 5000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 1500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
199 | GREGG: INS CB332-432 and CB342-442 Relay |  |  | Madera | In order to meet PRC-026, we had to enable Load Encroachment settings on the Gregg and Helms terminals of the Gregg-Helms #1 & #2 230kV Lines which intersected with the Zone 1 element. In order to avoid requiring this Load Encroachment into the Zone 1 elements, the project will replace the line relays currently configured for a POTT scheme with a Line Differential scheme. Line Differential relays will then meet the PRC-026 requirements without any updates to the Load Encroachment settings. Presently there is only one Microwave path available for set-A LCD relay and a 2nd path for set-B for proper redundancy will need to be added. This will most likely be a 2nd Microwave path since these are remote long lines and other options will be very expensive. Replace the following relays per latest PG&E standard using Line Differential scheme, and latest Breaker Failure and Reclosing Relays: • Gregg-Helms PP # 1 230 kV Line o Gregg CB 332-432: SEL 321, SEL 311C, BE1BPR and BE12579TR o Helm PP CB 250 -270: SEL 321, SEL 311C, BE1BPR and BE12579TR • Gregg-Helms PP #2 230 kV Line o Gregg CB 342-442: SEL 321, SEL 311C, BE1BPR and BE12579TR o Helm CB 260-290: SEL 321, SEL 311C, BE1BPR and BE12579TR | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-10 | 22 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.266 | NA | 230 kV | NA | NA | NA | 3.0021 | Non-IGP | 5792220 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-03-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 500 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
200 | HELM: INS CB250-270 and CB260-290 Relay |  |  | Fresno | In order to meet PRC-026, we had to enable Load Encroachment settings on the Gregg and Helms terminals of the Gregg-Helms #1 & #2 230kV Lines which intersected with the Zone 1 element. In order to avoid requiring this Load Encroachment into the Zone 1 elements, the project will replace the line relays currently configured for a POTT scheme with a Line Differential scheme. Line Differential relays will then meet the PRC-026 requirements without any updates to the Load Encroachment settings. Presently there is only one Microwave path available for set-A LCD relay and a 2nd path for set-B for proper redundancy will need to be added. This will most likely be a 2nd Microwave path since these are remote long lines and other options will be very expensive. Replace the following relays per latest PG&E standard using Line Differential scheme, and latest Breaker Failure and Reclosing Relays: • Gregg-Helms PP # 1 230 kV Line o Gregg CB 332-432: SEL 321, SEL 311C, BE1BPR and BE12579TR o Helm PP CB 250 -270: SEL 321, SEL 311C, BE1BPR and BE12579TR • Gregg-Helms PP #2 230 kV Line o Gregg CB 342-442: SEL 321, SEL 311C, BE1BPR and BE12579TR o Helm CB 260-290: SEL 321, SEL 311C, BE1BPR and BE12579TR | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 2026-03-10 | 22 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.7555 | NA | 230 kV | NA | NA | NA | 3.0021 | Non-IGP | 5792221 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-03-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 500 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
201 | EPSS 3F Monthly Fcst ONLY |  |  | NA | Forecast placeholder for EPPS protection relays | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | NA | NA | NA | Protection Studies | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.2021 | Non-IGP | 5550658 | NA | NA | NA | 3F | NA ¦ EX113137 ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 74850 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1712 | 10373 | 19765 | 21500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] PRC-002-2 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
202 | Relay NERC Compliance Upgrades |  |  | NA | Bucket placeholder for NERC Compliance upgrades to relays | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | NA | NA | NA | Protection Studies | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1021 | Non-IGP | 5529842 | NA | NA | NA | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 2000 | 2000 | 2000 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] PRC-002-2 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
203 | GE Relay - Compliance |  |  | NA | Forecast placeholder to replace GE relay for Cyber Issues | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | NA | NA | NA | Protection Studies | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0021 | Non-IGP | EX139360 | NA | NA | NA | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 2000 | 2000 | 2000 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] PRC-002-2 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
204 | PRC-002-2 - TESLA 230KV FR |  |  | Alameda | The Tesla substation Fault Recorders and Sequence of Event Recorders capabilities are required to ensure PG&E meets the NERC PRC-002-02. PRC-002-2 | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | NA | 2026-03-19 | 52 | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 627 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5522608 | T.0001939 | PRC-002-2 - Tesla 230kV FR | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-09-03 | 2021-06-15 | 2022-01-07 | Workforce | NA | FALSE | 1375 | NA ¦ NA | 2049.1541 | 2049.1541 | 105.2151 | 96.6108 | 122.4521 | 92.8885 | 0 | 0 | 0 | 0 | 0 | 0 | 2049.1541 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 105.2151 | 96.6108 | 122.4521 | 48.6763 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC PRC 002-2 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
205 | PRC 002-2 PITTSBURG 230KV FR |  |  | Pittsburg, Contra Costa | Project scope: • Upgrade a subset of the existing PG&E Fault Recorders and Sequence of Event Recorders to support PG&E’s efforts to meet the PRC-002-2 Implementation Plan. • New fault recorder(s) at Pittsburg PP 230kV will monitor 18 PG&E breaker status points. New Fault Recorder will not monitor NRG breakers. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | NA | 2026-03-06 | 22 | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.72358 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5772224 | T.0002234 | PRC 002-2 Pittsburg 230kV FR | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-05-01 | 2020-07-23 | 2021-10-27 | Project Design | NA | FALSE | 1000 | NA ¦ NA | 1509.746 | 1509.746 | 204.3884 | 31.3767 | 0.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1509.746 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1477.5922 | 31.3767 | 0.77708 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC PRC 002-2 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
206 | CONTRA COSTA: Repl 230 KV fault Recorder |  |  | Antioch, Contra Costa | Project recommend action: • Upgrade a subset of the existing PG&E Fault Recorders and Sequence of Event Recorders to support PG&E’s efforts to meet the PRC-002-2 Implementation Plan. • New fault recorder(s) at Contra Costa 230kV will monitor 230kV breaker status points. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | NA | 2026-03-03 | 20 | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.1779 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5772218 | T.0002236 | PRC 002-2 Contra Costa 230kV FR | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-09-01 | 2021-06-15 | 2021-10-27 | NA | NA | FALSE | 1740 | NA ¦ NA | 1373.0935 | 1373.0935 | 181.9804 | 24.2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1373.0935 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1348.089 | 25.0045 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC PRC 002-2 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
207 | Stagg: Install PRC-002-2 PMU |  |  | Stockton, San Joaquin | Based on the latest Reliability Coordinator list (Rev 10), PG&E will need to install PMU’s at two additional locations. PG&E has equipment already installed to cover 7 of the 9 Reliability Coordinator identified buses. PG&E needs this equipment to meet PRC-002-2 DDR Implementation plan requirements. Project recommend action: • Order and Install System A and System B PMU’s. Connect two Stagg 230V bus voltages to each PMU. • Install dedicated GPS antenna’s, SEL2488 clocks, and ethernet equipment • Assign IP addresses and Firewall change request to allow remote access and PTP time signal delivery • Install PDC’s (if necessary) • Telecom to establish MPLS data routes to PDC and/or SuperPDC • Integrate Stagg 230kV Voltage SynchroPhasor into SuperPDC Project recommend action unique to Stagg: • Update PACIRAS to N60 relays and use for both RAS and PMU at Stagg | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | NA | 2026-03-06 | 20 | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.5909 | NA | 230 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5783080 | T.0004396 | STAGG VACA SFGO PMU | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-26 | 2021-12-01 | 2021-11-17 | NA | NA | FALSE | 1127 | NA ¦ NA | 952.3577 | 952.3577 | 633.9299 | 36.2116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 952.3577 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 885.8651 | 34.9566 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] PRC-002-2 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
208 | Vaca Grid: Install PRC-002-2 PMU |  |  | Solano | Project recommend action: • New PACIRAS N60 relays will be installed at Vacaville Grid Control Center to replace existing RFL Gard 8000 devices. • New GE N60 relays at Stagg will serve a dual function of PACIRAS and Phasor Measurement Unit (PMU) for Synchrophasor functions. Stagg 230kV lines (CB 212 and CB 222) are a part of an existing IRAS load shedding group within PACIRAS. Trip signals are sent from PACIRAS central programmable logic controllers (PLCs) located at SFGO and VGCC to Stagg. The existing CB 212 (Eight Mile-Stagg 230kV) and CB 222 (Stagg-Tesla 230kV) are configured to be tripped by PACIRAS. CB 212 and CB 222 megawatt (MW) flow is monitored by PACIRAS and is sent from Stagg 230kV PACIRAS to SFGO and VGCC PLCs. The existing RFL-6745 and RFL-9800 analog PACIRAS equipment is to be replaced on this project with new GE N60 relays that will serve a dual function of PACIRAS and Phasor Measurement Unit (PMU) for Synchrophasor functions. New redundant digital communication circuits will need to be established between Stagg and SFGO/VGCC. New PACIRAS N60 relays will also be installed at SFGO and VGCC. The new Stagg N60 relays will stream PMU information to an existing Phasor Data Concentrator (PDC) located at Tesla Sub. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | NA | NA | 14 | Protection Studies | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 230 kV | 131 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5783081 | T.0004396 | STAGG VACA SFGO PMU | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-26 | 2021-12-01 | 2021-11-17 | NA | NA | FALSE | 773 | NA ¦ NA | 363.2747 | 363.2747 | 221.7343 | 11.3489 | 0.0902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363.2747 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 300.8422 | 9.631 | 0.0765 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] PRC-002-2 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
209 | SFGO: Install PRC-002-2 PMU |  |  | San Francisco, San Francisco | Project recommend action: • New PACIRAS N60 relays will be installed at SFGO to replace existing RFL Gard 8000 devices. • New GE N60 relays at Stagg will serve a dual function of PACIRAS and Phasor Measurement Unit (PMU) for Synchrophasor functions. Stagg 230kV lines (CB 212 and CB 222) are a part of an existing IRAS load shedding group within PACIRAS. Trip signals are sent from PACIRAS central programmable logic controllers (PLCs) located at SFGO and VGCC to Stagg. The existing CB 212 (Eight Mile-Stagg 230kV) and CB 222 (Stagg-Tesla 230kV) are configured to be tripped by PACIRAS. CB 212 and CB 222 megawatt (MW) flow is monitored by PACIRAS and is sent from Stagg 230kV PACIRAS to SFGO and VGCC PLCs. The existing RFL-6745 and RFL-9800 analog PACIRAS equipment is to be replaced on this project with new GE N60 relays that will serve a dual function of PACIRAS and Phasor Measurement Unit (PMU) for Synchrophasor functions. New redundant digital communication circuits will need to be established between Stagg and SFGO/VGCC. New PACIRAS N60 relays will also be installed at SFGO and VGCC. The new Stagg N60 relays will stream PMU information to an existing Phasor Data Concentrator (PDC) located at Tesla Sub. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | NA | NA | 20 | Protection Studies | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.2172 | NA | 230 kV | NA | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5783088 | T.0004396 | STAGG VACA SFGO PMU | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-26 | 2021-12-01 | 2021-11-17 | NA | NA | FALSE | 878 | NA ¦ NA | 358.394 | 358.394 | 172.4877 | 12.2008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358.394 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 338.8394 | 11.9249 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] PRC-002-2 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
210 | HFTD FULTON: ComAPS CB 632 Relays |  |  | Fulton CDP, Sonoma | Install protection, automation, and control equipment on the 230 kV system at Fulton Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 230 kV system and non-standard bus differential scheme that reduce the reliability of the station. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-11 | 19 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 13.4076 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814698 | T.0005940 | Fulton MPACs & Remote Ends | 8 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-10-29 | NA | 2029-01-18 | NA | NA | FALSE | NA | NA ¦ NA | 28.0903 | 3797.2669 | 0 | 0 | 0 | 0 | 17.267 | 156.2406 | 0 | 0 | 0 | 0 | 17.2671 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
211 | EM TESLA REPL METCALF SPS GE RELAY |  |  | San Joaquin | Replace System A & System B 500kV Metcalf Special Protection Scheme (MSPS) line outage relays at Tesla Substation. The replacement relays will be specified with a C37.94 fiber optic communications module to supplant the existing RS-422 copper/fiber communications module. This will require upgrades on the associated MSPS line outage detection relays at Metcalf Substation to convert from RS422 copper/fiber interface to the C37.94 fiber interface. The Moss Landing 500kV MSPS upgrades are to be referenced for this work. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 5.2961 | NA | 500 kV | NA | NA | NA | 5.2021 | Non-IGP | 5798126 | T.0007517 | TESLA: REPL Metcalf SPS GE RELAY | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-01-04 | NA | 2027-01-25 | NA | NA | TRUE | NA | NA ¦ NA | 456.3353 | 612.6758 | 0 | 1.1877 | 16.1285 | 214.8756 | 217.0636 | 74.7945 | 88.6259 | 0 | 0 | 0 | 449.2554 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
212 | METCALF: REPL METCALF SPS GE RELAY |  |  | Santa Clara | Replace System A & System B 500kV Metcalf Special Protection Scheme (MSPS) line outage relays at Tesla Substation. The replacement relays will be specified with a C37.94 fiber optic communications module to supplant the existing RS-422 copper/fiber communications module. This will require upgrades on the associated MSPS line outage detection relays at Metcalf Substation to convert from RS422 copper/fiber interface to the C37.94 fiber interface. The Moss Landing 500kV MSPS upgrades are to be referenced for this work. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 500 kV | NA | NA | NA | 5.2021 | Non-IGP | 5561524 | T.0007517 | TESLA: REPL Metcalf SPS GE RELAY | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-01-04 | NA | 2027-01-11 | NA | NA | TRUE | NA | NA ¦ NA | 13.8606 | 400.1215 | 0 | 0 | 0 | 0 | 5.9947 | 225.223 | 168.9038 | 0 | 0 | 0 | 5.9947 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 5.3953 | 7.0793 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
213 | COLGATE SW STA:EPSS REPL CB 52-42-32 RE |  |  | Yuba | The driver of the project is to address EPSS Priority 3 terminals that required full panel relay replacement to enable SCADA operable EPSS settings to meet the company need. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-04 | 32 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | Extreme Heat |  | NA | 1.3099 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5807646 | T.0009702 | COLGATE SW STA: EPSS REPL CB 52-42-32 RE | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-02 | 2026-02-06 | 2026-04-13 | NA | NA | TRUE | 4600 | NA ¦ NA | 1845.5491 | 3807.4763 | 0 | 0 | 0 | 177.4996 | 1068.1241 | 2367.1312 | 194.7215 | 0 | 0 | 0 | 1245.6237 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
214 | HFTD COTTONWOOD: COMAPS CB 62 RELAYS |  |  | Cottonwood CDP, Shasta | Due to a mis-operation of Benton 60 kV CB 62 system Protection is expediting a ComAPS project to replace the relays on the Cottonwood – Benton #2 60 kV Line. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-19 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | Extreme Heat |  | NA | 26.1945 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5810115 | T.0010206 | COTTONWOOD - ComAPS CB 62 Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-07 | 2026-04-20 | 2027-05-25 | Project Design | NA | TRUE | 3200 | NA ¦ NA | 536.5055 | 2678.8168 | 0 | 0 | 0 | 65.4479 | 399.7523 | 1837.1281 | 376.4884 | 0 | 0 | 0 | 465.2003 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
215 | HFTD BENTON: COMAPS CB 42 RELAYS |  |  | Redding, Shasta | Due to a mis-operation of Benton 60 kV CB 42 system Protection is expediting a ComAPS project to replace the relays on the Cottonwood – Benton #2 60 kV Line. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-01 | 27 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | Extreme Heat |  | NA | 2.0449 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5810116 | T.0010206 | COTTONWOOD - ComAPS CB 62 Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-22 | 2026-04-20 | 2027-05-25 | Project Design | NA | TRUE | 3200 | NA ¦ NA | 607.2544 | 1513.1534 | 0 | 0 | 0 | 73.5833 | 482.3905 | 867.4635 | 89.716 | 0 | 0 | 0 | 555.9738 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
216 | HFTD ATASCADEROComAPSCB22Relays |  |  | Atascadero, San Luis Obispo | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-04 | 17 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.52277 | NA | 70 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814607 | T.0011063 | ATASCADERO CAYUCOS CompAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-09 | NA | 2028-09-22 | NA | NA | FALSE | NA | NA ¦ NA | 22.5556 | 2650.1496 | 0 | 0 | 0 | 0 | 21.1646 | 182.8395 | 500 | 420 | 0 | 0 | 21.1646 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
217 | HFTD CAYUCOSComAPSCB32Relays |  |  | San Luis Obispo | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-06 | 9 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.62112 | NA | 70 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814608 | T.0011063 | ATASCADERO CAYUCOS CompAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-23 | NA | 2028-10-06 | NA | NA | FALSE | NA | NA ¦ NA | 20.565 | 2455.4417 | 0 | 0 | 0 | 0 | 18.8932 | 131.3432 | 500 | 420 | 0 | 0 | 18.8933 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
218 | REDBUDComAPSCB152Relays |  |  | Clearlake Oaks CDP, Lake | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-05 | 48 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 3.1825 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814610 | T.0011064 | MENDOCINO REDBUD ComAPS CB Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-03-10 | NA | 2028-04-26 | NA | NA | FALSE | NA | NA ¦ NA | 28.8387 | 1061.5734 | 0 | 0 | 0 | 0 | 28 | 113.3891 | 500 | 420 | 0 | 0 | 28.1843 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
219 | HFTD EAGLEROCKComAPSCB72Relays |  |  | Sonoma | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-02 | 29 | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 2.8266 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814612 | T.0011065 | KONOCTI EAGLE ROCK ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-06-21 | NA | 2028-11-02 | NA | NA | FALSE | NA | NA ¦ NA | 42.0519 | 3114.9909 | 0 | 0 | 0 | 0 | 31.0958 | 357.6904 | 1000 | 835 | 0 | 0 | 31.0958 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
220 | HFTD KONOCTIComAPSCB6032Relays |  |  | Lake | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-10 | 14 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 1.2325 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814611 | T.0011065 | KONOCTI EAGLE ROCK ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-06-22 | NA | 2028-11-03 | NA | NA | FALSE | NA | NA ¦ NA | 53.7453 | 3278.7384 | 0 | 0 | 0 | 0 | 36.3939 | 379.704 | 1000 | 835 | 0 | 0 | 36.3939 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
221 | HFTD GARBERVILLEComAPSCB42Relays |  |  | Garberville CDP, Humboldt | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-02 | 12 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 1.3066 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814613 | T.0011066 | GARBERVILLE LAYTONVILLE ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-01-20 | NA | 2028-06-02 | NA | NA | FALSE | NA | NA ¦ NA | 96.7723 | 2864.7042 | 0 | 0 | 0 | 0 | 55.3264 | 230.4577 | 834 | 667 | 250 | 0 | 55.3265 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
222 | HFTD LAYTONVILLEComAPSCB32Relays |  |  | Laytonville CDP, Mendocino | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-04 | 10 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.93959 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814614 | T.0011066 | GARBERVILLE LAYTONVILLE ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-02-17 | NA | 2028-07-03 | NA | NA | FALSE | NA | NA ¦ NA | 85.3743 | 2027.8717 | 0 | 0 | 0 | 0 | 48.9607 | 227.911 | 834 | 667 | 250 | 0 | 48.9607 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
223 | HFTD MENDOCINOComAPSCB52Relays |  |  | Mendocino | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-12 | 5 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 4.7328 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814615 | T.0011067 | MENDOCINO WILLITS FORT BRAGG ComAPS CB R | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-01-07 | NA | 2028-03-10 | NA | NA | FALSE | NA | NA ¦ NA | 54.6735 | 1535.831 | 0 | 0 | 0 | 0 | 37.8413 | 189.9896 | 612 | 501 | 195 | 0 | 37.8414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
224 | HFTD WILLITSAComAPSCB32Relays |  |  | Mendocino | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-03 | 21 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.88868 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814616 | T.0011067 | MENDOCINO WILLITS FORT BRAGG ComAPS CB R | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-01-14 | NA | 2028-04-26 | NA | NA | FALSE | NA | NA ¦ NA | 54.943 | 1430.2853 | 0 | 0 | 0 | 0 | 34.0251 | 88.2602 | 612 | 501 | 195 | 0 | 34.0251 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
225 | HFTD FORTBRAGGAComAPSCB42Relays |  |  | Fort Bragg, Mendocino | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-16 | 20 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.62895 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814617 | T.0011067 | MENDOCINO WILLITS FORT BRAGG ComAPS CB R | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-01-10 | NA | 2028-04-26 | NA | NA | FALSE | NA | NA ¦ NA | 108.7948 | 1523.3999 | 0 | 0 | 0 | 0 | 41.392 | 174.0079 | 612 | 501 | 195 | 0 | 41.392 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
226 | HFTD DESCHUTESComAPSCB32Relays |  |  | Palo Cedro CDP, Shasta | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-12 | 45 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 1.2762 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814619 | T.0011068 | VOLTA DESCHUTES ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-11-22 | NA | 2028-05-10 | NA | NA | FALSE | NA | NA ¦ NA | 32.0543 | 1672.5116 | 0 | 0 | 0 | 0 | 19.0941 | 218.3223 | 450 | 340 | 0 | 0 | 19.0941 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
227 | HFTD VOLTA1PHComAPSCB22Relays |  |  | Shasta | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-05 | 7 | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.38584 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814618 | T.0011068 | VOLTA DESCHUTES ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-10-28 | NA | 2028-08-29 | NA | NA | TRUE | NA | NA ¦ NA | 40.1128 | 4371.827 | 0 | 0 | 0 | 0 | 22.9292 | 259.7155 | 450 | 340 | 0 | 0 | 22.9292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
228 | HFTD SANGERComAPSCB15221532Relays |  |  | Fresno | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-18 | 5 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 11.0513 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814621 | T.0011069 | BALCH SANGER ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-23 | NA | 2028-10-06 | NA | NA | FALSE | NA | NA ¦ NA | 20.0811 | 1680.4643 | 0 | 0 | 0 | 0 | 19.6689 | 75.7893 | 450 | 0 | 0 | 0 | 19.6689 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
229 | HFTD BALCH1PHComAPSCB112Relays |  |  | Fresno | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-12 | 21 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.1256 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814620 | T.0011069 | BALCH SANGER ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-08-11 | NA | 2029-01-30 | NA | NA | FALSE | NA | NA ¦ NA | 22.5105 | 787.45 | 0 | 0 | 0 | 0 | 18.8694 | 94.555 | 450 | 0 | 0 | 0 | 18.8694 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
230 | HFTD CHSSComAPSCB13121322Relays |  |  | Prunedale CDP, Monterey | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-02 | 17 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 4.5976 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814622 | T.0011070 | CHSS SALINAS SOLEDAD ComAPS CB Relays | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2029-05-11 | NA | 2029-06-29 | NA | NA | FALSE | NA | NA ¦ NA | 20.4427 | 1242.7164 | 0 | 0 | 0 | 0 | 19.2554 | 2.3676 | 300 | 0 | 0 | 0 | 19.2554 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
231 | HFTD SALINASComAPSCB15221532Relays |  |  | Salinas, Monterey | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-05 | 17 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 7.4966 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814623 | T.0011070 | CHSS SALINAS SOLEDAD ComAPS CB Relays | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2029-05-11 | NA | 2029-06-29 | NA | NA | FALSE | NA | NA ¦ NA | 15.4288 | 1233.272 | 0 | 0 | 0 | 0 | 14.209 | 2.1091 | 300 | 0 | 0 | 0 | 14.209 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
232 | HFTD SOLEDADComAPSCB10621012Relays |  |  | Soledad, Monterey | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-03 | 17 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 5.5992 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814624 | T.0011070 | CHSS SALINAS SOLEDAD ComAPS CB Relays | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2029-05-11 | NA | 2029-06-29 | NA | NA | FALSE | NA | NA ¦ NA | 14.9958 | 1234.3586 | 0 | 0 | 0 | 0 | 13.8718 | 1.9743 | 300 | 0 | 0 | 0 | 13.8718 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
233 | HFTD CHSSComAPSCB14221432Relays |  |  | Prunedale CDP, Monterey | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-02 | 17 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 4.5976 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814625 | T.0011071 | CHSS SALINAS SOLEDAD ComAPS CB Relay2 | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2029-05-11 | NA | 2029-06-29 | NA | NA | FALSE | NA | NA ¦ NA | 20.4381 | 1241.2274 | 0 | 0 | 0 | 0 | 19.2509 | 2.3672 | 300 | 0 | 0 | 0 | 19.2509 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
234 | HFTD SALINASComAPSCB13221332Relays |  |  | Salinas, Monterey | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-05 | 17 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 7.4966 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814626 | T.0011071 | CHSS SALINAS SOLEDAD ComAPS CB Relay2 | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2029-05-11 | NA | 2029-06-29 | NA | NA | FALSE | NA | NA ¦ NA | 15.1197 | 1234.515 | 0 | 0 | 0 | 0 | 13.9943 | 1.9832 | 300 | 0 | 0 | 0 | 13.9943 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
235 | HFTD SOLEDADComAPSCB10321042Relays |  |  | Soledad, Monterey | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-03 | 17 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 5.5992 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814627 | T.0011071 | CHSS SALINAS SOLEDAD ComAPS CB Relay2 | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2029-05-11 | NA | 2029-07-02 | NA | NA | FALSE | NA | NA ¦ NA | 14.2507 | 1241.1867 | 0 | 0 | 0 | 0 | 13.1355 | 1.9204 | 300 | 0 | 0 | 0 | 13.1354 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
236 | HFTD TABLEMTNComAPSCB32Relays |  |  | Butte | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-20 | 14 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 47.516 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814631 | T.0011073 | TABLE MTN ComAPS CB 32 Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-06-07 | NA | 2027-08-30 | NA | NA | TRUE | NA | NA ¦ NA | 25.3588 | 1512.3719 | 0 | 0 | 0 | 0 | 21.4382 | 225.9337 | 1020.3066 | 315 | 0 | 0 | 21.4382 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
237 | HFTD CENTERVILLE PH: ComAPS CB 12 Relays |  |  | Butte Creek Canyon CDP, Butte | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-06 | 12 | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.85277 | NA | 60 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814922 | T.0011073 | TABLE MTN ComAPS CB 32 Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-06-18 | NA | 2027-09-13 | NA | NA | TRUE | NA | NA ¦ NA | 25.3493 | 1246.1156 | 0 | 0 | 0 | 0 | 23.0814 | 156.4818 | 1061.1722 | 0 | 0 | 0 | 23.0814 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
238 | HFTD ATASCADERO: ComAPS CB 42 Relays |  |  | Atascadero, San Luis Obispo | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-04 | 7 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.52277 | NA | 70 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814923 | T.0011074 | SAN LUIS OBISPO ComAPS CB 32 Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-01-14 | NA | 2028-05-30 | NA | NA | FALSE | NA | NA ¦ NA | 19.5297 | 2354.1851 | 0 | 0 | 0 | 0 | 17.9617 | 293.9724 | 0 | 0 | 0 | 0 | 17.9617 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
239 | HFTD SANLUISOBISPOComAPSCB32Relays |  |  | San Luis Obispo | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-10 | 7 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 3.8969 | NA | 70 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814632 | T.0011074 | SAN LUIS OBISPO ComAPS CB 32 Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-23 | NA | 2028-10-06 | NA | NA | FALSE | NA | NA ¦ NA | 22.2532 | 2341.0991 | 0 | 0 | 0 | 0 | 20.2546 | 106.4157 | 585 | 250 | 0 | 0 | 20.2546 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
240 | HFTD ROUNDMTNComAPSCB222Relays |  |  | Round Mountain CDP, Shasta | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-09 | 4 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 29.1389 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814634 | T.0011075 | PIT 4 ComAPS CB 312 Relays | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-10-27 | NA | 2028-03-16 | NA | NA | FALSE | NA | NA ¦ NA | 25.5032 | 1313.8519 | 0 | 0 | 0 | 0 | 14.1176 | 141.6897 | 460 | 376 | 0 | 0 | 14.1177 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
241 | HFTD PIT4ComAPSCB312Relays |  |  | Shasta | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | NA | 2 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 1.1576 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814633 | T.0011075 | PIT 4 ComAPS CB 312 Relays | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-12-01 | NA | 2028-04-17 | NA | NA | FALSE | NA | NA ¦ NA | 21.4348 | 1506.1986 | 0 | 0 | 0 | 0 | 12.7156 | 128.1963 | 460 | 376 | 0 | 0 | 12.7156 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
242 | HFTD JAMESBBLACKComAPSCB332342Relays |  |  | Shasta | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2025-07-22 | 51 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814598 | T.0011075 | PIT 4 ComAPS CB 312 Relays | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-02-04 | NA | 2028-06-20 | NA | NA | FALSE | NA | NA ¦ NA | 26.1139 | 1642.8945 | 0 | 0 | 0 | 0 | 13.9692 | 194.135 | 460 | 376 | 0 | 0 | 13.9691 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
243 | HFTD CRESTAPHComAPSCB282Relays |  |  | Butte | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-10 | 82 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 1.4913 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814599 | T.0011076 | CRESTA PH RIO OSO ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-06-04 | NA | 2027-08-27 | NA | NA | TRUE | NA | NA ¦ NA | 14.735 | 1099.7595 | 0 | 0 | 0 | 0 | 14.5502 | 93.182 | 990.2331 | 0 | 0 | 0 | 14.5502 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
244 | HFTD RIOOSOComAPSCB242Relays |  |  | Sutter | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-04 | 23 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 9.3219 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814600 | T.0011076 | CRESTA PH RIO OSO ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-06-23 | NA | 2027-09-16 | NA | NA | TRUE | NA | NA ¦ NA | 9.9428 | 1138.412 | 0 | 0 | 0 | 0 | 9.8181 | 104.261 | 1017.8803 | 0 | 0 | 0 | 9.8181 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
245 | HFTD PARDISEComAPSCB122Relays |  |  | Paradise, Butte | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-05 | 24 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.79098 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814601 | T.0011077 | PARDISE BUTTE ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-09-28 | NA | 2026-12-30 | NA | NA | TRUE | NA | NA ¦ NA | 28.8859 | 1439.4369 | 0 | 0 | 0 | 0 | 13.6207 | 925.8162 | 105.3991 | 0 | 0 | 0 | 13.6207 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
246 | HFTD BUTTEComAPSCB122Relays |  |  | Chico, Butte | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-06 | 26 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 3.1949 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814602 | T.0011077 | PARDISE BUTTE ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-11-03 | NA | 2026-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 38.7181 | 1227.977 | 0 | 0 | 0 | 0 | 21.6499 | 706.3271 | 202.004 | 0 | 0 | 0 | 21.6499 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
247 | HFTD RIOOSOComAPSCB232Relays |  |  | Sutter | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-04 | 24 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 9.3219 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814604 | T.0011081 | POE PH RIO OSO ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-07-21 | NA | 2027-10-13 | NA | NA | TRUE | NA | NA ¦ NA | 30.3314 | 942.6538 | 0 | 0 | 0 | 0 | 29.951 | 214.6593 | 671.7161 | 0 | 0 | 0 | 29.951 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
248 | HFTD POEPHComAPSCB222252Relays |  |  | Butte | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-13 | 10 | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 2.9596 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814603 | T.0011081 | POE PH RIO OSO ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-09-13 | NA | 2027-10-28 | NA | NA | TRUE | NA | NA ¦ NA | 51.2614 | 1985.287 | 0 | 0 | 0 | 0 | 45.5089 | 475.4618 | 1458.5357 | 0 | 0 | 0 | 45.5089 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
249 | HFTD PUEBLOComAPSCB152Relays |  |  | Napa | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-02 | 26 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 1.4799 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814606 | T.0011083 | SONOMA A PUEBLO ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-06-28 | NA | 2027-11-09 | NA | NA | TRUE | NA | NA ¦ NA | 89.1861 | 1328.0892 | 0 | 0 | 0 | 0 | 66.5087 | 474.754 | 706.3567 | 0 | 0 | 0 | 66.5087 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
250 | HFTD SONOMAAComAPSCB142Relays |  |  | Santa Rosa, Sonoma | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-02 | 3 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.91804 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814605 | T.0011083 | SONOMA A PUEBLO ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-06-29 | NA | 2027-11-10 | NA | NA | TRUE | NA | NA ¦ NA | 74.2743 | 1281.4966 | 0 | 0 | 0 | 0 | 53.1878 | 506.7405 | 650.86 | 0 | 0 | 0 | 53.1878 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
251 | RIO OSO: ComAPS CB 412/422 Relays |  |  | Sutter | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-04 | 3 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 9.3219 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814784 | T.0011132 | RIO OSO and DRUM: ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-05-12 | NA | 2027-07-29 | NA | NA | TRUE | NA | NA ¦ NA | 23.4728 | 849.8549 | 0 | 0 | 0 | 0 | 22.2336 | 196.339 | 631.2822 | 0 | 0 | 0 | 22.2337 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
252 | DRUM: ComAPS CB 340/350/360 Relays |  |  | Placer | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-12 | 20 | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 2.2491 | NA | 115 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814783 | T.0011132 | RIO OSO and DRUM: ComAPS CB Relays | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-05-12 | NA | 2027-09-10 | NA | NA | TRUE | NA | NA ¦ NA | 37.892 | 885.9891 | 0 | 0 | 0 | 0 | 36.7145 | 246.8749 | 602.3996 | 0 | 0 | 0 | 36.7145 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
253 | CLOVERDALE: ComAPS CB 132 Relays |  |  | Cloverdale, Sonoma | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-02-12 | 35 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 1.7377 | NA | 115 kV | NA | NA | NA | 5.1021 | Non-IGP | 5814657 | T.0011139 | CLOVERDALE ComAPS CB 132 Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-01-10 | NA | 2028-02-11 | NA | NA | FALSE | NA | NA ¦ NA | 27.9754 | 2342.6421 | 0 | 0 | 0 | 0 | 24 | 148.7383 | 1000 | 835 | 335 | 0 | 23.9038 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
254 | HFTD HAASPHComAPSCB212Relays |  |  | Fresno | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-12 | 22 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 1.684 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814628 | T.0011291 | HAAS BALCH PH MCCALL ComAPS CB Relays | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-30 | NA | 2028-10-12 | NA | NA | FALSE | NA | NA ¦ NA | 25.4201 | 1832.6519 | 0 | 0 | 0 | 0 | 22.9172 | 114.4838 | 450 | 250 | 0 | 0 | 22.9172 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
255 | HFTD BALCHPHComAPSCB242Relays |  |  | Fresno | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-12 | 23 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 0.1256 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814629 | T.0011291 | HAAS BALCH PH MCCALL ComAPS CB Relays | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-30 | NA | 2028-10-12 | NA | NA | FALSE | NA | NA ¦ NA | 27.5728 | 1962.1084 | 0 | 0 | 0 | 0 | 25.0896 | 126.2373 | 450 | 250 | 0 | 0 | 25.0896 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
256 | HFTD MCCALLComAPSCB262Relays |  |  | Fresno | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-06 | 12 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 16.2494 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | 5814630 | T.0011291 | HAAS BALCH PH MCCALL ComAPS CB Relays | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-30 | NA | 2028-10-12 | NA | NA | FALSE | NA | NA ¦ NA | 23.7505 | 1820.5581 | 0 | 0 | 0 | 0 | 25.1072 | 108.0163 | 585 | 250 | 0 | 0 | 25.1072 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
257 | FULTON: ComAPS CB 632 Relays |  |  | Fulton CDP, Sonoma | Install relays, associated telecom equipment, and establish telecom circuits to enable communication-assisted protection (ComAPS) for the associated transmission line. Requires coordination of scope at all terminals of the subject transmission line. Specific ComAPS type to be determined by system protection engineer. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Wildfire Mitigation | Relay Upgrades | NA | NA | 2026-03-11 | 21 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | 13.4076 | NA | 230 kV | NA | NA | NA | 5.2021 | Non-IGP | EX130474 | TBD | TBD | TBD | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1751 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 834 | 667 | 250 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Wildfire Related] ComAPS are EPSS related projects and are to reduce fire ignitions. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
258 | EM 3RD DTT MIDWAY CB 422 |  |  | Buttonwillow CDP, Kern | Per system requirement, replace the existing DTT RFL 6745 with the new GARD 8000 in Midway communicating with Frito Lay Cogen (CB 422). | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5530322 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-12-01 | 2020-12-07 | 2021-08-04 | Prioritization | NA | FALSE | 325 | NA ¦ NA | 129.0425 | 129.0425 | 22.4024 | 1.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.0425 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 19.2882 | 1.2667 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
259 | EM TEMBLOR REPL 3RD DTT |  |  | Kern | Per system requirement, replace the existing DTT RFL 6745s with the new GARD 8000s for McKittrick Cogen on Temblor HVCB 312. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.93942 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5535099 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-11-02 | NA | 2020-12-18 | NA | NA | FALSE | NA | NA ¦ NA | 152.8475 | 152.8475 | 26.6771 | 3.0043 | 69.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152.8475 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 26.6771 | 3.0043 | 38.8332 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
260 | EM MCKITTRICK REPL 3RD DTT |  |  | McKittrick CDP, Kern | Per system requirement, install a complete two (2) terminal rack in PG&E Telecom Control room outside of the station fence including two new GARD 8000 DTT (direct transfer trip) devices for two terminals: Midway Sub and Temblor Sub. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.80646 | NA | 70 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5534306 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-02-01 | NA | 2021-02-22 | NA | NA | FALSE | NA | NA ¦ NA | 163.7141 | 163.7141 | 20.8416 | 2.6799 | 69.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163.7141 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 20.8416 | 2.6799 | 53.0313 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
261 | EM SARATOGA REPL ODN |  |  | Saratoga, Santa Clara | Bring ODN into Saratoga Sub through a new MVRF. Retire the existing UDN router due to lack of security. The performance and functionality of ODN will meet PG&E policies and standards. Cybersecurity has determined that replacing the UDN router with new ODN router per the latest standard will meet PG&E policies and standards. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 26 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.4212 | NA | 230 kV | 437 | NA | NA | NA | NA | 5526963 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-07-01 | NA | 2022-11-15 | NA | NA | FALSE | NA | NA ¦ NA | 46.9271 | 46.9271 | 13.0775 | 17.6134 | 8.466 | 3.4199 | 0 | 0 | 0 | 0 | 0 | 0 | 46.9271 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 13.0775 | 17.6134 | 8.466 | 3.4199 | -4.6927 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
262 | EM 3RD DTT SONOMA LANDFILL |  |  | Fulton CDP, Sonoma | Per system requirement, install a complete one (1) terminal rack in Sonoma Landfill Cogen to replace the one existing DTT RFL 6745 with the new GARD 8000 for Sonoma Landfill Cogen to Fulton substation. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-11 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.4076 | NA | 60 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5777638 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-08-18 | NA | 2026-03-31 | NA | NA | TRUE | NA | NA ¦ NA | 341.8068 | 356.4908 | 14.2104 | 35.7764 | 32.1528 | 60.5183 | 51.6116 | 26.1166 | 0 | 0 | 0 | 0 | 330.3742 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
263 | EM SIMPSON RIPON COGEN REPL 3RD DTT |  |  | Alameda | Tesla Substation has several existing Direct Transfer Trip (DTT) Equipment to the 3rd party COGEN Facilities that need to be upgraded or retired. The objective of this project is to replace/upgrade the identified in-service DTT Transmitters. At Ripon Cogen existing RFL 6745 will be replaced with a new GARD 8000. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | 33 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 115 kV | 437 | NA | NA | 4.0111 | Non-IGP | 5526953 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-04 | NA | 2026-05-14 | NA | NA | TRUE | NA | NA ¦ NA | 100.7295 | 142.1093 | 17.7757 | 5.8436 | 12.7602 | 7.1518 | 16.5006 | 41.4912 | 0 | 0 | 0 | 0 | 100.6181 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 17.7757 | 5.8436 | 12.7602 | 7.1518 | 16.5006 | 0.11136 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
264 | EM 3RD DTT TESLA CB 332 |  |  | Alameda | Tesla Substation has several existing Direct Transfer Trip (DTT) Equipment to the 3rd party COGEN Facilities that need to be upgraded or retired. The objective of this project is to retire/remove identified DTT Transmitters to 3rd party facilities that are no longer in service, and to replace/upgrade the identified in-service DTT Transmitters. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | 33 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 177 | NA | NA | 4.0111 | Non-IGP | 5530326 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-30 | NA | 2026-08-05 | NA | NA | TRUE | NA | NA ¦ NA | 381.2551 | 481.6934 | 157.5804 | 131.0312 | 30.9841 | 5.6891 | 31.4894 | 33.4314 | 67.1259 | 0 | 0 | 0 | 381.1361 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 157.5804 | 131.0312 | 30.9841 | 5.6891 | 31.4894 | 0.11901 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
265 | EM TESLA REPL 3RD DTT, US WINDPOWER 4 |  |  | Alameda | Tesla Substation has several existing Direct Transfer Trip (DTT) Equipment to the 3rd party COGEN Facilities that need to be upgraded or retired. The objective of this project is to replace/upgrade the identified in-service DTT Transmitters. At US Windpower 4 (Ralph Sub) existing RFL 6745 will be replaced with a new GARD 8000. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | 33 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 177 | NA | NA | 4.0111 | Non-IGP | 5526955 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-12-28 | NA | 2026-12-28 | NA | NA | FALSE | NA | NA ¦ NA | 202.6978 | 206.8294 | 14.2577 | 30.6483 | 11.5834 | 1.3603 | 0 | 0 | 4.1316 | 0 | 0 | 0 | 202.6978 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 ¦ 2027 | 14.2577 | 30.6483 | 11.5834 | 1.3603 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
266 | EM COALINGA #1 REPL 3RD DTT, OIL CITY |  |  | Coalinga, Fresno | Per system requirement, install a standard two (2) terminal rack RFL-CD65809 in PG&E Telecom control room to replace the two existing DTT with the new GARD 8000 for Oil City sub to two terminals: Coalinga #1 and Coalinga #2 substation | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-13 | 38 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.98563 | NA | 70 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5526950 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-02-02 | NA | 2027-02-09 | NA | NA | FALSE | NA | NA ¦ NA | 278.044 | 278.044 | 63.3449 | 42.1053 | 7.4762 | 20.6603 | 0 | 0 | 40.3331 | 0 | 0 | 0 | 278.044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 63.3449 | 42.1053 | 7.4762 | 20.6603 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
267 | EM 3RD DTT FLOWIND 2 SUB |  |  | Alameda | Tesla Substation has several existing Direct Transfer Trip (DTT) Equipment to the 3rd party COGEN Facilities that need to be upgraded or retired. The objective of this project is to replace/upgrade the identified in-service DTT Transmitters. At US Power (Flowind 2 Sub) existing RFL 6745 will be replaced with a new GARD 8000. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | 33 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 437 | NA | NA | 4.0111 | Non-IGP | 5526942 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-04-12 | NA | 2027-04-26 | NA | NA | FALSE | NA | NA ¦ NA | 105.6304 | 105.6304 | 13.2454 | 10.1437 | 0.3054 | 18.2072 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6304 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 13.2454 | 10.1437 | 0.30543 | 18.2072 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
268 | EM 3RD DTT COALINGA #1 CB 12 |  |  | Coalinga, Fresno | Per system requirement, replace the three existing DTT RFL 6745s with the new GARD 8000s for Oil City sub, Coalinga Cogen and Chevron Derrick sub. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-13 | 38 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.98563 | NA | 70 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5530324 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-05-03 | NA | 2027-05-10 | NA | NA | FALSE | NA | NA ¦ NA | 123.7988 | 123.7988 | 52.3293 | 26.0731 | 7.5969 | 20.6603 | 0 | 0 | 40.4394 | 0 | 0 | 0 | 123.7988 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 ¦ 2027 | 52.3293 | 26.0731 | 7.597 | 20.6603 | 0 | -12.3799 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
269 | EM 3RD DTT COALINGA #2 CB 22 |  |  | Fresno | Per system requirement, replace the three existing DTT RFL 6745s with the new GARD 8000s for Oil City sub, Coalinga Cogen and Chevron Derrick sub. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-16 | 38 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.5937 | NA | 70 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5530325 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-05-03 | NA | 2027-05-10 | NA | NA | FALSE | NA | NA ¦ NA | 113.9766 | 113.9766 | 43.1831 | 22.0416 | 7.5224 | 20.6603 | 0 | 0 | 40.4394 | 0 | 0 | 0 | 113.9766 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 ¦ 2027 | 43.1831 | 22.0416 | 7.5224 | 20.6603 | 0 | -11.3977 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
270 | EM COALINGA COGEN #1 REPL 3RD DTT |  |  | Coalinga, Fresno | Per system requirement, install a standard two (2) terminal rack RFL-CD62677 in PG&E Telecom control room to replace the two existing DTT with the new GARD 8000 for Coalinga Cogen to two terminals: Coalinga #1 and Coalinga #2 substation. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-13 | 38 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.98563 | NA | 70 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5526940 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-08-05 | NA | 2027-08-12 | NA | NA | FALSE | NA | NA ¦ NA | 134.8187 | 134.8187 | 38.7451 | 42.5712 | 8.1367 | 21.5677 | 0 | 0 | 37.7645 | 0 | 0 | 0 | 134.8187 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 38.7451 | 42.5712 | 8.1367 | 21.5677 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
271 | EM DERRICK REPL 3RD DTT |  |  | Coalinga, Fresno | Per system requirement, install a complete two (2) terminal rack in Chevron Coalinga Cogen – Derrick substation telecom room to replace the existing DTT RFL 6745s with two new GARD 8000s for Derrick sub to Coalinga #1 sub and Derrick Sub to Coalinga #2 substation. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-13 | 38 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.98563 | NA | 70 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5526941 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-09-07 | NA | 2027-09-14 | NA | NA | FALSE | NA | NA ¦ NA | 137.2598 | 137.2598 | 43.8419 | 39.467 | 9.1771 | 20.6603 | 0 | 0 | 76.4122 | 0 | 0 | 0 | 137.2598 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 43.8419 | 39.467 | 9.1771 | 20.6603 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
272 | EM TESLA REPL 3RD DTT, PATTERSON PASS |  |  | Alameda | Tesla Substation has several existing Direct Transfer Trip (DTT) Equipment to the 3rd party COGEN Facilities that need to be upgraded or retired. The objective of this project is to retire/remove identified DTT Transmitters at Patterson Pass (ADCC Sub). | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 177 | NA | NA | NA | NA | 5526951 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-12-01 | NA | 2023-01-05 | NA | NA | FALSE | NA | NA ¦ NA | 58.4872 | 58.4872 | 21.9254 | 11.6136 | 5.9821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.4872 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 ¦ 2026 | 21.9254 | 11.6136 | 5.9821 | 0 | -52.6385 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
273 | EM TESLA REPL 3RD DTT, JV ENTERP HOWDEN |  |  | Alameda | Tesla Substation has several existing Direct Transfer Trip (DTT) Equipment to the 3rd party COGEN Facilities that need to be upgraded or retired. The objective of this project is to retire/remove identified DTT Transmitters at JVE Enterprise (Howden Sub). | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 437 | NA | NA | NA | NA | 5526945 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-06-08 | NA | 2023-06-08 | NA | NA | FALSE | NA | NA ¦ NA | 80.3193 | 80.3193 | 19.7445 | 30.2347 | 19.3222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3193 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 ¦ 2026 | 19.7445 | 30.2347 | 19.3222 | 0 | -72.2873 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
274 | EM: 3RD DTT SAN LUIS OBISPO CB112 |  |  | San Luis Obispo | Replace 6 obsolete SEL-221 relays on SLO CB142,152,162 SEL with SEL 311C relays. The existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need a shorter maintenance cycle. They are no longer adequately supported by the manufacturers. The manufacturer’s software used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This creates a risk of maintenance non-compliance. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-10 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.8969 | NA | 115 kV | 437 | NA | NA | NA | NA | 5530323 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-09-18 | 2020-09-18 | 2020-12-01 | NA | NA | FALSE | 169 | NA ¦ NA | 130.5587 | 130.5587 | 42.6351 | 1.2502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130.5587 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 42.6351 | 1.2502 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
275 | 3rd DTT Frito Lay Cogen |  |  | Buttonwillow CDP, Kern | Replace the existing obsolete RFL 6745, used for direct transfer trip (DTT) to Midway substation, with a new RFL Gard 8000. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new Gard 8000 units. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5526943 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-07-01 | 2020-07-20 | 2021-04-23 | Prioritization | NA | FALSE | 208 | NA ¦ NA | 201.3083 | 201.3083 | 22.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.3083 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 103.8578 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
276 | MCCALL: REPL COMM PROC |  |  | Fresno | As a part of communication processor lifecycle, changing out 5 SEL 2020’s and one 2032 with 6 RuggedCom RS416 terminal servers at McCall Substation. This will get the rest of the remote relay access off of dial up and get all of it on the ODN. ODN will need to be extended to the small MPAC Capacitor Building. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 16.2494 | NA | 230 kV | 437 | NA | NA | NA | NA | 5526958 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-08-05 | 2021-08-18 | 2021-08-18 | NA | NA | FALSE | 110 | NA ¦ NA | 340.9847 | 340.9847 | 210.0008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340.9847 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 189.9213 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
277 | EM 3RD DTT KERNRIDGE SUB |  |  | Buttonwillow CDP, Kern | This is a Project Authorization and Post Job Estimate to install the emergency replacement of EM3RD DTT KERNRIDGE SUB at MIDWAY SUB, which failed on or around 08/24/2017. The failed equipment was replaced and placed back into service on 09/22/2021. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 115 kV | 437 | NA | NA | NA | NA | 5526946 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-09-01 | 2021-09-22 | 2021-09-22 | NA | NA | FALSE | 357 | NA ¦ NA | 337.1212 | 337.1212 | 35.4873 | 2.1212 | 0.3054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337.1212 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 35.4873 | 2.1212 | -67.1188 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
278 | EM SAN RAMON REPL ODN |  |  | San Ramon, Contra Costa | As part of System Protection and Telecom TED effort to bring digital infrastructure to critical PG&E substations for relay protection and relay access, San Ramon has been identified as a candidate. Currently San Ramon Substation has only single DSO’s for SCADA, Relay Access, and telephone. This station has fiber outside the station where the electrical tap is located. The fiber has been identified by Telecom Architects to be functioning fiber and adequate for Protection, ODN, and UDN. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 24 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.3628 | NA | 230 kV | 483 | NA | NA | NA | NA | 5526962 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-03 | 2018-10-31 | 2023-02-03 | Prioritization | NA | TRUE | 331 | NA ¦ NA | 871.2484 | 877.1096 | 375.9825 | 152.2862 | 11.7956 | 1.9787 | -3.8456 | 5.8612 | 0 | 0 | 0 | 0 | 871.2484 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 375.9825 | 152.2862 | 11.7956 | 1.9787 | -3.8456 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
279 | EM: HONEY LAKE,AMEOLE,WINGL REPL 3RD DTT |  |  | Plumas | Honey Lake Generation facility has a DTT application between their facility and LMUD facility located next to PGE Westwood Substation. The DTT in the LMUD facility is initiated by the CB 22 in the PGE Westwood Substation via a copper cable. Due to lease line failures, and the difficulty accessing the LMUD facility, PGE will relocate new DTT equipment to the Westwood Substation and change the existing circuit from 2 wire to 4 wire. | Substation - Other Equipment | Relocate | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-10 | 22 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.96252 | NA | 60 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5526944 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-04-15 | 2027-04-26 | 2025-04-18 | NA | NA | TRUE | 714 | NA ¦ NA | 671.3602 | 671.3602 | 450.1058 | 121.3619 | -1.1943 | -328.4149 | 134.7593 | 0 | 0 | 0 | 0 | 0 | 671.3602 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 450.1058 | 121.3619 | -1.1943 | -328.4149 | 134.7593 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
280 | EM 3RD DTT WESTWOOD CB 22 |  |  | Westwood CDP, Lassen | Honey Lake Generation facility has a DTT application between their facility and LMUD facility located next to PGE Westwood Substation. The old RFL 6745’s used in the DTT application will be replaced with RFL Gard 8000’s. In addition, due to lease line failures, and the difficulty accessing the LMUD facility, PGE will relocate new DTT equipment from the LMUD facility to the Westwood Substation, and install a new T1. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-09 | 32 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.47411 | NA | 60 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5530331 | T.0003298 | EM: IT Replacements | 30 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-04-14 | 2025-04-18 | 2025-04-18 | NA | NA | FALSE | 680.03 | NA ¦ NA | 275.3111 | 275.3111 | 14.6412 | 28.5478 | 2.6594 | 79.9799 | 87.7866 | 0.1979 | 40.4394 | 0 | 0 | 0 | 275.1132 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 14.6412 | 28.5478 | 2.6594 | 79.9799 | 87.7866 | 0.19786 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
281 | EM UPLC PANOCHE SUB CB 212 |  |  | Fresno | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 12 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | 177 | NA | NA | NA | NA | 5527510 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-01 | NA | 2021-10-19 | NA | NA | FALSE | NA | NA ¦ NA | 50.2081 | 50.2081 | 16.2688 | 18.4586 | -0.1148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2081 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 13.9312 | 20.5548 | -0.10917 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
282 | EM UPLC MERCED FALLS |  |  | Merced | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | 13 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.4194 | NA | 70 kV | NA | NA | NA | NA | NA | 5529844 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-02 | NA | 2021-12-09 | NA | NA | FALSE | NA | NA ¦ NA | 72.0039 | 72.0039 | 21.0238 | 25.9947 | 24.9854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0039 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 21.0238 | 22.6998 | 23.2345 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
283 | EM UPLC COTTLE SUB (MELONES) |  |  | Oakdale, Stanislaus | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | 13 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.0963 | NA | 230 kV | 437 | NA | NA | NA | NA | 5527439 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-03-28 | NA | 2022-05-10 | NA | NA | FALSE | NA | NA ¦ NA | 102.2181 | 102.2181 | 7.0833 | 75.3888 | -0.3422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2181 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 9.9698 | 75.3888 | -0.34222 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
284 | EM UPLC PITTSBURG PP CB 612 |  |  | Pittsburg, Contra Costa | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 13 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.72358 | NA | 230 kV | 437 | NA | NA | NA | NA | 5527546 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-08-02 | 2022-06-16 | 2018-08-07 | NA | NA | FALSE | 46.1965 | NA ¦ NA | 46.1965 | 46.1965 | 19.2807 | 2.0388 | 0.3054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.1965 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 19.2807 | 2.0388 | 0.30543 | -4.6197 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
285 | EM UPLC LOS BANOS SUB CB 252 |  |  | Merced | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 12 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 230 kV | 177 | NA | NA | NA | NA | 5527509 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-08-24 | 2021-10-19 | 2021-10-19 | NA | NA | FALSE | 46.0031 | NA ¦ NA | 46.0031 | 46.0031 | 15.9551 | 14.5314 | -0.0789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.0031 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 13.6625 | 16.7908 | -0.07502 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
286 | EM BELLOTA REPL CB 230 UPLC 285/298-230 |  |  | San Joaquin | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-14 | 16 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | NA | NA | 5531106 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-05 | 2022-08-30 | 2021-11-10 | NA | NA | FALSE | 65.8829 | NA ¦ NA | 65.8829 | 65.8829 | 33.8377 | 29.4919 | 0.3056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.8829 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 65.5772 | 0.30563 | -13.1766 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
287 | EM RANCHO SECO REPL UPLC-1 |  |  | San Joaquin | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-14 | 13 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | NA | NA | 5531107 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-05 | 2022-08-30 | 2021-11-10 | NA | NA | FALSE | 18.3315 | NA ¦ NA | 18.3315 | 18.3315 | 5.7961 | 6.9757 | 2.5596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3315 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 5.7961 | 6.9757 | 2.5596 | -3.6663 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
288 | EM BELLOTA REPL CB 240 UPLC 285-240 |  |  | San Joaquin | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-14 | 16 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | NA | NA | 5531108 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-02-28 | 2022-03-15 | 2022-03-08 | NA | NA | FALSE | 99.5123 | NA ¦ NA | 99.5123 | 99.5123 | 10.8881 | 85.867 | 0.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5123 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 99.0405 | 0.47182 | -19.9025 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
289 | EM CAMANCHE PUMPING PLANT REPL UPLC-2 |  |  | San Joaquin | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-14 | 13 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | NA | NA | 5531109 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-02-28 | 2022-03-15 | 2022-03-08 | NA | NA | FALSE | 15.089 | NA ¦ NA | 15.089 | 15.089 | 3.4046 | 6.6248 | 2.5596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.089 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 12.5293 | 2.5596 | -3.0178 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
290 | EM BELLOTA REPL CB 240 UPLC 298A-240 |  |  | San Joaquin | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-14 | 16 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | NA | NA | 5531110 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-02-28 | 2022-03-15 | 2022-03-08 | NA | NA | FALSE | 41.2154 | NA ¦ NA | 41.2154 | 41.2154 | 5.9046 | 28.8311 | 6.4797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.2154 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 34.7356 | 6.4797 | -8.2431 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
291 | EM CAMANCHE PUMPING PLANT REPL UPLC 298 |  |  | San Joaquin | Replace existing UPLC at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-14 | 13 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | NA | NA | 5531111 | T.0003356 | EM: UPLC Projects | 14 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-02-28 | 2022-03-15 | 2022-03-08 | NA | NA | FALSE | 14.2895 | NA ¦ NA | 14.2895 | 14.2895 | 5.9046 | 5.8252 | 2.5596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.2895 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 11.7298 | 2.5596 | -1.4289 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
292 | BUCKET: 3rd Party DTT |  |  | NA | Forecast placeholder for 3rd Party Direct Transfer Trip installations | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Asset Condition | Relay Upgrades | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 128 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5528933 | T.0003749 | EM: 3RD DTT | 8 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 22.2884 | 22.2884 | -679.9258 | 22.7787 | 35.3049 | -85.3778 | 7.6144 | 0 | 0 | 0 | 0 | 0 | 22.2884 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | -679.9258 | 22.7787 | 35.3049 | -85.3778 | 7.6144 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
293 | EM FULTON REPL 3RD DTT LAGUNA WW TREAT |  |  | Fulton CDP, Sonoma | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-11 | 37 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.4076 | NA | 60 kV | 128 | 3. Emergency Preparedness | NA | 4.0111 | Non-IGP | 5532738 | T.0003749 | EM: 3RD DTT | 8 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-10-01 | NA | 2026-03-26 | NA | NA | TRUE | NA | NA ¦ NA | 330.885 | 346.1014 | 38.1179 | 16.7497 | 22.6126 | 43.9729 | 148.9894 | 42.0875 | 0 | 0 | 0 | 0 | 302.9276 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 38.1179 | 16.7497 | 22.6126 | 43.9729 | 148.9894 | 27.9574 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
294 | EM LAGUNA WW TREAT REPL 3RD DTT FULTON |  |  | Fulton CDP, Sonoma | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-11 | 37 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.4076 | NA | 60 kV | 128 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5532782 | T.0003749 | EM: 3RD DTT | 8 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-02-02 | NA | 2027-02-17 | NA | NA | TRUE | NA | NA ¦ NA | 435.2611 | 546.4951 | 9.0383 | 30.374 | 167.7586 | 59.7793 | 66.5977 | 2.39 | 110.7655 | 0 | 0 | 0 | 433.3396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 9.0383 | 30.374 | 167.7586 | 59.7793 | 66.5977 | 1.9215 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
295 | EM CHOW II PEAK REPL 3RD DTT LEGRND-CH |  |  | Chowchilla, Madera | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-17 | 36 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.723 | NA | 115 kV | 128 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5532729 | T.0003749 | EM: 3RD DTT | 8 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-02-08 | NA | 2027-02-22 | NA | NA | TRUE | NA | NA ¦ NA | 98.059 | 415.5914 | 8.4302 | 22.9042 | 9.695 | 35.6003 | 0 | 183.4724 | 95.2582 | 0 | 0 | 0 | 98.059 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 8.4302 | 22.9042 | 9.695 | 35.6003 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
296 | EM CHOWCHILLA REPL 3RD DTT LEGRND-CHOW |  |  | Chowchilla, Madera | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-17 | 36 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.723 | NA | 115 kV | 128 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5532730 | T.0003749 | EM: 3RD DTT | 8 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-02-08 | NA | 2027-02-22 | NA | NA | TRUE | NA | NA ¦ NA | 119.0833 | 301.6929 | 26.7683 | 22.9904 | 9.4399 | 37.899 | 0 | 92.9323 | 75.933 | 0 | 0 | 0 | 119.0833 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 26.7683 | 22.9904 | 9.4399 | 37.899 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
297 | EM LE GRAND REPL 3RD DTT LEGRND-CHOW |  |  | Merced | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-17 | 36 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.8754 | NA | 115 kV | 128 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5532784 | T.0003749 | EM: 3RD DTT | 8 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-02-08 | NA | 2027-02-22 | NA | NA | TRUE | NA | NA ¦ NA | 108.6403 | 338.186 | 29.8095 | 24.9238 | 10.1561 | 23.8146 | 0 | 143.8111 | 32.9126 | 0 | 0 | 0 | 108.6403 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 29.8095 | 24.9238 | 10.1561 | 23.8146 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
298 | EM CALPINEAG REPL 3RD DTT LOS EST -AG |  |  | San Jose, Santa Clara | Emergency replacement of EMCALPINEAG3RD DTT LOS EST AG at LOS ESTEROS SUB, which failed on or around 10/30/2018. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-09 | 21 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.1703 | NA | 115 kV | 128 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5532728 | T.0003749 | EM: 3RD DTT | 8 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-03 | 2021-12-17 | 2021-12-17 | NA | NA | FALSE | 278 | NA ¦ NA | 258.0009 | 258.0009 | 137.1238 | 85.216 | 3.9801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.0009 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 137.1238 | 85.216 | -47.6201 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
299 | EM LOS ESTEROS REPL 3RD DTT LOS EST -A |  |  | San Jose, Santa Clara | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-09 | 21 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.1703 | NA | 230 kV | 128 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5532787 | T.0003749 | EM: 3RD DTT | 8 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-03 | 2022-01-14 | 2021-12-17 | NA | NA | FALSE | 154.0049 | NA ¦ NA | 154.0049 | 154.0049 | 74.2828 | 48.2798 | 0.8471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.0049 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 74.2828 | 48.2798 | -29.9538 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
300 | EM MCCALL REPL CB 552 3RD DTT_KING COGEN |  |  | Fresno | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 24 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 16.2494 | NA | 230 kV | 131 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5534707 | T.0004621 | EM: 3rd Party DTT | 9 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-11-08 | NA | 2027-11-15 | NA | NA | FALSE | NA | NA ¦ NA | 78.1833 | 78.1833 | 29.5308 | 3.8383 | 6.0591 | 20.6603 | 0 | 0 | 68.3558 | 0 | 0 | 0 | 78.1833 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 29.5308 | 3.8383 | 6.0591 | 20.6603 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
301 | EM KINGSBURG COGEN REPL CB 3RD DTT_KIN |  |  | Fresno | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 35 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.3704 | NA | 115 kV | 131 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5534708 | T.0004621 | EM: 3rd Party DTT | 9 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-12-07 | NA | 2027-12-13 | NA | NA | FALSE | NA | NA ¦ NA | 38.1088 | 39.308 | 1.8343 | 3.7484 | 1.4081 | 20.6603 | 0 | 0 | 39.308 | 0 | 0 | 0 | 38.1088 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 1.8343 | 3.7484 | 1.4081 | 20.6603 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
302 | EM KINGSBURG REPL CB112 3RD DTT_KING C |  |  | Fresno | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 35 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.3704 | NA | 115 kV | 131 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5534706 | T.0004621 | EM: 3rd Party DTT | 9 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-02-02 | NA | 2027-02-08 | NA | NA | FALSE | NA | NA ¦ NA | 87.8325 | 87.8325 | 27.0259 | 19.6673 | 7.3399 | 20.6603 | 0 | 0 | 41.8992 | 0 | 0 | 0 | 87.8325 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 27.0259 | 19.6673 | 7.34 | 20.6603 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
303 | EM COBURN REPL CB 52-92 3RD DTT_CAL PE |  |  | Monterey | Replace the existing RFL 6745 DTT (direct transfer trip) device 98TT-COB to Calpine King City with one new GARD 8000 at Coburn substation. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-04 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.435 | NA | 60 kV | 174 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5534725 | T.0004621 | EM: 3rd Party DTT | 9 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-02-02 | NA | 2027-02-22 | NA | NA | FALSE | NA | NA ¦ NA | 71.9245 | 71.9245 | 6.7724 | 23.2835 | 6.6647 | 20.6603 | 0 | 0 | 39.308 | 0 | 0 | 0 | 71.9245 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 6.7724 | 23.2835 | 6.6647 | 20.6603 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
304 | EM KING CITY REPL 3RD DTT_COBURN |  |  | King City, Monterey | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-03 | 32 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.68845 | NA | 60 kV | 131 | 3. Emergency Preparedness | NA | 4.0111 | Non-IGP | 5534726 | T.0004621 | EM: 3rd Party DTT | 9 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-02-02 | NA | 2027-02-22 | NA | NA | FALSE | NA | NA ¦ NA | 61.5725 | 61.5725 | 6.9812 | 22.4962 | 5.3474 | 20.6603 | 0.0969 | 0 | 24.833 | 0 | 0 | 0 | 61.5725 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2027 | 6.9812 | 22.4962 | 5.3474 | 20.6603 | 0.09689 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
305 | EM MENDOTA BIO REPL 3RD DTT_MENDOTA |  |  | Fresno | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-06 | 36 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.0936 | NA | 70 kV | 131 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5534705 | T.0004621 | EM: 3rd Party DTT | 9 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-10-01 | NA | 2026-10-14 | NA | NA | TRUE | NA | NA ¦ NA | 116.5651 | 419.2273 | 1.8608 | 54.2755 | 16.8883 | 34.2568 | 0 | 233.319 | 0 | 22.7557 | 0 | 0 | 116.5651 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 1.8608 | 54.2755 | 16.8883 | 34.2568 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
306 | EM MENDOTA REPL CB 42 3RD DTT_MENDOTA |  |  | Fresno | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-06 | 36 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.0936 | NA | 70 kV | 131 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5534704 | T.0004621 | EM: 3rd Party DTT | 9 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-12-10 | NA | 2026-12-23 | NA | NA | TRUE | NA | NA ¦ NA | 138.986 | 432.9304 | 31.6752 | 34.6731 | 12.1957 | 36.6555 | 0 | 254.6364 | 10.1766 | 0 | 0 | 0 | 138.986 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 ¦ 2027 | 31.6752 | 34.6731 | 12.1957 | 36.6555 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
307 | EM LIVE OAK SW REPL CB 172-182 3RD DTT |  |  | Oildale CDP, Kern | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-10 | 34 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.29953 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5534727 | T.0004621 | EM: 3rd Party DTT | 9 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-12-01 | 2020-12-16 | 2020-12-16 | NA | NA | FALSE | 172.9686 | NA ¦ NA | 172.9686 | 172.9686 | 37.0997 | 8.4058 | 3.6547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172.9686 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 37.0997 | 8.4058 | -30.939 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
308 | EM LIVE OAK COGEN REPL 3RD DTT_LIVE OA |  |  | Live Oak, Sutter | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-11 | 34 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.39793 | NA | 60 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | 4.0111 | Non-IGP | 5534703 | T.0004621 | EM: 3rd Party DTT | 9 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-19 | 2024-01-30 | 2024-01-19 | NA | NA | FALSE | 114.4449 | NA ¦ NA | 114.4449 | 114.4449 | 9.6119 | 2.0388 | 8.3362 | 1.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 114.4449 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 9.6119 | 2.0388 | 8.3362 | -9.5356 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
309 | WEEDPATCH SUB - NU INSTALL DTT |  |  | Kern | This project will establishthe necessary protection and metering to separate the Kern Canyon Powerhouse from PG&E ownership. In response to the changing energy landscape in California, combined with increasing costs associated with relicensing and aging generation infrastructure, PG&E launched its small hydro disposition program in 2016. The current strategy is focused on removing small uneconomic hydro assets from the portfolio to reduce operational risk and improve overall value of the generation provided to PG&E customers. Kern Canyon PH is one of the facilities in the generation deposition portfolio.. The implementation of this project is necessary to execute the safe transfer of ownership to the 3rd Party. | Substation - Protection Relay | New | NA | NA | Asset Condition | Relay Upgrades | NA | NA | 2026-02-11 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.2535 | NA | 70 kV | 124 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5791073 | T.0005987 | KERN PH DIVESTITURE | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-17 | 2020-12-31 | 2023-04-18 | Prioritization | NA | FALSE | 3500 | NA ¦ NA | 1508.8158 | 1508.8158 | 823.6164 | 391.2724 | 174.448 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 1508.8158 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 1471.23 | 0.05347 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
310 | KERN PP SUB - NU INSTALL DTT |  |  | Bakersfield, Kern | This project will establishthe necessary protection and metering to separate the Kern Canyon Powerhouse from PG&E ownership. In response to the changing energy landscape in California, combined with increasing costs associated with relicensing and aging generation infrastructure, PG&E launched its small hydro disposition program in 2016. The current strategy is focused on removing small uneconomic hydro assets from the portfolio to reduce operational risk and improve overall value of the generation provided to PG&E customers. Kern Canyon PH is one of the facilities in the generation deposition portfolio.. The implementation of this project is necessary to execute the safe transfer of ownership to the 3rd Party. | Substation - Protection Relay | New | NA | NA | Asset Condition | Relay Upgrades | NA | NA | 2026-03-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.7504 | NA | 70 kV | 124 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5791074 | T.0005987 | KERN PH DIVESTITURE | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-01 | 2020-12-31 | 2023-04-18 | Prioritization | NA | FALSE | 3500 | NA ¦ NA | 813.0128 | 813.0128 | 449.3244 | 195.716 | 67.6089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 813.0128 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 805.7463 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
311 | Emergency Replacement of Protective Equi |  |  | NA | Bucket for Emergency Replacement of Protective Equipment | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 ¦ 115 ¦ 70 ¦ 60 kV | 1013 | 5a.Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5512259 | NA | NA | NA | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 4700.6391 | 103748.3711 | 0 | 0 | 0 | 0 | 0 | 0.007 | 18337.926 | 19045.873 | 19781.151 | 20544.815 | 4700.6391 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
312 | METCALF: EM Repl Diff Cabinet Bus 2 Sec |  |  | Santa Clara | Emergency replacement of Metcalf 230kV Differential Cabinet Bus 2 Sect. E. This work supports System Protection’s concern that the differential cabinet could fail and potentially cause an unplanned sustained outage of Metcalf 230kV bus. This project will replace the 230kV Bus Section E outdoor differential cabinet at Metcalf. Replacement of this cabinet is complicated by the necessary construction sequence. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 28 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 230 kV | 1013 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5774779 | T.0002867 | METCALF 230KV DIFF CAB BUS 2E 74011033 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-07-22 | 2020-05-31 | 2020-07-29 | NA | NA | FALSE | 4326 | NA ¦ NA | 3057.4979 | 3057.4979 | 15.4833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3057.4979 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 14.5423 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
313 | DIXON: Repl CB 142 Relay |  |  | Dixon, Solano | Replace old electromechanical IRD and IRV relays with newer relays on Dixon CB 142. Polarizing potential is from low side of bank that is non-standard. With bank outage, we can lose line protection. Relays are obsolete (installed in 1987) | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-12 | 34 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.89932 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5521163 | T.0003200 | Dixon CB 142 Relay Replacment | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-06-23 | 2021-06-07 | 2021-03-26 | NA | NA | FALSE | 1332 | NA ¦ NA | 1313.4521 | 1313.4521 | 419.1149 | 2.3188 | 0.0232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1313.4521 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 377.2035 | 38.7398 | 0.02149 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
314 | EAGLE ROCK: Repl CB 112 Relay |  |  | Sonoma | The Geysers #3 – Eagle Rock is one of three 115kv lines that serves the Mendocino and Lake counties. It is a critical line that provides power flow from Cortina and Geysers units to maintain the voltage stability in this area. This line is 1.8 miles long that located over rough and hilly terrain in the Calpine facility. The protection is two SPD 11A line current differential and a backup SEL 121G relays. The communication path for the differential is a twisted pair of copper wires with isolating transformers. While the SPD11A differential relays are still testing good, the isolating transformers are failing. There are no spare parts available to replace the isolating transfomers, thus making the scheme useless. The Set B differential scheme is cutout for this reason. The remaining Set A differential and backup SEL 121G relays will provide line protection for the duration. Protection recommends replacing the entire scheme with new SMP SEL 411L and 451 relays for line protection and automatics control. This will be a non-integrated design. This proposal will correct the potential failure of the high speed protection scheme and maintain the service reliability in the Mendocino and Lake areas. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-02 | 34 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.8266 | NA | 115 kV | 131 | 3. Emergency Preparedness | NA | NA | NA | 5775579 | T.0003257 | Eagle Rock: Repl Relay 187-A6 & 187-B6 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-01-29 | 2021-04-22 | 2021-04-22 | NA | NA | FALSE | 3700 | NA ¦ NA | 3059.1588 | 3059.1588 | 753.9394 | 1904.4385 | 86.2671 | 1.6405 | 0 | 0 | 0 | 0 | 0 | 0 | 3059.1588 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 962.3325 | 1713.9948 | 77.0991 | 1.4761 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
315 | GEYSER 3: Repl Eagle R-Geyser 3 Relays |  |  | Sonoma | The scope of work for the this project: Remove the following relays: Geyser 3 & 4 115kV 121Z2/167N-1 – SEL 121G 187L-1 – GE SPD relay 187LB-1 – GE SPD relay Eagle Rock 115kV 121/167N-6 – SEL 121G 187A-6 – GE SPD relay 187B-6 – GE SPD relay 150-6 – GE PJC Relay Install new SMP SEL 411L and 451relays for line protection and automatics control.Since the line is 1.8 miles long, fiber (twoseparate paths) will be required | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-02 | 34 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.31702 | NA | 115 kV | 437 | 3. Emergency Preparedness | NA | NA | NA | 5776123 | T.0003269 | Geyser 3&4: Repl Relays 187L-1 187LB-1 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-01 | 2021-05-26 | 2021-05-26 | NA | NA | FALSE | 176 | NA ¦ NA | 2115.7421 | 2115.7421 | 633.9097 | 1003.2816 | 22.9955 | 1.8561 | 0 | 0 | 0 | 0 | 0 | 0 | 2115.7421 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 1049.3463 | 967.1231 | 22.1667 | -119.817 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
316 | CARIBOU: REPL CB 122 Relays |  |  | Plumas | This project will replace line relays at Caribou CB122 with SMP standard line and breaker package (two SEL 411L’s and two SEL 451’s). This terminal has electromechanical relays which is overcurrent only with no distance protection and do not provide adequate protection during PSPS. In addition, during two PSPS events in September 2020, System Protection had to de-energize the Butt Valley – Caribou 115kV line because of inadequate protection when the Caribou Island is established. | Substation - Protection Relay | Replace | NA | T.0007887 ¦ T.0010888 ¦ EX112246 ¦ T.0007507 | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-10 | 86 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ False | FALSE | Heat Wave |  | NA | 0.96252 | NA | 115 kV | 718 | 3. Emergency Preparedness | NA | 3.0021 | Non-IGP | 5777925 | T.0003628 | Butte-Caribou Relay Project | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-01-12 | NA | 2027-03-09 | NA | NA | TRUE | NA | NA ¦ NA | 871.9007 | 1100.635 | 228.8674 | 386.5681 | 89.7446 | 71.7886 | 68.9506 | 63.7538 | 175.6669 | 0 | 0 | 0 | 861.2143 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
317 | EM TEMBLOR CB 332 SEL |  |  | Kern | Per system requirement, replace obsolete 2 SEL 221 relays with an SEL 311C relays and replace RC reclosing relay with SEL-451 on Temblor CB 332 SEL. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.93942 | NA | 115 kV | 210 | NA | NA | NA | NA | 5528858 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-02-11 | NA | 2020-04-24 | NA | NA | FALSE | NA | NA ¦ NA | 131.1011 | 131.1011 | 0 | 16.0592 | 2.5626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131.1011 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 16.0592 | 2.5626 | -13.1101 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
318 | EM WATSONVILLE CB 42 SEL |  |  | Watsonville, Santa Cruz | Per system requirement, replace obsolete 1 SELPG10 relay on – EM: Watsonville CB 42 SEL with a SEL 311C relay. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-04 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.3384 | NA | 60 kV | 253 | NA | NA | NA | NA | 5528861 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-09-10 | NA | 2020-10-21 | NA | NA | FALSE | NA | NA ¦ NA | 90.3968 | 90.3968 | 3.8686 | 37.2113 | 6.5863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3968 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 3.8686 | 37.2113 | 6.5863 | -9.0391 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
319 | EM COBURN CB 12 AND CB 22 SEL |  |  | Monterey | Per system requirement, replace obsolete 2 SEL2PG10 relays on – EM: Coburn CB 12 and CB 22 SEL with an SEL 311C relay. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-04 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.435 | NA | 60 kV | 253 | NA | NA | 3.0021 | Non-IGP | 5528810 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-05 | NA | 2021-05-27 | NA | NA | FALSE | NA | NA ¦ NA | 96.2572 | 96.2572 | 66.1349 | 4.5433 | 3.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2572 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 66.1349 | 4.5433 | 3.568 | -9.6257 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
320 | EM BAY MEADOWS SUB CB152 & CB162 SEL |  |  | San Mateo, San Mateo | Per system requirement, replace obsolete 4 SEL- 167 relays on – EM: Bay Meadows Sub CB 152 & CB 162 SEL with an SEL 311C relay. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-11 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3929 | NA | 115 kV | 516 | 3. Emergency Preparedness | NA | NA | NA | 5528802 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-02-13 | NA | 2023-02-27 | NA | NA | FALSE | NA | NA ¦ NA | 324.712 | 324.712 | 1.1614 | 85.3379 | 208.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.712 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 1.1614 | 85.3379 | 208.0561 | -32.4712 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
321 | Bucket: One for One Relay 2018 |  |  | NA | Bucket to replace existing relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement or full panel replacement based upon need at each job site. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 797 | NA | NA | NA | NA | 5528799 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1096.9341 | 1096.9341 | 23.355 | -75.0549 | -6.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1096.9341 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 23.355 | -75.0549 | -6.2778 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
322 | EM MILLBRAE CB 112 SEL |  |  | Millbrae, San Mateo | Per system requirement, replace obsolete 1 SEL- 167 relay on – EM: Bay Meadows Sub CB 112 SEL with a SEL 311C relay. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-09 | 34 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.0501 | NA | 115 kV | 516 | NA | NA | 3.0021 | Non-IGP | 5528835 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-02 | NA | 2026-06-09 | NA | NA | TRUE | NA | NA ¦ NA | 189.7743 | 250.0966 | 1.7703 | 2.2762 | 22.0678 | 32.2543 | 116.4168 | 64.123 | 0 | 0 | 0 | 0 | 185.9736 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 1.7703 | 2.2762 | 22.0678 | 32.2543 | 116.4168 | 3.8007 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
323 | EM: RIO OSO CB472 SEL |  |  | Sutter | Replace the existing obsolete SEL PG10 relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-04 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.3219 | NA | 115 kV | NA | NA | NA | NA | NA | 5528846 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-12-04 | 2018-11-02 | 2018-12-31 | NA | NA | FALSE | 29 | NA ¦ NA | 38.1294 | 38.1294 | 0 | 6.9813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.1294 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 ¦ 2026 | 0 | 6.7582 | 0 | -2.5943 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
324 | EM RIVERBANK CB 132 AND CB 142 REL AND |  |  | Stanislaus | Riverbank substation is located in Stanislaus County and is a critical part of PG&E's 115kV transmission system. The existing line relays and CB 132 & CB 142 relays are are at the end of their useful life cycle time. Their performance and functionality are not as good as the latest digital relays, This project includes relaying upgrade for Bellota - Riverbank line, Bellota - Riverbank - Melones SW Sta line and breaker controls for HVCB 132 & 142. The existing line relays will be upgraded with the installation of redundant SEL-411L relays. The existing breaker controls for HVCB 132 & 142 will also be replaced with the installation of SEL-451 relays. The existing potential device on the line side of CB 142 will be replaced with the installation of CCVTs. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-10 | 25 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.3123 | NA | 115 kV | 516 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5528847 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-01 | 2019-12-31 | 2021-04-08 | Prioritization | NA | FALSE | 832 | NA ¦ NA | 1312.2724 | 1312.2724 | -14.3578 | 4.6467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.2724 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | -13.8247 | 4.4741 | -116.8446 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
325 | EM SYCAMORE CREEK CB 122 SEL |  |  | Chico, Butte | Per system requirement, replace obsolete 1 SEL121G relay on – EM: Sycamore Creek CB 122 SEL with a SEL 311C relay. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-11 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.5676 | NA | 115 kV | NA | NA | NA | NA | NA | 5528856 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-09-07 | 2021-09-07 | 2021-12-08 | NA | NA | FALSE | 74 | NA ¦ NA | 53.351 | 53.351 | 18.2246 | 19.1474 | 0.0949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.351 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 18.2243 | 18.2348 | -2.3781 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
326 | EM TRINITY CB 22 SEL |  |  | Weaverville CDP, Trinity | Per system requirement, replace obsolete 1 SELPG10 relay on – EM: Trinity CB 22 SEL with a SEL 311C relay | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | 17 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.3227 | NA | 60 kV | 253 | NA | NA | NA | NA | 5528859 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-11-18 | 2020-12-02 | 2021-12-08 | Prioritization | NA | FALSE | 166 | NA ¦ NA | 144.404 | 144.404 | 10.0593 | 25.1237 | 0.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144.404 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 10.0593 | 25.1237 | -18.8038 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
327 | EM BELLE HAVEN CB 162 AND CB 42 SEL |  |  | Menlo Park, San Mateo | Per system requirement, remove obsolete SEL- 121G relay on Belle Heaven Sub on Transformer No. 4 | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-11 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.4588 | NA | 60 kV | NA | NA | NA | NA | NA | 5528803 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-08 | 2022-08-09 | 2022-08-09 | NA | NA | FALSE | 56 | NA ¦ NA | 104.3751 | 104.3751 | 1.14 | 92.0131 | 0.6549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.3751 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1.14 | 92.0131 | 0.65491 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
328 | EM CARIBOU PH #2 DEVICE 621/621G-11 |  |  | Plumas | Install the emergency replacement of #2 DEVICE 621/62at CARIBOU PH, which failed on or around 04/11/2018. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-02 | 20 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.2068 | NA | 230 kV | 210 | NA | NA | NA | NA | 5528807 | T.0003721 | One to One Relay Projects | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-05-07 | 2019-05-23 | 2022-09-28 | Prioritization | NA | FALSE | 110 | NA ¦ NA | 89.1602 | 89.1602 | 1.3186 | 8.997 | 0.0949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1602 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1.3185 | 8.997 | -10.893 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
329 | Bucket: Repl SEL-2488 clocks antennas |  |  | NA | Bucket for replacement of SEL-2488 clocks antennas | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5533139 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 27.8635 | 27.8635 | -225.1298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.8635 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -225.1298 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
330 | EM FRESNO OP REPL SEL-2488 CLOCKS ANTE |  |  | Fresno, Fresno | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | NA | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.0247 | NA | NA | NA | NA | NA | NA | NA | 5783095 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-01 | NA | 2022-05-24 | NA | NA | FALSE | NA | NA ¦ NA | 108.5438 | 108.5438 | 1.1614 | 77.7595 | 20.8542 | 8.7687 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5438 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 78.0085 | 20.6117 | 8.9329 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
331 | EM SANTA ROSA REPL SEL-2488 CLOCKS ANT |  |  | Santa Rosa, Sonoma | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-02 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.91804 | NA | NA | NA | NA | NA | NA | NA | 5783114 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-18 | NA | 2022-08-19 | NA | NA | FALSE | NA | NA ¦ NA | 32.5268 | 32.5268 | 0.0024 | 23.7436 | 7.1733 | 1.5748 | 0 | 0 | 0 | 0 | 0 | 0 | 32.5268 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 23.7787 | 7.1733 | -1.664 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
332 | EM LOS BANOS REPL SEL-2488 CLOCKS ANTE |  |  | Merced | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | NA | NA | NA | NA | NA | NA | 5783084 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-03 | NA | 2022-10-07 | NA | NA | FALSE | NA | NA ¦ NA | 73.2607 | 73.2607 | 1.3233 | 31.4878 | 16.2301 | 24.2194 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2607 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 31.9858 | -0.73145 | 34.7428 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
333 | EM DIABLO CANYON REPL SEL-2488 CLOCKS |  |  | San Luis Obispo | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 14 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 35.6227 | NA | NA | NA | NA | NA | 3.0021 | Non-IGP | 5783094 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-11 | NA | 2022-10-14 | NA | NA | TRUE | NA | NA ¦ NA | 46.5078 | 63.0318 | 0.6892 | 25.5281 | 11.6167 | 7.5361 | 0.6806 | 16.5241 | 0 | 0 | 0 | 0 | 46.5078 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 25.8764 | 11.2647 | 7.233 | 0.65884 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
334 | EM METCALF REPL SEL-2488 CLOCKS ANTENN |  |  | Santa Clara | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 37.8815 | NA | NA | NA | NA | NA | 3.0021 | Non-IGP | 5783103 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-04 | NA | 2022-10-18 | NA | NA | TRUE | NA | NA ¦ NA | 35.6922 | 50.3994 | 1.1177 | 18.1536 | 14.5173 | 0.6614 | 0.7852 | 14.7072 | 0 | 0 | 0 | 0 | 35.6922 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 34.2457 | 0.66136 | 0.78517 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
335 | EM MOSS LANDING REPL SEL-2488 CLOCKS A |  |  | Monterey | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-10 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 41.3213 | NA | NA | NA | NA | NA | NA | NA | 5783105 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-14 | NA | 2022-10-19 | NA | NA | FALSE | NA | NA ¦ NA | 79.8276 | 79.8276 | 1.3731 | 23.1164 | 9.6686 | 41.8049 | 3.4076 | 0 | 0 | 0 | 0 | 0 | 79.8276 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 24.1628 | 9.3567 | 40.4799 | -2.0896 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
336 | EM PITTSBURG REPL SEL-2488 CLOCKS ANTE |  |  | Pittsburg, Contra Costa | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.72358 | NA | NA | NA | NA | NA | 3.0021 | Non-IGP | 5783108 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-27 | NA | 2022-10-27 | NA | NA | TRUE | NA | NA ¦ NA | 33.5269 | 48.8269 | 4.1095 | 13.4202 | 9.5799 | 0.9275 | 1.9789 | 18.8111 | 0 | 0 | 0 | 0 | 30.0158 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 17.5297 | 9.5799 | 0.92746 | 1.9789 | 3.5111 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
337 | EM MARTIN REPL SEL-2488 CLOCKS ANTENNAS |  |  | Brisbane, San Mateo | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-12 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 18.2105 | NA | NA | NA | NA | NA | 3.0021 | Non-IGP | 5783091 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-11-01 | NA | 2022-11-15 | NA | NA | TRUE | NA | NA ¦ NA | 40.6367 | 60.8257 | 0.1423 | 13.9516 | 11.1087 | 6.2663 | 5.538 | 23.8188 | 0 | 0 | 0 | 0 | 37.0069 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 14.0939 | 11.1087 | 6.2663 | 5.538 | 3.6298 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
338 | EM MCCALL REPL SEL-2488 CLOCKS ANTENNA |  |  | Fresno | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 16.2494 | NA | NA | NA | NA | NA | NA | NA | 5783099 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-01 | 2022-05-26 | 2022-05-24 | NA | NA | FALSE | 60.0045 | NA ¦ NA | 60.0045 | 60.0045 | 0.3106 | 14.8365 | 34.7162 | 10.1412 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0045 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 14.4611 | 33.1381 | 6.4103 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
339 | EM VACA DIXON REPL SEL-2488 CLOCKS ANT |  |  | Solano | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-25 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 42.1076 | NA | NA | NA | NA | NA | NA | NA | 5783087 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-22 | 2022-09-26 | 2022-08-23 | NA | NA | FALSE | 47.3619 | NA ¦ NA | 47.3619 | 47.3619 | 1.4539 | 24.6377 | 21.2703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.3619 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 26.0916 | 19.5741 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
340 | EM TABLE MOUNTAIN REPL SEL-2488 CLOCKS |  |  | Butte | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-20 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 47.516 | NA | NA | NA | NA | NA | NA | NA | 5783116 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-22 | 2022-09-26 | 2022-08-23 | NA | NA | FALSE | 72.8267 | NA ¦ NA | 72.8267 | 72.8267 | 27.0885 | 24.9228 | 20.8154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.8267 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 52.0113 | 20.2815 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
341 | EM IGNACIO REPL SEL-2488 CLOCKS ANTENN |  |  | Novato, Marin | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 11.9486 | NA | NA | NA | NA | NA | NA | NA | 5783111 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-19 | 2022-08-25 | 2022-08-25 | NA | NA | FALSE | 47.9539 | NA ¦ NA | 47.9539 | 47.9539 | 0.0329 | 19.8293 | 27.6347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.9539 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 20.3193 | 27.6347 | -4.7752 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
342 | EM FULTON REPL SEL-2488 CLOCKS ANTENNAS |  |  | Fulton CDP, Sonoma | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-11 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.4076 | NA | NA | NA | NA | NA | NA | NA | 5783115 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-19 | 2022-08-25 | 2022-08-25 | NA | NA | FALSE | 58.8995 | NA ¦ NA | 58.8995 | 58.8995 | 0.28 | 19.4554 | 37.1034 | 0.1476 | 0 | 0 | 0 | 0 | 0 | 0 | 58.8995 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 21.6485 | 37.1034 | -5.6864 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
343 | EM ROUND MOUNTAIN REPL SEL-2488 CLOCKS |  |  | Round Mountain CDP, Shasta | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-09 | 14 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 29.1389 | NA | NA | NA | NA | NA | NA | NA | 5783112 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-02 | 2022-09-26 | 2022-09-01 | NA | NA | FALSE | 26.2065 | NA ¦ NA | 26.2065 | 26.2065 | 1.1433 | 22.3019 | 2.7613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.2065 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 23.4452 | 2.2112 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
344 | EM COTTONWOOD REPL SEL-2488 CLOCKS ANT |  |  | Cottonwood CDP, Shasta | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 26.1945 | NA | NA | NA | NA | NA | NA | NA | 5783113 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-09 | 2022-09-26 | 2022-09-01 | NA | NA | FALSE | 80.9903 | NA ¦ NA | 80.9903 | 80.9903 | 43.0684 | 19.1105 | 18.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9903 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 62.1788 | 18.4912 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
345 | EM GATES REPL SEL-2488 CLOCKS ANTENNAS |  |  | Fresno | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-12 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | NA | NA | NA | NA | NA | NA | 5783096 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-26 | 2022-10-10 | 2022-10-04 | NA | NA | FALSE | 82.0667 | NA ¦ NA | 82.0667 | 82.0667 | 20.3971 | 19.9243 | 33.1058 | 8.6395 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0667 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 39.4786 | 32.3861 | 2.1509 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
346 | EM GREGG REPL SEL-2488 CLOCKS ANTENNAS |  |  | Madera | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-10 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.266 | NA | NA | NA | NA | NA | NA | NA | 5783097 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-05 | 2022-10-10 | 2022-10-10 | NA | NA | FALSE | 101.4552 | NA ¦ NA | 101.4552 | 101.4552 | 50.0056 | 20.0137 | 24.4335 | 7.0024 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4552 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 69.1406 | 24.112 | -1.6193 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
347 | EM MIDWAY REPL SEL-2488 CLOCKS ANTENNA |  |  | Buttonwillow CDP, Kern | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | NA | NA | NA | NA | NA | NA | 5783100 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-30 | 2022-10-10 | 2022-10-10 | NA | NA | FALSE | 104.0389 | NA ¦ NA | 104.0389 | 104.0389 | 30.3325 | 32.3079 | 30.6192 | 10.7793 | 0 | 0 | 0 | 0 | 0 | 0 | 104.0389 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 61.7673 | 30.1754 | 1.9317 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
348 | EM BELLOTTA REPL SEL-2488 CLOCKS ANTEN |  |  | San Joaquin | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-14 | 15 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | NA | NA | NA | NA | NA | NA | 5783086 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-04 | 2022-10-13 | 2022-10-12 | NA | NA | FALSE | 56.5384 | NA ¦ NA | 56.5384 | 56.5384 | 0 | 28.724 | 27.8144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.5384 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 28.724 | 27.8144 | -5.6038 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
349 | EM SAN MATEO REPL SEL-2488 CLOCKS ANTE |  |  | San Mateo, San Mateo | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-17 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 17.354 | NA | NA | NA | NA | NA | NA | NA | 5783109 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-11 | 2022-10-12 | 2022-10-12 | NA | NA | FALSE | 54.7997 | NA ¦ NA | 54.7997 | 54.7997 | 0.1423 | 18.9634 | 26.8099 | 8.8842 | 0 | 0 | 0 | 0 | 0 | 0 | 54.7997 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 19.1056 | 26.8099 | 3.422 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
350 | EM SALINAS REPL SEL-2488 CLOCKS ANTENN |  |  | Salinas, Monterey | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 7.4966 | NA | NA | NA | NA | NA | NA | NA | 5783106 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-17 | 2022-12-14 | 2022-10-21 | NA | NA | FALSE | 58.5763 | NA ¦ NA | 58.5763 | 58.5763 | 0.0815 | 25.9494 | 13.8826 | 18.2056 | 0 | 0 | 0 | 0 | 0 | 0 | 58.5763 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 25.6796 | 13.4488 | 13.652 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
351 | EM MONTA VISTA REPL SEL-2488 CLOCKS ANT |  |  | Cupertino, Santa Clara | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 15.8314 | NA | NA | NA | NA | NA | NA | NA | 5783104 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-04 | 2022-10-27 | 2022-10-26 | NA | NA | FALSE | 77.4438 | NA ¦ NA | 77.4438 | 77.4438 | 26.3392 | 18.7273 | 27.0118 | 4.9085 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4438 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 45.5235 | 27.0118 | 4.9085 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
352 | EM CINNABAR REPL SEL-2488 CLOCKS ANTEN |  |  | NA | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | NA | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5783102 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-24 | 2022-12-14 | 2022-10-28 | NA | NA | FALSE | 107.3722 | NA ¦ NA | 107.3722 | 107.3722 | 21.3838 | 65.0089 | 18.6524 | 1.1324 | 0 | 0 | 0 | 0 | 0 | 0 | 107.3722 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 86.6857 | 18.4519 | 1.1202 | -9.2508 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
353 | EM EAST BAY COMM REPL SEL-2488 CLOCKS |  |  | San Francisco, San Francisco | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | NA | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.2172 | NA | NA | NA | NA | NA | NA | NA | 5783089 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-24 | 2022-11-15 | 2022-11-01 | NA | NA | FALSE | 39.6515 | NA ¦ NA | 39.6515 | 39.6515 | 0.272 | 24.9226 | 13.9998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.6515 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 25.6517 | 13.9998 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
354 | EM NEWARK REPL SEL-2488 CLOCKS ANTENNA |  |  | Fremont, Alameda | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 27.7611 | NA | NA | NA | NA | NA | NA | NA | 5783107 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-31 | 2022-11-15 | 2022-11-01 | NA | NA | FALSE | 92.4711 | NA ¦ NA | 92.4711 | 92.4711 | 29.4325 | 15.6287 | 33.6942 | 13.7157 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4711 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 45.0611 | 33.6942 | 4.6938 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
355 | EM TESLA REPL SEL-2488 CLOCKS ANTENNAS |  |  | Alameda | Replace existing SEL 2488 relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | NA | NA | NA | NA | NA | NA | 5783085 | T.0004407 | Repl SEL-2488 Clock Antennas | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-11-01 | 2022-11-15 | 2022-11-15 | NA | NA | FALSE | 40.0726 | NA ¦ NA | 40.0726 | 40.0726 | 0 | 11.1562 | 17.0537 | 11.8627 | 0 | 0 | 0 | 0 | 0 | 0 | 40.0726 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 11.1562 | 17.0537 | 7.8858 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
356 | Bucket: Order SEL T400L Devices |  |  | NA | Bucket for ordering SEL T400L Devices | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 516 | NA | NA | NA | NA | 5533799 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 185.627 | 185.627 | -344.9561 | -3.9405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185.627 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | -344.9561 | -3.9405 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
357 | Tesla: Install CB 132 SEL-T400L Relay |  |  | Alameda | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | 115 kV | NA | NA | NA | NA | NA | 5535179 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-12-03 | NA | 2019-12-20 | NA | NA | FALSE | NA | NA ¦ NA | 19.8319 | 19.8319 | 6.702 | 0.1774 | 1.3865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.8319 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 6.702 | 0.17739 | 1.3865 | -1.9832 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
358 | Newark: Install CB 230 SEL-T400L Relay |  |  | Fremont, Alameda | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 27.7611 | NA | 230 kV | NA | NA | NA | NA | NA | 5535181 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-12-03 | NA | 2019-12-20 | NA | NA | FALSE | NA | NA ¦ NA | 99.1152 | 99.1152 | 62.5397 | 0.0957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1152 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 ¦ 2026 | 62.5397 | 0.09569 | 0 | -9.9112 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
359 | Pittsburg: Install CB532 SEL-T400L Relay |  |  | Pittsburg, Contra Costa | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.72358 | NA | 230 kV | NA | NA | NA | NA | NA | 5534567 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-12-17 | NA | 2020-06-01 | NA | NA | FALSE | NA | NA ¦ NA | 120.8607 | 120.8607 | 61.7671 | 1.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.8607 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 ¦ 2026 | 61.7671 | 1.5093 | 0 | -12.086 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
360 | Los Est: Install CB352-452 SEL-T400L Rly |  |  | San Jose, Santa Clara | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-09 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.1703 | NA | 230 kV | NA | NA | NA | NA | NA | 5534573 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-12-16 | NA | 2020-06-01 | NA | NA | FALSE | NA | NA ¦ NA | 116.4959 | 116.4959 | 45.0701 | 0.4809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.4959 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 ¦ 2026 | 45.0701 | 0.48086 | 0 | -11.6495 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
361 | Gregg: Install CB 332-432 SEL-T400L Rela |  |  | Madera | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-10 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.266 | NA | 230 kV | NA | NA | NA | NA | NA | 5534558 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-04-13 | 2020-12-10 | 2020-06-08 | NA | NA | FALSE | 86.7901 | NA ¦ NA | 86.7901 | 86.7901 | 40.2362 | 1.2517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7901 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 36.9015 | 1.2029 | -13.9745 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
362 | Helms: Install CB260-290 SEL-T400L Relay |  |  | Fresno | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-10 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 6.7555 | NA | 230 kV | NA | NA | NA | NA | NA | 5534559 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-04-13 | 2020-12-10 | 2020-06-08 | NA | NA | FALSE | 132.876 | NA ¦ NA | 132.876 | 132.876 | 81.8336 | 2.2219 | 0.5969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.876 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 77.3513 | 2.1454 | -21.4195 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
363 | EM TEMBLOR INSTALL CB 332 SEL-T400L RE |  |  | Kern | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.93942 | NA | 115 kV | NA | NA | NA | NA | NA | 5534579 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-04-13 | 2020-12-10 | 2020-06-10 | NA | NA | FALSE | 765.4943 | NA ¦ NA | 765.4943 | 765.4943 | 681.9417 | 1.8928 | 0.3528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765.4943 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 661.5644 | 1.8422 | 0.34339 | -56.1121 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
364 | Helms: Install CB250-270 SEL-T400L Relay |  |  | Fresno | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-10 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 6.7555 | NA | 230 kV | NA | NA | NA | NA | NA | 5534557 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-06-08 | 2020-12-10 | 2020-12-10 | NA | NA | FALSE | 59.4108 | NA ¦ NA | 59.4108 | 59.4108 | 5.1447 | 1.3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.4108 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1.772 | 1.2259 | -8.434 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
365 | Gregg: Install CB 332-342 SEL-T400L Rela |  |  | Madera | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-10 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.266 | NA | 230 kV | NA | NA | NA | NA | NA | 5534560 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-05-26 | 2020-12-10 | 2020-12-10 | NA | NA | FALSE | 83.1013 | NA ¦ NA | 83.1013 | 83.1013 | 17.4516 | 0.2907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1013 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 14.2376 | 0.27942 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
366 | EM HUMBOLDT INSTALL CB 172 SEL-T400L R |  |  | Humboldt | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-02 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.569 | NA | 115 kV | NA | NA | NA | NA | NA | 5534546 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-01 | 2022-01-05 | 2021-12-22 | NA | NA | FALSE | 184.9184 | NA ¦ NA | 184.9184 | 184.9184 | 80.6676 | 35.0037 | 19.1444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184.9184 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 80.6676 | 35.0037 | 0.6525 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
367 | EM BRIDGEVILLE INSTALL CB 1012-1022 SE |  |  | Humboldt | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 12 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.1134 | NA | 115 kV | NA | NA | NA | NA | NA | 5534548 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-21 | 2022-01-05 | 2021-12-22 | NA | NA | FALSE | 180.79 | NA ¦ NA | 180.79 | 180.79 | 82.3531 | 34.1867 | 9.7459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.79 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 82.3531 | 34.1867 | -8.3332 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
368 | EM COTTONWOOD INSTALL CB 142 SEL-T400L |  |  | Cottonwood CDP, Shasta | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 26.1945 | NA | 115 kV | NA | NA | NA | NA | NA | 5534549 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-15 | 2021-12-29 | 2021-12-22 | NA | NA | FALSE | 115.8861 | NA ¦ NA | 115.8861 | 115.8861 | 30.2525 | 16.3457 | 11.8499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.8861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 30.2525 | 16.3457 | 11.85 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
369 | EM TRINITY INSTALL CB 1012-1032 SEL-T4 |  |  | Weaverville CDP, Trinity | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3227 | NA | 115 kV | NA | NA | NA | NA | NA | 5535328 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-29 | 2021-12-29 | 2021-12-22 | NA | NA | FALSE | 147.191 | NA ¦ NA | 147.191 | 147.191 | 42.4526 | 47.4629 | 11.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.191 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 42.4526 | 47.4629 | -3.6718 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
370 | EM COTTONWOOD INSTALL CB 132 SEL-T400L |  |  | Cottonwood CDP, Shasta | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 26.1945 | NA | 115 kV | NA | NA | NA | NA | NA | 5535329 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-25 | 2021-12-29 | 2021-12-22 | NA | NA | FALSE | 111.654 | NA ¦ NA | 111.654 | 111.654 | 55.4291 | 22.3423 | 7.2444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.654 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 55.4291 | 22.3423 | -3.921 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
371 | EM TRINITY INSTALL CB 1012-1022 SEL-T4 |  |  | Weaverville CDP, Trinity | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3227 | NA | 115 kV | NA | NA | NA | NA | NA | 5534547 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-09-17 | 2021-12-29 | 2021-12-30 | NA | NA | FALSE | 153.0952 | NA ¦ NA | 153.0952 | 153.0952 | 68.6865 | 15.8403 | 13.4515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.0952 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 68.6865 | 15.8403 | -1.8581 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
372 | EM VLY SP INSTALL CB2112-2122 SEL-T400L |  |  | Calaveras | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2025-10-03 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.8736 | NA | 230 kV | NA | NA | NA | NA | NA | 5534581 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-08-03 | 2022-05-26 | 2022-05-26 | NA | NA | FALSE | 379.7003 | NA ¦ NA | 418.6467 | 418.6467 | 43.6357 | 47.7147 | 107.1399 | 91.4245 | 0 | 0 | 0 | 0 | 0 | 0 | 418.6467 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 43.6357 | 47.7147 | 74.4177 | 82.2819 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
373 | EM BELLOTA INSTALL CB 260 SEL-T400L RE |  |  | San Joaquin | This project is to install SEL-T400L relaying System on Various Lines in the PG&E territory (lines out lined below). The SEL-T400L will be used for low energy event monitoring which will proactively identify problems on the line before fault conditions occur (no tripping presently). | Substation - Protection Relay | New | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-14 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 115 kV | NA | NA | NA | NA | NA | 5534582 | T.0004473 | EM: Bucket: Order Sel T400L Devices | 28 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-08-03 | 2022-05-26 | 2022-05-26 | NA | NA | FALSE | 121.4806 | NA ¦ NA | 125.101 | 125.101 | 34.39 | 13.5098 | 30.6342 | 22.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 125.101 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 34.39 | 13.5098 | 20.3574 | 20.0995 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
374 | BUCKET: ONE FOR ONE RELAY 2019 |  |  | NA | Bucket to replace existing relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement or full panel replacement based upon need at each job site. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5533911 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 799.8367 | 799.8367 | -7568.9255 | -594.9058 | 250.9974 | -250.9644 | 300.971 | 87.5403 | 0 | 0 | 0 | 0 | 712.2964 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | -7568.9256 | -594.9058 | 250.9973 | -250.9644 | 300.971 | 87.5403 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
375 | EM CURTIS REPL CB152 SEL RELAYS |  |  | East Sonora CDP, Tuolumne | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 30 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.9153 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534814 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2024-01-03 | NA | 2026-05-27 | NA | NA | TRUE | NA | NA ¦ NA | 601.1234 | 658.325 | 0.8075 | 23.9623 | 391.4309 | 147.2542 | 37.6685 | 57.2016 | 0 | 0 | 0 | 0 | 601.1234 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0.8075 | 23.9623 | 391.4309 | 90.9087 | 33.9017 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
376 | EM: MORAGA: REPL SEL RELAY FPR |  |  | Orinda, Contra Costa | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 24 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 15.8714 | NA | 230 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534850 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-12-28 | NA | 2028-02-29 | NA | NA | FALSE | NA | NA ¦ NA | 62.8169 | 62.8169 | 0.0214 | 38.8482 | 19.8336 | 2.4168 | 0 | 0 | 0 | 0 | 0 | 0 | 62.8169 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2028 | 0.02085 | 37.8081 | 19.3026 | 2.3521 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
377 | EM: ALTO:REPL SEL RELAYS FPR |  |  | Mill Valley, Marin | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-11 | 32 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.89452 | NA | 60 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534800 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-01-13 | NA | 2028-03-15 | NA | NA | FALSE | NA | NA ¦ NA | 32.4918 | 32.4918 | 0.8075 | 6.6752 | 8.9693 | 15.8501 | -0.9909 | 0 | 0 | 0 | 0 | 0 | 32.4918 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2028 | 0 | 0 | 0 | 33.4827 | -0.99094 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
378 | EM: MELONES: REPL SEL RELAYS FPR |  |  | Tuolumne | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | 28 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.85823 | NA | 115 kV | NA | NA | NA | 4.0121 | Non-IGP | 5534846 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-22 | NA | 2026-07-27 | NA | NA | TRUE | NA | NA ¦ NA | 434.3166 | 1427.1437 | 0.8075 | 38.4021 | 20.6647 | 183.2831 | 165.2049 | 1018.7813 | 0 | 0 | 0 | 0 | 408.3624 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 58.7229 | 179.7585 | 162.0279 | 25.4551 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
379 | EM: MERCED: REPL CB122 SEL RELAY FPR |  |  | Merced | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-03 | 29 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7481 | NA | 115 kV | NA | NA | NA | 4.0121 | Non-IGP | 5534848 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-01 | NA | 2026-08-11 | NA | NA | TRUE | NA | NA ¦ NA | 367.8094 | 752.9701 | 0 | 11.9956 | 53.6071 | 178.4555 | 101.8681 | 407.0436 | 0 | 0 | 0 | 0 | 345.9264 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 65.6027 | 178.4555 | 101.8681 | 21.883 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
380 | EM BAHIA REPL SEL RELAY |  |  | Benicia, Solano | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-02 | 32 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.2232 | NA | 230 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534802 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-11-02 | NA | 2026-11-06 | NA | NA | TRUE | NA | NA ¦ NA | 151.3658 | 171.7138 | 0.3019 | 6.9909 | 91.0242 | 43.7983 | 8.7915 | 20.348 | 0 | 0 | 0 | 0 | 151.3658 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 142.5742 | 8.7915 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
381 | EM APPLIED MATERIAL REPL SEL RELAYS |  |  | Sunnyvale, Santa Clara | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-06 | 28 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.0337 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5537765 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-10-29 | NA | 2026-11-13 | NA | NA | FALSE | NA | NA ¦ NA | 25.8162 | 25.8162 | 1.493 | 5.5242 | 10.4416 | 9.3484 | -0.9909 | 0 | 0 | 0 | 0 | 0 | 25.8162 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 25.8162 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
382 | EM PUEBLO REPL CB152 SEL RELAYS |  |  | Napa | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-02 | 27 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.4799 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534860 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-09-13 | NA | 2027-11-10 | NA | NA | TRUE | NA | NA ¦ NA | 28.3508 | 28.3508 | 0 | 7.0492 | 11.4165 | 9.8851 | 0 | 0 | 0 | 0 | 0 | 0 | 28.3508 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2027 | 0 | 0 | 0 | 28.3508 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
383 | EM LOCKEFORD REPL SEL RELAYS |  |  | Lockeford CDP, San Joaquin | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 29 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.2719 | NA | 115 ¦ 60 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534838 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-01-05 | NA | 2021-02-26 | NA | NA | TRUE | NA | NA ¦ NA | 205.562 | 229.2085 | 26.7946 | 12.405 | 6.2553 | 1.2081 | 0 | 23.6465 | 0 | 0 | 0 | 0 | 205.562 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 26.7946 | 12.405 | 6.2553 | 1.2081 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
384 | Weber: EM Repl SEL Relay |  |  | San Joaquin | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 25 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 6.1366 | NA | 60 kV | NA | NA | NA | NA | Non-IGP | 5534874 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-05 | NA | 2021-04-22 | NA | NA | FALSE | NA | NA ¦ NA | 105.3202 | 105.3202 | 5.0594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3202 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 5.0594 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
385 | EM EIGHT MILE CB 222/232,232/242,242/25 |  |  | San Joaquin | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | 23 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.9554 | NA | 230 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534819 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-04-21 | NA | 2021-12-03 | NA | NA | TRUE | NA | NA ¦ NA | 57.3908 | 68.3919 | 12.9593 | 11.6289 | 4.4933 | 0.4739 | 4.9967 | 11.0011 | 0 | 0 | 0 | 0 | 57.3908 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 35.798 | 11.6289 | 4.4933 | 0.47388 | 4.9967 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
386 | EM CORCORAN REPL SEL RELAYS |  |  | Kings | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 28 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.8529 | NA | 115 kV | NA | NA | NA | NA | NA | 5534812 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-25 | NA | 2023-02-03 | NA | NA | FALSE | NA | NA ¦ NA | 220.5387 | 220.5387 | 0.8075 | 123.2597 | 58.2133 | 32.7986 | 5.4595 | 0 | 0 | 0 | 0 | 0 | 220.5387 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 123.2459 | 57.8279 | 32.5814 | -15.1705 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
387 | EM SONOMA REPL SEL RELAYS |  |  | Sonoma, Sonoma | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-03 | 24 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.5781 | NA | 115 kV | NA | NA | NA | NA | NA | 5534867 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-03-09 | NA | 2023-04-04 | NA | NA | FALSE | NA | NA ¦ NA | 152.3546 | 152.3546 | 0 | 57.8268 | 92.0546 | 2.4732 | 0 | 0 | 0 | 0 | 0 | 0 | 152.3546 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 57.8268 | 92.0546 | -12.7623 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
388 | EM POTTER VALLEY PH REPL SEL RELAY |  |  | Mendocino | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-04 | 30 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.45584 | NA | 60 kV | NA | NA | NA | NA | NA | 5534859 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-05-04 | NA | 2023-05-18 | NA | NA | FALSE | NA | NA ¦ NA | 211.6478 | 211.6478 | 0 | 65.7632 | 145.8846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211.6478 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 65.7632 | 123.0494 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
389 | EM MENDOCINO REPL SEL RELAYS |  |  | Mendocino | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-12 | 26 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.7328 | NA | 115 ¦ 60 kV | NA | NA | NA | NA | NA | 5534847 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-05-31 | NA | 2023-06-01 | NA | NA | FALSE | NA | NA ¦ NA | 157.9159 | 157.9159 | 0 | 67.5217 | 90.3942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157.9159 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 63.6964 | 85.273 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
390 | EM WILLTS REPL SEL RELAY |  |  | Mendocino | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-03 | 27 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.88868 | NA | 60 kV | NA | NA | NA | NA | NA | 5534876 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-07-12 | NA | 2023-08-01 | NA | NA | FALSE | NA | NA ¦ NA | 104.2564 | 104.2564 | 0 | 35.8188 | 61.6022 | 6.8354 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2564 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 87.679 | 6.1519 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
391 | EM KERCKHOFF #2 PH REPL SEL RELAYS |  |  | Fresno | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-03 | 30 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.75506 | NA | 115 kV | NA | NA | NA | NA | NA | 5534832 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-09-12 | NA | 2023-09-13 | NA | NA | FALSE | NA | NA ¦ NA | 169.7154 | 169.7154 | 29.7089 | 38.5389 | 44.3173 | 57.1503 | 0 | 0 | 0 | 0 | 0 | 0 | 169.7154 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 29.7089 | 38.5389 | 44.3173 | 40.1788 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
392 | EM GOLDHILL REPL SEL RELAYS |  |  | Folsom, Sacramento | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 12.8702 | NA | 115 ¦ 60 kV | NA | NA | NA | NA | NA | 5534824 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-10-26 | NA | 2023-10-27 | NA | NA | FALSE | NA | NA ¦ NA | 142.3217 | 142.3217 | 0.8075 | 37.0176 | 85.1912 | 19.3053 | 0 | 0 | 0 | 0 | 0 | 0 | 142.3217 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 123.0164 | 19.3053 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
393 | EM MARTELL REPL CB22 SEL RELAYS |  |  | Martell CDP, Amador | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-09 | 27 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.28962 | NA | 60 kV | NA | NA | NA | NA | NA | 5534844 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-12-01 | NA | 2023-12-22 | NA | NA | FALSE | NA | NA ¦ NA | 691.4919 | 691.4919 | 2.8105 | 152.0742 | 461.5093 | 71.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 691.4919 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 158.1024 | 461.5093 | 2.731 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
394 | EM ELK REPL CB22 SEL RELAYS |  |  | Mendocino | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-12 | 23 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.0338 | NA | 60 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534820 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-02-20 | NA | 2024-02-24 | NA | NA | FALSE | NA | NA ¦ NA | 935.9949 | 935.9949 | 42.1743 | 58.9364 | 650.5251 | 184.3591 | 0 | 0 | 0 | 0 | 0 | 0 | 935.9949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 50.5557 | 326.1059 | 465.7338 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
395 | EM SANTA ROSA REPL CB162 SEL RELAYS |  |  | Santa Rosa, Sonoma | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-02 | 25 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.91804 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534863 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-12-01 | NA | 2025-12-16 | NA | NA | TRUE | NA | NA ¦ NA | 67.7599 | 67.7599 | 0 | 4.6538 | 27.2421 | 16.9918 | 15.0715 | 3.8007 | 0 | 0 | 0 | 0 | 63.9592 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 48.8877 | 15.0715 | 3.8007 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
396 | EM EAGLE ROCK REPL CB72 SEL RELAYS |  |  | Sonoma | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-02 | 23 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.8266 | NA | 60 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534818 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-11-03 | NA | 2025-12-21 | NA | NA | TRUE | NA | NA ¦ NA | 1393.0191 | 1394.2402 | 2.8188 | 5.0039 | 53.0221 | 519.8911 | 792.2632 | 21.2409 | 0 | 0 | 0 | 0 | 1372.9993 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 60.8449 | 519.8911 | 792.2632 | 20.0198 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
397 | EM COALINGA #2 REPL CB32 SEL RELAY |  |  | Fresno | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-16 | 26 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.5937 | NA | 70 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534809 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2026-02-13 | NA | 2026-03-04 | NA | NA | TRUE | NA | NA ¦ NA | 126.3314 | 141.3314 | 1.0283 | 34.9963 | 11.1899 | 47.6362 | 20.0553 | 26.4254 | 0 | 0 | 0 | 0 | 114.906 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 94.8507 | 20.0553 | 11.4254 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
398 | Britton: EM Repl SEL Relays |  |  | Sunnyvale, Santa Clara | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 28 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.4779 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534806 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-11-25 | 2024-12-05 | 2026-12-07 | Prioritization | NA | FALSE | 88 | NA ¦ NA | 33.4757 | 33.4757 | 1.9639 | 10.5729 | 8.0165 | 12.7687 | 0 | 0 | 0 | 0 | 0 | 0 | 33.4757 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 1.904 | 10.2501 | 7.7718 | 12.3789 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
399 | Manteca: EM Repl SEL Relays |  |  | Manteca, San Joaquin | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-14 | 29 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.8539 | NA | 115 ¦ 60 kV | NA | NA | NA | NA | NA | 5534843 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-07-29 | 2020-12-10 | 2020-09-24 | NA | NA | FALSE | 89.3053 | NA ¦ NA | 89.3053 | 89.3053 | 22.215 | 2.3074 | 24.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3053 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 16.8932 | 2.1094 | 12.6528 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
400 | EM HAMMER REPL CB32 SEL RELAYS |  |  | Stockton, San Joaquin | Per system requirement, replace obsolete 1 SEL-221 and 1 SEL-321 relays on Hammer CB 32 SEL with SEL 311C relays. Indoor Work: The 1 SEL-221 and 1 SEL-321 relays are to be replaced on a one for one “like for like” basis. No engineering will be provided. PG&E Test technicians are to replace the relays and provide markups (red/green) changes to be submitted as as-builts. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | 27 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.8348 | NA | 60 kV | NA | NA | NA | NA | NA | 5534827 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-07 | 2020-10-20 | 2020-10-20 | NA | NA | FALSE | 89 | NA ¦ NA | 84.3384 | 84.3384 | 7.182 | 33.9733 | 13.0426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3384 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 37.3225 | 33.9733 | -3.8251 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
401 | EM STAGG REPL SEL RELAY |  |  | Stockton, San Joaquin | Emergency replacement of EM:SEL RELAY at STAGG SUB, which failed on or around 10/06/2020. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 29 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.5909 | NA | 230 kV | NA | NA | NA | NA | NA | 5534868 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-23 | 2020-10-30 | 2020-10-30 | NA | NA | FALSE | 58 | NA ¦ NA | 53.0624 | 53.0624 | 2.6883 | 18.1 | 6.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.0624 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 28.8177 | 18.1 | 6.1447 | -5.3062 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
402 | EM SEMITROPIC REPL SEL RELAY |  |  | Kern | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-12 | 24 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.2701 | NA | 115 kV | NA | NA | NA | NA | NA | 5534864 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-01 | 2021-04-16 | 2021-03-26 | NA | NA | FALSE | 117.7585 | NA ¦ NA | 117.7585 | 117.7585 | 71.7545 | 20.1407 | 0.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.7585 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 97.3092 | 20.1407 | -12.2624 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
403 | Louise: EM Repl CB82 SEL Relays |  |  | Lathrop, San Joaquin | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 28 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.62417 | NA | 60 kV | NA | NA | NA | NA | NA | 5534841 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-13 | 2021-04-22 | 2021-04-22 | NA | NA | FALSE | 62.5479 | NA ¦ NA | 62.5479 | 62.5479 | 19.8687 | 0.9798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.5479 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 61.5681 | 0.97977 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
404 | EM SLO REPL SEL RELAYS |  |  | San Luis Obispo | Emergency replacement of EMSLOSEL RELAYS at SAN LUIS OBISPO SUB, which failed on or around 10/13/2020. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-10 | 28 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.8969 | NA | 115 kV | NA | NA | NA | NA | NA | 5534865 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-02-26 | 2021-02-26 | 2021-05-20 | NA | NA | FALSE | 243 | NA ¦ NA | 237.6414 | 237.6414 | 160.48 | 30.7623 | 37.7996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237.6414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 169.0795 | 24.3945 | 20.4033 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
405 | EM HERDON REPL BK2 SEL RELAY |  |  | Fresno, Fresno | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-12 | 26 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.3414 | NA | 230 kV | NA | NA | NA | NA | NA | 5534828 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-13 | 2022-01-05 | 2021-12-17 | NA | NA | FALSE | 113.4112 | NA ¦ NA | 113.4112 | 113.4112 | 77.0409 | 34.96 | 1.4103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.4112 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 77.0409 | 34.96 | -5.9078 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
406 | EM BORDEN REPL SEL RELAYS |  |  | Madera | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-16 | 24 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 7.1874 | NA | 70 kV | NA | NA | NA | NA | NA | 5534805 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-15 | 2022-01-19 | 2022-01-19 | NA | NA | FALSE | 166.6199 | NA ¦ NA | 166.6199 | 166.6199 | 113.8392 | 53.0556 | -0.2748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166.6199 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 113.8392 | 42.1126 | -0.25682 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
407 | Monte Rio: EM Repl CB22 SEL Relays |  |  | Monte Rio CDP, Sonoma | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-18 | 29 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.19407 | NA | 60 kV | NA | NA | NA | NA | NA | 5534849 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-08-16 | 2022-01-26 | 2022-01-26 | NA | NA | FALSE | 78.1204 | NA ¦ NA | 78.1204 | 78.1204 | 76.822 | 1.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1204 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 76.822 | -0.56067 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
408 | Paul Sweet: EM Repl CB152 SEL Relay |  |  | Live Oak CDP, Santa Cruz | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-03 | 26 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.5678 | NA | 115 kV | NA | NA | NA | NA | NA | 5534856 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-06-22 | 2022-01-28 | 2022-01-28 | NA | NA | FALSE | 33.2359 | NA ¦ NA | 33.2359 | 33.2359 | 31.7241 | 1.5118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2359 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 31.7241 | -0.45955 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
409 | EM PLEASANT GROVE REPL SEL RELAYS |  |  | Placer | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-12 | 27 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3205 | NA | 115 kV | NA | NA | NA | NA | NA | 5534858 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-07 | 2022-02-23 | 2022-02-23 | NA | NA | FALSE | 197.2418 | NA ¦ NA | 197.2418 | 197.2418 | 102.0313 | 95.0206 | 0.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197.2418 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 102.0313 | 95.0206 | -23.982 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
410 | Barton: EM Repl CB162 SEL Relays |  |  | Fresno, Fresno | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-12 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.5149 | NA | 115 kV | NA | NA | NA | NA | NA | 5534803 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-23 | 2022-04-27 | 2022-04-27 | NA | NA | FALSE | 52.1701 | NA ¦ NA | 52.1701 | 52.1701 | 49.5787 | 0.8946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.1701 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 48.2886 | 0.87126 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
411 | EM DRUM #1 PH REPL SEL RELAYS |  |  | Placer | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-12 | 29 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.2491 | NA | 115 ¦ 60 kV | NA | NA | NA | NA | NA | 5534816 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-19 | 2022-09-20 | 2022-09-16 | NA | NA | FALSE | 225.2261 | NA ¦ NA | 225.2261 | 225.2261 | 33.4156 | 172.8782 | 18.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.2261 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 203.6602 | -9.768 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
412 | EM GARBERVILLE REPL SEL RELAYS |  |  | Garberville CDP, Humboldt | Replace the existing obsolete SEL-221 and 321 Relays on CB 32 and 42 with SEL 311C relays. The targeted SEL-221 existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The targeted SEL 221 and 321 relays are at the end of their useful life cycle and are no longer supported by the manufacturer. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-02 | 26 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3066 | NA | 60 kV | NA | NA | NA | NA | NA | 5534823 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-05-01 | 2020-05-22 | 2022-09-26 | Prioritization | NA | FALSE | 87 | NA ¦ NA | 47.5562 | 47.5562 | 0 | 35.2962 | 12.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.5562 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 34.2194 | 11.1881 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
413 | EM LOGAN CREEK REPL CB262 SEL RELAY |  |  | Glenn | Per system requirement, replace obsolete 1 SEL-221 relays on Logan Creek CB 262 SEL with SEL 311C relays | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-11 | 28 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.8188 | NA | 230 kV | NA | NA | NA | NA | NA | 5534840 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-23 | 2022-09-28 | 2022-09-28 | NA | NA | FALSE | 82 | NA ¦ NA | 74.2977 | 74.2977 | 0 | 61.0603 | 13.2375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2977 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 61.0603 | 7.339 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
414 | EM BOGUE REPL SEL RELAYS |  |  | Yuba City, Sutter | Per system requirement, replace obsolete 1 SEL-221 and 3 SEL 321 relays on Bogue CB 112/122, 112/152, and 142/152 with an SEL 311C relay. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 24 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7823 | NA | 115 kV | NA | 3. Emergency Preparedness | NA | NA | NA | 5534804 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-04 | 2022-10-04 | 2022-10-04 | NA | NA | FALSE | 71 | NA ¦ NA | 56.7089 | 56.7089 | 1.9475 | 46.6776 | 6.5693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.7089 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 50.1396 | 2.8584 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
415 | EM SYCAMORE CREEK REPL SEL RELAY |  |  | Chico, Butte | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-11 | 30 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.5676 | NA | 115 kV | NA | NA | NA | NA | NA | 5534869 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-10 | 2022-10-24 | 2022-10-11 | NA | NA | FALSE | 83.1001 | NA ¦ NA | 83.1001 | 83.1001 | 0 | 69.0808 | 14.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1001 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 68.199 | 8.6417 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
416 | EM LOWER LAKE REPL CB182 SEL RELAY |  |  | Lower Lake CDP, Lake | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 30 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.34501 | NA | 115 kV | NA | NA | NA | NA | NA | 5534842 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-03 | 2022-10-21 | 2022-10-21 | NA | NA | FALSE | 142.7879 | NA ¦ NA | 142.7879 | 142.7879 | 0.8075 | 126.0281 | 15.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.7879 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 125.2165 | 1.051 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
417 | EM KINGBURG REPL SEL RELAY |  |  | Fresno | Emergency replacement of EMKINGBURGSEL RELAY at KINGSBURG SUB, which failed on or around 03/05/2021. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 29 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.3704 | NA | 115 kV | NA | NA | NA | NA | NA | 5534834 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-26 | 2022-11-17 | 2022-11-17 | NA | NA | FALSE | 154 | NA ¦ NA | 149.2484 | 149.2484 | 94.3097 | 47.2477 | 6.5587 | 1.1323 | 0 | 0 | 0 | 0 | 0 | 0 | 149.2484 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 94.3096 | 47.2477 | 6.5587 | -13.7925 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
418 | EM BUTTE REPL SEL RELAYS |  |  | Chico, Butte | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-06 | 24 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.1949 | NA | 115 ¦ 60 kV | NA | NA | NA | NA | NA | 5534807 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-11-30 | 2022-12-01 | 2022-12-01 | NA | NA | FALSE | 252.4032 | NA ¦ NA | 252.4032 | 252.4032 | 3.5625 | 212.8657 | 35.9751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252.4032 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 213.6652 | 5.553 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
419 | Llagas: EM Repl SEL Relay |  |  | Gilroy, Santa Clara | Emergency replacement of SEL RELAY at LLAGAS SUB, which failed on or around 04/27/2021. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 31 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.3037 | NA | 115 kV | NA | NA | NA | NA | NA | 5534837 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-12-06 | 2022-12-30 | 2022-12-30 | NA | NA | FALSE | 242 | NA ¦ NA | 237.0595 | 237.0595 | 53.2123 | 108.92 | 74.0595 | 0.8678 | 0 | 0 | 0 | 0 | 0 | 0 | 237.0595 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 51.0403 | 104.4742 | 71.0366 | -13.1974 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
420 | EM GRASS VALLEY REPL CB22 SEL RELAY |  |  | Grass Valley, Nevada | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-09 | 26 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.1378 | NA | 60 kV | NA | NA | NA | NA | NA | 5534826 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-01-18 | 2023-01-19 | 2023-01-19 | NA | NA | FALSE | 88.8533 | NA ¦ NA | 88.8533 | 88.8533 | 0.0214 | 34.926 | 52.2091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8533 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 0.02107 | 34.3194 | 51.3024 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
421 | EM KERN OIL REPL CB142 SEL RELAYS |  |  | Oildale CDP, Kern | Emergency replacement of EMCB142 SEL RELAYS at KERN OIL SUB, which failed on or around 03/21/2023. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-06 | 27 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.2122 | NA | 115 kV | NA | NA | NA | NA | NA | 5534833 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-04-28 | 2023-04-28 | 2023-05-04 | NA | NA | FALSE | 138 | NA ¦ NA | 133.2579 | 133.2579 | 0.3018 | 13.1415 | 119.8146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133.2579 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 0.30179 | 13.1415 | 106.4889 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
422 | EM RAVENSWOOD REPL BK1 SEL RELAY |  |  | Menlo Park, San Mateo | Emergency replacement of EMBK1 SEL RELAY at RAVENSWOOD SUB, which failed on or around 02/10/2022. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 20 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 11.3472 | NA | 230 kV | NA | NA | NA | NA | NA | 5534861 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-05-02 | 2023-05-05 | 2023-05-05 | NA | NA | FALSE | 91 | NA ¦ NA | 86.1343 | 86.1343 | 0 | 15.0162 | 71.1181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1343 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 77.5209 | -2e-05 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
423 | EM COLEMAN PH REPL SEL RELAY |  |  | Shasta | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-13 | 28 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.7347 | NA | 60 kV | NA | NA | NA | NA | NA | 5534810 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-11-08 | 2023-11-16 | 2023-11-15 | NA | NA | FALSE | 547.9176 | NA ¦ NA | 547.9176 | 547.9176 | 0.0707 | 13.2198 | 507.4054 | 25.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 547.9176 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0.06883 | 12.8659 | 493.8191 | -15.2866 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
424 | EM CORONA REPL SEL RELAYS |  |  | Petaluma, Sonoma | Emergency replacement of EMSEL RELAYS at CORONA SUB, which failed on or around 07/01/2022. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-17 | 25 | NA | Other - Status Quo | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.57982 | NA | 115 kV | NA | NA | NA | NA | NA | 5534813 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-08-08 | 2023-11-16 | 2023-11-16 | NA | NA | FALSE | 98 | NA ¦ NA | 93.4934 | 93.4934 | 0.8075 | 5.6601 | 70.1882 | 16.8376 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4934 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 75.4943 | 8.6497 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
425 | EM COALINGA #1 REPL CB22 SEL RELAYS |  |  | Coalinga, Fresno | Replace the existing obsolete SEL relay with an SEL 311C relay. The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no/limited fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Also, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. The relays are at the end of life. System protection recommends replacing the relays with new line relays per the latest standard. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-13 | 29 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.98563 | NA | 70 kV | NA | NA | NA | 3.0021 | Non-IGP | 5534808 | T.0004503 | EM: Bucket: One For One Relay 2019 | 69 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-10-27 | 2024-11-07 | 2025-10-13 | Prioritization | NA | TRUE | 51 | NA ¦ NA | 130.7321 | 145.7321 | 0.0536 | 27.747 | 15.1288 | 26.3902 | 57.4473 | 17.2686 | 0 | 0 | 0 | 0 | 128.4635 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0.05355 | 27.2347 | 14.8661 | 25.9318 | 56.4496 | 2.2292 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
426 | Midway: EM Diablo RAS |  |  | Buttonwillow CDP, Kern | Emergency replacement of relays st EM Diablo. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 14 | NA | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 ¦ 230 kV | 1110 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5784341 | T.0004511 | DIABLO: EM DIABLO SPS RELAY | 3 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-08-02 | 2019-12-21 | 2019-12-22 | NA | NA | FALSE | 2500 | NA ¦ NA | 335.2217 | 335.2217 | 0 | 5.7237 | 2.8491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335.2217 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 5.4614 | 2.7186 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
427 | EM ROUND MOUNTAIN REP CB 222 RELAY |  |  | Round Mountain CDP, Shasta | Round Mountain CB 212 and CB 222 protect the Pit #5–Round Mountain #1 and Pit #5–Round Mountain #2 230kV lines respectively. The existing electromechanical line relays on these terminals were installed in 1966. They have no fault locating capability and are old, obsolete and failing relays. They are no longer manufactured and spare parts are not available if they fail. Both lines run through Tier 3 – Extreme Fire Risk Zone. The scope summary is to replace Protection Relay’s and install a new SMP relay package for CB 212 & CB 222 at Round Mountain and add digital communications to Pit #5 PH CB 232 & 252 relays. This relay scheme will become a “mirror bit” piloted relay scheme and there will be C37.94 circuits provisioned for this Round Mountain to Pit #5 line. System Protection will build and set the relays to accept the C37.94 circuits once these circuits get built should the emergency relay replacement installation precede the new telecom circuit installation. There are requirements for connections to terminal servers for relay access. Round Mountain Substation has existing ODN network devices for relay DNP Polling and Remote Relay Access. There will be a total of eight (8) new SMP Relays and four (4) SEL 2411 relays being installed. At Round Mountain, each relay will have fiber runs between the control panels and the Cisco Switches located in the Telecom Room. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-09 | 57 | NA | Other - Deferral | $1 Mil - $2 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 230 kV | 210 | 3. Emergency Preparedness | NA | NA | NA | 5534119 | T.0004524 | ROUND MOUNTAIN: EM REP CB 222 RELAY | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-06-01 | 2022-08-10 | 2022-08-10 | NA | NA | FALSE | 1406 | NA ¦ NA | 1412.7413 | 1412.7413 | 167.8422 | 828.6783 | 31.2853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1412.7413 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 167.8422 | 828.6783 | -110.2642 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
428 | Gregg: EM Repl 230 KV BUS DIFF RELAYS |  |  | Madera | Emergency replacement of bus differential relays on Gregg 230 kV Bus | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-10 | 40 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.266 | NA | 230 kV | 426 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5783412 | T.0004631 | GREGG: EM REP 230 KV BUS DIFF RLYS | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-06-01 | 2021-03-12 | 2021-05-19 | NA | NA | FALSE | 2000 | NA ¦ NA | 1978.5763 | 1978.5763 | 721.5678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1978.5763 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1978.5763 | -271.0285 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
429 | REDBUD: EM Repl CB 152 Relays |  |  | Clearlake Oaks CDP, Lake | Redbud CB 152 & 162 Relay Replacement. The following protection requirements are based on the existing PG&E transmission system. 1.Remove all existing equipment on Panel 1R & 1C. 2.Remove equipment on Panel 2R related to CB 162, including 125-2, 127-2, 125X-2, 194BU-2, 127B-2, 127X-2, 194-2, 150B-2, 162B-2. Retain equipment related to 115kV Bus protection. 3.Remove CB 162 line relaying equipment from Panel 4C. This includes Device 185-2, 121/167N-2, 121/167NBU-2, 143T-2, 143C-2, FT switches, and Cut-Outs. Also, remove equipment related to Sync Check scheme, including 125RE, 162RE, RE104SC-1, RE104SC-2, 125REX. Sync check for 115kV breakers will be performed by SMP relays. The only remaining equipment on 4C will be the annunciator and D20S-1 board. Confirm with Automation regarding these two devices. We may consider moving this equipment to 5C to completely spare out 4C. 4.Verify whether Sync swing panel is still needed. If not needed, then remove. 5.Install (2) SMP Line Panels & (2) SMP Breaker Panels as shown in Table 1. 6.Confirm existing broker delta PT winding is no longer used and rewire second winding on existing Bus PTs from broken delta to wye. Wire CB 162 new relays to separate PT windings, per standard. 7.Install three new CCVTs on CB 152 side of Sw 357. Wire new CB 152 relays to separate PT windings, per standard 8.Wire relay fail and relay operate alarms to station annunciator. 9.Connect new relays for remote communication access per Automation requirements. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | 29 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.1825 | NA | 115 kV | NA | 3. Emergency Preparedness | NA | 3.0021 | Non-IGP | 5537442 | T.0005148 | REDBUD: EM REPL CB 152 RELAYS 74029062 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-03-11 | 2022-12-03 | 2025-03-07 | Project Design | NA | TRUE | 1430 | NA ¦ NA | 2244.8646 | 2244.8646 | 42.9263 | 75.3689 | 133.9581 | 1094.8162 | 437.134 | -0.122 | 0 | 0 | 0 | 0 | 2244.9866 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 38.6338 | 67.832 | 120.5621 | 985.3345 | 505.6702 | -0.1159 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
430 | STANISLAUS: EM REPL Manteca 154/164 Rem |  |  | Tuolumne | Install two SEL 2411 relays for dual digital POTT pilot protection on Stanislaus PH – Manteca #2 115KV line. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-03 | 29 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.932 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5548563 | T.0005445 | MANTECA: EM REPL CB144-154 RELAYS | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-12-18 | 2024-03-16 | 2024-02-09 | NA | NA | FALSE | 711 | NA ¦ NA | 648.9129 | 648.9129 | 0 | 230.1189 | 197.2828 | 221.459 | 0.0523 | 0 | 0 | 0 | 0 | 0 | 648.9129 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 207.1068 | 177.5545 | 199.3132 | 0.04718 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
431 | MANTECA: EM Repl CB144-154 RELAYS |  |  | Manteca, San Joaquin | The project proposes to replace all line & breaker panel relays for CB 144,154 & 164 at Manteca Substation and the relays will be installed in the new MPAC building. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-14 | 30 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.8539 | NA | 115 kV | NA | 3. Emergency Preparedness | NA | 3.0021 | Non-IGP | 5788361 | T.0005445 | MANTECA: EM REPL CB144-154 RELAYS | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-07-03 | 2024-03-16 | 2024-03-16 | NA | NA | FALSE | 711 | NA ¦ NA | 5087.5889 | 5087.5889 | 83.1996 | 510.4004 | 2585.0284 | 1840.9368 | -76.6617 | 0 | 0 | 0 | 0 | 0 | 5087.5889 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 5164.2505 | -76.6617 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
432 | TESLA: EM REPL CB 132 RELAYS |  |  | Alameda | Emergency replacement of the relays to line CB 132. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | 52 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 115 kV | NA | 5a. Mitigates System Wide Failure Risk | NA | 3.0021 | Non-IGP | 5788359 | T.0005708 | TESLA: EM REPL CB132 RELAYS | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-12-15 | NA | 2024-03-22 | NA | NA | FALSE | NA | NA ¦ NA | 1059.6458 | 1059.6458 | 220.421 | 51.3027 | 174.261 | 487.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 1059.6458 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 961.585 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
433 | SOBRANTE: EM REPL 230KV BUS DIFFERENTIAL |  |  | Orinda, Contra Costa | After the Sobrante 230kV inspection was completed it was determined that the Bus Differential may not operate for an internal bus fault. If a bus fault occurs and the scheme does not operate, all lines and transformers connected to the 230kV bus will trip on a time delay. This may cause system stability issues, additional thermal and mechanical stress, and customer power quality complains. Additionally, Crockett Cogen will be out of service. On this project the existing Sobrante 230kV paddle scheme and electromechanical relays will be replaced on an emergency basis with a redundant low impedance SMP Bus Differential System A and System B design. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-04 | 50 | NA | Other - Deferral | $3 Mil -$5 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.0767 | NA | 230 kV | NA | NA | NA | NA | NA | 5791193 | T.0005995 | Sobrante 230 kV Differential | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-01 | 2022-03-23 | 2022-03-23 | NA | NA | FALSE | 3020 | NA ¦ NA | 3001.054 | 3001.054 | 1830.9488 | 1016.9004 | 0.2863 | -0.705 | 0 | 0 | 0 | 0 | 0 | 0 | 3001.054 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 2710.7903 | 67.7314 | -0.65086 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
434 | POE PH: EM Repl CB212/252 Com |  |  | Butte | Install new SMP Style relays for a Current Differential Scheme on the 230kV Belden - Rock Creek – Poe Transmission Line | Substation - Protection Relay | Replace | NA | T.0004687 | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-13 | 15 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.9596 | NA | 230 kV | NA | NA | NA | 3.0021 | Non-IGP | 5790909 | T.0006046 | POE PH: Em Repl CB 212/252 Com | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2024-08-12 | NA | 2026-03-31 | NA | NA | TRUE | NA | NA ¦ NA | 1731.2058 | 1951.3489 | 199.3471 | 283.3886 | 159.5231 | 249.2352 | 461.2144 | 577.6309 | 0 | 0 | 0 | 0 | 1373.7179 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
435 | COLGATE: EM REPLCB 212/262 Relay |  |  | Yuba | Emergency replacement existing 230KV line relays with new SMP package at Colgate substation for CB 212/262 | Substation - Protection Relay | Replace | NA | T.0006792 | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 59 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 1.5839 | NA | 230 kV | NA | NA | NA | 3.0021 | Non-IGP | 5542340 | T.0006759 | Colgate: Repl CB 212/262 Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-01-05 | NA | 2027-04-30 | NA | NA | TRUE | NA | NA ¦ NA | 1053.784 | 1865.2283 | 182.3873 | 218.164 | 313.7032 | -1.6858 | 224.7116 | 102.0662 | 789.9309 | 0 | 0 | 0 | 973.2312 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 196.5044 | 196.3477 | 282.3328 | -1.5171 | 202.2407 | 72.4976 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
436 | COLGATE: EM REPL CB222/272 COM |  |  | Yuba | Emergency replacement existing 230KV line relays with new SMP package at Colgate substation for CB 222/272 | Substation - Protection Relay | Replace | NA | T.0006759 | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 25 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 1.5839 | NA | 230 kV | NA | NA | NA | 3.0021 | Non-IGP | 5542440 | T.0006792 | Colgate: Repl CB 222/272 Com | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2025-09-17 | NA | 2027-01-20 | NA | NA | TRUE | NA | NA ¦ NA | 3511.5686 | 3513.8904 | 187.0902 | 163.8255 | 217.9037 | 26.6681 | 1823.1795 | 1067.4879 | 0 | 0 | 0 | 0 | 2446.4025 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 193.3433 | 147.4427 | 196.1131 | 24.001 | 1640.8611 | 958.6493 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
437 | EM: TABLE MOUNTAIN REPL PMU AND PDC |  |  | Butte | Project scope: o Install new SEL PMU/PDC system to monitor all four 500kV line terminals and 230kV Oroville Thermalito-Table Mountain line #1, #2 and #3. o Remove PMU function from PACIRAS relays. o Remove PDCs at Table Mountain. o Replace existing MSC PLCs with new redundant SEL controllers for the two 500kV MSC banks at Table Mountain Justification: Existing A/C PDC at Table Mountain has not been working for a while. PMU/PDC systems are required at Table Mountain to meet NERC PRC-002 and existing internal requirements as determined by the Systems Operations Group led by Sherman Chen. We would like to replace Table Mountain A/C PMUs and PDC with SEL PMU/PDC system. B/D unit should also be replaced to keep consistency between A/C and B/D units. Table Mountain redundant MSC PLCs are part of the PACIRAS scheme. The PLC system is designed to provide Table Mountain 500kV bus voltage support in response to PACIRAS event and/or significant system disturbance. The PLC has presented difficulties for operation evaluation in the past years due to limitations on the device’s event recording capabilities. In addition, based on results from several operation analysis, the implementation of the PLC logics needs to be re-evaluated and adjusted accordingly. It is recommended to install new SEL controllers which will be internally programmed by System Protection. The replacement will improve the controller performance and make following operation analysis easier for meeting NERC PRC-012 requirements. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-20 | 14 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Corrosion |  | NA | 47.516 | NA | 500 kV | NA | NA | NA | 3.0021 | Non-IGP | 5794501 | T.0006896 | TABLE MOUNTIN_REPL PMU and PDC | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-01-19 | NA | 2026-08-21 | NA | NA | TRUE | NA | NA ¦ NA | 1505.3619 | 2074.2769 | 28.0252 | 17.4861 | 84.0226 | 389.2862 | 843.2843 | 712.1724 | 0 | 0 | 0 | 0 | 1362.1044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
438 | RIO DELL JCT: EM REPL 42 and 22 Relays |  |  | Hydesville CDP, Humboldt | Emergency replacement of relays for CB 22, 42 and Rio Dell Tap due to equipment failure. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-05 | 18 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.41044 | NA | 60 kV | NA | NA | NA | NA | NA | 5543979 | T.0006948 | RIODELLJCT: EM REPL CB 42&22 REPL | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-15 | 2023-08-04 | 2023-08-04 | NA | NA | FALSE | 1807.3405 | NA ¦ NA | 1817.5537 | 1817.5537 | 190.2751 | 617.9597 | 977.4707 | 30.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 1817.5537 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 191.2321 | 537.0404 | 879.7234 | 27.8023 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
439 | WEIMAR: EM REPL CB 72 Relay |  |  | Placer | Emergency Replacement of CB 72 relays at Weimar sub | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-10 | 64 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.82438 | NA | 60 kV | NA | NA | NA | 3.0021 | Non-IGP | 5548202 | T.0007900 | WEIMAR-EM REPL CB 72 RELAYS | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-06-12 | NA | 2024-01-25 | NA | NA | TRUE | NA | NA ¦ NA | 1241.2478 | 1250.6959 | 0.7664 | 156.2279 | 730.9469 | 309.2485 | 36.5876 | 16.9185 | 0 | 0 | 0 | 0 | 1233.7774 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 141.2948 | 657.8521 | 278.3236 | 32.9288 | 6.7234 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
440 | BELL - EM REPLACE LINE RELAYS |  |  | Placer | Replacing Bell Line Relays due to failed Optical CT | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 25 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.91963 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5549728 | T.0008373 | BELL EM REPL OPT MTR CT_PT | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-11-12 | NA | 2025-04-11 | NA | NA | TRUE | NA | NA ¦ NA | 1270.6093 | 1277.4621 | 0 | 15.7936 | 400.0841 | 331.4772 | 522.02 | 8.0872 | 0 | 0 | 0 | 0 | 1269.3749 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 14.2142 | 360.0756 | 298.3294 | 469.8177 | 1.1109 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
441 | SONOMA: EM REPL CB 132 RECLOSING RELAY |  |  | Sonoma, Sonoma | Emergency replacement of CB 132 relays at Sonoma A substation. Scope of work includes: Remove Basler relay 179-1 on Panel 1C and it’s all connected accessories. • Install new SEL-451 Vertical mounted unit on its place for breaker failure and reclosing on CB- 132. • Connect all the necessary test switches and controllers according to the EDS 4131802-4131805. • Add 3-gang test switch to the relay control and testing. • Replace existing incandescent status indicator light bulbs with LED lights. • Wire relay fail and relay operate alarms to station annunciator. • Connect new relays for remote communication access per Automation requirements. • Run LC-LC MM F.O. from the relays to the Cisco switch per IT requirements. Panel 2C • Remove Basler relay 179-4 on Panel 1C and it’s all connected accessories. • Install new SEL-451 Vertical mounted unit on its place for reclosing on MOAS 176. • This unit will not use for Breaker failure option. • Connect all the necessary test switches and controllers according to the EDS 4131802-4131805. • Replace existing incandescent status indicator light bulbs with LED lights. • Connect new relays for remote communication access per Automation requirements. • Wire relays fail and relay operate alarms to station annunciator. • Run LC-LC MM F.O. from the relays to the Cisco switch per IT requirements. Panel 3C • Rewire existing 179-3 (SEL-451) on Panel 3C to implement breaker failure protection. • Connect all the necessary test switches and controllers according to the EDS 4131802-4131805. Panel 4C • Remove all equipment related to obsolete Automatics Test Panel Scheme. • Remove existing Annunciator 30-1 unit. • Replace with 2X SEL-2523 digital annunciators. (replacement part# 252301H23A0A0XX ) • This will include all devices on Panel 4C and some equipment on Panel 2R. • The RTU will connect serially to the annunciators using a UNICOM2500 (RS232 to RS485 converter). • Use EDS 4160439 and rewire the existing annunciator alarms in the same order until one of the new annunciators fully utilized with all 36 windows. • Windows 37 to 48 of the existing annunciator should be wired to the windows 1 through 12 of the second annunciator. • Provide trip targets and relay fail alarms for all new microprocessor relays to the station annunciator. Panel 0R • Remove D20S unit from the Rack. • Install a new SEL -2488 Satellite Clock. This substation is in a high fire zone. Connect the IRIG- B clock to the RTU, and all existing and new relay per EDS 4117078. • Install pest shield on the RTU chassis. (Utilize Lucasey part#PGEPCS01) Panel 1R • Remove auxiliary relay 152Z-1 and 43Y-1 relays. • Use blank covers to cover the vacant cutouts. Panel 2R • Remove all the auxiliary relay connected to test panel. • Remove all the Aux relay connections to existing RTU. • Transfer all the tripping contacts to Panel 4R new MVAJ relays. • Use blank covers to cover the vacant cutouts. Panel 3R • Remove all the auxiliary relay connected to test panel. • Remove all the Aux relay connections to existing annunciator. • Use blank covers to cover the vacant cutouts. Panel 4R • Add 2 new MVAJ units to transfer Aux relay tripping from Panel 2R. • Use Available DC panel spares for new relay DC 125V power (DWG.458301). | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-03 | 18 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 1.5781 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5551780 | T.0009111 | Sonoma Repl CB 132 Reclose Rly | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-29 | 2025-03-19 | 2025-03-19 | NA | NA | TRUE | 1290 | NA ¦ NA | 1264.0571 | 1264.0571 | 0 | 0 | 268.5471 | 312.8196 | 682.6904 | 0 | 0 | 0 | 0 | 0 | 1264.0571 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 241.6925 | 281.5378 | 614.4214 | 0.00026 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
442 | EM REPL DEV 187 |  |  | Fresno | The project will replace the existing Westinghouse (CO-ADJ INVERSE) Electromechanical 70KV Bus Differential Relays in the 230KV Control Building. Last relay testing was performed in January 2020, and it was passed barely. The relay was inconsistent during the testing and close to out of tolerance +/- 7 (always need mechanical adjustment to be w/in +/- 5 %). Lastly, the existing relays do not have fault recording capability for quick restoration of system after a 70KV Bus Fault. Since the manufacturer no longer support the replacement parts for the existing relays, System Protection recommended the installation of new SMP Low Impedance Bus Differential Protection Relays. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-12 | 50 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 77.6619 | NA | 70 kV | NA | NA | NA | 3.0021 | Non-IGP | 5552265 | T.0009226 | GATES: EM REPL DEV 187 | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-09-09 | NA | 2025-11-12 | NA | NA | TRUE | NA | NA ¦ NA | 1021.8664 | 1022.0495 | 0 | 0 | 59.0759 | 292.7004 | 669.2815 | 0.9918 | 0 | 0 | 0 | 0 | 1021.0578 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 59.0759 | 292.7004 | 669.2815 | 0.80863 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
443 | BRIDGEVILLE: EM INSTALL CB 1012/1022 REL |  |  | Humboldt | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-04 | 26 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.1134 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5553909 | T.0009264 | LOW GAP: EM REPLACE BANK 1 | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-12-01 | NA | 2023-12-11 | NA | NA | FALSE | NA | NA ¦ NA | 37.4457 | 37.4457 | 0 | 0 | 35.8458 | 1.4893 | 0.1106 | 0 | 0 | 0 | 0 | 0 | 37.4457 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 37.3351 | 0.11063 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
444 | COTTONWOOD CB 142 - DTT EQUIPMENT |  |  | Cottonwood CDP, Shasta | Replace existing DTT at various sites with in Pacific Gas And Electric that are considered obsolete. These replacements will involve one for one replacement. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-19 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 26.1945 | NA | 115 kV | NA | NA | NA | 3.0021 | Non-IGP | 5553908 | T.0009264 | LOW GAP: EM REPLACE BANK 1 | 2 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-11 | NA | 2024-01-25 | NA | NA | FALSE | NA | NA ¦ NA | 108.0657 | 108.0657 | 0 | 0 | 47.1693 | 60.0836 | 0.8127 | 0 | 0 | 0 | 0 | 0 | 108.0657 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 107.2529 | 0.81275 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
445 | BOLINAS: REPLACE CB 12 RELAYS |  |  | Bolinas CDP, Marin | Emergency replaced failed Bolinas CB 12 relays | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-02-02 | 49 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.81301 | NA | 60 kV | NA | NA | NA | 3.0021 | Non-IGP | 5553079 | T.0009325 | Bolinas: EM Replacement CB 12 Relays | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-02 | NA | 2026-11-23 | NA | NA | TRUE | NA | NA ¦ NA | 1645.3466 | 2882.9928 | 0 | 0 | 252.9646 | 904.8081 | 451.1851 | 1256.7889 | 17.2461 | 0 | 0 | 0 | 1608.9578 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 227.6681 | 814.3275 | 406.0668 | 32.7499 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
446 | METCALF: EM REPL Traveling Wave |  |  | Santa Clara | This Emergency project will replace existing failed Mark 5 traveling wave quipment with a new Qualitrol FL-8 equipment to monitor Tesla - Metcalf 500kV line and Moss Landing - Metcalf 500kV line. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-05 | 15 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 500 kV | NA | NA | NA | 3.0021 | Non-IGP | 5555740 | T.0009964 | METCALF: EM REP TRAVELING WAVE 500KV | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-01 | NA | 2026-06-23 | NA | NA | TRUE | NA | NA ¦ NA | 92.4753 | 1306.0319 | 0 | 0 | 0 | 76.7758 | 11.979 | 1217.2771 | 0 | 0 | 0 | 0 | 88.7548 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 69.0982 | 10.7811 | 3.3485 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
447 | COCO SUB: EM REPL BANK 1 RELAY |  |  | Antioch, Contra Costa | Contra Costa Sub Bank 1 has inadequate protection and cannot be put in service per Test Department. After Bank 1 Devices 67-17 and 87-1 failed the routine relay maintenance, System Protection concurred to replace the relays on an emergency basis. The bank panel has aux relays for the existing obsolete reclosing relays for CB 172 and CB 70. Therefore CB 172 and CB 70 breaker relays will be replaced. | Substation - Protection Relay | Replace | NA | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | 2026-03-03 | 63 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 15.1779 | NA | 115 ¦ 60 kV | NA | NA | NA | 3.0021 | Non-IGP | 5556440 | T.0010115 | CoCo Sub: EM Repl Bank 1 Relay | 1 | 3F | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-10-20 | NA | 2026-08-12 | NA | NA | TRUE | NA | NA ¦ NA | 1396.3031 | 1823.9269 | 0 | 0 | 0 | 187.1634 | 774.3579 | 862.4056 | 0 | 0 | 0 | 0 | 961.5212 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 168.4469 | 696.9217 | 391.3036 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
448 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5810800 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2026-02-15 | NA | NA | TRUE | NA | NA ¦ NA | 3243.6218 | 5045.8464 | 0 | 0 | 0 | 344.4226 | 2737.0346 | 1963.5057 | 0 | 0 | 0 | 0 | 3082.3407 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 1650.7659 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
449 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5804859 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2024-12-31 | NA | NA | FALSE | NA | NA ¦ NA | 2189.4568 | 2189.4568 | 0 | 0 | 74.6994 | 2111.5177 | 3.2397 | 0 | 0 | 0 | 0 | 0 | 2189.4568 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 2186.2171 | 3.2396 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
450 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5803546 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2025-03-15 | NA | NA | FALSE | NA | NA ¦ NA | 2142.1664 | 2142.1664 | 0 | 127.4427 | 705.2016 | 787.5994 | 485.7989 | 0 | 0 | 0 | 0 | 0 | 2142.1664 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2025 ¦ 2026 | 0 | 0 | 107.7491 | 0 | 2034.4173 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
451 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5809298 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2025-04-15 | NA | NA | FALSE | NA | NA ¦ NA | 16663.0415 | 16663.0415 | 0 | 0 | 0 | 15948.1327 | 678.4153 | 0 | 0 | 0 | 0 | 0 | 16663.0415 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 16663.0415 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
452 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5811509 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 3503.3975 | 0 | 0 | 0 | 0 | 0 | 993.2213 | 600 | 618 | 636.54 | 655.6362 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
453 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5811510 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 9893.3667 | 0 | 0 | 0 | 0 | 0 | 2153.6567 | 1850 | 1905.5 | 1962.665 | 2021.5449 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
454 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5811511 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 6486.7883 | 0 | 0 | 0 | 0 | 0 | 897.4626 | 1336 | 1376.08 | 1417.3624 | 1459.8833 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
455 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5816690 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2712.6055 | 0 | 0 | 0 | 0 | 0 | 202.4293 | 600 | 618 | 636.54 | 655.6362 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
456 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Wires - Minimum Required Scope (spot repair) Alternative | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5545863 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | 964 | NA ¦ NA | 5924.2839 | 5926.6228 | 19.0256 | 283.0645 | 340.9026 | 2289.4356 | 2971.5217 | 22.9417 | 0 | 0 | 0 | 0 | 5903.6811 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 19.0256 | 147.701 | 132.0903 | 7.4364 | 4568.3973 | 870.4267 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
457 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | 30 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5803040 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2023-12-18 | 2023-12-18 | NA | NA | FALSE | 3700 | NA ¦ NA | 10600.8564 | 10600.8564 | 0 | 0 | 10555.0249 | 45.8315 | 0 | 0 | 0 | 0 | 0 | 0 | 10600.8564 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 10555.0249 | 45.8315 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 & 6 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
458 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5793242 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2024-09-06 | 2023-12-31 | NA | NA | FALSE | NA | NA ¦ NA | 1487.215 | 1487.215 | 974.8356 | 144.477 | 299.5408 | 49.4633 | 0 | 0 | 0 | 0 | 0 | 0 | 1487.215 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 883.1342 | 255.0767 | 299.5408 | 49.4633 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
459 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5794298 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2022-11-15 | NA | NA | FALSE | NA | NA ¦ NA | 8822.6638 | 8822.6638 | 3997.4515 | 3937.1977 | -16.6846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8822.6638 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 2260.3645 | 6578.9838 | -16.6846 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
460 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | New | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5788371 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1493.6602 | 1493.6602 | 210.7767 | 298.0999 | 490.3234 | 419.3812 | 22.1623 | 0.2434 | 0 | 0 | 0 | 0 | 1493.4168 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 71.7407 | 435.5682 | 409.0035 | 364.4578 | 0.15424 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
461 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Replace | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5517419 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2360.1556 | 2360.1556 | 209.1569 | 101.5376 | 38.8499 | 391.898 | 319.2115 | 33.1373 | 0 | 0 | 0 | 0 | 2327.0183 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 227.8035 | 101.5376 | 38.8499 | 391.898 | 93.8443 | 9.4075 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
462 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | New | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5788374 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ 5784566 ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2023-12-15 | NA | NA | FALSE | NA | NA ¦ NA | 14272.92 | 14272.92 | 9702.7292 | 3600.8301 | -191.7588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14272.92 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 9784.8808 | 4488.0391 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
463 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5788220 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2021-12-15 | NA | NA | FALSE | 2400 | NA ¦ NA | 2603.9745 | 2603.9745 | -80.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2603.9745 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -93.8811 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
464 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5781555 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2022-11-29 | 2022-12-31 | NA | NA | FALSE | 3500 | NA ¦ NA | 3493.4312 | 3493.4312 | 2142.8168 | 1053.2631 | -13.3836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3493.4312 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 3506.8148 | -13.3836 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
465 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Non-IGP | 5800016 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2024-09-20 | 2024-08-14 | NA | NA | FALSE | NA | NA ¦ NA | 3307.5898 | 3307.5898 | 0 | 865.8554 | 2257.2606 | 187.7504 | 0 | 0 | 0 | 0 | 0 | 0 | 3307.5898 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 989.9972 | 2317.5926 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 6 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
466 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | New | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-25 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 42.1076 | NA | 500 kV | NA | NA | NA | NA | Non-IGP | 5788377 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2020-11-04 | 2020-12-31 | NA | NA | FALSE | 1200 | NA ¦ NA | 1419.4292 | 1419.4292 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1419.4292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
467 | Placeholder Emergent Need in MWC 60/61 |  |  | NA | Forecast placeholder for CAISO Transmission Plan Approved Projects | Transmission Line/Substation | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | T-Line Capacity | NERC TPL Standards | NA | NA | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | EX113287 | NA | NA | NA | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 484675 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 3199.454 | 81820.546 | 167950 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
468 | Christie-Sobrante 115 kV Line Reconductor |  |  | Contra Costa ¦ Orinda, Contra Costa | Reconductor the Christie - Sobrante 115 kV line with a larger capacity conductor | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-06-26 | 72 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 7.8 | NA | 115 | NA | NA | NA | NA | 4.01 | Non-IGP | EX113223 | T.0005969 | Christie-Sobrante 115 kV Line Reconductor | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-01-02 | 2022-12-31 | 2028-02-01 | Prioritization | NA | FALSE | 10500 | NA ¦ NA | 0 | 15300 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 13000 | 1800 | 500 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
469 | Gold Hill-El Dorado Reinforcement Project |  |  | Shingle Springs CDP, El Dorado | Serve Diamond Springs 115 kV Substation from Missouri Flat – Gold Hill #1 115 kV Line. Convert Shingle Springs Substation 115 kV bus to BAAH. Reconductor ~8.8 circuit miles between El Dorado and 008/062 of the El Dorado – Missouri Flat #2 115 kV Line with larger conductor to achieve minimum 577 Amps of summer emergency rating. Remove any limiting components as necessary to achieve full conductor capacity | Transmission Line/Substation | Upgrade/Retrofit | NA | T.0004920 ¦ T.0004950 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-02-13 | 46 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 8.8 | 1.0218 | 115 | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX138973 | T.0011182 | Gold Hill-El Dorado Reinforcement | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-12-01 | 2032-05-01 | 2037-12-01 | Prioritization | NA | FALSE | 127000 | NA ¦ NA | 0 | 19050 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 6350 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
470 | Moraga 230/115kV Transformer Bank Addition |  |  | Orinda, Contra Costa | Install a new 230/115 kV transformer bank at Moraga Substation with minimum 420 MVA for summer normal rating and 462 MVA for summer emergency rating. | Substation - Transformer | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.8714 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX138985 | T.0011211 | Moraga 230/115 kV Transformer Bank Addition | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | 2031-05-01 | 2033-12-01 | Prioritization | NA | FALSE | 40000 | NA ¦ NA | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
471 | Metcalf Substation 500/230kV Transformer Bank Addition |  |  | Santa Clara | Install a new 500/230 kV transformer bank at the Metcalf Substation, which will have a minimum summer normal and emergency rating of 1122 MVA. | Substation - Transformer | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX138982 | T.0011326 | Metcalf Substation 500/230 kV Transformer Bank Addition | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2033-12-01 | 2034-05-01 | 2034-12-01 | Prioritization | NA | FALSE | 182000 | NA ¦ NA | 0 | 1400 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
472 | Ames Distribution – Palo Alto 115 kV transmission line |  |  | Mountain View, Santa Clara | Construction of a new Ames Distribution – Palo Alto 115 kV line using existing vacant tower positions and idle lines, with a minimum capacity requirement of 1500 Amps, and the expansion of the Ames Distribution and Palo Alto Switching Station buses to allow for one additional 115 kV connection at each location. | Transmission Line/Substation | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2025-08-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 3.5 | NA | 115 | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX138971 | T.0011327 | Ames Distribution – Palo Alto 115 kV transmission line | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | 2034-05-01 | 2034-12-01 | Prioritization | NA | FALSE | 84000 | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
473 | San Miguel New 70 kV Line Project |  |  | San Miguel CDP, San Luis Obispo | Build new 70kV line from the loop-in point on the future Union-Paso Robles 70 kV line to San Miguel Substation. | Transmission Line - Multiple | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | TBD | 0.77704 | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | EX138987 | T.0011337 | San Miguel New 70 kV Line | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | 2032-05-01 | 2033-12-01 | Prioritization | NA | FALSE | 30000 | NA ¦ NA | 0 | 2500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
474 | Lakeville #2 60 kV Line Upgrade Project |  |  | Marin ¦ Novato, Marin ¦ Petaluma, Sonoma ¦ Sonoma | Reconductor the line sections on the Lakeville #2 60 kV Line between Petaluma A to Lakeville Junction (tower 4/100) and Cotati to tower 11/236 (approx. 3.39 miles) with 397.5 AAC. Upgrade the capacity of the Petaluma A bus. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-03-24 | 25 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 3.4 | NA | 60 | NA | NA | NA | NA | 3.0011 | Non-IGP | EX112208 | T.0011375 | Lakeville 60 kV Area Reinforcement | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2022 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-10-01 | 2021-12-01 | 2028-12-01 | Prioritization | NA | FALSE | 7000 | NA ¦ NA | 0 | 6500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1500 | 5000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
475 | GWF-Kingsburg 115 kV Line reconductoring |  |  | Fresno ¦ Hanford, Kings ¦ Kings | Reconductor the entire GWF-Kingsburg 115 kV Line with minimum summer emergency rating of 1500 Amps or higher and update the limiting components at the substations if there is any. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2026-02-10 | 32 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 21.6 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | EX138983 | T.0011378 | Reconductor of GWF – Kingsburg 115 kV line | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2033-12-01 | 2034-05-01 | 2036-12-01 | Prioritization | NA | FALSE | 81600 | NA ¦ NA | 0 | 2100 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 600 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
476 | South Bay Reinforcement Project |  |  | San Jose, Santa Clara | Reconductor the 115 kV transmission lines and components to higher capacity: San Jose B – Trimble, Kiefer – FMC,San Jose A – El Patio, Mountain View – Monta Vista, Whisman – Monta Vista, and Los Esteros – Metcalf 230 kV. Additionally, it includes the loop-in of the Los Esteros – Montague 115 kV line at Ringwood substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-12 | 72 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 89.8 | NA | 230 ¦ 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | EX138970 | T.0011380 | South Bay Reinforcement Project | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | 2034-05-01 | 2035-12-01 | Prioritization | NA | FALSE | 434000 | NA ¦ NA | 0 | 131298.78 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 36298.78 | 50000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
477 | Pittsburg-Kirker 115kV Line Section Limiting Elements Upgrade |  |  | Antioch, Contra Costa ¦ Contra Costa ¦ Pittsburg, Contra Costa | Upgrade the limiting elements on the Pittsburg-Kirker-Columbia Steel 115 kV transmission line (Pittsburg-Kirker section) to achieve the full conductor rating of 1126 Amps summer normal rating. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-12 | 38 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 1.5 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | EX138981 | T.0011863 | Pittsburg-Kirker 115 kV Line Section Limiting Elements Upgrade | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-12-01 | 2028-05-01 | 2031-12-01 | Prioritization | NA | FALSE | 200 | NA ¦ NA | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 800 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
478 | Helm 230/70 kV Transformer Bank Addition project |  |  | Fresno | New Helm 230/70 kV Bank #2 | Substation - Transformer | New | NA | NA | Policy | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-10 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.7555 | NA | 230 ¦ 70 kV | NA | NA | NA | 5.1001 | Non-IGP | EX138975 | T.0011876 | New Helm 230/70 kV Bank #2 | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2033-12-01 | 2034-05-01 | 2035-12-01 | Prioritization | NA | FALSE | 115000 | NA ¦ NA | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
479 | West Fresno 115 kV Voltage Support Project |  |  | Fresno, Fresno | Install 75 MVar voltage support at West Fresno substation | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-02-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.7382 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX138974 | T.0011878 | West Fresno 115 kV Voltage Support | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-12-01 | 2031-05-01 | 2034-12-01 | Prioritization | NA | FALSE | 60000 | NA ¦ NA | 0 | 9000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
480 | San Mateo 230/115 kV Transformer Bank Addition Project |  |  | San Mateo, San Mateo | Install a new 230/115 kV transformer bank at the San Mateo Substation, which will have a minimum summer normal rating of 420 MVA and a summer emergency rating of 462 MVA. | Substation - Transformer | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-17 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX138986 | T.0011984 | San Mateo 230/115 kV Transformer Bank Addition Project | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | 2032-05-01 | 2034-12-01 | Prioritization | NA | FALSE | 110000 | NA ¦ NA | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
481 | Plainfield substation reconfiguration |  |  | Yolo | Reconfigure Plainfield substation and energize bank #1 through Nicolaus-Plainfield 60KV and Bank#2 through Vaca-Plainfield 60KV. It can be achieved with opening SW#167 and closing SW#177. Upgrade SW 167, 177 and 179 to Circuit Breakers. Make protection system upgrades as required. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | System Design Upgrade | NERC TPL Standards | NA | 2026-03-04 | 18 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.82985 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | EX112242 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-10-01 | NA | 2027-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 5000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 4500 | 500 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
482 | Jefferson 230 kV BAAH Bus #1&2 redundant relay |  |  | San Mateo | Install Jefferson 230 kV BAAH Bus #1&2 redundant relay to resolve P5 issues. | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.7091 | NA | 230 kV | NA | NA | NA | 4.01 | Non-IGP | Tx000752 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-01-02 | NA | 2027-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1700 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1700 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
483 | Salinas 115kV BAAH Bus #1 &2 redundant relay |  |  | Salinas, Monterey | Install Salinas 115kV BAAH Bus #1 &2 redundant relay to resolve P5 issues. | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.4966 | NA | 115 kV | NA | NA | NA | 4.01 | Non-IGP | EX113219 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-09-01 | NA | 2028-12-31 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 5000 | 2000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
484 | Mendocino 115 kV Redundant Relay |  |  | Mendocino | Install the redundant bus protection relay mitigate overloads identified for P5 contingency on Mendocino 115 kV bus. | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.7328 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | EX112158 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1400 | 2800 | 2800 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
485 | Herndon #1 115 kV bus redundent relay |  |  | Fresno, Fresno | Add redundent relay for Herndon #1 115 kV bus | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.3414 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | EX112159 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 9500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 2000 | 2000 | 5000 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
486 | Las Positas 230 kV Redundant Bus Diffrential Relay |  |  | Livermore, Alameda | Install the redundant bus protection relay mitigate overloads identified for P5 contingency on Las Positas 230 kV Bus. | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-04-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.2184 | NA | 230 kV | NA | NA | NA | 3.0011 | Non-IGP | EX112165 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 5200 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 500 | 1500 | 3000 | 200 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
487 | Plumas Separation and Load Shedding Scheme Upgrade |  |  | Plumas Lake CDP, Yuba | The project scope is to add monitoring element (Table Mountain 230 kV Circuit Breaker 242) to the Plumas Separation and Load Shedding Scheme. Table Mountain CB 242 status will be added as additional input to the scheme. | Substation - Circuit Breaker | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.2058 | NA | 230 kV | NA | NA | NA | 3.0011 | Non-IGP | EX112245 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-03-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1350 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 250 | 1100 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
488 | Lakeville 115 kV Redundant Relay |  |  | Sonoma | Install Lakeville 115 kV Redundant Relay to resolve P5 issues. | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-13 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 14.7021 | NA | 115 kV | NA | NA | NA | 4.01 | Non-IGP | EX113218 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 500 | 2000 | 5500 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
489 | San Jose B - NRS 230 kV line |  |  | San Jose, Santa Clara | Build a new 230 kV line between the new San Jose B 230 kV (to be created as part of the Metcalf-San Jose B HVDC project) and Silicon Valley Power (SVP) NRS 230 kV station. | Transmission Line - Multiple | New | NA | T.0003803 | Reliability | New T-Line | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 6.6 | 2.1017 | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | EX138988 | TBD | San Jose B – NRS 230 kV line | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | TRUE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | 2030-12-01 | 2033-12-01 | Prioritization | NA | FALSE | 200000 | NA ¦ NA | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power, San Jose B - NRS 230 kV line | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
490 | Greater Bay Area 500 kV Transmission Reinforcement |  |  | San Benito | Rebuild Panoche-Las Aguillas-Metcalf 230 kV DCTL to a Manning-Las Aguillas-Moss Landing 500 kV line. Convert Las Aguillas 230 kV to 500/230 kV station, with two 500/230 kV transformers. Build a new 500 kV line from Moss Landing to Metcalf, or build a new 500 kV line from Maning to Metcalf. | Transmission Line/Substation | New | Upgrade/Retrofit | T.0009194 | Reliability | New T-Line | NERC TPL Standards | NA | 2026-02-10 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | TBD | 6.0534 | 500 ¦ 230 | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX138989 | TBD | Greater Bay Area 500 kV Transmission Reinforcement | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | TRUE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2033-12-01 | 2034-05-01 | 2034-12-01 | Prioritization | NA | FALSE | 700000 | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | TBD | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf [TPP Phase 3] The competitive scope of this project has not been awarded to any outside developer yet.
491 | Trimble 230 kV/115 kV Substation expansion looping onto NRS-San Jose B 230 kV Line |  |  | San Jose, Santa Clara | Capacity Upgrade: • Trimble 230 kV/115 kV Substation expansion looping onto NRS-San Jose B 230 kV Line | Substation - Multiple | Upgrade/Retrofit | NA | T.0010908 | Load Growth | Substation Capacity | NERC TPL Standards | NA | 2026-02-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2309 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX138957 | TBD | Trimble 230 kV/115 kV Substation expansion looping onto NRS-San Jose B 230 kV Line | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-05-01 | 2031-05-01 | 2033-12-01 | Resources | NA | FALSE | 276000 | NA ¦ NA | 0 | 114000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 18000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
492 | Third 230 kV/115 kV transformer at Eastshore |  |  | Hayward, Alameda | Capacity Upgrade: • Partial 230 kV BAAH bay at Eastshore 230 kV and a third 230 kV/115 kV transformer | Substation - Transformer | New | NA | NA | Load Growth | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.9849 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX138967 | TBD | Third 230 kV/115 kV transformer at Eastshore | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-05-01 | 2031-05-01 | 2033-12-01 | Resources | NA | FALSE | 371000 | NA ¦ NA | 0 | 24500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3250 | 3750 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
493 | MORAGA 230kV Bus #1 &2 Bus Redundant Relay |  |  | Orinda, Contra Costa | As done on previous upgrades, GE recommends that all relay cards be removed and later version cards for 7.2x be installed. he overview of the program is a s follows: • GE relays with firmware versions of 3 and below, are no longer supported by GE. • GE released service bulletin GER-4654A to address this vulnerably. • GE Multilin UR / URPlus / B95Plus Protection Relay Cryptographic Algorithm o UR relays below firmware 5.83 have the possible susceptibility. o Some relays such as firmware versions 3.x and 4.x are not provided firmware updates by GE and no upgrade to eliminate the vulnerability is available. o The remainder of relays with firmware family’s 5.x and 6.x will be evaluated for potential upgrade when GE relays are scheduled for regular relay maintenance according to SAP relay scheduled work • We can capitalize on the maintenance outage cycle – replace these relays during maintenance. o Will need to do full replacements due to new designs on equipment. Chassis is same size, but conversion settings are required, will need to put together instructions, etc. o 88 relays that are at Medium NERC sites o Program will be completed in 6 Years • Will need to get Automation involved as they were polling some of these devices for SCADA. | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 15.8714 | NA | 230 kV | NA | NA | NA | 3.0011 | Non-IGP | EX112160 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-09-01 | NA | 2028-12-31 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 6000 | 2000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
494 | RECOND. SAN MIGUEL-PASO ROBLES 70KV PH.1 |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Transmission Line - Conductor | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2025-07-28 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 6 | NA | 70 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767231 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ 5757620 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Construction (50%-75%) | 2 | 2025-11-13 | 2019-05-01 | 2026-04-22 | Prioritization | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 18714.8727 | 20413.1182 | 4.6013 | 218.9252 | 3537.2202 | 1967.8203 | 6301.975 | 8052.4905 | 157.5382 | 163.9298 | 0 | 0 | 12039.1597 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
495 | ESTRELLA_CPUC LIC/PER |  |  | NA | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Other | New | NA | NA | Reliability | T-Line Capacity | NERC TPL Standards | NA | NA | 17 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | 230 ¦ 70 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767230 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ 5757620 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering less than 50% complete | 4 | NA | 2019-05-01 | 2028-01-28 | Prioritization | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 1679.8473 | 2925.5469 | 2245.3985 | 6944.1063 | -27721.5643 | 380.8222 | 357.9277 | 524.6354 | 491.7283 | 312.883 | 0 | 0 | 1596.3003 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
496 | MORRO BAY - CAL FLATS 230KV LINE SHOOFLY |  |  | El Paso de Robles, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Transmission Line - Conductor | New | NA | NA | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-03-03 | 70 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion ¦ Flooding |  | 0.1 | 1.6272 | 230 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5771718 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ 5757620 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2018 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-01-04 | 2019-05-01 | 2027-03-31 | Prioritization | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 122.8807 | 907.9767 | 41.9105 | 39.5365 | 14.4304 | 15.7343 | 2.8291 | 357.5181 | 429.5861 | 0 | 0 | 0 | 120.8725 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
497 | MORRO BAY-CAL FLATS 230KV INTERCONNECTIO |  |  | El Paso de Robles, San Luis Obispo ¦ Fresno ¦ Kings ¦ Monterey ¦ San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Transmission Line - Conductor | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2026-04-07 | 71 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.1 | NA | 230 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767208 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ 5757620 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-02-09 | 2019-05-01 | 2028-05-26 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 1454.9216 | 9262.9352 | 162.0752 | 163.2229 | 178.6983 | 89.1682 | 53.2747 | 1587.8554 | 5950.8489 | 303.755 | 0 | 0 | 1420.4759 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
498 | UNION-SAN MIGUEL_PASO ROBLES 70KV - EST |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Transmission Line - Conductor | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2025-07-28 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 21 | NA | 70 | NA | 61 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5771719 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ 5757620 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2020 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-10-19 | 2019-05-01 | 2029-01-31 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 11872.8407 | 37956.3033 | 0.3821 | 1.9285 | 9290.0459 | 1187.731 | 1209.8249 | 1214.7414 | 3124.5601 | 14670.4779 | 7224.9118 | 31.5891 | 11690.0229 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
499 | UNION-SAN MIGUEL_PASO ROBLES 70KV - ENG |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2025-07-28 | 98 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion ¦ Flooding |  | 21 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5806384 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-10-19 | 2019-05-01 | 2029-01-31 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 6037.3099 | 21764.7177 | 0 | 0 | 4585.8925 | 618.5465 | 742.6716 | 1193.7002 | 7136.1535 | 5196.5527 | 2291.2008 | 0 | 5947.1106 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
500 | ROW UNION-SAN MIGUEL_PASO ROBLES 70KV |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Transmission Line - Conductor | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2025-07-28 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 21 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5554011 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Programmatic Work | NA | NA | 2019-05-01 | OAI | NA | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 244.5971 | 4067.1576 | 0 | 0 | 0 | 92.8901 | 151.498 | 492.0421 | 3060.2729 | 270.4545 | 0 | 0 | 244.3881 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 92.8901 | 151.498 | 0.209 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
501 | RECONDUCTOR KERN PP_STOCKDALE 230KV |  |  | Bakersfield, Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Transmission Line - Conductor | New | NA | T.0000220 ¦ T.0000144 | Reliability | New T-Line | NERC TPL Standards | NA | 2025-10-15 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.25 | NA | 230 ¦ 115 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767236 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 60 | NA ¦ 5756004 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-05-16 | 2020-05-01 | 2031-06-06 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 402.0709 | 17333.5993 | 0 | 0 | 0 | 141.0849 | 224.2994 | 249.7915 | 486.1617 | 572.789 | 5162.3434 | 9230.1091 | 372.7778 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
502 | VOLTAGE UPGRADE STOCKDALE_ LAMONT 115KV |  |  | Bakersfield, Kern ¦ East Niles CDP, Kern ¦ Fairfax CDP, Kern ¦ Fuller Acres CDP, Kern ¦ Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-03-17 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 18.23 | NA | 115 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767235 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 60 | NA ¦ 5756004 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-03-12 | 2020-05-01 | 2032-03-24 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 235.5948 | 27060.9736 | 0 | 0 | 0 | 64.6779 | 144.6435 | 229.8428 | 472.9094 | 391.8958 | 868.5331 | 18607.8726 | 215.7913 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
503 | VOLTAGE UPGRADE WHEELER RIDGE_LAMONT 115 |  |  | Bakersfield, Kern ¦ Fuller Acres CDP, Kern ¦ Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2025-11-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 19.65 | NA | 115 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767234 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 60 | NA ¦ 5756004 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2032-10-29 | 2020-05-01 | 2034-04-25 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 346.399 | 69566.8812 | 0 | 0 | 0 | 78.0715 | 219.4031 | 389.4657 | 1154.9409 | 3380.5547 | 4095.1615 | 3212.833 | 304.5705 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
504 | WRJ NONCOMPETITIVE_CPUC LIC/PER |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Other | New | NA | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.403 | 230 ¦ 115 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767233 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 60 | NA ¦ 5756004 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-05-01 | 2020-05-01 | 2034-04-26 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 17790.3868 | 34703.3571 | 399.3553 | 0 | 0 | 1260.8254 | 2223.2688 | 2466.5086 | 1807.923 | 1937.9948 | 2000.5237 | 1915.3753 | 17388.616 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
505 | Purchase Land for New Transmission Line |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Other | New | NA | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.403 | NA | NA | 236 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.1001 | Non-IGP | 5523422 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Planning | 5 | NA | 2020-05-01 | 2029-05-09 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
506 | W R -WEEDPATCH (9/119 - WR) |  |  | Bakersfield, Kern ¦ Kern ¦ Weedpatch CDP, Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2025-11-26 | 73 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 22.4 | NA | 70 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | 490 | 5.1001 | Non-IGP | 5773278 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2019 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Planning | 5 | 2032-10-29 | 2020-05-01 | 2033-04-25 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 26.807 | 2968.7721 | 0 | 0 | 0 | 13.008 | 3.7645 | 2.6989 | 2.0602 | 2.2112 | 2.3732 | 2.5472 | 25.7311 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
507 | RECONDUCTOR STOCKDALE_MAGUNDEN 115KV |  |  | Bakersfield, Kern ¦ Fuller Acres CDP, Kern ¦ Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2025-11-11 | 124 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 6 | NA | 115 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767237 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 60 | NA ¦ 5756004 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Planning | 5 | 2030-03-07 | 2020-05-01 | 2033-12-21 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 37.776 | 115.441 | 0 | 0 | 0 | 16.5528 | 6.4848 | 3.2753 | 2.8934 | 3.1054 | 3.3331 | 3.5774 | 36.7603 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
508 | Loop HZ1 into Egbert Sw. Stat |  |  | Brisbane, San Mateo ¦ Daly City, San Mateo ¦ San Francisco, San Francisco | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Transmission Line - Conductor | Relocate | NA | T.0008764 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-03-26 | 52 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 7.5 | NA | 230 | NA | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | 3.0011 | Non-IGP | 5767213 | T.0000159 | Egbert 230kV Switching Station | 10 | 60 | NA ¦ 5763199 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Engineering more than 50% complete | 3 | 2027-12-06 | 2021-12-01 | 2028-10-12 | Prioritization | NA | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 4015.3552 | 49542.9535 | 219.9909 | 760.7488 | 866.5053 | 566.9816 | 273.383 | 3412.8595 | 289.1415 | 10352.9871 | 8409.3191 | 3371.5908 | 3946.6935 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil
509 | REROUTE JEFFERSON_MARTIN 230KV |  |  | Millbrae, San Mateo ¦ San Bruno, San Mateo ¦ San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Transmission Line - Conductor | Relocate | NA | T.0008764 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-03-20 | 19 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 3.5 | NA | 230 | NA | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | 3.0011 | Non-IGP | 5767217 | T.0000159 | Egbert 230kV Switching Station | 10 | 60 | NA ¦ 5763199 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Engineering more than 50% complete | 3 | 2027-02-03 | 2021-12-01 | 2028-10-27 | Prioritization | NA | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 32222.2331 | 97982.6147 | 790.8575 | 21258.0216 | 10929.1741 | 626.0773 | -2960.1301 | 5291.1336 | 0 | 39.6495 | 67.6609 | 41039.5321 | 31771.8472 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil
510 | Wilson 115kV STATCOM T-Line Relocation |  |  | Brentwood, Contra Costa ¦ Contra Costa | Install a 115kV +100/-100 Mega Volt-Ampere reactive (MVAR) voltage control system (STATCOM) at Wilson Substation. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2025-08-25 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | 318 | 8. Compliance/Commitments With Low Safety Risk | 7 | NA | NA | 5773698 | T.0001381 | Wilson 115kv STATCOM | 2 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2019 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-07-01 | 2020-05-01 | 2021-03-30 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 1004.379 | 1004.379 | 24.3053 | 1.0972 | 0.0491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.379 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 785.7605 | 0.85318 | 0.03786 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
511 | Wilson Transmssion Line Work |  |  | Merced ¦ Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0001381 ¦ T.0002231 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2025-05-28 | 71 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 230 ¦ 115 | NA | 58 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5783478 | T.0004116 | WILSON: 115 kV ARP - BAAH | 7 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-01-13 | 2015-05-01 | 2028-10-26 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 172.9222 | 14619.4888 | 0.6286 | 0 | 0 | 15.1784 | 118.4367 | 234.7763 | 2300 | 2300 | 2300 | 2300 | 169.6448 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil
512 | North Tower 115kV Looping |  |  | Vallejo, Solano | This project proposes to loop North Tower Substation into the Martinez-Sobrante 115 kV Line by utilizing an idle 115 kV line into North Tower and reconfiguring the connection points at Martinez JCT. This project is needed to provide transmission capacity to serve customers in the North Bay Division. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2026-03-09 | 60 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 5.8111 | 115 | NA | NA | 8. Compliance/Commitments (But Low Safety Risk) | NA | 3.0011 | Non-IGP | 5816702 | T.0004418 | North Tower 115 kV Looping Project | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2022 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-11-16 | 2015-05-01 | 2029-12-17 | Prioritization | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 4.5173 | 8474.5408 | 0 | 0 | 0 | 0 | 0.5284 | 426.7817 | 0 | 0 | 0 | 0 | 0.5284 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
513 | North Tower 115kV Looping |  |  | Vallejo, Solano | This project proposes to loop North Tower Substation into the Martinez-Sobrante 115 kV Line by utilizing an idle 115 kV line into North Tower and reconfiguring the connection points at Martinez JCT. This project is needed to provide transmission capacity to serve customers in the North Bay Division. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2026-03-09 | 60 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 5.8111 | 115 | NA | NA | 8. Compliance/Commitments (But Low Safety Risk) | NA | 3.0011 | Non-IGP | 5816527 | T.0004418 | North Tower 115 kV Looping Project | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2022 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-11-28 | 2015-05-01 | 2029-12-26 | Prioritization | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 5.7111 | 15631 | 0 | 0 | 0 | 0 | 0 | 730.8059 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
514 | Newark - HVDC Connection - TLine |  |  | Fremont, Alameda | The Newark – NRS HVDC project is modified to Newark – NRS 230 kV project. No HVDC converters or lines are required in the modified scope and the modified scope includes only a high capacity 230 kV AC line (1,000 MVA) from PG&E’s Newark substation to Silicon Valley Power’s (SVP’s) NRS substation. | Transmission Line - Conductor | New | NA | NA | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | 8.75 | 27.7611 | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5806599 | T.0009168 | Newark - HVDC Connection | 2 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-10-12 | 2028-06-01 | 2027-05-28 | NA | NA | TRUE | $325,000 ¦ $510,000 | NA ¦ NA | 82.7343 | 1770.0515 | 0 | 0 | 34.0988 | 33.4304 | 14.2199 | 1172.046 | 516.2564 | 0 | 0 | 0 | 81.7491 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 67.5292 | 81.749 | 82.7343 | 0% ¦ LS Power, San Jose Area HVDC 230 kV Line (Newark - NRS) | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
515 | San Jose B - HVDC Connection - TLine |  |  | San Jose, Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Transmission Line - Conductor | New | NA | T.0003803 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.1 | 2.1017 | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5806625 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7391-E | 2024-10-10 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-07-06 | 2028-06-01 | 2027-12-31 | NA | NA | TRUE | $425,000 ¦ $615,000 | NA ¦ NA | 284.7413 | 7964.6111 | 0 | 0 | 31.8588 | 41.9981 | 146.7458 | 181.7785 | 6255.1849 | 1254.415 | 52.6302 | 0 | 220.6027 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 73.8569 | 220.6027 | 284.7413 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
516 | Loop Vaca Dixon-Tesla in Collinsville |  |  | Alameda ¦ Byron CDP, Contra Costa ¦ Contra Costa ¦ Discovery Bay CDP, Contra Costa ¦ Knightsen CDP, Contra Costa ¦ Oakley, Contra Costa ¦ Sacramento ¦ Solano ¦ Vacaville, Solano | This project will support connection of a new 500kV substation between Vaca Dixon and Tesla Substations to the PG&E electric system. The new 500kV substation (named Collinsville), to be installed by the third-party entity (LS Power), is needed to address a number of identified transmission constraints and provide an additional supply from the 500kV system into the northern Greater Bay Area, to increase reliability to the area and advance additional renewable generation in the northern area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Vaca Dixon – Tesla 500kV line into the new 500kV Collinsville substation and build the associated transmissioin line. • Modify Vaca Dixon 500kV Series Capacitor Bank 2 reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Connect two 230kV lines to Pittsburg 230kV bus in separate bus sections and install 115kV bus reactors in bus sections D&E. • Upgrade line protection of Tesla 500kV line at Tesla substation as needed | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004581 | Policy | T-Line Capacity | NERC TPL Standards | NA | 2025-12-10 | NA | Steady State Power Flow System Analysis | Wires - System Configuration Alternative | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 500 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5804858 | T.0009189 | New Collinsville 500kV Sub Connection Pr | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-09-16 | 2028-01-01 | 2028-05-30 | NA | NA | FALSE | $475,000 ¦ $675,000 | NA ¦ NA | 2188.4391 | 42094.9934 | 0 | 0 | 113.7176 | 1071.2042 | 931.4508 | 5886.0796 | 17099.1299 | 16535.8524 | 457.5589 | 0 | 2116.3726 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 1184.9218 | 2116.3726 | 2188.4391 | 0% ¦ LS Power, New Collinsville 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
517 | Loop Los Ban-Gates#1 & Los Bano-Mid#2 |  |  | Fresno ¦ Merced | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0009550 | Policy | T-Line Capacity | NERC TPL Standards | NA | 2025-09-22 | 59 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | NA | 500 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5804800 | T.0009194 | Manning New 500kV Sub Connection | 18 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-12-14 | 2028-01-01 | 2028-06-01 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 1162.0432 | 27737.0069 | 0 | 0 | 85.5375 | 353.19 | 586.7535 | 2458.79 | 22211.0423 | 2041.6936 | 0 | 0 | 1025.481 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 438.7275 | 1025.481 | 1162.0432 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
518 | Loop 2 Panoche-Tranq lines in Manning |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0009550 | Policy | T-Line Capacity | NERC TPL Standards | NA | 2025-08-18 | 79 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5804801 | T.0009194 | Manning New 500kV Sub Connection | 18 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2027-05-06 | 2028-01-01 | 2028-06-01 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 895.898 | 17268.0301 | 0 | 0 | 75.1229 | 309.1118 | 449.0092 | 1054.9759 | 15171.306 | 208.5043 | 0 | 0 | 833.2439 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 384.2348 | 833.2439 | 895.898 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
519 | RECONDUCTOR 230KV MANNING -TRANQUILITY#1 |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Transmission Line - Conductor | New | NA | T.0009550 | Policy | T-Line Capacity | NERC TPL Standards | NA | 2025-08-18 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 24.3 | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5804811 | T.0009194 | Manning New 500kV Sub Connection | 18 | 60 | NA ¦ EX113203 ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-07-13 | 2028-01-01 | 2028-06-01 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 1828.3284 | 55372.9069 | 0 | 0 | 50.226 | 653.4546 | 836.6131 | 24194.1618 | 28715.4665 | 922.985 | 0 | 0 | 1540.2938 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 701.6937 | 1540.2937 | 1828.3284 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
520 | PLAINFIELD SUB - RELOCATE TSPS T-LINE |  |  | Hartley CDP, Solano ¦ Monument Hills CDP, Yolo ¦ Solano ¦ Winters, Yolo ¦ Woodland, Yolo ¦ Yolo | The California ISO’s 2018-2019 Transmission Planning Process (TPP) has identified the need for the Vaca – Dixon Area Reinforcement Project. This project will mitigate overloads and voltage criteria violations in the 115kV and 60kV transmission systems among Vaca Dixon, Davis, Rio Oso and Brighton Substations. The project will include the following work: 1. Install two 5.0 MVAR capacitor banks at Plainfield Substation. 2. Replace Vaca Dixon 115/60kV Bank 5 with a larger unit. 3. Replace the limiting elements on the 60kV equipment at Dixon Substation. 4. Re-rate the Woodland - Davis 115kV Line and the Rio Oso - West Sac 115kV Line. 5. Modify the existing special protection schemes (SPS) or add new SPS’s to trip load for select multiple contingencies. | Transmission Line - Pole/Tower | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-11-14 | 66 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5785807 | T.0000007 | Vaca Dixon Area Reinforcement Project | 7 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2022 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2024-07-17 | EIR | NA | CPUC | NA | PTC: A.24-06-008 | 2024-06-28 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 3 | 2027-03-08 | 2023-12-01 | 2027-05-13 | Prioritization | NA | TRUE | $70,000 ¦ $107,000 | NA ¦ NA | 1095.6036 | 5653.8515 | 0 | 16.4884 | 338.2082 | 230.113 | 443.0739 | 1233.9893 | 3391.9786 | 277.424 | 0 | 0 | 1027.8836 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
521 | RERATE WOODLAND - DAVIS T-LINE |  |  | Davis, Yolo ¦ Woodland, Yolo ¦ Yolo | The California ISO’s 2018-2019 Transmission Planning Process (TPP) has identified the need for the Vaca – Dixon Area Reinforcement Project. This project will mitigate overloads and voltage criteria violations in the 115kV and 60kV transmission systems among Vaca Dixon, Davis, Rio Oso and Brighton Substations. The project will include the following work: 1. Install two 5.0 MVAR capacitor banks at Plainfield Substation. 2. Replace Vaca Dixon 115/60kV Bank 5 with a larger unit. 3. Replace the limiting elements on the 60kV equipment at Dixon Substation. 4. Re-rate the Woodland - Davis 115kV Line and the Rio Oso - West Sac 115kV Line. 5. Modify the existing special protection schemes (SPS) or add new SPS’s to trip load for select multiple contingencies. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-04-01 | 123 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 11.7 | NA | 115 | NA | 137 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5766694 | T.0000007 | Vaca Dixon Area Reinforcement Project | 7 | 60 | NA ¦ 5738753 ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2016 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7542-E | 2025-03-12 | Approved | 2025 | Operational | 1 | 2025-09-26 | 2023-12-01 | 2025-11-13 | Prioritization | NA | TRUE | $70,000 ¦ $107,000 | NA ¦ NA | 4679.7685 | 4805.971 | 104.3332 | 71.199 | 188.4017 | 523.6159 | 3179.954 | 208.5042 | 0 | 0 | 0 | 0 | 4597.4668 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 4240.3939 | 75.2233 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
522 | KERN 230 KV AREA REINFORCEMENT (TLINE) |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 37.7504 | 230 | NA | 764 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767328 | T.0000204 | Kern 230kV Bus Upgrade | 13 | 60 | NA ¦ 5748541 ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-10-22 | 2013-05-01 | 2021-03-29 | Prioritization | NA | FALSE | $32,000 ¦ $44,000 | NA ¦ NA | 3493.8506 | 3493.8506 | 169.7584 | 4.7196 | 3.6543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3493.8506 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 3487.1129 | 4.7196 | 3.6543 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
523 | KERN 230 KV AREA REINFORMCEMENT (TLINE) |  |  | Bakersfield, Kern ¦ Kern ¦ Oildale CDP, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-03-04 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | NA | 230 | NA | 764 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767359 | T.0000204 | Kern 230kV Bus Upgrade | 13 | 60 | NA ¦ 5748541 ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-12-12 | 2013-05-01 | 2021-03-29 | Prioritization | NA | FALSE | $32,000 ¦ $44,000 | NA ¦ NA | 4582.5096 | 4582.5096 | 373.0205 | 6.7546 | 4.4216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4582.5096 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 4573.8166 | 6.7545 | 4.4216 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
524 | Lodi Sub: 60 kV T-Line Rearrangement |  |  | Lockeford CDP, San Joaquin ¦ Lodi, San Joaquin ¦ San Joaquin ¦ Victor CDP, San Joaquin | This project will replace all 60kV circuit breakers, 60kV Main and Auxiliary bus structure and the associated equipment at Lodi Substation.The replacement criteria were developed based on technical assessments of the switches including design characteristics, system criticality, historical failure rates, onsite inspections, vintage, environmental factors, and operating conditions. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Asset Condition | System Design Upgrade | NA | NA | 2025-11-20 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | 48 | 8. Compliance/Commitments With Low Safety Risk | NA | 3.0011 | Non-IGP | 5774920 | T.0000303 | LODI SUB: REPL CB 12, 22 AND 32 | 2 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-12-10 | 2019-10-17 | 2021-01-14 | Clearances | NA | FALSE | 7215 | NA ¦ NA | 2185.8307 | 2185.8307 | 418.6112 | 376.9374 | 41.5102 | 27.35 | 0 | 0 | 0 | 0 | 0 | 0 | 2185.8307 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 1533.5626 | 330.8741 | 36.4349 | 24.0059 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
525 | VIERRA ACQUIRE PERM LAND RIGHTS |  |  | Lathrop, San Joaquin ¦ San Joaquin ¦ Tracy, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other | New | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-08-29 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | NA | 5527666 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2021 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2020-10-16 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Operational | 1 | 2024-11-01 | 2014-05-01 | 2025-02-23 | Prioritization | NA | TRUE | $10,000 ¦ $15,000 | NA ¦ NA | 1685.4127 | 1919.9127 | 246.792 | 291.0599 | 585.7096 | 0 | 0 | 256.813 | 0 | 0 | 0 | 0 | 1663.0997 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 246.7919 | 291.0599 | 585.7096 | 0 | 0 | 22.313 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
526 | VIERRA 115KV TLINE RECONFIGURATION |  |  | Lathrop, San Joaquin ¦ San Joaquin ¦ Tracy, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Transmission Line - Multiple | Upgrade/Retrofit | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-08-29 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5805561 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2024 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2020-10-16 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Operational | 1 | 2025-10-01 | 2014-05-01 | 2025-11-24 | Prioritization | NA | TRUE | $10,000 ¦ $15,000 | NA ¦ NA | 295.1152 | 642.4977 | 0 | 0 | 0 | 10.9966 | 254.5989 | 330.2462 | 0 | 0 | 0 | 0 | 265.5955 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 217.2657 | 24.0507 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
527 | Pease Transformer Addition - T Line |  |  | Sutter | Install a second 115/60kV transformer and upgrade the 115kV and 60kV buses at Pease Substation. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2026-02-10 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.6809 | 115 | NA | 76 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5771838 | T.0000598 | Pease Transformer Add & Bus Upgrade | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2018 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-10-30 | 2016-05-31 | 2020-12-10 | Material | NA | FALSE | $25,000 ¦ $35,000 | NA ¦ NA | 2466.9077 | 2466.9077 | 366.172 | 82.4473 | 1.9617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2466.9077 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 352.7643 | 79.4259 | 1.8898 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $50 Mil – $75 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
528 | Rio Oso Sub: T-Line Re-String Conduc |  |  | Lincoln, Placer ¦ Placer ¦ Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-11-02 | 71 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | 1782 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5777058 | T.0000614 | Rio Oso Substation Upgrade | 12 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-29 | 2009-05-01 | 2025-05-09 | Prioritization | NA | TRUE | $10,000 ¦ $20,000 | NA ¦ NA | 1859.8474 | 2460.0458 | 390.9557 | 262.9666 | 86.1491 | 902.3398 | -302.9271 | 706.1959 | 2.4155 | 0 | 0 | 0 | 1751.4344 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 1723.4769 | 106.2751 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
529 | CASCADE: Support Tline Configuration |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2026-02-16 | 25 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | 115 | NA | 58 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.1001 | Non-IGP | 5780281 | T.0000651 | Cascade Substation Upgrade | 10 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2019-10-01 | 2014-03-01 | 2026-04-30 | Prioritization | NA | TRUE | $20,000 ¦ $30,000 | NA ¦ NA | 3397.848 | 3552.5221 | 190.2037 | 143.1207 | 332.7432 | 444.8216 | 603.7796 | 203.5543 | 0 | 0 | 0 | 0 | 3348.9678 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
530 | Evergreen Sub Upgrade: T-Line |  |  | San Jose, Santa Clara ¦ Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Transmission Line - Multiple | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-10-28 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 3.0011 | Non-IGP | 5549360 | T.0001685 | Evergreen Substation Upgrade | 7 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-11-01 | 2018-05-21 | 2023-11-16 | Prioritization | NA | FALSE | 27200 | NA ¦ NA | 642.9467 | 642.9467 | 0 | 98.1214 | 540.59 | 4.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 642.9467 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 83.0763 | 457.7002 | 3.5859 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
531 | Lerdo-Kern Oil-7th Standard 115kV Rerate |  |  | Bakersfield, Kern ¦ Kern ¦ Oildale CDP, Kern | The Project proposes to reconductor approximately 38 circuit miles of various 115 kV lines serving Bakersfield area in Kern County. The scope of the project include reconductoring 3.8 miles of the Kern PP-Westpark Nos. 1 and 2 115 kV Lines; 16.5 miles of the Kern-Magunden-Witco 115 kV Line; 3.5 miles of the Westpark-Magunden 115 kV Line; 5.0 miles of the Kern-Lamont 115 kV Line from Kern PP to Tevis Jct.; 5.0 miles of the Kern-Stockdale 115 kV line from Kern PP to Tevis Jct. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2025-10-22 | 125 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 16.3 | NA | 115 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 881 | 5.1001 | Non-IGP | 5784386 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 8 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Planning | 5 | 2029-03-23 | 2016-03-01 | 2029-05-24 | Prioritization | NA | FALSE | $40,000 ¦ $65,000 | NA ¦ NA | 12.7635 | 2295.6974 | 0 | 0 | 0 | 10.6341 | 1.1472 | 0.1601 | 0 | 0 | 0 | 0 | 12.6034 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
532 | Five Points-Huron Gates SS TSP Line work |  |  | Fresno | This project proposes to install a new 70/12 kV 30 MVA transformer bank at Calflax Substation in order to prevent projected substantial overloads on Coalinga #2 Bank 1. To support the additional transformer bank at Calflax the existing 70 kV transmission tap that serves Calflax Bank 1 will be reconfigured into a four-element ring bus. In addition to the new transformer bank at Calflax Substation one new 12 kV circuit breaker and associated distribution work will be installed to serve the proposed additional 10 MW Tesla EV charging infrastructure load at Harris Ranch. | Transmission Line - Multiple | Upgrade/Retrofit | NA | NA | Load Growth | T-Line Capacity | NA | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.68286 | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5795148 | T.0003879 | Calflax Substation Bank 2 Installation | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-11-27 | 2023-02-08 | 2024-01-05 | Prioritization | NA | FALSE | 19400 | NA ¦ NA | 364.3218 | 364.3218 | 103.6395 | 28.6347 | 194.4258 | 27.8379 | 9.7838 | 0 | 0 | 0 | 0 | 0 | 364.3218 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 344.6419 | 9.4917 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
533 | Grant RAS Project |  |  | San Leandro, Alameda | Modify the existing San Leandro U Substation, which will include all the necessary requirements, including time of day and seasonal setting changes, iterative tripping, and ability to accommodate bypass scenarios. The main driver for this RAS is the ISO planning standard that does not allow for load tripping in Greater Bay Area as a high population density area. The New RAS will monitor the outages and flows on five critical lines in Moraga-Oakland J area and take corrective actions to resolve any overloads on these lines without dropping the load. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.6572 | 115 | NA | NA | NA | NA | 5.2 | Non-IGP | 5803540 | T.0004580 | San Leandro U: Ras Project | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-11-03 | 2022-09-30 | 2026-09-30 | Prioritization | NA | TRUE | 4000 | NA ¦ NA | 548.7933 | 908.2407 | 0 | 0 | 130.778 | 4.2535 | 285.2211 | 457.988 | 2.9181 | 0 | 0 | 0 | 420.2527 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
534 | San Ardo Tap: T-Line Voltage Support |  |  | Monterey | The project scope of work includes following: Install a 10 Mvar Shunt Capacitor at San Ardo Substation. This location has been revised due to space limitation at Oil Fields Substation. Convert San Ardo 60 kV bus into a ring-bus configuration; loop Coburn - Oil Fields #1 & #2 lines into the new ring bus and install the capacitor bank. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-07-21 | 63 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.05 | NA | 60 | NA | 76 | NA | NA | 4.01 | Non-IGP | 5791730 | T.0004889 | San Ardo: Oil Fields Voltage Support | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-05-17 | 2022-05-01 | 2030-09-25 | Prioritization | NA | FALSE | $7,000 ¦ $10,000 | NA ¦ NA | 82.8409 | 2848.4051 | 3.864 | 0 | 0 | 0 | 0 | 6.4902 | 500 | 1000 | 0 | 0 | 81.4001 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
535 | Replacement of 60KV T-line |  |  | Pittsburg, Contra Costa | This project will provide the capacity increase required to meet the new business loads coming into the area. The project scope will: • Reconfigure the 115 kV high side bus to a ring bus. • Replace Bank 1 with a 115/21 kV 75 MVA transformer. • Relocate existing Bank 3, 115/21 kV 30 MVA transformer to a new foundation compatible with 75 MVA bank for future upgrades. • Install three 21 kV feeders. • Install two 21/12 kV, 7500 kVA auto banks. • Reconfigure the existing BART Bank on the new 115 kV ring bus at Willow Pass substation. • Install Supervisory Control and Data Acquisition system for the new substation bank and breakers. • Install one new 60 kV transmission switch to interconnect structure 000/006 on Willow Pass-Contra Costa 60 kV and structure 015/281 on Christie-Willow Pass 60 kV at the corner of Willow Pass Road and Port Chicago Highway. • Remove sections of Willow Pass-Contra Costa 60 kV and Christie-Willow Pass 60 kV from the structures towards Willow Pass substation. • Install a new Microwave system from Willow Pass to Pittsburg to comply with redundancy requirements for the Set A and Set B protection relays. Execution of this project will improve the future capacity expansion, operational flexibility, and reliability of the Willow Pass substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Load Growth | System Design Upgrade | NA | NA | 2026-03-06 | 126 | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 0.72358 | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815739 | T.0005844 | Willow Pass Sub_Repl Willow Pass Bk1 | 10 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-01-04 | 2025-07-31 | 2027-01-12 | Scope Change | NA | TRUE | 42500 | NA ¦ NA | 1166.0059 | 2233.5582 | 0 | 0 | 0 | 0 | 1111.5486 | 392.8999 | 729.1096 | 0 | 0 | 0 | 1111.5486 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
536 | Banta Sub, Replace Bank 1 |  |  | San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Transmission Line - Conductor | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.54319 | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5798131 | T.0006962 | Banta: Repl Bk 1 & Inst 115kV Ring Bus | 8 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2022 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 2 | 2026-02-11 | 2024-12-31 | 2027-12-10 | Prioritization | NA | TRUE | 17500 | NA ¦ NA | 921.5447 | 2851.9398 | 0 | 0 | 132.4502 | 196.8025 | 521.3652 | 701.322 | 1001.4052 | 300 | 0 | 0 | 850.6179 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
537 | Kasson-Banta 60 kV Line Rerouting |  |  | San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Transmission Line - Conductor | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2024-11-15 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5810839 | T.0006962 | Banta: Repl Bk 1 & Inst 115kV Ring Bus | 8 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2022 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-11-12 | 2024-12-31 | 2024-11-18 | NA | NA | FALSE | 17500 | NA ¦ NA | 223.0358 | 223.0358 | 0 | 0 | 0 | 198.9836 | 24.0521 | 0 | 0 | 0 | 0 | 0 | 223.0358 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 185.6987 | 22.4392 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
538 | Banta 60 kV Dead Ending |  |  | San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Transmission Line - Other Equipment | Upgrade/Retrofit | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2024-11-15 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5558319 | T.0006962 | Banta: Repl Bk 1 & Inst 115kV Ring Bus | 8 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-11-08 | 2024-12-31 | 2024-12-19 | NA | NA | FALSE | 17500 | NA ¦ NA | 128.3761 | 128.3761 | 0 | 0 | 0 | 80.0485 | 48.3276 | 0 | 0 | 0 | 0 | 0 | 128.3761 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
539 | Carbona Sub, Replace Bank 2 |  |  | San Joaquin | Replace Carbona Transformer Bank 2 with a larger transformer, upgrade 60kV equipment, replace the Carbona Bank 1 foundation, replace the entire 12kV bus with switchgear, and establish a new distribution circuit outside of the substation. The capacity increase is needed to eliminate a 30 percent normal overload of Carbona Bank 1, a 33 percent normal overload of the Carbona 1104 distribution feeder, and a 38 percent normal overload of the Tracy 1102 distribution feeder. These overloads are forecasted to occur by summer 2022 and are the result of several large new business applications including Amazon and Home Depot warehouse-distribution centers. Transmission Substation Work (MWC 61) under this Project – Planning Order 5797580: • Install 60 kV main bus comprised of 2300Al bare conductor. • Install two 60 kV, 1200 A circuit breakers and associated disconnect switches. • Install one 60 kV, 1200 motor-operated air switch (MOAS) to sectionalize the 60 kV bus. • Install current and potential transformers and surge arresters as required for system protection. • Install 60kV control and protection racks inside the new switchgear building. | Transmission Line - Multiple | New | NA | NA | Load Growth | Transformer Addition/Replacement | NA | NA | 2025-11-24 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5797579 | T.0007094 | Carbona Substation Bank 2 Replacement | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-21 | 2023-09-30 | 2022-04-29 | NA | NA | FALSE | 32000 | NA ¦ NA | 467.7181 | 467.7181 | 51.0521 | 272.6941 | 27.9639 | 34.2982 | 81.7097 | 0 | 0 | 0 | 0 | 0 | 467.7181 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 257.129 | 21.8886 | 26.8468 | 63.9579 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
540 | Carbona Sub, 60kV Line Work |  |  | San Joaquin | Replace Carbona Transformer Bank 2 with a larger transformer, upgrade 60kV equipment, replace the Carbona Bank 1 foundation, replace the entire 12kV bus with switchgear, and establish a new distribution circuit outside of the substation. The capacity increase is needed to eliminate a 30 percent normal overload of Carbona Bank 1, a 33 percent normal overload of the Carbona 1104 distribution feeder, and a 38 percent normal overload of the Tracy 1102 distribution feeder. These overloads are forecasted to occur by summer 2022 and are the result of several large new business applications including Amazon and Home Depot warehouse-distribution centers. Transmission Substation Work (MWC 61) under this Project – Planning Order 5797580: • Install 60 kV main bus comprised of 2300Al bare conductor. • Install two 60 kV, 1200 A circuit breakers and associated disconnect switches. • Install one 60 kV, 1200 motor-operated air switch (MOAS) to sectionalize the 60 kV bus. • Install current and potential transformers and surge arresters as required for system protection. • Install 60kV control and protection racks inside the new switchgear building. | Transmission Line - Conductor | Relocate | NA | NA | Load Growth | System Design Upgrade | NA | NA | 2026-02-05 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.27151 | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5802121 | T.0007094 | Carbona Substation Bank 2 Replacement | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-11-17 | 2023-09-30 | 2025-05-16 | Prioritization | NA | TRUE | 32000 | NA ¦ NA | 1190.4565 | 1190.4565 | 0 | 144.9963 | 247.5129 | 320.5276 | 477.3038 | 0.1157 | 0 | 0 | 0 | 0 | 1190.3408 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1189.236 | 0.11563 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
541 | Ortiga Sub - Reroute 70 kV for new bank |  |  | Fresno ¦ Los Banos, Merced ¦ Merced | Ortiga Sub: Install one new 70/12 kV, 30 MVA three-phase transformer, four 70 kV breakers, one new 12 kV bus 1/bus 2 structure with four breaker bays, one bus-tie breaker and two circuit breakers, two new 12 kV distribution circuit outlets, and extend two new Ortiga distribution circuits to off-load existing Canal and Ortiga circuits and substation transformers. Transmission Substation Work (MWC 61) • Remove one 70 kW Motor Operated Air Switch 56 that protects existing Bank 1 • Install four 70 kV Circuit Breakers to create four-element ring bus with two 70 kV lines and two substation transformers. | Transmission Line - Multiple | New | NA | NA | Load Growth | System Design Upgrade | NA | NA | 2025-08-18 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5806925 | T.0007259 | Ortiga Sub - Install Bk 2 and 2 Circuits | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-08-10 | 2026-12-15 | 2026-11-19 | NA | NA | TRUE | 13300 | NA ¦ NA | 57.5131 | 326.5082 | 0 | 0 | 0 | 8.5561 | 45.0184 | 32.9918 | 239.9419 | 0 | 0 | 0 | 53.5744 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
542 | Ortiga T-Line Install New 1102 Circuit |  |  | Merced | Ortiga Sub: Install one new 70/12 kV, 30 MVA three-phase transformer, four 70 kV breakers, one new 12 kV bus 1/bus 2 structure with four breaker bays, one bus-tie breaker and two circuit breakers, two new 12 kV distribution circuit outlets, and extend two new Ortiga distribution circuits to off-load existing Canal and Ortiga circuits and substation transformers. Transmission Substation Work (MWC 61) • Remove one 70 kW Motor Operated Air Switch 56 that protects existing Bank 1 • Install four 70 kV Circuit Breakers to create four-element ring bus with two 70 kV lines and two substation transformers. | Transmission Line - Multiple | New | NA | NA | Load Growth | System Design Upgrade | NA | NA | 2025-09-15 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5562663 | T.0007259 | Ortiga Sub - Install Bk 2 and 2 Circuits | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-03-09 | 2026-12-15 | 2028-08-11 | Bundling Dependencies | NA | FALSE | 13300 | NA ¦ NA | 8.6419 | 818.0723 | 0 | 0 | 0 | 0 | 8.0591 | 140.9993 | 155.8472 | 0 | 0 | 0 | 8.0591 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
543 | Birds Landing-Contra Costa 230kV Swap |  |  | Antioch, Contra Costa ¦ Contra Costa ¦ Sacramento ¦ Solano | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-11-16 | 20 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5800030 | T.0008048 | Contra Costa PP Line Swaps | 9 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-01-08 | 2025-05-01 | 2025-05-29 | NA | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 2462.339 | 2465.2257 | 0 | 265.8149 | 464.1632 | 807.2039 | 921.6232 | 6.4205 | 0 | 0 | 0 | 0 | 2458.8052 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 2435.8327 | 3.4981 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
544 | Contra Costa-Lone Tree 230kV Swap |  |  | Antioch, Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-11-18 | 16 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence ¦ Corrosion |  | NA | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5800031 | T.0008048 | Contra Costa PP Line Swaps | 9 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-02-03 | 2025-05-01 | 2025-05-30 | NA | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 1703.5909 | 1703.9075 | 0 | 38.84 | 100.2092 | 589.4259 | 975.1159 | 0.3166 | 0 | 0 | 0 | 0 | 1703.5909 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1703.5909 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
545 | Contra Costa-Delta Yard Swap |  |  | Alameda ¦ Antioch, Contra Costa ¦ Brentwood, Contra Costa ¦ Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-09-03 | 45 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence ¦ Corrosion |  | NA | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5800032 | T.0008048 | Contra Costa PP Line Swaps | 9 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2026-01-19 | 2025-05-01 | 2026-02-24 | Workforce | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 1406.7343 | 1839.927 | 0 | 24.524 | 80.2305 | 594.0455 | 441.0857 | 700.0412 | 0 | 0 | 0 | 0 | 1139.8857 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 1393.8525 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
546 | Los Esteros T-Line Remote End |  |  | San Jose, Santa Clara | To address the near-term critical, category P1 contingency driven issues, the ISO is recommending approval of adding series compensation devices on the Los Esteros-Nortech 115 kV line. As part of this scope, 2 Ohms reactor will be added on the Los Esteros-Nortech 115kV Line at Los Esteros Substation. | Transmission Line - Other Equipment | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2025-10-22 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5808477 | T.0008698 | Los Esteros-Nortech 115kV Series Reactor | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-01 | 2023-06-01 | 2026-04-16 | Prioritization | NA | TRUE | $10,000 ¦ $15,000 | NA ¦ NA | 170.6679 | 935.1567 | 0 | 0 | 0 | 34.5342 | 101.8385 | 798.784 | 0 | 0 | 0 | 0 | 136.3727 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
547 | Los Banos: Rearrange 230kV T-line |  |  | Merced | Based on 2022 Short Circuit Analysis results and study plan , Los Banos 230 kV CBs 212, 222, 252, and 262 will be overstressed in 2030. Planning analyses show that the Los Banos 230 kV CBs 212, 222, 252 and 262 are projected to overload in 2030. Manning 500 kV Project has been added to 2023 TPP project list that contributes overstressed to Los Banos 230 kV CBs. • Replace 230 kV CBs 212, 222 in place with 3,000 Amps, 63 kA CBs, new SMP Relays. Foundations/structures may need to be replaced. • Replace 230 kV CBs 252, 262 with two (2) new BAAH Bays in the new BAAH bus section to meet the ultimate plan. New CBs will be 3,000 Amps, 63 kA CBs. Need T line relocations into new BAAH positions. | Transmission Line - Conductor | Relocate | NA | T.0009177 | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-09-25 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5817618 | T.0009550 | Los Banos: 230kV CB Overstress | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2026 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-22 | 2032-12-31 | 2028-12-28 | NA | NA | FALSE | 66000 | NA ¦ NA | 0.8144 | 243.0169 | 0 | 0 | 0 | 0 | 0.1249 | 62.9306 | 0 | 0 | 0 | 0 | 0.1249 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
548 | NEWARK DIST_82N_INSTALL NEWARK BANK 23 |  |  | Fremont, Alameda ¦ Milpitas, Santa Clara ¦ San Jose, Santa Clara | The project scope of work includes following: Substation Work: T.0010142.01: MAT 10R, Planning Order 5809764, OAA 74059542 Install Newark Bank 23, Extend 21 kV outdoor bus, Install 2112, 2113 and 2114 Circuit Breakers • Install Newark Bank 23, 75 MVA, 230/21kV substation transformer • Extend and build 21 kV bus structure • Install 21 kV, 1200A, 25kA feeder Breaker 2112 with protection package • Install 21 kV, 1200A, 25kA feeder Breaker 2113 with protection package • Install 21 kV, 1200A, 25kA feeder Breaker 2114 with protection package • Install 21 kV, 2000A, 25kA bank/bus tie Breaker 2200/2 with protection package • Required by 6/30/2026 T.0010142.02: MAT 82N, Planning Order 5809765, OAA 74059543 • Install new 230 kV circuit breaker • Required by 6/30/2026 Distribution Work: MAT 10Q Install Newark 2112, 2113 and 2114 circuits and extend circuits to three Primary Metering Sites • Required by Q2 2026 – Q2 2028 Associated switches and primary meters to be installed on New Business Orders 35486286, 35553914 and 35552721 Newark 2112 circuit: PO 5810760, OAA 35564690 - • Trench and install approximately 5,500 Feet of new 1100 AL cables in new 6’’conduits • Install 2 subsurface 3-Way, 3-Way switched 600A switches with new #7 enclosures Newark 2113 circuit: PO 5810761, • Trench and install approximately 12,000 Feet of new 1100 AL cables in new 6’’conduits • Install approximately 2,000 Feet of new 1100 AL cables in existing 6’’conduits • Install 4 subsurface 3-Way, 3-Way switched 600A switches with new #7 enclosures Newark 2114 circuit: PO 5810762, OAA 35564692 - • Trench and install approximately 6,500 Feet of new 1100 AL cables in new 6’’conduits • Install 4 subsurface 3-Way, 3-Way switched 600A switches with new #7 enclosures | Transmission Line - Pole/Tower | New | NA | NA | Load Growth | T-Line Capacity | NA | NA | 2025-08-18 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | NA | 230 | NA | NA | NA | NA | 5.301 | Non-IGP | 5558578 | T.0010142 | NEWARK DIST_INSTALL NEWARK BANK 23 | 2 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-05-28 | 2026-06-30 | 2026-06-30 | NA | NA | TRUE | 63700 | NA ¦ NA | 1031.5603 | 2941.5508 | 0 | 0 | 0 | 62.5444 | 868.6352 | 2009.6437 | 0.72747 | 0 | 0 | 0 | 931.1796 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 931.1796 | 100.3807 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
549 | SAN JOSE A - SUBSTATION REBUILD SYS DESG |  |  | San Jose, Santa Clara | This project proposes to rebuild San Jose A Substation into a substation capable of serving new load. The rebuild calls for one 115kV Breaker-and-a-Half (BAAH) GIS (Gas Insulated Switchgear) with fifteen (15) transmission circuit breakers. It will install two (2) distribution transformers, two (2) distribution switchgears, three (3) new 21kV feeders, and five (5) 12kV feeders. This AA will fund all pre-construction activities, including detailed engineering and cost estimating, substation design, project team meetings, job walkdowns and field verifications, contract execution support, permit applications, traffic control, long lead time materials, and civil site preparation. | Transmission Line - Multiple | Upgrade/Retrofit | NA | T.0011286 | Load Growth | System Design Upgrade | NA | NA | 2026-03-03 | 69 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.1997 | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811200 | T.0010465 | San Jose A -Substation rebuild | 2 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-01-25 | NA | 2028-11-07 | NA | NA | FALSE | NA | NA ¦ NA | 377.9269 | 8130.3525 | 0 | 0 | 0 | 63.5766 | 259.5489 | 315.8461 | 1332.4656 | 4081.8423 | 824.6322 | 30.071 | 323.1255 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
550 | FRENCH CAMP: 230KV TLINE LOOP TO FC SUB |  |  | Alameda ¦ Lathrop, San Joaquin ¦ Peters CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin ¦ Taft Mosswood CDP, San Joaquin ¦ Tracy, San Joaquin | Loop French Camp substation into Bellota-Tesla #2 230 kV line to add a new 230 kV bus at French Camp. The total length of transmission circuit is about 4.4 miles. Addressing overloads at Weber 60 kV line #2 (Weber - French Camp) starting in the near-term under NERC Category P1 contingencies | Transmission Line - Multiple | Upgrade/Retrofit | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-10-31 | 40 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5812673 | T.0010675 | French Camp Reinforcement | 2 | 60 | NA ¦ EX113699 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2031-11-03 | 2030-06-01 | 2033-11-17 | Prioritization | NA | FALSE | $42,100 ¦ $84,200 | NA ¦ NA | 254.0733 | 29855.5749 | 0 | 0 | 0 | 0 | 206.1635 | 499.4113 | 2200 | 4400 | 9900 | 11000 | 206.1635 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
551 | Distribution - Dixon Landing Repl Bk2 |  |  | Fremont, Alameda | This project proposes to upgrade existing Dixon Landing Bank 3 from 45 MVA bank to new 115/21 kV, 75 MVA bank; and extend the existing idled 21 kV Distribution feeder, Dixon Landing 2110. Dixon Landing Bank 2 is projected to be overloaded in 2027 by 6.5% (2.9 MW) due to ~20 MW of total requested load increases from multiple New Businesses in the City of Fremont. Upgrading Dixon Landing Bank 3 with a 75 MVA bank and extending the existing Dixon Landing 2110 feeder, will alleviate the overload on Dixon Landing Bank 2 and increase new capacity to serve future customers in the City of Fremont area. It will also improve service reliability, operating flexibility and allow for more emergency capacity. | Transmission Line - Multiple | Upgrade/Retrofit | NA | NA | Load Growth | Transformer Addition/Replacement | NA | NA | 2026-03-03 | 29 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.79979 | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | EX139351 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-10-01 | NA | 2028-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 500 | 500 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
552 | Distribution - New sub - Mariposa Rd |  |  | TBD | 230 kV Tline work related to potential new distribution substation for large load customer (near Stockton) | Transmission Line - Multiple | New | NA | NA | Load Growth | New Substation | NA | NA | NA | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | TBD | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | EX139353 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 11000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 3000 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
553 | Distribution - New sub - Johnson Canyon |  |  | TBD | 115 kV Tline work related to potential new distribution substation for large load customer (near Gonzales) | Transmission Line - Multiple | New | NA | NA | Load Growth | New Substation | NA | NA | NA | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | TBD | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | EX139355 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 11000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 3000 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
554 | Distribution - New substation - S Fresno |  |  | TBD | 115 kVTline work related to potential new distribution substation due to organic load growth (southern Fresno) | Transmission Line - Multiple | New | NA | NA | Load Growth | New Substation | NA | NA | NA | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | TBD | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | EX139358 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 11000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 3000 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
555 | COLEMAN-RED BLUFF RECONDUCTOR-PHASE I |  |  | Cottonwood CDP, Shasta | This project is revised scope of the original Cottonwood-Red Bluff No. 2 60 kV Line Project & Red Bluff 230/60 kV Substation Project. The new revised scope includes: Reconductor Coleman - Red Bluff 60 kV Line, section from Coleman to Red Bluff (Approx 19 miles) with 730 Amps emergency rating or higher. Also, Install sectionalizing breaker at Cottonwood 60 kV Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-19 | 25 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 48 | 26.1945 | 60 | NA | 137 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.1001 | Non-IGP | 5766750 | T.0000013 | Coleman - Red Bluff Project | 3 | 60 | NA ¦ 5738259 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7766-E | 2025-11-25 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-09-28 | 2021-12-01 | 2028-12-31 | Prioritization | NA | FALSE | $43,000 ¦ $57,000 | NA ¦ NA | 5583.9715 | 16011.3608 | 678.6917 | 403.12 | 295.9382 | 436.3388 | 787.1368 | 8563.2763 | 2000 | 0 | 0 | 0 | 5448.0845 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
556 | COLEMAN- RED BLUFF RECONDUCTOR-PHASE II |  |  | Gerber CDP, Tehama ¦ Los Molinos CDP, Tehama ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama ¦ Tehama, Tehama | This project is revised scope of the original Cottonwood-Red Bluff No. 2 60 kV Line Project & Red Bluff 230/60 kV Substation Project. The new revised scope includes: Reconductor Coleman - Red Bluff 60 kV Line, section from Coleman to Red Bluff (Approx 19 miles) with 730 Amps emergency rating or higher. Also, Install sectionalizing breaker at Cottonwood 60 kV Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-12-01 | 76 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 48.3 | NA | 60 | NA | NA | 5. Compliance/Commitments With Strong Safety Link | 65 | 5.1001 | Non-IGP | 5784598 | T.0000013 | Coleman - Red Bluff Project | 3 | 60 | NA ¦ 5738259 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2020 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7766-E | 2025-11-25 | Approved | 2025 | Engineering more than 50% complete | 3 | 2027-02-04 | 2021-12-01 | 2028-12-31 | Prioritization | NA | FALSE | $43,000 ¦ $57,000 | NA ¦ NA | 864.6073 | 20601.4844 | 238.8814 | 218.1229 | 35.1038 | 39.1803 | 282.4337 | 581.5108 | 18100 | 1100 | 0 | 0 | 819.9737 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
557 | Fulton-Fitch Mountain 60 kV Reconductori |  |  | Fulton CDP, Sonoma | Reconductor approximately 8 miles of the Fulton-Hopland 60kV Line and 1.3 miles of the Geysers 12-Fulton 230kV Line, rerate another section of the Fulton-Hopland 60kV Line and Fitch Mountain #2 60kV Tap, and upgrade switches and associated equipment at Fitch Mountain Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-11 | 51 | Steady State Power Flow System Analysis | Wires - System Configuration Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 8 | 13.4076 | 60 | NA | 490 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5735399 | T.0000039 | Fulton-Fitch Mtn 60kV Reconductor | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2014 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-10-11 | IS/MND | NA | CPUC | NA | PTC: A.15-12-005 | 2015-12-03 | Approved | 2017 | Operational | 1 | 2018-10-01 | 2013-05-01 | 2019-03-18 | Prioritization | NA | FALSE | 5000 | NA ¦ NA | 28267.9424 | 28267.9424 | 81.1073 | 17.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28267.9424 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 74.7722 | 16.4754 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
558 | Reconductor: Fitch Mtn #2 Tap |  |  | Healdsburg, Sonoma ¦ Sonoma | Reconductor approximately 8 miles of the Fulton-Hopland 60kV Line and 1.3 miles of the Geysers 12-Fulton 230kV Line, rerate another section of the Fulton-Hopland 60kV Line and Fitch Mountain #2 60kV Tap, and upgrade switches and associated equipment at Fitch Mountain Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2024-08-16 | 51 | Steady State Power Flow System Analysis | Wires - System Configuration Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.06 | NA | 60 | NA | NA | NA | NA | NA | NA | 5795385 | T.0000039 | Fulton-Fitch Mtn 60kV Reconductor | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2021 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-10-11 | IS/MND | NA | CPUC | NA | PTC: A.15-12-005 | 2015-12-03 | Approved | 2017 | Operational | 1 | 2021-09-09 | 2013-05-01 | 2021-10-06 | Prioritization | NA | FALSE | 5000 | NA ¦ NA | 242.7757 | 242.7757 | 239.8184 | 2.9572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242.7757 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 228.1696 | 2.8112 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
559 | Bellota-Warnerville Land Acq. |  |  | East Oakdale CDP, Stanislaus ¦ Oakdale, Stanislaus ¦ San Joaquin ¦ Stanislaus | Reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations. Key construction elements are as follows: • Replace 22.5 miles of the Bellota-Warnerville 230 kV circuit • Replace 19.9 miles of the Bellota-Cottle 230 kV circuit • Replace 2.5 miles of the Cottle-Melones 230 kV circuit • Replace 0.1 mile of the Warnerville-Wilson 230 kV circuit • Upgrade transmission line terminals at Bellota, Cottle, and Warnerville substations | Transmission Line - Right of Way | New | NA | NA | Policy | T-Line Capacity | NERC TPL Standards | NA | 2024-06-10 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5547482 | T.0000043 | Bellota-Warnerville 230kV Reinforcement | 8 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2021 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6047-E | 2021-01-06 | Approved | 2021 | Operational | 1 | NA | 2024-12-31 | 2023-04-28 | NA | NA | FALSE | 28000 | NA ¦ NA | 62.0527 | 62.0527 | 2.4693 | 40.4189 | 5.5451 | 13.6194 | 0 | 0 | 0 | 0 | 0 | 0 | 62.0527 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 42.899 | 5.5451 | 13.6194 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
560 | Warnerville-Bellota 230 kV line reconduc |  |  | East Oakdale CDP, Stanislaus ¦ Oakdale, Stanislaus ¦ San Joaquin ¦ Stanislaus | Reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations. Key construction elements are as follows: • Replace 22.5 miles of the Bellota-Warnerville 230 kV circuit • Replace 19.9 miles of the Bellota-Cottle 230 kV circuit • Replace 2.5 miles of the Cottle-Melones 230 kV circuit • Replace 0.1 mile of the Warnerville-Wilson 230 kV circuit • Upgrade transmission line terminals at Bellota, Cottle, and Warnerville substations | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2024-06-10 | 33 | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 23 | NA | 230 | NA | 318 | 8. Compliance/Commitments With Low Safety Risk | 1067 | 5.1001 | Non-IGP | 5756012 | T.0000043 | Bellota-Warnerville 230kV Reinforcement | 8 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2016 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6047-E | 2021-01-06 | Approved | 2021 | Operational | 1 | 2022-06-01 | 2024-12-31 | 2023-04-28 | NA | NA | FALSE | 28000 | NA ¦ NA | 78804.0396 | 78804.0396 | 1286.234 | 54985.3305 | 17193.1914 | 1330.6337 | 146.7724 | 0 | 0 | 0 | 0 | 0 | 78804.0396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 74177.666 | 1273.1826 | 140.4354 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
561 | Reconductor Bellota-Cottle 230 kV |  |  | East Oakdale CDP, Stanislaus ¦ Oakdale, Stanislaus ¦ San Joaquin ¦ Stanislaus | Reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations. Key construction elements are as follows: • Replace 22.5 miles of the Bellota-Warnerville 230 kV circuit • Replace 19.9 miles of the Bellota-Cottle 230 kV circuit • Replace 2.5 miles of the Cottle-Melones 230 kV circuit • Replace 0.1 mile of the Warnerville-Wilson 230 kV circuit • Upgrade transmission line terminals at Bellota, Cottle, and Warnerville substations | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2025-08-26 | 92 | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 45 | NA | 230 | NA | 318 | 5. Compliance/Commitments With Strong Safety Link | 498 | 5.1001 | Non-IGP | 5785878 | T.0000043 | Bellota-Warnerville 230kV Reinforcement | 8 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2016 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6047-E | 2021-01-06 | Approved | 2021 | Operational | 1 | 2023-11-01 | 2024-12-31 | 2024-03-31 | NA | NA | FALSE | 28000 | NA ¦ NA | 16757.0924 | 16757.0924 | 1.5763 | 3855.097 | 4702.4345 | 8194.0483 | -1.7449 | 0 | 0 | 0 | 0 | 0 | 16757.0924 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 15736.9492 | -1.6347 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
562 | Kingsburg-Lemoore 70 kV Line Reconduct |  |  | Armona CDP, Kings ¦ Fresno ¦ Hanford, Kings ¦ Kings ¦ Lemoore, Kings | The following work scope is required to complete the Kingsburg – Lemoore 70 kV Line Reconductoring Project:•Continue permitting and environmental activities.•Acquire temporary construction easements for pull and crane sites.•Procure long lead time materials in accordance with the construction schedule.•Complete approximately 8.3 miles of reconductoring.•Reconductor the line with a conductor capable of handling at least 742 Amps during emergency conditions.•To gain efficiencies, the substation scope of upgrading and relocation of the terminal equipment (Lemoore CB 12 and associated switches) will be completed as part of the Lemoore 70 kV Disconnect Switches project. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-22 | 16 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 8.3 | NA | 70 | NA | 564 | 8. Compliance/Commitments With Low Safety Risk | 609 | 3.0011 | Non-IGP | 5738261 | T.0000105 | KINGSBURG-LEMOORE 70KV RECONDUCTOR | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2015 | TBD | FALSE | 2019 | TBD | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5236-E | 2018-02-21 | Approved | 2018 | On Hold | 4 | 2032-11-09 | NA | 2033-03-09 | NA | NA | FALSE | NA | NA ¦ NA | 2717.0808 | 10432.8373 | 0 | 0 | 0 | 53.5796 | 44.4667 | 0 | 0 | 0 | 0 | 0 | 2717.0808 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
563 | NRS-Scott Transmission Line Work |  |  | Santa Clara, Santa Clara | Reconductor the NRS – Scott Nos. 1 and 2 Lines with a conductor having a capacity of at least 1,500 Amps. This project will reduce safety risk and improve service reliability. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-17 | 44 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 2 | NA | 115 | NA | 58 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5752089 | T.0000113 | NRS-SCOTT NO. 1 LINE RECONDUCTORING | 2 | 60 | NA ¦ 5767086 ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2014 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5325-E | 2018-07-03 | Approved | 2018 | Operational | 1 | 2019-01-14 | 2016-05-31 | 2019-02-25 | Prioritization | NA | FALSE | $2,000 ¦ $4,000 | NA ¦ NA | 6480.7572 | 6480.7572 | 6.5258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6480.7572 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 6.4334 | 1e-05 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
564 | East Shore-Oakland J 115 kV Reconductor |  |  | Alameda ¦ Hayward, Alameda ¦ San Leandro, Alameda ¦ San Lorenzo CDP, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-09 | 103 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 15 | NA | 115 | NA | 2167 | 8. Compliance/Commitments With Low Safety Risk | 425 | 5.1001 | Non-IGP | 5747763 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 60 | NA ¦ 5767363 ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2014 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E ¦ AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020 ¦ 2022 | Operational | 1 | 2021-06-01 | 2015-03-01 | 2023-09-13 | Prioritization | NA | FALSE | $15,000 ¦ $30,000 | NA ¦ NA | 49021.0449 | 49021.0449 | 21238.9048 | 8584.9668 | 12685.948 | 601.2897 | 261.9673 | 36.1872 | 0 | 0 | 0 | 0 | 48984.8577 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 46621.6606 | 524.3305 | 252.4592 | 34.8737 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil
565 | LEMOORE NAS 70 KV SCADA SW#55 65 |  |  | Fresno ¦ Kings ¦ Lemoore Station CDP, Kings ¦ Riverdale CDP, Fresno | Reconductor 25 circuit miles of 70 kV electric transmission lines between Caruthers, Camden and Lemoore Naval Air Station (NAS) Substations, construct a new 2 mile 70 kV line from Lemoore NAS to Henrietta Substation and upgrade protection at Henrietta Substation.. This project will increase transmission capacity, improve operational flexibility and service reliability, and modernize electric equipment for serving electric customers in Fresno and Kings County, resulting in increased customer satisfaction. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | T-Line Reliability | NA | NA | 2025-12-08 | 109 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | 318 | 8. Compliance/Commitments With Low Safety Risk | 455 | 5.1001 | Non-IGP | 5767093 | T.0000134 | LEMOORE NAS SCADA SW 55, 65 | 1 | 60 | NA ¦ 5734813 ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-03-12 | 2019-04-23 | 2027-03-28 | Prioritization | NA | TRUE | 3953 | NA ¦ NA | 5392.0113 | 5743.1998 | 419.918 | 544.0664 | 0 | 160.2721 | 414.1061 | 425.4418 | 0 | 0 | 0 | 0 | 5317.758 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $15 Mil - $20 Mil ¦ $20 Mil - $30 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
566 | METCALF - EVERGREEN RECONDUCTORING (TL) |  |  | San Jose, Santa Clara ¦ Santa Clara | The project work will involve upgrading the capacity of the Metcalf – Evergreen Nos. 1 and 2 115 kV Lines, so that both lines have an emergency rating of at least 1,100 Amps. Substation equipment at Metcalf and Evergreen will be upgraded, as needed. The proposed line reinforcement work will involve reconductoring these 115 kV lines with a conductor having an emergency capability of at least 1,100 Amps. Substation equipment will also be upgraded as needed to meet the capability of the new transmission line conductor. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-24 | 71 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 21.4 | NA | 115 | NA | 137 | NA | NA | NA | NA | 5767164 | T.0000147 | METCALF - EVERGREEN RECONDUCTORING (TL) | 2 | 60 | NA ¦ 5731270 ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2017 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5200-E | 2017-12-19 | Approved | 2018 | Operational | 1 | 2018-10-08 | 2019-05-21 | 2019-05-22 | NA | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 21873.0358 | 21873.0358 | 32.12 | -4.4324 | -205.8008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21873.0358 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 32.0735 | -4.4259 | -205.5013 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $40 Mil - $50 Mil
567 | REC SAN MIGUEL-PASO ROBLES 70KV PH.2 EST |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-07-28 | 98 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion ¦ Flooding |  | 6 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5805505 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-11-20 | 2019-05-01 | 2027-03-31 | Prioritization | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 4742.62 | 14340.0163 | 0 | 0 | 3129.3728 | 511.7149 | 834.6554 | 6744.7794 | 3116.8293 | 2.6645 | 0 | 0 | 4475.7432 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
568 | REC SAN MIGUEL-PASO ROBLES 70KV PH.2 ENG |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-07-28 | 98 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion ¦ Flooding |  | 6 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5810240 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2024 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-11-20 | 2019-05-01 | 2027-04-30 | Prioritization | Project Design | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 339.2282 | 3707.5016 | 0 | 0 | 0 | 0 | 273.1641 | 2973.6348 | 444.0927 | 16.61 | 0 | 0 | 273.1641 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
569 | ROW SAN MIGUEL-PASO ROBLES 70KV PH.1 |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Transmission Line - Right of Way | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2025-07-28 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion ¦ Flooding |  | 6 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5554009 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2024 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Programmatic Work | NA | NA | 2019-05-01 | OAI | NA | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 477.3745 | 477.3745 | 0 | 0 | 0 | 45.2482 | 432.1263 | 0 | 0 | 0 | 0 | 0 | 477.3745 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 45.2482 | 432.1263 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
570 | ROW SAN MIGUEL-PASO ROBLES 70KV PH. 2 |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Transmission Line - Right of Way | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2025-07-28 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion ¦ Flooding |  | 6 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5554010 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2024 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Programmatic Work | NA | NA | 2019-05-01 | OAI | NA | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 176.4636 | 1013.2596 | 0 | 0 | 0 | 3.629 | 112.8949 | 896.7356 | 0 | 0 | 0 | 0 | 116.524 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 3.629 | 112.8949 | 59.9396 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
571 | MERCY SPRINGS - CANAL SS T-LINE RECONDUT |  |  | Fresno ¦ Los Banos, Merced ¦ Merced | The Oro Loma 70 kV Area Reinforcement project will reconductor 70 kV lines in the Oro Loma area to help ensure reliable electric service to customers in the Merced County. The project will reconductor 2.4 miles of the Los Banos - Livingston Jct – Canal 70 kV Line, from Los Banos to Santa Nella substations and 10.8 miles of the Mercy Springs SW STA – Canal – Oro Loma 70 kV Line, from Mercy Springs SW STA to Canal Substation. The conductor should be capable of handling at least 825 Amps and 975 Amps during summer normal and emergency conditions, respectively. Associated substation terminal equipment will be upgraded as needed to meet the ratings of the new line conductor. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-18 | 73 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 10.8 | NA | 70 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | 578 | 5.1001 | Non-IGP | 5767240 | T.0000157 | Oro Loma 70kV Reinforcement | 7 | 60 | NA ¦ 5746746 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-10-12 | 2015-05-01 | 2027-12-30 | Prioritization | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 5955.9951 | 23352.0671 | 2609.703 | 27.6674 | 0 | 108.7557 | 935.0586 | 1921.6326 | 15489.4282 | 6200 | 0 | 0 | 5807.7045 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
572 | LOS BANOS-SANTA NELLA RECONDUCTOR |  |  | Los Banos, Merced ¦ Merced ¦ Santa Nella CDP, Merced ¦ Volta CDP, Merced | The Oro Loma 70 kV Area Reinforcement project will reconductor 70 kV lines in the Oro Loma area to help ensure reliable electric service to customers in the Merced County. The project will reconductor 2.4 miles of the Los Banos - Livingston Jct – Canal 70 kV Line, from Los Banos to Santa Nella substations and 10.8 miles of the Mercy Springs SW STA – Canal – Oro Loma 70 kV Line, from Mercy Springs SW STA to Canal Substation. The conductor should be capable of handling at least 825 Amps and 975 Amps during summer normal and emergency conditions, respectively. Associated substation terminal equipment will be upgraded as needed to meet the ratings of the new line conductor. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-07-22 | 41 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | 2.4 | NA | 70 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | 304 | 5.1001 | Non-IGP | 5767204 | T.0000157 | Oro Loma 70kV Reinforcement | 7 | 60 | NA ¦ 5746746 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-02-16 | 2015-05-01 | 2028-05-23 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 720.2639 | 13354.3426 | 0 | 0 | 0 | 6.6642 | 378.3254 | 1190.3264 | 5300 | 500 | 0 | 0 | 661.0701 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
573 | Egbert T-Line-Visitacion Ave Easement |  |  | Millbrae, San Mateo ¦ San Bruno, San Mateo ¦ San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-03-20 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 230 | NA | 741 | NA | NA | 5.1001 | Non-IGP | 5551310 | T.0000159 | Egbert 230kV Switching Station | 10 | 60 | NA ¦ 5763199 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2024 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Planning | 5 | NA | 2021-12-01 | 2026-05-29 | Permitting | NA | TRUE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | -0.6374 | 839.3626 | 0 | 0 | 0 | 12.9029 | 13.6546 | 812.8051 | 0 | 0 | 0 | 0 | 26.5575 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 11.6126 | 12.2892 | -24.5392 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil
574 | MIDWAY-KERN PP #2 230 KV LINE KERN AREA |  |  | Bakersfield, Kern ¦ Buttonwillow CDP, Kern ¦ Greenacres CDP, Kern ¦ Kern ¦ Rosedale CDP, Kern | Reconductor and split 42 circuit miles of the Midway-Kern No. 1 230kV Line and relocate Stockdale 230kV lines 1 and 2. The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Multiple | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2025-11-03 | 81 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | 21 | NA | 230 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5756002 | T.0000220 | Midway-Kern Nos. 1 and 2 230kV Line | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2015 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5026-E | 2017-02-21 | Approved | 2017 | Operational | 1 | 2018-11-01 | 2019-05-01 | 2019-03-25 | NA | NA | FALSE | $60,000 ¦ $90,000 | NA ¦ NA | 22597.7315 | 22597.7315 | 0.3615 | -38.1858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22597.7315 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 0.32387 | -34.2091 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $40 Mil - $50 Mil
575 | Stockdale 230kV Tap #1 & 2 Removal Ph. 2 |  |  | Bakersfield, Kern | Reconductor and split 42 circuit miles of the Midway-Kern No. 1 230kV Line and relocate Stockdale 230kV lines 1 and 2. The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Removal | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-07-22 | 45 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 12.4 | NA | 230 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 962 | NA | NA | 5785941 | T.0000220 | Midway-Kern Nos. 1 and 2 230kV Line | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2020 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5026-E | 2017-02-21 | Approved | 2017 | Operational | 1 | 2021-01-08 | 2019-05-01 | 2021-02-10 | Clearances | NA | FALSE | $60,000 ¦ $90,000 | NA ¦ NA | 1843.5264 | 1843.5264 | 532.2941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1843.5264 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 1871.6268 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $40 Mil - $50 Mil
576 | Midway-Kern PP #2 230 kV Line - Ph 2 |  |  | Bakersfield, Kern ¦ Buttonwillow CDP, Kern ¦ Greenacres CDP, Kern ¦ Kern ¦ Rosedale CDP, Kern | Reconductor and split 42 circuit miles of the Midway-Kern No. 1 230kV Line and relocate Stockdale 230kV lines 1 and 2. The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | New | NA | T.0001650 ¦ T.0003202 | Reliability | New T-Line | NERC TPL Standards | NA | 2025-11-03 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | 21 | NA | 230 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 404 | 5.101 | Non-IGP | 5777198 | T.0000220 | Midway-Kern Nos. 1 and 2 230kV Line | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5026-E | 2017-02-21 | Approved | 2017 | Planning | 5 | 2028-06-02 | 2019-05-01 | 2028-12-05 | Prioritization | NA | FALSE | $60,000 ¦ $90,000 | NA ¦ NA | 117.4229 | 10586.2819 | 7.5434 | 2.402 | 0 | 11.2335 | 5.5846 | 330.027 | 804.6656 | 5674.1539 | 186.4389 | 0 | 113.7112 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $40 Mil - $50 Mil
577 | MOSHER-LOCKFORD 60KV RECOND PHASE 2 |  |  | Lockeford CDP, San Joaquin ¦ Morada CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | This project proposes to reconductor 11.6 miles of the Lockeford 60 kV Line No. 1 with a higher capacity conductor. Completion of this project would allow both the Hammer-Country Club and Lockeford 60 kV Line No. 1 to normally serve Mosher Substation. This will increase transmission capacity and reliability for PG&E’s customers in San Joaquin County. This project will increase transmission capacity, improve operational flexibility and service reliability for the electric customers in San Joaquin County. Upon completion of this project, the risk of electric service interruptions due to a single line outage will be mitigated for the customers served by Mosher Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-21 | 18 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | 11.6 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5814975 | T.0000304 | MOSHER-LOCKEFORD RECONDUCTOR | 2 | 60 | NA ¦ 5767827 ¦ NA ¦ NA | FALSE | 2010 | Project Management Governance Standard | 2025 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-04-01 | 2017-12-01 | 2029-03-23 | Prioritization | NA | FALSE | $10,000 ¦ $15,000 | NA ¦ NA | 369.0244 | 35228.8103 | 0 | 0 | 0 | 0 | 269.9545 | 1414.6946 | 0 | 0 | 0 | 0 | 269.9544 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
578 | Mosher-Lockeford 60kv Reconductor |  |  | Lockeford CDP, San Joaquin ¦ Morada CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | This project proposes to reconductor 11.6 miles of the Lockeford 60 kV Line No. 1 with a higher capacity conductor. Completion of this project would allow both the Hammer-Country Club and Lockeford 60 kV Line No. 1 to normally serve Mosher Substation. This will increase transmission capacity and reliability for PG&E’s customers in San Joaquin County. This project will increase transmission capacity, improve operational flexibility and service reliability for the electric customers in San Joaquin County. Upon completion of this project, the risk of electric service interruptions due to a single line outage will be mitigated for the customers served by Mosher Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-21 | 18 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 11 | NA | 60 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | 727 | 5.1001 | Non-IGP | 5738689 | T.0000304 | MOSHER-LOCKEFORD RECONDUCTOR | 2 | 60 | NA ¦ 5767827 ¦ NA ¦ NA | FALSE | 2012 | Project Management Governance Standard | 2014 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-11-17 | 2017-12-01 | 2028-10-25 | Prioritization | NA | FALSE | $10,000 ¦ $15,000 | NA ¦ NA | 4656.7315 | 21856.0573 | -260.8814 | -0.0001 | 0 | 90.2136 | 82.2268 | 0 | 13755.6996 | 8100.3577 | 0 | 0 | 4656.7315 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
579 | SOUTH OF PALERMO REINFORCEMENT (PH-3) |  |  | Palermo CDP, Butte | This project will reinforce 80.3 circuit miles of the 115kV transmission lines between Palermo, Pease, Bogue, and Rio Oso substations with 477 kcmil steel-supported aluminum conductors with emergency capability of 970 Amps. This includes the installation of five Supervisory Control and Data Acquisition (SCADA) controlled transmission line switches on the Palermo – Pease, Pease – Rio Oso, Palermo – Bogue, and Bogue – Rio Oso 115kV lines to improve reliability and service restoration time. Key construction elements are as follows:  Replacement of 238 steel electric transmission lattice towers with 238 new hybrid tubular steel poles (HTSP), which include a concrete foundation and steel pole on top  Replacement of 21 steel electric transmission lattice towers with 21 tubular steel poles (TSP).  Replacement of 45 steel electric transmission lattice steel poles with new lattice steel poles.  Replacement of 2 steel electric transmission lattice towers with new steel lattice towers.  Reinforcement of 61 steel electric transmission lattice tower foundations with screw anchors.  Reinforcement of 23 steel electric transmission lattice towers with 19 top or waist cage extensions.  Upgrade 8 transmission relay terminals at 4 surrounding substations. This project has been divided into three construction phases as follows:  Phase 1: Rio Oso Substation to Pease Junction  Phase 2: Pease Substation to Palermo Substation  Phase 3: Bogue Substation to Bogue Junction | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-13 | 119 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 12.8 | 8.0464 | 115 | NA | 180 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5767548 | T.0000450 | South of Palermo 115kV Reinforcement | 8 | 60 | NA ¦ 5743570 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-08-30 | IS/MND | NA | CPUC | NA | PTC: A.16-04-23 | 2016-04-28 | Approved | 2018 | Operational | 1 | 2018-08-27 | 2014-05-01 | 2019-02-07 | Prioritization | NA | FALSE | $80,000 ¦ $100,000 | NA ¦ NA | 11940.0642 | 11940.0642 | 67.3652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11940.0642 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 64.1995 | 243.7213 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
580 | SOUTH OF PALERMO REINFORCEMENT (PH-2) |  |  | Palermo CDP, Butte | This project will reinforce 80.3 circuit miles of the 115kV transmission lines between Palermo, Pease, Bogue, and Rio Oso substations with 477 kcmil steel-supported aluminum conductors with emergency capability of 970 Amps. This includes the installation of five Supervisory Control and Data Acquisition (SCADA) controlled transmission line switches on the Palermo – Pease, Pease – Rio Oso, Palermo – Bogue, and Bogue – Rio Oso 115kV lines to improve reliability and service restoration time. Key construction elements are as follows:  Replacement of 238 steel electric transmission lattice towers with 238 new hybrid tubular steel poles (HTSP), which include a concrete foundation and steel pole on top  Replacement of 21 steel electric transmission lattice towers with 21 tubular steel poles (TSP).  Replacement of 45 steel electric transmission lattice steel poles with new lattice steel poles.  Replacement of 2 steel electric transmission lattice towers with new steel lattice towers.  Reinforcement of 61 steel electric transmission lattice tower foundations with screw anchors.  Reinforcement of 23 steel electric transmission lattice towers with 19 top or waist cage extensions.  Upgrade 8 transmission relay terminals at 4 surrounding substations. This project has been divided into three construction phases as follows:  Phase 1: Rio Oso Substation to Pease Junction  Phase 2: Pease Substation to Palermo Substation  Phase 3: Bogue Substation to Bogue Junction | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-13 | 119 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 34.9 | 8.0464 | 115 | NA | 180 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5767547 | T.0000450 | South of Palermo 115kV Reinforcement | 8 | 60 | NA ¦ 5743570 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-08-30 | IS/MND | NA | CPUC | NA | PTC: A.16-04-23 | 2016-04-28 | Approved | 2018 | Operational | 1 | 2019-02-04 | 2014-05-01 | 2020-02-27 | Prioritization | NA | FALSE | $80,000 ¦ $100,000 | NA ¦ NA | 25473.7715 | 25473.7715 | -85.3816 | 63.9456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25473.7715 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | -82.2918 | 61.6316 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
581 | SOUTH OF PALERMO REINFORCEMENT (PH-1) |  |  | Palermo CDP, Butte | This project will reinforce 80.3 circuit miles of the 115kV transmission lines between Palermo, Pease, Bogue, and Rio Oso substations with 477 kcmil steel-supported aluminum conductors with emergency capability of 970 Amps. This includes the installation of five Supervisory Control and Data Acquisition (SCADA) controlled transmission line switches on the Palermo – Pease, Pease – Rio Oso, Palermo – Bogue, and Bogue – Rio Oso 115kV lines to improve reliability and service restoration time. Key construction elements are as follows:  Replacement of 238 steel electric transmission lattice towers with 238 new hybrid tubular steel poles (HTSP), which include a concrete foundation and steel pole on top  Replacement of 21 steel electric transmission lattice towers with 21 tubular steel poles (TSP).  Replacement of 45 steel electric transmission lattice steel poles with new lattice steel poles.  Replacement of 2 steel electric transmission lattice towers with new steel lattice towers.  Reinforcement of 61 steel electric transmission lattice tower foundations with screw anchors.  Reinforcement of 23 steel electric transmission lattice towers with 19 top or waist cage extensions.  Upgrade 8 transmission relay terminals at 4 surrounding substations. This project has been divided into three construction phases as follows:  Phase 1: Rio Oso Substation to Pease Junction  Phase 2: Pease Substation to Palermo Substation  Phase 3: Bogue Substation to Bogue Junction | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-13 | 119 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 34 | 8.0464 | 115 | NA | 180 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5767546 | T.0000450 | South of Palermo 115kV Reinforcement | 8 | 60 | NA ¦ 5743570 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-08-30 | IS/MND | NA | CPUC | NA | PTC: A.16-04-23 | 2016-04-28 | Approved | 2018 | Operational | 1 | 2020-02-03 | 2014-05-01 | 2021-01-14 | Prioritization | NA | FALSE | $80,000 ¦ $100,000 | NA ¦ NA | 38518.8528 | 38518.8528 | 1741.1675 | -70.2669 | 0.0918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38518.8528 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 36032.2653 | -310.0864 | 0.08437 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
582 | MISSOURI FLAT-GOLD HILL 115 KV - LINE |  |  | Cameron Park CDP, El Dorado ¦ Diamond Springs CDP, El Dorado ¦ El Dorado ¦ El Dorado Hills CDP, El Dorado ¦ Folsom, Sacramento ¦ Shingle Springs CDP, El Dorado | Reconductor a 24 circuit-mile section of the Missouri Flat-Gold Hill 115 kV lines. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-21 | 35 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 24 | NA | 115 | NA | 137 | NA | NA | NA | NA | 5767622 | T.0000453 | Missouri Flat - Gold Hill Reconductor | 1 | 60 | NA ¦ 5758023 ¦ NA ¦ NA | FALSE | 2012 | Project Management Governance Standard | 2017 | 2008 | FALSE | 2008 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2015-10-22 | IS/MND | NA | CPUC | NA | PTC: A.13-08-014 | 2013-08-13 | Approved | 2015 | Operational | 1 | 2016-10-11 | 2011-12-01 | 2018-04-17 | Project Design | Scope Change | FALSE | $10,000 ¦ $20,000 | NA ¦ NA | 50530.3331 | 50530.3331 | 85.6277 | 42.5032 | 54.3477 | 34.5499 | 2.7928 | 0 | 0 | 0 | 0 | 0 | 50530.3331 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 78.7211 | 39.0748 | 49.9639 | 31.763 | 2.5675 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
583 | WEBER-SANTA FE JUNCTION 60 KV RECONDUCTOR |  |  | Stockton, San Joaquin | Reconductor the Stockton ‘A’-Weber 60kV Line Nos. 1 and 2 (8.8 circuit miles) and upgrade terminal equipment at Stockton ‘A’ and Weber 60kV substations | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-02-06 | 10 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 4.4 | 2.4271 | 60 | NA | 58 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767625 | T.0000454 | STOCKTON 'A' - WEBER Reconductor | 2 | 60 | NA ¦ 5738191 ¦ NA ¦ NA | FALSE | 2012 | Project Management Governance Standard | 2017 | 2010 | FALSE | 2010 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5264-E | 2018-04-02 | Approved | 2018 | Operational | 1 | 2019-02-12 | 2011-05-01 | 2019-07-09 | Project Design | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 11227.3471 | 11227.3471 | -30.3175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11227.3471 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -26.9246 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
584 | Stockton 'A' - Weber 60 kV Lines Recondu |  |  | Kennedy CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | Reconductor the Stockton ‘A’-Weber 60kV Line Nos. 1 and 2 (8.8 circuit miles) and upgrade terminal equipment at Stockton ‘A’ and Weber 60kV substations | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-25 | 10 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 4.4 | NA | 60 | NA | 58 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5739682 | T.0000454 | STOCKTON 'A' - WEBER Reconductor | 2 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2012 | Project Management Governance Standard | 2016 | 2010 | FALSE | 2010 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5264-E | 2018-04-02 | Approved | 2018 | Operational | 1 | 2018-08-02 | 2011-05-01 | 2019-09-23 | Project Design | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 9495.5801 | 9495.5801 | 10.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9495.5801 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 9.8194 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
585 | ELECTRA-VALLEY SPRINGS CAP RECONDUCTORING |  |  | Amador ¦ Calaveras ¦ Mokelumne Hill CDP, Calaveras ¦ Pine Grove CDP, Amador ¦ Pioneer CDP, Amador ¦ Red Corral CDP, Amador | Reconductor a 10.9-mile section on the West Point – Valley Springs 60 kilovolt (kV) Line. This project will increase transmission capacity to reliably serve electric customers in Calaveras County. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-07-23 | 61 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $100 Mil – $125 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 10.9 | NA | 60 | NA | 20 | 8. Compliance/Commitments With Low Safety Risk | 1 | NA | NA | 5767632 | T.0000458 | West Point-Valley Springs 60kV Reinforce | 1 | 60 | NA ¦ 5726146 ¦ NA ¦ NA | FALSE | 2007 | Project Management Governance Standard | 2017 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5327-E | 2018-07-06 | Approved | 2018 | Operational | 1 | 2019-03-18 | 2009-05-01 | 2020-05-05 | ISO Action | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 21360.6501 | 21360.6501 | -59.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21360.6501 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -52.9746 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
586 | Ravenswood-Cooley Landing 115 kV |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo | This project proposes to reconductor the Ravenswood-Cooley Landing Nos. 1 & 2 115 kV Lines. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-22 | 62 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1.8 | NA | 115 | NA | 270 | 8. Compliance/Commitments With Low Safety Risk | 577 | NA | NA | 5743555 | T.0000612 | RAVENSWOOD-COOLEY LANDING 115 KV Recondu | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2014 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2019-04-04 | IS/MND | NA | CPUC | NA | PTC: A.17-12-010 | 2017-12-23 | Approved | 2019 | Operational | 1 | 2022-09-22 | 2015-12-01 | 2022-12-15 | Project Design | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 14245.7843 | 14245.7843 | 1577.6778 | 8391.3818 | 364.5435 | 52.3881 | 1.222 | 0 | 0 | 0 | 0 | 0 | 14245.7843 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 12770.3848 | 1131.4018 | 51.205 | 1.1944 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
587 | Pittsburg Sub: Inst BK14 T-line TSP |  |  | Pittsburg, Contra Costa | This project proposes to add a third Pittsburg 230/115 kV Transformer with a rating of 420 MVA. Completion of this project will provide adequate transmission capacity to enable safe and reliable electric service to electric customers served by Pittsburg Substation | Transmission Line - Conductor | New | NA | T.0004581 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 28.8512 | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5813539 | T.0000946 | PITTSBURG: Install 230/115KV TRANSFORMER | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-04-04 | 2011-05-01 | 2029-01-23 | Prioritization | NA | FALSE | $10,000 ¦ $20,000 | NA ¦ NA | 50.0572 | 6116.3789 | 0 | 0 | 0 | 0 | 38.5684 | 269.3943 | 0 | 0 | 0 | 0 | 38.5684 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
588 | Panoche- Oro Loma 115 kV Reconductoring |  |  | Fresno | Reconductoring the Panoche-Oro Loma 115kV Line will increase transmission capacity and grid reliability in the area, as well as provide capability for future interconnections. The project scope are as follows: • Reconductor approximately 17 miles of the Panoche-Oro Loma 115kV Line with a conductor capable of handling at least 825 Amps and 975 Amps under summer normal and emergency conditions, respectively. The conductor type proposed by the project team is 1113 AAC conductor. • Upgrade the 115kV bus and install two SCADA switch automatics at Hammonds Substation • Upgrade terminal equipment at Panoche, Oro Loma and Hammonds substations • Install new SCADA switches at Panoche and De Francesco Junctions • Remove 183 wood poles and install 156 new light duty steel poles (LDSP), reframe 35 existing LDSPs | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-26 | 14 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 5.7 | NA | 115 | NA | 604 | 8. Compliance/Commitments With Low Safety Risk | 365 | NA | NA | 5760564 | T.0002127 | PANOCHE-ORO LOMA 115 KV RECONDUCTORING | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2018 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5390-E | 2018-09-28 | Approved | 2018 | Operational | 1 | 2022-01-17 | 2021-05-01 | 2022-03-21 | Prioritization | NA | FALSE | 20000 | NA ¦ NA | 7146.2861 | 7146.2861 | 2057.1132 | 3464.4635 | 3.6115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7146.2861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 6096.2833 | 3.0436 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
589 | Panoche - Oro Loma Phase 2 |  |  | Fresno | Reconductoring the Panoche-Oro Loma 115kV Line will increase transmission capacity and grid reliability in the area, as well as provide capability for future interconnections. The project scope are as follows: • Reconductor approximately 17 miles of the Panoche-Oro Loma 115kV Line with a conductor capable of handling at least 825 Amps and 975 Amps under summer normal and emergency conditions, respectively. The conductor type proposed by the project team is 1113 AAC conductor. • Upgrade the 115kV bus and install two SCADA switch automatics at Hammonds Substation • Upgrade terminal equipment at Panoche, Oro Loma and Hammonds substations • Install new SCADA switches at Panoche and De Francesco Junctions • Remove 183 wood poles and install 156 new light duty steel poles (LDSP), reframe 35 existing LDSPs | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-26 | 14 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 10.7 | NA | 115 | NA | NA | NA | NA | NA | NA | 5800299 | T.0002127 | PANOCHE-ORO LOMA 115 KV RECONDUCTORING | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2022 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5390-E | 2018-09-28 | Approved | 2018 | Operational | 1 | 2022-10-18 | 2021-05-01 | 2023-02-22 | Prioritization | NA | FALSE | 20000 | NA ¦ NA | 3326.9249 | 3326.9249 | 0 | 2889.7092 | 437.2156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3326.9249 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 2812.9364 | -1e-05 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
590 | Panoche - Oro Loma Phase 3 |  |  | Fresno | Reconductoring the Panoche-Oro Loma 115kV Line will increase transmission capacity and grid reliability in the area, as well as provide capability for future interconnections. The project scope are as follows: • Reconductor approximately 17 miles of the Panoche-Oro Loma 115kV Line with a conductor capable of handling at least 825 Amps and 975 Amps under summer normal and emergency conditions, respectively. The conductor type proposed by the project team is 1113 AAC conductor. • Upgrade the 115kV bus and install two SCADA switch automatics at Hammonds Substation • Upgrade terminal equipment at Panoche, Oro Loma and Hammonds substations • Install new SCADA switches at Panoche and De Francesco Junctions • Remove 183 wood poles and install 156 new light duty steel poles (LDSP), reframe 35 existing LDSPs | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-26 | 14 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.6 | NA | 115 | NA | NA | NA | NA | 3.0011 | Non-IGP | 5804579 | T.0002127 | PANOCHE-ORO LOMA 115 KV RECONDUCTORING | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2023 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5390-E | 2018-09-28 | Approved | 2018 | Operational | 1 | 2024-03-18 | 2021-05-01 | 2024-04-09 | Prioritization | NA | FALSE | 20000 | NA ¦ NA | 1270.9337 | 1270.9337 | 0 | 0 | 43.3376 | 1173.2201 | 54.3761 | 0 | 0 | 0 | 0 | 0 | 1270.9337 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1024.5586 | 45.7559 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
591 | Wilson - Le Grand 115 kV line reconducto |  |  | Merced ¦ Merced, Merced | This project proposes to reconductor approximately 14 miles of the Wilson -LeGrand 115kV Line with 477 ACSS conductor or equivalent and replaces 146 wood poles with new light duty steel poles (LDSP). This project was recommended by the CAISO as a policy driven upgrade.. Completion of this project will provide additional transmission capacity to serve over 30,000 electric customers in Merced County. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2025-05-28 | 62 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 14 | NA | 115 | NA | 102 | 8. Compliance/Commitments With Low Safety Risk | 512 | NA | NA | 5763769 | T.0002231 | Wilson-LeGrand | 2 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2018 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5293-E | 2018-05-15 | Approved | 2018 | Operational | 1 | 2021-01-05 | 2020-12-31 | 2021-12-06 | Prioritization | NA | FALSE | 15000 | NA ¦ NA | 8670.1277 | 8670.1277 | 3863.4181 | 142.3734 | 1.2913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8670.1277 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 7582.214 | 125.3426 | 1.1369 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
592 | KERN-MAGUNDEN-WITCO 115KV RERATE |  |  | Bakersfield, Kern ¦ East Niles CDP, Kern ¦ Kern ¦ Oildale CDP, Kern | The Project proposes to reconductor approximately 38 circuit miles of various 115 kV lines serving Bakersfield area in Kern County. The scope of the project include reconductoring 3.8 miles of the Kern PP-Westpark Nos. 1 and 2 115 kV Lines; 16.5 miles of the Kern-Magunden-Witco 115 kV Line; 3.5 miles of the Westpark-Magunden 115 kV Line; 5.0 miles of the Kern-Lamont 115 kV Line from Kern PP to Tevis Jct.; 5.0 miles of the Kern-Stockdale 115 kV line from Kern PP to Tevis Jct. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2025-11-03 | 46 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 19.6 | NA | 60 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 336 | 5.1001 | Non-IGP | 5767363 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 8 | 60 | NA ¦ 5747850 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-03-23 | 2016-03-01 | 2029-05-24 | Prioritization | NA | FALSE | $40,000 ¦ $65,000 | NA ¦ NA | 670.1572 | 2988.4215 | 0 | 0 | 0 | 21.9138 | 11.8334 | 0 | 0 | 0 | 0 | 0 | 670.1572 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
593 | WESTPARK-MAGUNDEN RECONDUCTOR |  |  | Bakersfield, Kern ¦ Kern | The Project proposes to reconductor approximately 38 circuit miles of various 115 kV lines serving Bakersfield area in Kern County. The scope of the project include reconductoring 3.8 miles of the Kern PP-Westpark Nos. 1 and 2 115 kV Lines; 16.5 miles of the Kern-Magunden-Witco 115 kV Line; 3.5 miles of the Westpark-Magunden 115 kV Line; 5.0 miles of the Kern-Lamont 115 kV Line from Kern PP to Tevis Jct.; 5.0 miles of the Kern-Stockdale 115 kV line from Kern PP to Tevis Jct. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-23 | 125 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 12.3 | NA | 60 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 361 | 5.1001 | Non-IGP | 5767364 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 8 | 60 | NA ¦ 5747850 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-03-23 | 2016-03-01 | 2029-05-24 | Prioritization | NA | FALSE | $40,000 ¦ $65,000 | NA ¦ NA | 700.6647 | 2983.2746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700.6647 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
594 | VALLEYSPRINGS-MARTELL NO.2 SCADA |  |  | Amador ¦ Calaveras ¦ Jackson, Amador ¦ Martell CDP, Amador | Phase 1 of this project will replace 6 manually operated switches with SCADA-operable switches on the Valley Springs-Martell No. 1, Valley Springs – Clay, and the Pardee No. 2 Tap 60kV lines. The associated wood poles will be replaced with 4 Tubular Steel Poles (TSP) and 2 Engineered Direct Embedded Poles (EDEP) as required. This project will improve customer electric service reliability by reducing outage durations and allowing greater operational flexibility. Phase 2 of this project will replace 4 manually operated switches with SCADA-operable switches on the Clay - Martell 60kV line. The associated wood poles will be replaced with 3 Fiberglass Poles and one Engineered Direct Embedded Poles (EDEP) as required. The manual switches will be replaced with either Cleveland/Price or SEECO switches. The project is being constructed in 2 phases due to testing required for the new fiberglass pole design. | Transmission Line - Switch | New | NA | NA | Reliability | T-Line Reliability | NA | NA | 2025-06-19 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 58 | 5. Compliance/Commitments With Strong Safety Link | 41 | NA | NA | 5775027 | T.0003024 | ValleySprings-Martell No.2 SCADA | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5801-E | 2020-04-03 | Approved | 2020 | Operational | 1 | 2019-12-06 | 2021-03-31 | 2020-07-03 | NA | NA | FALSE | 10500 | NA ¦ NA | 3962.8553 | 3962.8553 | 82.3715 | 2.2797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3962.8553 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 80.0036 | 2.2139 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ $50 Mil – $75 Mil
595 | Bakersfield-Kern Ph1 Tap 2 |  |  | Bakersfield, Kern ¦ Buttonwillow CDP, Kern ¦ Greenacres CDP, Kern ¦ Kern ¦ Rosedale CDP, Kern | This project will loop the Bakersfield 230kV Substation onto the Midway-Kern No. 2 230kV Line and reconductor approximately 14 circuit miles of the Bakersfield Nos. 1 and 2 230kV Tap Lines to provide operational flexibility and service reliability in the area. The project scope of work includes the following: o Loop Bakersfield 230kV substation onto the Midway – Kern No. 2 230kV line; o Upgrade terminal equipment at Bakersfield Substation, as necessary, to accommodate the rating of the transmission line conductor; o Reconductor 14 circuit miles of the Bakersfield Nos. 1 and 2 230kV Taps; o Upgrade distribution equipment to accommodate transmission work; o Install protection and telecommunication upgrades | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000220 ¦T.0001650 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-03 | 77 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 14 | NA | 230 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 404 | 5.101 | Non-IGP | 5767355 | T.0003202 | Bakersfield-Kern Taps 1&2 230kV Recon | 4 | 60 | NA ¦ 5756002 ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2017 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5924-E | 2020-08-19 | Approved | 2020 | Engineering more than 50% complete | 3 | 2029-03-29 | 2019-05-01 | 2029-09-12 | Prioritization | NA | FALSE | $60,000 ¦ $90,000 | NA ¦ NA | 1229.5977 | 12765.4784 | 35.8187 | 0 | 0 | 117.6067 | 61.7403 | 102.4549 | 2000 | 4726.1643 | 4707.2615 | 0 | 1229.5977 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ NA
596 | Midway-Temblor 115kV Recon & Voltage Sup |  |  | Buttonwillow CDP, Kern ¦ Kern | This project proposes to upgrade 14.5 miles of conductor and four (4) transmission switches (Nos. 137, 139, and 157) on the Midway – Temblor 115 kV Line, and install 39 MVAR shunt capacitors with 13 MVAR steps (a total of 3 steps), and convert existing 115kV bus at Temblor Substation to 5-element ring bus (expandable to 6-element in future). | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000423 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-25 | 53 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | 14.5 | NA | 115 | NA | 137 | 8. Compliance/Commitments With Low Safety Risk | 417 | 5.1001 | Non-IGP | 5781145 | T.0004113 | Midway-Temblor 115kV Recon & Voltage Sup | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-10-18 | 2018-05-01 | 2028-03-10 | Prioritization | NA | FALSE | $25,000 ¦ $35,000 | NA ¦ NA | 1034.9863 | 18981.9915 | 21.7897 | 3.9541 | 0 | 25.403 | 569.883 | 1572.1032 | 6100 | 6300 | 0 | 0 | 886.9497 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
597 | MIDWAY-TEMBLOR 115KV RECON ENGINEERING |  |  | Buttonwillow CDP, Kern ¦ Kern | This project proposes to upgrade 14.5 miles of conductor and four (4) transmission switches (Nos. 137, 139, and 157) on the Midway – Temblor 115 kV Line, and install 39 MVAR shunt capacitors with 13 MVAR steps (a total of 3 steps), and convert existing 115kV bus at Temblor Substation to 5-element ring bus (expandable to 6-element in future). | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-25 | 53 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | 14.5 | NA | 115 | NA | NA | NA | NA | 3.0011 | Non-IGP | 5813946 | T.0004113 | Midway-Temblor 115kV Recon & Voltage Sup | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-10-19 | 2018-05-01 | 2028-03-13 | Prioritization | NA | FALSE | $25,000 ¦ $35,000 | NA ¦ NA | 105.4168 | 8904.5826 | 0 | 0 | 0 | 0 | 117.6902 | 371.5221 | 5000 | 2700 | 0 | 0 | 117.6902 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
598 | METCALF - GREEN VALLEY 115KV: ACQUIRE EASEMENT |  |  | Interlaken CDP, Santa Cruz ¦ Morgan Hill, Santa Clara ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Other | Upgrade/Retrofit | NA | 5792891 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-04-03 | 40 | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 15 | NA | 115 | NA | 137 | 8. Compliance/Commitments With Low Safety Risk | 50 | 3.0011 | Non-IGP | 5531782 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 10 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2019 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2025-07-29 | 2021-12-01 | 2028-12-29 | Prioritization | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 49.099 | 3579.9211 | 0 | 0 | 0 | 10.4627 | 23.8553 | 1179.781 | 2365.1642 | 0 | 0 | 0 | 34.318 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 10.4627 | 23.8553 | 14.781 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
599 | LOOP METCALF-LLAGAS 115KV INTO MORG HILL |  |  | Interlaken CDP, Santa Cruz ¦ Morgan Hill, Santa Clara ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Transmission Line - Conductor | Upgrade/Retrofit | NA | 5792891 | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2026-04-03 | 40 | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | NA | NA | 50 | 5.1001 | Non-IGP | 5786320 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 10 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2023 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 2 | 2025-12-01 | 2021-12-01 | 2028-10-17 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1000 | 200 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
600 | METCALF - GREEN VALLEY 115KV: RECONDUCTO |  |  | Interlaken CDP, Santa Cruz ¦ Morgan Hill, Santa Clara ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Transmission Line - Conductor | Upgrade/Retrofit | NA | 5792891 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-04-03 | 97 | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 15 | NA | 115 | NA | 2135 | 8. Compliance/Commitments With Low Safety Risk | 50 | 5.1001 | Non-IGP | 5782106 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 10 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2019 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-05-03 | 2021-12-01 | 2028-05-31 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 6632.356 | 92251.041 | 610.6841 | 443.1191 | 1.4268 | 1244.4162 | -645.0131 | 8022.5666 | 9593.0008 | 47669.0007 | 20675 | 0 | 6291.4728 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
601 | Morgan Hill - Green Valley: IT |  |  | Morgan Hill, Santa Clara | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Other - IT | Upgrade/Retrofit | NA | 5792891 ¦ T.0011276 | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.8017 | 115 | NA | NA | NA | NA | 3.0011 | Non-IGP | 5810958 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 10 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2024 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-03-16 | 2021-12-01 | 2028-12-29 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 18.9393 | 1016.5138 | 0 | 0 | 0 | 2.8089 | 15.893 | 326.8089 | 0 | 0 | 0 | 0 | 18.7018 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
602 | Herndon - Bullard Nos. 1 and 2 115 kV RC |  |  | Fresno, Fresno ¦ Madera | This project proposes to reconductor roughly 8 circuit miles (4 miles of double circuit transmission line) between Pinedale Jct and Bullard Substation on the Herndon - Bullard Nos. 1 and 2 115 kV lines. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0003307 ¦ T.0003310 ¦ T.0003306 ¦ T.0003309 ¦ T.0003311 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-08 | 18 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 22.8 | NA | 115 | NA | 69 | 8. Compliance/Commitments With Low Safety Risk | 415 | 5.1001 | Non-IGP | 5782638 | T.0004347 | Herndon - Bullard Nos. 1 and 2 115 kV RC | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-14 | 2021-01-01 | 2027-11-02 | Prioritization | NA | TRUE | $6,000 ¦ $8,000 | NA ¦ NA | 488.9774 | 13048.5211 | 26.9297 | 26.9412 | 0 | 0 | 78.0935 | 512.1277 | 6051.9432 | 771 | 0 | 0 | 475.3934 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
603 | South of Mesa Upgrade - Tline Recond |  |  | Santa Barbara ¦ Sisquoc CDP, Santa Barbara | This project proposes to upgrade approximately 21.3 miles of conductor on the Sisquoc – Santa Ynez SW STA 115 kV Line, install 20 Mega Volt-ampere reactive (MVAR) shunt capacitors at Cabrillo Substation and install Remedial Action Scheme (RAS) (formerly known as Special Protection Scheme (SPS)) on the Sisquoc – Santa Ynez SW STA 115 kV Line. Completion of this project is needed to improve the electric transmission system reliability and operational flexibility in the Santa Barbara County. This project will be funded under Major Work Category (MWC) 60, Electric Transmission Line Capacity and 61, Electric Transmission Substation Capacity. The project has a Risk Informed Budget Allocation (RIBA) score of 137. The RIBA score is based on the impact and frequency of three risk categories: safety, reliability and environmental. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-23 | 37 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 21.3 | NA | 115 | NA | 137 | 8. Compliance/Commitments With Low Safety Risk | 30 | 5.1001 | Non-IGP | 5785927 | T.0004832 | South Of Mesa Upgrade Project | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-12-09 | 2023-12-31 | 2029-06-28 | Prioritization | NA | FALSE | $29,600 ¦ $59,200 | NA ¦ NA | 1081.8765 | 24463.8008 | 182.176 | 0 | 0 | 11.5588 | 50.0632 | 302.0738 | 2342.9413 | 13884.4513 | 6927.6866 | 0 | 1006.6478 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
604 | Giffen 70 kV Tap Line Reconductoring |  |  | Fresno | Reconductor approximately 5 miles of the Giffen 70 kV Tap Line with a conductor having summer emergency (SE) rating of at least 742 Amps (715 AAC conductor or equivalent) | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Economic | Line Reconductoring | NERC TPL Standards | NA | 2025-09-05 | 79 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 5 | NA | 70 | NA | NA | 5. Compliance/Commitments With Strong Safety Link | 1209 | NA | NA | 5785942 | T.0004833 | Giffen 70 kV Tap Line Reconductoring | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6600-E | 2022-05-23 | Approved | 2022 | Operational | 1 | 2023-11-01 | 2023-03-01 | 2023-12-21 | Prioritization | NA | FALSE | 5000 | NA ¦ NA | 3941.9332 | 3941.9332 | 410.8895 | 352.239 | 2884.1198 | 259.1381 | -49.2547 | 0 | 0 | 0 | 0 | 0 | 3941.9332 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 3389.0611 | 234.5113 | -44.5738 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
605 | Mountain View: 115kV Line Relocation |  |  | Mountain View, Santa Clara | This project proposes to replace existing substation transformer Bank 1 in order to eliminate a growing deficiency on both Mountain View Bank 1 and Mountain View Bank 3. Replace two existing 115 kV motor-operated switches (157 and 159) with circuit breakers. Presently any bus or bank fault will trip both existing 115 kV breakers CB 112 & CB 122. By adding two additional 115 kV circuit breakers, only the faulted bus or bank would experience an outage. This additional scope will improve the looped bus, provide a logical path to an ultimate five-element 115 kV ring bus, improve bank clearances and increase reliability by reducing momentary outages to the 39,141 existing customers on Mountain View Substation. Transmission Substation Work (MWC 61): • Replace 115 kV circuit switchers 159 and 157 with 115 kV circuit breakers. • Extend existing control building will to accommodate the new relays for the breakers. with 115 kV circuit breakers. • Replace existing CB 112 with new circuit breaker/disconnect switches. | Transmission Line - Conductor | Relocate | NA | NA | Load Growth | Line Termination | NA | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8224 | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5558301 | T.0005971 | Mountain View - Replace Bank 1 | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-26 | 2028-12-06 | 2027-07-12 | NA | NA | TRUE | 22100 | NA ¦ NA | 1008.1823 | 2395.0306 | 0 | 0 | 0 | 40.2909 | 827.1886 | 427.5511 | 359.3619 | 0 | 0 | 0 | 867.4795 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 867.4795 | 140.7028 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
606 | Wilson-Oro Loma 115 kV Reconductoring |  |  | El Nido CDP, Merced ¦ Fresno ¦ Madera ¦ Merced ¦ Merced, Merced | Reconductor approximately 9 circuit miles between Wilson and El Nido on the Wilson-Oro Loma 115 kV Line with a larger conductor to achieve at least 650 Amps of summer emergency rating. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-03 | 77 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 9 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5791341 | T.0006016 | Wilson-Oro Loma 115 kV Reconductoring | 2 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2022 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-01-14 | 2026-12-31 | 2028-05-22 | Project Design | Construction Delays | FALSE | $11,300 ¦ $22,700 | NA ¦ NA | 211.8219 | 8032.1355 | 0.0084 | 2.1089 | 6.7262 | 0.3181 | 162.6764 | 1281.9301 | 1000 | 0 | 0 | 0 | 171.9546 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
607 | Manteca #1: Recon. From 9/147 to 10/165 |  |  | Grayson CDP, Stanislaus ¦ Manteca, San Joaquin ¦ San Joaquin ¦ Stanislaus | This project proposes to reconductor the 1.13-mile section from Manteca Junction (Jct) to Banta Carbona Jct on the Manteca #1 60 kV Line with a conductor rated for a minimum of 368 Amps for summer normal conditions to mitigate normal overloads | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-22 | 23 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 1.13 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5795383 | T.0007053 | Manteca #1 Recon. From 9/147 to 10/165 | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2021 | 2021 | FALSE | 2021 | NA | https://www.caiso.com/Documents/BoardApproved2020-2021TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7359-E | 2024-08-23 | Approved | 2024 | Operational | 1 | 2024-12-09 | 2024-12-31 | 2024-12-23 | NA | NA | TRUE | $1,400 ¦ $2,800 | NA ¦ NA | 1907.7864 | 1907.7864 | 15.9375 | 29.2373 | 325.5676 | 1377.9999 | 156.0863 | 2.9578 | 0 | 0 | 0 | 0 | 1904.8286 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1661.5731 | 148.0363 | 2.8052 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2020-2021TransmissionPlan.pdf
608 | Wheeler Bank: Wheeler Ridge-Adobe |  |  | Kern | This project proposes to install one new 230 kV breaker-and-a-half (BAAH) bay with two new 230 kV breakers, one 230/21 kV, 75 MVA three-phase transformer, one 21/12 kV 30 MVA autotransformer, one 2,000 ampere (A) rated 21 kV bus 1/bus 2 structure with six breaker bays, three 1,200 A 21 kV feeder breakers, one 2,000 A 21 kV bus tie breaker, three 21 kV distribution feeder outlets, and three new 21 kV underground distribution circuits from the substation to the customer site.This project will allow 50 MW of new electric vehicle (EV) charging load from Tesla Motors Company (Tesla) and future load from other EV customers to connect to the PG&E system. Transmission Substation Work (MWC 61): • Install one 230 kV BAAH bay • Install two 230 kV breakers in new BAAH bay • Extend 230 kV line north from new BAAH bay in 230 kV yard to location of new 230/21 kV transformer • Potential rearrangement of Wheeler Ridge-Adobe Switching Station 115 kV and Wheeler Ridge-San Bernard 70 kV lines within substation | Transmission Line - Multiple | Relocate | NA | NA | Load Growth | Line Reconductoring | NA | NA | 2026-04-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5808166 | T.0008068 | Wheeler Ridge Sub: Install 21 kV bank | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | PTC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-01-13 | NA | 2027-03-23 | NA | NA | TRUE | NA | NA ¦ NA | 101.5793 | 335.7161 | 0 | 0 | 0 | 0 | 92.1375 | 175.2596 | 63.3191 | 0 | 0 | 0 | 92.1375 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
609 | Wheeler Bank: Wheeler Ridge-Weedpatch |  |  | Bakersfield, Kern ¦ Kern ¦ Weedpatch CDP, Kern | This project proposes to install one new 230 kV breaker-and-a-half (BAAH) bay with two new 230 kV breakers, one 230/21 kV, 75 MVA three-phase transformer, one 21/12 kV 30 MVA autotransformer, one 2,000 ampere (A) rated 21 kV bus 1/bus 2 structure with six breaker bays, three 1,200 A 21 kV feeder breakers, one 2,000 A 21 kV bus tie breaker, three 21 kV distribution feeder outlets, and three new 21 kV underground distribution circuits from the substation to the customer site.This project will allow 50 MW of new electric vehicle (EV) charging load from Tesla Motors Company (Tesla) and future load from other EV customers to connect to the PG&E system. Transmission Substation Work (MWC 61): • Install one 230 kV BAAH bay • Install two 230 kV breakers in new BAAH bay • Extend 230 kV line north from new BAAH bay in 230 kV yard to location of new 230/21 kV transformer • Potential rearrangement of Wheeler Ridge-Adobe Switching Station 115 kV and Wheeler Ridge-San Bernard 70 kV lines within substation | Transmission Line - Multiple | Relocate | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2025-11-26 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5808520 | T.0008068 | Wheeler Ridge Sub: Install 21 kV bank | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | PTC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-01-28 | NA | 2027-04-16 | NA | NA | TRUE | NA | NA ¦ NA | 60.4664 | 326.974 | 0 | 0 | 0 | 0 | 52.8497 | 188.0139 | 81.1104 | 0 | 0 | 0 | 52.8497 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
610 | Reconductor: Rio Oso-Lincoln 115 kV |  |  | Lincoln, Placer ¦ Placer ¦ Sutter | Reconductor Rio Oso–SPI Jct–Lincoln 115kV line | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0009604 | Policy | Line Reconductoring | NERC TPL Standards | NA | 2025-11-02 | 25 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 11 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5800761 | T.0008394 | Reconductor Rio Oso-Lincoln 115 kV | 1 | 60 | NA ¦ EX112249 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-12-14 | 2028-05-01 | 2029-07-06 | Project Design | NA | FALSE | $10,600 ¦ $21,200 | NA ¦ NA | 184.9401 | 18557.759 | 0 | 0 | 0 | 0 | 163.5421 | 654.2169 | 9141 | 5122 | 2897 | 474 | 163.5421 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
611 | Willits Substation - Transmission Line |  |  | Mendocino ¦ Redwood Valley CDP, Mendocino | Distribution Substation Work (MWC 46) under this Project: Install new 60/12kV 30MVA transformer, replace 12kV bus structure, reconnect feeder outlets, $13.625 million • Substation Reinforcement – Install additional 30MVA 60/12kV transformer • Install new 12kV Bus structure • Install 3 new 1200A circuit breakers • Reconnect feeder 1102, 1103, 1104 outlets to new breakers Distribution Line Work (MWC 06) under this Project: • Install 3 1100 AL feeder outlets with risers outside sub fence about 500ft. • Install 3 900A circuit outlet switches. | Transmission Line - Conductor | Relocate | NA | NA | Load Growth | Substation Capacity | NA | NA | 2025-10-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5816878 | T.0008672 | Willits Substation - Replace Transformer | 1 | 60 | NA ¦ EX113698 ¦ NA ¦ 61# | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-02-29 | NA | 2028-03-27 | NA | NA | FALSE | NA | NA ¦ NA | 34.2027 | 2223 | 0 | 0 | 0 | 0 | 22.6242 | 875.3614 | 0 | 0 | 0 | 0 | 22.6242 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
612 | Riverbank-Ripon - Line Reconductor |  |  | Ripon, San Joaquin ¦ San Joaquin ¦ Stanislaus | This project will increase operating flexibility, load serving capability, customer reliability, eliminate contingency overloads, and harden the transmission system by performing the following scope: • Reconductor 1.3 circuit miles between Riverbank Junction Switching Station and Structure 035/212 of the Stanislaus – Melones Switching Station–Riverbank Junction Switching Station 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Reconductor 1.8 circuit miles between Riverbank Junction Switching Station and Valley Home Tap (038/233) of the Riverbank Switching Station – Ripon 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Reconductor 3.1 circuit miles between Stanislaus - Manteca #2 035/212 and Stanislaus - Manteca #2 038/233 of the Stanislaus - Manteca #2 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Design for OPGW and install OPGW Peaks (do not install OPGW at this time) • Include all open maintenance tags within the project scope where applicable (including replacing Bellota-Riverbank Junction SW-179, Notification 121744057) • Replace structures, all insulators and insulator hardware to accommodate the increase in conductor size | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004301 ¦ T.0007979 ¦ T.0004515 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-06-29 | 90 | Steady State Power Flow System Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 1.8 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5803072 | T.0008743 | Riverbank-Ripon - Line Reconductor | 5 | 60 | NA ¦ Ex112172 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7732-E | 2025-10-15 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-04-29 | 2028-05-01 | 2027-03-04 | NA | NA | TRUE | $6,800 ¦ $13,600 | NA ¦ NA | 1272.0878 | 7272.5784 | 0 | 0 | 19.5435 | 250.5619 | 686.9686 | 4030.4783 | 281.9894 | 0 | 0 | 0 | 957.074 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
613 | Stanislaus-Melones Sw Sta-Riverbank Jct |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | This project will increase operating flexibility, load serving capability, customer reliability, eliminate contingency overloads, and harden the transmission system by performing the following scope: • Reconductor 1.3 circuit miles between Riverbank Junction Switching Station and Structure 035/212 of the Stanislaus – Melones Switching Station–Riverbank Junction Switching Station 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Reconductor 1.8 circuit miles between Riverbank Junction Switching Station and Valley Home Tap (038/233) of the Riverbank Switching Station – Ripon 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Reconductor 3.1 circuit miles between Stanislaus - Manteca #2 035/212 and Stanislaus - Manteca #2 038/233 of the Stanislaus - Manteca #2 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Design for OPGW and install OPGW Peaks (do not install OPGW at this time) • Include all open maintenance tags within the project scope where applicable (including replacing Bellota-Riverbank Junction SW-179, Notification 121744057) • Replace structures, all insulators and insulator hardware to accommodate the increase in conductor size | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004301 ¦ T.0007979 ¦ T.0004515 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-07-23 | 100 | Steady State Power Flow System Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 1.3 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5803073 | T.0008743 | Riverbank-Ripon - Line Reconductor | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7732-E | 2025-10-15 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-12-01 | 2028-05-01 | 2027-04-29 | NA | NA | TRUE | $6,800 ¦ $13,600 | NA ¦ NA | 741.8568 | 5379.23 | 0 | 0 | 15.5877 | 120.3504 | 479.1389 | 3672.4721 | 397.3034 | 0 | 0 | 0 | 615.0769 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
614 | Weber-Mormon Jct Reconductor |  |  | Garden Acres CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | The project will increase operating flexibility, load serving capability, customer reliability, eliminate normal overloads and improve asset health by performing the following scope: • Rebuild 6.2 circuit miles between Weber (000/004) and Mormon (006/103) of the Weber - Mormon Jct. 60 kV Line and conductor with a larger conductor to achieve at least 742 Amps of summer interior emergency rating. • New poles will be sized to accommodate future distribution under build conductor. • Upgrade substation terminal equipment to achieve full conductor capacity, if needed. • Include all open maintenance tags within the project scope where applicable. • When replacing structures, all insulators and insulator hardware should be replaced. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-09-23 | 126 | Steady State Power Flow System Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.2 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5803222 | T.0008749 | Weber-Mormon Jct Reconductor | 2 | 60 | NA ¦ Ex112173 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7813-E | 2026-01-15 | Approved | 2026 | Engineering more than 50% complete | 3 | 2026-10-19 | 2027-05-01 | 2027-03-31 | NA | NA | TRUE | $9,300 ¦ $18,600 | NA ¦ NA | 1217.4424 | 12349.2446 | 0 | 0 | 5.0164 | 382.9864 | 665.4523 | 8254.8804 | 2429.573 | 35.732 | 0 | 0 | 1053.4551 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
615 | Coppermine 70 kV Reinforcement Tline |  |  | Fresno ¦ Fresno, Fresno ¦ Madera ¦ Madera Ranchos CDP, Madera ¦ Rolling Hills CDP, Madera | This project proposes to reconductor roughly 13 circuit miles of the Borden - Coppermine 70 kV Line and to install a voltage support device in the area. This will provide additional transmission capacity to serve electric customers in Madera and Fresno Counties. The project scope of work includes following: •Reconductor roughly 9.5 circuit miles of line between Borden and Cassidy Substations (from Pole 19/10A to Cassidy Substation) on the Borden-Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 700 Amps during summer normal conditions •Reconductor roughly 3.6 circuit miles of line between Cassidy and Coppermine Substations (from Pole 03/07 to Coppermine Substation) on the Borden - Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 500 Amps during summer normal conditions. •Remove any limiting components to achieve the full conductor capability •Install 20 MVar voltage support device at Coppermine Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-09-12 | 63 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 13 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5803379 | T.0008870 | Coppermine 70 kV Reinforcement Project | 5 | 60 | NA ¦ Ex112247 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-11-17 | 2027-05-01 | 2028-05-16 | Material | NA | FALSE | $15,800 ¦ $31,600 | NA ¦ NA | 576.107 | 24157.0844 | 0 | 0 | 0 | 4.7051 | 497.793 | 8354.5864 | 15300 | 0 | 0 | 0 | 502.4981 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
616 | Delevan - Cortina Line Reconductoring |  |  | Colusa | The Delevan – Cortina 230 kV transmission line, located in Colusa county, is 18.0 miles long and supported by 122 structures. The Delevan – Cortina 230 kV line is a critical component of the 230 kV corridor in the North Valley connecting the Round Mountain and Vaca-Dixon substations. This project will help facilitate the delivery of an additional 437 MW of renewable generation and energy storage to PG&E’s local grid. The project scope of work includes: • Reconductor approximately 17.7 miles of the Delevan – Cortina 230 kV Line with a conductor able to achieve at least 1517 Amps of summer interior emergency rating. The use of Aluminum conductor composite reinforced (ACCR) or Aluminum conductor composite core (ACCC) conductors will be investigated to minimize unnecessary structure replacement. • Conduct a field verification to determine if the existing structures will need to be replaced, repaired or recoated. • Replace all insulators and insulator hardware. When reinsulating and reconductoring on double circuit structures, the scope is limited to insulators and hardware on the subject line. • Upgrade terminal equipment at Delevan and Cortina substations, as needed, to accommodate transmission line conductor capacity. • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2025-11-25 | 124 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 18 | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5804245 | T.0009013 | Delevan - Cortina Line Reconductoring | 2 | 60 | NA ¦ Ex112248 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-10-28 | 2028-12-01 | 2028-02-28 | NA | NA | FALSE | $17,700 ¦ $35,400 | NA ¦ NA | 1406.0895 | 39698.393 | 0 | 0 | 0 | 358.5142 | 982.5758 | 603.479 | 26894.887 | 9858.937 | 1000 | 0 | 1341.09 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
617 | Manning: Tranq POCO Man-Tranq#3 |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Transmission Line - Conductor | New | NA | T.0009550 | Policy | T-Line Capacity | NERC TPL Standards | NA | 2025-08-18 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 11 | NA | 500 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5809623 | T.0009194 | Manning New 500kV Sub Connection | 18 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2027-03-15 | 2028-01-01 | 2028-05-31 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 87.3248 | 1627.1313 | 0 | 0 | 0 | 12.1458 | 59.7805 | 902.7131 | 596.8891 | 55.6029 | 0 | 0 | 71.9262 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 12.1458 | 71.9262 | 87.3248 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
618 | Panoche-Excelsior SW STA #1 & #2 115Kv |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0009550 | Policy | T-Line Capacity | NERC TPL Standards | NA | 2025-08-29 | 77 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 57 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5809641 | T.0009194 | Manning New 500kV Sub Connection | 18 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-04-27 | 2028-01-01 | 2028-05-31 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 260.5296 | 2441.6131 | 0 | 0 | 0 | 11.0155 | 128.7044 | 2212.3545 | 33.9624 | 55.5763 | 0 | 0 | 139.7199 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 11.0155 | 139.7199 | 250.3953 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
619 | Manning: Gates-Panoche #1 & #2 230kV |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0009550 | Policy | T-Line Capacity | NERC TPL Standards | NA | 2025-09-16 | 79 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 87.2 | NA | 500 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5809639 | T.0009194 | Manning New 500kV Sub Connection | 18 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-04-06 | 2028-01-01 | 2028-06-01 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 543.2814 | 5573.1083 | 0 | 0 | 0 | 43.7811 | 223.0501 | 4841.509 | 398.9421 | 65.826 | 0 | 0 | 266.8312 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 43.7811 | 266.8313 | 516.4975 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
620 | Manning: Panoche Shoofly |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Transmission Line - Conductor | New | NA | T.0009550 | Policy | T-Line Capacity | NERC TPL Standards | NA | 2025-09-16 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.1 | NA | 500 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5809640 | T.0009194 | Manning New 500kV Sub Connection | 18 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2027-09-14 | 2028-01-01 | 2028-06-01 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 301.7831 | 2356.4123 | 0 | 0 | 0 | 77.2988 | 166.7692 | 93.7721 | 1725.5474 | 293.0247 | 0 | 0 | 244.0681 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 77.2988 | 244.068 | 301.7831 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
621 | MANNING SUB_LAND RIGHTS |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Other | New | NA | NA | Policy | Substation Capacity | NERC TPL Standards | NA | 2025-09-16 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5560999 | T.0009194 | Manning New 500kV Sub Connection | 18 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2025 | 2023 | TRUE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | NA | 2028-01-01 | 2027-02-02 | NA | NA | TRUE | $325,000 ¦ $485,000 | NA ¦ NA | 383.7665 | 4772.5665 | 0 | 0 | 0 | 0 | 127.2665 | 2945.3 | 1700 | 0 | 0 | 0 | 127.2665 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 127.2665 | 256.5 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
622 | PIERCY-METCALF 10390_RECONDUCTOR |  |  | Fremont, Alameda | The revised scope aims to reconductor the following 115 kV lines using advanced conductors to achieve a summer emergency rating of 3,000 Amps or higher: Piercy-Metcalf, Swift-Metcalf, Newark-Dixon Landing, and McKee-Piercy. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0003803 ¦ T.0005211 ¦ T.0009571 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-07-01 | 30 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | 4.7 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5806848 | T.0009536 | Dixon Landing 115 kV Upgrade | 10 | 60 | NA ¦ EX113207 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-10-18 | 2008-12-31 | 2030-12-26 | Prioritization | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 307.265 | 28935.5054 | 0 | 0 | 0 | 12.5746 | 226.6391 | 586.3628 | 2000 | 5000 | 1000 | 0 | 239.2137 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
623 | SWIFT-METCALF 10326_RECONDUCTOR |  |  | San Jose, Santa Clara ¦ Santa Clara | The revised scope aims to reconductor the following 115 kV lines using advanced conductors to achieve a summer emergency rating of 3,000 Amps or higher: Piercy-Metcalf, Swift-Metcalf, Newark-Dixon Landing, and McKee-Piercy. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0003803 ¦ T.0005211 ¦ T.0009571 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-09-23 | 30 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 4.7 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5806849 | T.0009536 | Dixon Landing 115 kV Upgrade | 10 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-10-11 | 2008-12-31 | 2030-12-26 | Prioritization | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 931.0055 | 56686.1686 | 0 | 0 | 0 | 182.7605 | 635.4574 | 867.9507 | 17500 | 30000 | 7000 | 500 | 818.2179 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
624 | McKee- Piercy 115kV: Swift- Metcalf Upgr |  |  | San Jose, Santa Clara | The revised scope aims to reconductor the following 115 kV lines using advanced conductors to achieve a summer emergency rating of 3,000 Amps or higher: Piercy-Metcalf, Swift-Metcalf, Newark-Dixon Landing, and McKee-Piercy. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0003803 ¦ T.0005211 ¦ T.0009571 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-09-24 | 30 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 7.75 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815001 | T.0009536 | Dixon Landing 115 kV Upgrade | 10 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Planning | 5 | 2028-10-18 | 2008-12-31 | 2030-12-26 | Scope Change | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 53.2641 | 34976.0738 | 0 | 0 | 0 | 0 | 13.7504 | 417.4047 | 0 | 0 | 0 | 0 | 13.7504 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
625 | NEWARK-DIXON LANDING 10227_RECONDUCTOR |  |  | San Jose, Santa Clara ¦ Santa Clara | The revised scope aims to reconductor the following 115 kV lines using advanced conductors to achieve a summer emergency rating of 3,000 Amps or higher: Piercy-Metcalf, Swift-Metcalf, Newark-Dixon Landing, and McKee-Piercy. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0003803 ¦ T.0005211 ¦ T.0009571 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-29 | 30 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 8.9 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5806850 | T.0009536 | Dixon Landing 115 kV Upgrade | 10 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Planning | 5 | 2028-10-18 | 2008-12-31 | 2030-12-27 | Prioritization | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 365.1412 | 57779.9519 | 0 | 0 | 0 | 0.3444 | 192.9632 | 1586.6443 | 15500 | 30000 | 10500 | 0 | 193.3076 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
626 | GARBERVILLE 60KV AREA REINFORCEMENT |  |  | Garberville CDP, Humboldt ¦ Humboldt | This project proposes to: • Reconductor the entire Bridgeville-Garberville 60 kV line to achieve at least 631Amps of summer normal rating (715 AAC conductor) which is about 36 circuit miles in length. • Install a 20 MVAR STATCOM at Fort Seward 60 kV Substation. • Establish a control point to open line section from Garberville to Kekawaka 60 kVline. • Establish a control point to open line section from Rio Dell Jct. to Carlotta 60 kV line. | Transmission Line/Substation | New | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-09-02 | 125 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | 36.2 | NA | 60 | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807359 | T.0009603 | Garberville 60kV Area Reinforcement | 1 | 60 | NA ¦ EX113225 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-06-08 | 2032-12-31 | 2028-12-05 | NA | NA | FALSE | 204000 | NA ¦ NA | 892.1377 | 66283.9871 | 0 | 0 | 0 | 380.1026 | 462.6857 | 1059.18 | 18668.573 | 21511.779 | 0 | 0 | 842.7883 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
627 | Tulucay-Napa 60kV Line Reconductoring |  |  | Napa ¦ Napa, Napa | Reconductor the Tulucay-Napa #2 60 kV line from Tulucay to Basalt | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-05-08 | 126 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 1.4 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807341 | T.0009607 | Tulucay-Napa 60kV Line Reconductoring | 1 | 60 | NA ¦ EX113226 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-10-14 | 2028-12-31 | 2026-12-14 | NA | NA | TRUE | 14600 | NA ¦ NA | 765.6381 | 6057.0602 | 0 | 0 | 0 | 130.5423 | 565.6334 | 4959.1575 | 154.4134 | 0 | 0 | 0 | 696.1757 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
628 | Sonoma-Pueblo 115kV Reconductor |  |  | Napa ¦ Napa, Napa ¦ Sonoma ¦ Sonoma, Sonoma | Reconductoring of the Fulton-Santa Rosa #1 and #2, Santa Rosa-Corona and Corona-Lakeville 115 kV lines | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0003477 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-05-22 | 124 | Steady State Power Flow System Analysis | TBD | TBD | Zone 1 - HHZ ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 18.5 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807467 | T.0009626 | Santa Rosa 115kV Reinforcement Project | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2031-10-16 | 2028-12-31 | 2031-11-13 | Prioritization | NA | FALSE | 74000 | NA ¦ NA | 31.9515 | 11629.8694 | 0 | 0 | 0 | 31.5732 | 0.3783 | 1.9447 | 0 | 0 | 0 | 0 | 31.9515 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
629 | Fulton-Santa Rosa#1 115kV Reconductor |  |  | Cotati, Sonoma ¦ Penngrove CDP, Sonoma ¦ Petaluma, Sonoma ¦ Rohnert Park, Sonoma ¦ Santa Rosa, Sonoma ¦ Sonoma | Reconductoring of the Fulton-Santa Rosa #1 and #2, Santa Rosa-Corona and Corona-Lakeville 115 kV lines | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000555 ¦ T.0002317 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-07-31 | 22 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 6.7 | NA | 115 | NA | NA | NA | NA | 4.01 | Non-IGP | 5807463 | T.0009626 | Santa Rosa 115kV Reinforcement Project | 5 | 60 | NA ¦ EX113227 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-04-01 | 2028-12-31 | 2031-04-28 | Prioritization | NA | FALSE | 74000 | NA ¦ NA | 152.5431 | 40711.6027 | 0 | 0 | 0 | 67.9298 | 5.5621 | 688.1108 | 1000 | 950 | 3000 | 15000 | 73.4919 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
630 | Corona-Lakeville 115kV Reconductor |  |  | Petaluma, Sonoma ¦ Sonoma | Reconductoring of the Fulton-Santa Rosa #1 and #2, Santa Rosa-Corona and Corona-Lakeville 115 kV lines | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000555 ¦ T.0002317 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-08-29 | 27 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 5.8 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807466 | T.0009626 | Santa Rosa 115kV Reinforcement Project | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-10-16 | 2028-12-31 | 2031-11-13 | Prioritization | NA | FALSE | 74000 | NA ¦ NA | 26.4292 | 17764.3969 | 0 | 0 | 0 | 26.1163 | 0.313 | 1.6086 | 0 | 0 | 0 | 0 | 26.4292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
631 | FULTON-SANTA ROSA#2 115KV RECONDUCTOR |  |  | Santa Rosa, Sonoma ¦ Sonoma | Reconductoring of the Fulton-Santa Rosa #1 and #2, Santa Rosa-Corona and Corona-Lakeville 115 kV lines | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000555 ¦ T.0002317 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-07-30 | 22 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 6.3 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807464 | T.0009626 | Santa Rosa 115kV Reinforcement Project | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-11-14 | 2028-12-31 | 2031-12-15 | Prioritization | NA | FALSE | 74000 | NA ¦ NA | 52.76 | 1222.9012 | 0 | 0 | 0 | 51.8283 | 0.9316 | 3.2112 | 0 | 0 | 0 | 0 | 52.76 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
632 | Santa Rosa-Corona 115kV Reconductor |  |  | Cotati, Sonoma ¦ Penngrove CDP, Sonoma ¦ Petaluma, Sonoma ¦ Rohnert Park, Sonoma ¦ Santa Rosa, Sonoma ¦ Sonoma | Reconductoring of the Fulton-Santa Rosa #1 and #2, Santa Rosa-Corona and Corona-Lakeville 115 kV lines | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000555 ¦ T.0002317 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-07-31 | 27 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 14.3 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807465 | T.0009626 | Santa Rosa 115kV Reinforcement Project | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-11-14 | 2028-12-31 | 2031-12-15 | Prioritization | NA | FALSE | 74000 | NA ¦ NA | 46.7122 | 17751.5478 | 0 | 0 | 0 | 45.6188 | 1.0933 | 2.8431 | 0 | 0 | 0 | 0 | 46.7122 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
633 | Midway-Shafter 115kV Line Recond |  |  | Buttonwillow CDP, Kern ¦ Kern | This project proposes to: • Reconductor ~13.6 circuit miles of Midway – Shafter 115 kV Line • Reconductor ~8.3 circuit miles on the Shafter-Rio Bravo 115 kV • Reconductor ~3.9 circuit miles on the Midway-Tupman-Rio Bravo-Renfro 115 kV (between Rio Bravo and Renfro Junction From 11/62 To Rio Bravo Sub) • Reconductor ~3.5 circuit miles on the Lerdo-Kern Oil-7th Standard 115 kV Line (between Lerdo J and Kern Oil, from 023/005 To Kern Oil Sub) • Reconductor ~6.8 circuit miles on the Smyrna-Semitropic-Midway 115 kV Line (between Midway and Ganso from Midway to 081/634 and from 081/634 to Ganso) • Reconductor ~14.1 circuit miles on the Semitropic-Midway #1 115 kV Line (between Midway and Semitropic_E) • Convert the existing control point to a summer setup to open line section from Wasco to McFarland 70 kV line. • Convert the existing control point to a summer setup to open line section from Famoso to Cawelo C 115 kV line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-12-01 | 78 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | 13.6 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5814001 | T.0009633 | NorthEast Kern 115kV Reconductor | 7 | 60 | NA ¦ EX113342 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-07-25 | 2032-12-31 | 2028-12-04 | NA | NA | FALSE | 256000 | NA ¦ NA | 108.8531 | 30915.3479 | 0 | 0 | 0 | 0 | 88.7673 | 378.9051 | 0 | 0 | 0 | 0 | 88.7673 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
634 | Shafter-Rio Bravo 115kV Line Recond |  |  | Kern | This project proposes to: • Reconductor ~13.6 circuit miles of Midway – Shafter 115 kV Line • Reconductor ~8.3 circuit miles on the Shafter-Rio Bravo 115 kV • Reconductor ~3.9 circuit miles on the Midway-Tupman-Rio Bravo-Renfro 115 kV (between Rio Bravo and Renfro Junction From 11/62 To Rio Bravo Sub) • Reconductor ~3.5 circuit miles on the Lerdo-Kern Oil-7th Standard 115 kV Line (between Lerdo J and Kern Oil, from 023/005 To Kern Oil Sub) • Reconductor ~6.8 circuit miles on the Smyrna-Semitropic-Midway 115 kV Line (between Midway and Ganso from Midway to 081/634 and from 081/634 to Ganso) • Reconductor ~14.1 circuit miles on the Semitropic-Midway #1 115 kV Line (between Midway and Semitropic_E) • Convert the existing control point to a summer setup to open line section from Wasco to McFarland 70 kV line. • Convert the existing control point to a summer setup to open line section from Famoso to Cawelo C 115 kV line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2024-10-03 | 62 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | 8.3 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5813999 | T.0009633 | NorthEast Kern 115kV Reconductor | 7 | 60 | NA ¦ EX113342 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-07-26 | 2032-12-31 | 2029-11-27 | NA | NA | FALSE | 256000 | NA ¦ NA | 72.8211 | 26346.0376 | 0 | 0 | 0 | 0 | 52.3605 | 217.1992 | 0 | 0 | 0 | 0 | 52.3604 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
635 | Midway-Tupman-Rio Bravo-Renfro 115kV Rec |  |  | Bakersfield, Kern ¦ Buttonwillow CDP, Kern ¦ Greenacres CDP, Kern ¦ Kern ¦ Rosedale CDP, Kern | This project proposes to: • Reconductor ~13.6 circuit miles of Midway – Shafter 115 kV Line • Reconductor ~8.3 circuit miles on the Shafter-Rio Bravo 115 kV • Reconductor ~3.9 circuit miles on the Midway-Tupman-Rio Bravo-Renfro 115 kV (between Rio Bravo and Renfro Junction From 11/62 To Rio Bravo Sub) • Reconductor ~3.5 circuit miles on the Lerdo-Kern Oil-7th Standard 115 kV Line (between Lerdo J and Kern Oil, from 023/005 To Kern Oil Sub) • Reconductor ~6.8 circuit miles on the Smyrna-Semitropic-Midway 115 kV Line (between Midway and Ganso from Midway to 081/634 and from 081/634 to Ganso) • Reconductor ~14.1 circuit miles on the Semitropic-Midway #1 115 kV Line (between Midway and Semitropic_E) • Convert the existing control point to a summer setup to open line section from Wasco to McFarland 70 kV line. • Convert the existing control point to a summer setup to open line section from Famoso to Cawelo C 115 kV line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-24 | 125 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | 3.9 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5813955 | T.0009633 | NorthEast Kern 115kV Reconductor | 7 | 60 | NA ¦ EX113342 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-11-09 | 2032-12-31 | 2030-06-21 | NA | NA | FALSE | 256000 | NA ¦ NA | 70.8076 | 37618.8192 | 0 | 0 | 0 | 0 | 46.4937 | 590.3123 | 0 | 0 | 0 | 0 | 46.4938 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
636 | NorthEast Kern 115kV Reconductor |  |  | Buttonwillow CDP, Kern ¦ Kern | This project proposes to: • Reconductor ~13.6 circuit miles of Midway – Shafter 115 kV Line • Reconductor ~8.3 circuit miles on the Shafter-Rio Bravo 115 kV • Reconductor ~3.9 circuit miles on the Midway-Tupman-Rio Bravo-Renfro 115 kV (between Rio Bravo and Renfro Junction From 11/62 To Rio Bravo Sub) • Reconductor ~3.5 circuit miles on the Lerdo-Kern Oil-7th Standard 115 kV Line (between Lerdo J and Kern Oil, from 023/005 To Kern Oil Sub) • Reconductor ~6.8 circuit miles on the Smyrna-Semitropic-Midway 115 kV Line (between Midway and Ganso from Midway to 081/634 and from 081/634 to Ganso) • Reconductor ~14.1 circuit miles on the Semitropic-Midway #1 115 kV Line (between Midway and Semitropic_E) • Convert the existing control point to a summer setup to open line section from Wasco to McFarland 70 kV line. • Convert the existing control point to a summer setup to open line section from Famoso to Cawelo C 115 kV line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-12-01 | 78 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 3.5 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807525 | T.0009633 | NorthEast Kern 115kV Reconductor | 7 | 60 | NA ¦ EX113342 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-09-06 | 2032-12-31 | 2030-12-18 | NA | NA | FALSE | 256000 | NA ¦ NA | 642.1423 | 186257.7729 | 0 | 0 | 0 | 21.9233 | 559.4705 | 676.3791 | 33000 | 32500 | 40000 | 40000 | 581.3938 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
637 | Smyrna-Semitropic-Midway 115kV Line Reco |  |  | Buttonwillow CDP, Kern ¦ Kern | This project proposes to: • Reconductor ~13.6 circuit miles of Midway – Shafter 115 kV Line • Reconductor ~8.3 circuit miles on the Shafter-Rio Bravo 115 kV • Reconductor ~3.9 circuit miles on the Midway-Tupman-Rio Bravo-Renfro 115 kV (between Rio Bravo and Renfro Junction From 11/62 To Rio Bravo Sub) • Reconductor ~3.5 circuit miles on the Lerdo-Kern Oil-7th Standard 115 kV Line (between Lerdo J and Kern Oil, from 023/005 To Kern Oil Sub) • Reconductor ~6.8 circuit miles on the Smyrna-Semitropic-Midway 115 kV Line (between Midway and Ganso from Midway to 081/634 and from 081/634 to Ganso) • Reconductor ~14.1 circuit miles on the Semitropic-Midway #1 115 kV Line (between Midway and Semitropic_E) • Convert the existing control point to a summer setup to open line section from Wasco to McFarland 70 kV line. • Convert the existing control point to a summer setup to open line section from Famoso to Cawelo C 115 kV line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-13 | 23 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | 6.8 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5813957 | T.0009633 | NorthEast Kern 115kV Reconductor | 7 | 60 | NA ¦ EX113342 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2031-06-09 | 2032-12-31 | 2031-09-19 | NA | NA | FALSE | 256000 | NA ¦ NA | 24.2582 | 31948.1293 | 0 | 0 | 0 | 0 | 5.9193 | 410.4712 | 0 | 0 | 0 | 0 | 5.9193 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
638 | Semitropic-Midway #1 115kV Line Recond |  |  | Buttonwillow CDP, Kern ¦ Kern | This project proposes to: • Reconductor ~13.6 circuit miles of Midway – Shafter 115 kV Line • Reconductor ~8.3 circuit miles on the Shafter-Rio Bravo 115 kV • Reconductor ~3.9 circuit miles on the Midway-Tupman-Rio Bravo-Renfro 115 kV (between Rio Bravo and Renfro Junction From 11/62 To Rio Bravo Sub) • Reconductor ~3.5 circuit miles on the Lerdo-Kern Oil-7th Standard 115 kV Line (between Lerdo J and Kern Oil, from 023/005 To Kern Oil Sub) • Reconductor ~6.8 circuit miles on the Smyrna-Semitropic-Midway 115 kV Line (between Midway and Ganso from Midway to 081/634 and from 081/634 to Ganso) • Reconductor ~14.1 circuit miles on the Semitropic-Midway #1 115 kV Line (between Midway and Semitropic_E) • Convert the existing control point to a summer setup to open line section from Wasco to McFarland 70 kV line. • Convert the existing control point to a summer setup to open line section from Famoso to Cawelo C 115 kV line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-27 | 86 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | 14.1 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5813952 | T.0009633 | NorthEast Kern 115kV Reconductor | 7 | 60 | NA ¦ EX113342 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2031-09-26 | 2032-12-31 | 2032-05-21 | NA | NA | FALSE | 256000 | NA ¦ NA | 150.3405 | 48185.4492 | 0 | 0 | 0 | 0 | 119.7348 | 481.4266 | 0 | 0 | 0 | 0 | 119.7349 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
639 | REDWD CITY AREA REINF_SAN MATEO-BELMONT |  |  | Belmont, San Mateo ¦ Foster City, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The scope of this project is to install a new 230/115 kV Transformer at Ravenswood Substation, and reconductor 6.5 circuit miles of the San Mateo - Belmont 115 kV Line and 7.5 circuit miles of the Ravenswood - Bair 115 kV Line #1. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0002156 ¦ T.0002155 ¦T.0006509 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-09 | 126 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 6.5 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807399 | T.0009638 | Redwd City Area Reinf Projects | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2013 | FALSE | 2023 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-04-24 | 2030-12-31 | 2030-02-08 | NA | NA | FALSE | 110800 | NA ¦ NA | 395.5692 | 25377.0521 | 0 | 0 | 0 | 111.9754 | 242.0187 | 483.715 | 0 | 0 | 0 | 0 | 353.9941 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
640 | REDWD CITY AREA REINF_RAVENSWOOD-BAIR |  |  | Menlo Park, San Mateo ¦ Redwood City, San Mateo | The scope of this project is to install a new 230/115 kV Transformer at Ravenswood Substation, and reconductor 6.5 circuit miles of the San Mateo - Belmont 115 kV Line and 7.5 circuit miles of the Ravenswood - Bair 115 kV Line #1. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0002156 ¦ T.0002155 ¦T.0006509 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-10 | 124 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 14 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807418 | T.0009638 | Redwd City Area Reinf Projects | 3 | 60 | NA ¦ EX113232 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-04-24 | 2030-12-31 | 2030-02-08 | NA | NA | FALSE | 110800 | NA ¦ NA | 343.9484 | 102254.7221 | 0 | 0 | 0 | 102.8236 | 206.7911 | 545.1076 | 17900 | 81000 | 2500 | 0 | 309.6146 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
641 | S of SM Cap Incr: Ravenswood-San Mateo |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The project work will involve upgrading the capacity of the Ravenswood-San Mateo 115 kV Line. Specifically, this work will include: • Reconductoring of the 12-mile Ravenswood-San Mateo 115 kV Line, with a conductor having an emergency capability of at least 1,100 Amps; • Reinforcing the lattice steel towers, where needed, to support the new conductor; and • Replacement of limiting equipment within the substations. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0006761 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-21 | 67 | Steady State Power Flow System Analysis | Wires - Location/Route Alternative | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 12 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807522 | T.0009639 | S of SM Cap Incr Ravenswood San Mateo | 1 | 60 | NA ¦ EX113213 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-02-15 | 2009-05-01 | 2031-12-31 | Prioritization | NA | FALSE | $10,000 ¦ $20,000 | NA ¦ NA | 1094.2746 | 113710.7371 | 0 | 0 | 1.0183 | 280.6392 | 711.3035 | 575.2201 | 10100 | 40200 | 2300 | 0 | 992.9611 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
642 | Cortina #1 60050: Reconductor |  |  | Arbuckle CDP, Colusa ¦ Colusa ¦ Yolo | The Cortina #1 60 kV transmission line, located in Colusa County, is approximately 26.2 miles long and supported by 447 structures. The Arbuckle, Harrington and Dunnigan 60 kV substations are radially served by the Cortina #1 60 kV line with the Cortina #2 60 kV line serving as an alternate source with normally open switches. This project will help facilitate the delivery of an additional 10 MW to serve increased load in the Cortina area due to the addition of Tesla charging banks. The project scope of work includes: • Reconductor approximately 26.2 miles of the Cortina #1 60 kV Line between Cortina Substation and Dunnigan Substation with a conductor able to achieve at least 818 Amps of summer interior normal rating. • If new structures are required, they will be sized to accommodate a future distribution underbuild conductor of 715 AAC. • Existing distribution underbuild will be relocated to new transmission structures. • Removal of the idle Drake Substation tap and Switch 25. • Upgrade substation terminal equipment to achieve full conductor capacity. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-26 | 126 | Steady State Power Flow System Analysis | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 26.2 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807521 | T.0009641 | Cortina #1 60 kV Line Reconductoring | 4 | 60 | NA ¦ EX113241 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7836-E | 2026-02-11 | Approved | 2026 | Engineering more than 50% complete | 3 | 2026-10-15 | 2028-06-01 | 2027-02-11 | NA | NA | TRUE | $47,100 ¦ $94,300 | NA ¦ NA | 950.5027 | 32529.1362 | 0 | 0 | 0 | 144.1975 | 667.1392 | 11417.7995 | 3045.407 | 18300 | 0 | 0 | 811.3367 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
643 | Cortina #1 Recond: Arbuckle to Dunnigan |  |  | Arbuckle CDP, Colusa ¦ Colusa ¦ Yolo | The Cortina #1 60 kV transmission line, located in Colusa County, is approximately 26.2 miles long and supported by 447 structures. The Arbuckle, Harrington and Dunnigan 60 kV substations are radially served by the Cortina #1 60 kV line with the Cortina #2 60 kV line serving as an alternate source with normally open switches. This project will help facilitate the delivery of an additional 10 MW to serve increased load in the Cortina area due to the addition of Tesla charging banks. The project scope of work includes: • Reconductor approximately 26.2 miles of the Cortina #1 60 kV Line between Cortina Substation and Dunnigan Substation with a conductor able to achieve at least 818 Amps of summer interior normal rating. • If new structures are required, they will be sized to accommodate a future distribution underbuild conductor of 715 AAC. • Existing distribution underbuild will be relocated to new transmission structures. • Removal of the idle Drake Substation tap and Switch 25. • Upgrade substation terminal equipment to achieve full conductor capacity. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-26 | 126 | Steady State Power Flow System Analysis | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 26.2 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811325 | T.0009641 | Cortina #1 60 kV Line Reconductoring | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7836-E | 2026-02-11 | Approved | 2026 | Engineering more than 50% complete | 3 | 2027-09-23 | 2028-06-01 | 2028-01-27 | NA | NA | FALSE | $47,100 ¦ $94,300 | NA ¦ NA | 499.065 | 65563.5607 | 0 | 0 | 0 | 22.1073 | 394.3472 | 347.1061 | 43200 | 21600 | 0 | 0 | 416.4545 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
644 | Borden-Storey 230 kV 1 & 2 Recond |  |  | Chowchilla, Madera ¦ Madera ¦ Madera Acres CDP, Madera ¦ Merced ¦ Merced, Merced ¦ Parksdale CDP, Madera | Reconductoring the Borden – Storey section(s) of the Wilson – Borden #1 and #2 230 kV lines | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2025-08-21 | 20 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 10 | NA | 230 | NA | NA | NA | NA | 3.0011 | Non-IGP | 5807523 | T.0009662 | Borden-Storey Project | 4 | 60 | NA ¦ EX113239 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-07-12 | 2032-12-31 | 2030-01-09 | NA | NA | FALSE | 50000 | NA ¦ NA | 614.5616 | 42105.8349 | 0 | 0 | 0 | 24.7764 | 410.6747 | 1069.2662 | 17771.1805 | 9039.7308 | 13749.8627 | 40.3436 | 435.4511 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-F-Board-Approved_2022-2023_Transmission-Plan.pdf
645 | BORDEN-STOREY_LINE_#2 230kV |  |  | Chowchilla, Madera ¦ Madera ¦ Madera Acres CDP, Madera ¦ Merced ¦ Merced, Merced ¦ Parksdale CDP, Madera | CAISO has identified constraints on these lines and is recommending reconducting the Borden-Storey 230 kV Nos. 1 & 2 line sections as a policy-driven project. Completion of this project will allow interconnection of new projects in the Greater Fresno area. The project scope of work includes following: • Reconductor roughly 5.1 miles DCTL (10.2 circuit miles) of the Borden-Storey 230 kV Nos. 1 & 2 line sections of the Wilson-Borden 230 kV Nos. 1 & 2 lines. CAISO is recommending a conductor with ampacity of at least 1,517 Amps. • Upgrade associated substation terminal equipment and remove any limiting components to achieve the full conductor capability. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2025-08-21 | 21 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 10.2 | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5817322 | T.0009662 | Borden-Storey Project | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2026 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-07-12 | 2032-12-31 | 2030-01-09 | NA | NA | FALSE | 50000 | NA ¦ NA | 9.1771 | 20075.1199 | 0 | 0 | 0 | 0 | 0 | 69.9912 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-F-Board-Approved_2022-2023_Transmission-Plan.pdf
646 | STOREY SUB 230KV LINE TERMS |  |  | Chowchilla, Madera ¦ Madera ¦ Madera Acres CDP, Madera ¦ Merced ¦ Merced, Merced ¦ Parksdale CDP, Madera | CAISO has identified constraints on these lines and is recommending reconducting the Borden-Storey 230 kV Nos. 1 & 2 line sections as a policy-driven project. Completion of this project will allow interconnection of new projects in the Greater Fresno area. The project scope of work includes following: • Reconductor roughly 5.1 miles DCTL (10.2 circuit miles) of the Borden-Storey 230 kV Nos. 1 & 2 line sections of the Wilson-Borden 230 kV Nos. 1 & 2 lines. CAISO is recommending a conductor with ampacity of at least 1,517 Amps. • Upgrade associated substation terminal equipment and remove any limiting components to achieve the full conductor capability. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2025-08-21 | 21 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5817321 | T.0009662 | Borden-Storey Project | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2026 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-11-07 | 2032-12-31 | 2029-12-20 | NA | NA | FALSE | 50000 | NA ¦ NA | 4.5175 | 1403.9891 | 0 | 0 | 0 | 0 | 0 | 81.8932 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-F-Board-Approved_2022-2023_Transmission-Plan.pdf
647 | Ignacio Area Upgrade: Ignacio-Las Galina |  |  | Marin ¦ Novato, Marin ¦ San Rafael, Marin | Reconductor Ignacio - San Rafael No. 1 115 kV Line, Ignacio - Alto 60 kV Line, and Ignacio - San Rafael No. 3 115 kV Line section from Ignacio - Las Gallinas as well as upgrade limiting equipment on lines. Add a 10 MVAR shunt capacitor at Greenbrae 60 kV Substation and associated substation upgrades to accommodate this installation | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-04-03 | 50 | Steady State Power Flow System Analysis | Wires - Location/Route Alternative | Over $500 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 4.1 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807461 | T.0009719 | Ignacio Area Upgrade | 6 | 60 | NA ¦ EX113201 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2012 ¦ 2018 | FALSE | 2012 ¦ 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-09-03 | 2023-12-01 | 2027-11-30 | Prioritization | NA | TRUE | 37000 | NA ¦ NA | 505.0162 | 17305.9044 | 0 | 0 | 0 | 59.0422 | 205.6071 | 1066.2409 | 7564.3004 | 8000 | 0 | 0 | 264.6493 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
648 | ALTO SUB UPGRADES |  |  | Mill Valley, Marin | Reconductor Ignacio - San Rafael No. 1 115 kV Line, Ignacio - Alto 60 kV Line, and Ignacio - San Rafael No. 3 115 kV Line section from Ignacio - Las Gallinas as well as upgrade limiting equipment on lines. Add a 10 MVAR shunt capacitor at Greenbrae 60 kV Substation and associated substation upgrades to accommodate this installation | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-11 | 39 | Steady State Power Flow System Analysis | Wires - Location/Route Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 0.89452 | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5814486 | T.0009719 | Ignacio Area Upgrade | 6 | 60 | NA ¦ EX113201 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2012 ¦ 2018 | FALSE | 2012 ¦ 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-11-09 | 2023-12-01 | 2029-03-29 | Prioritization | NA | FALSE | 37000 | NA ¦ NA | 78.0178 | 4209.9994 | 0 | 0 | 0 | 0 | 50.1935 | 123.5136 | 2036.2923 | 2000 | 0 | 0 | 50.1935 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
649 | Ignacio Area Upgrade: Ignacio-Alto |  |  | Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin | Reconductor Ignacio - San Rafael No. 1 115 kV Line, Ignacio - Alto 60 kV Line, and Ignacio - San Rafael No. 3 115 kV Line section from Ignacio - Las Gallinas as well as upgrade limiting equipment on lines. Add a 10 MVAR shunt capacitor at Greenbrae 60 kV Substation and associated substation upgrades to accommodate this installation | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-08 | 50 | Steady State Power Flow System Analysis | Wires - Location/Route Alternative | Over $500 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 17.8 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807460 | T.0009719 | Ignacio Area Upgrade | 6 | 60 | NA ¦ EX113201 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2012 ¦ 2018 | FALSE | 2012 ¦ 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-12-15 | 2023-12-01 | 2029-08-15 | Prioritization | NA | FALSE | 37000 | NA ¦ NA | 281.7805 | 30885.5305 | 0 | 0 | 0 | 61.7913 | 195.1234 | 495.7122 | 1738.2682 | 5000 | 22615.2344 | 106.1903 | 256.9147 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
650 | Ignacio Area Upgrade: Ignacio-San Rafael |  |  | Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin | Reconductor Ignacio - San Rafael No. 1 115 kV Line, Ignacio - Alto 60 kV Line, and Ignacio - San Rafael No. 3 115 kV Line section from Ignacio - Las Gallinas as well as upgrade limiting equipment on lines. Add a 10 MVAR shunt capacitor at Greenbrae 60 kV Substation and associated substation upgrades to accommodate this installation | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-31 | 65 | Steady State Power Flow System Analysis | Wires - Location/Route Alternative | Over $500 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 11.4 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807459 | T.0009719 | Ignacio Area Upgrade | 6 | 60 | NA ¦ EX113201 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2012 ¦ 2018 | FALSE | 2012 ¦ 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-02-25 | 2023-12-01 | 2028-04-07 | Prioritization | NA | FALSE | 37000 | NA ¦ NA | 428.2155 | 7369.5888 | 0 | 0 | 0 | 139.3696 | 231.5917 | 785.7619 | 3212.8655 | 3000 | 0 | 0 | 370.9614 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
651 | Tejon Reinfor: Wheeler Ridge-San Bernard |  |  | Kern | Reconductor of the Wheeler Ridge – Tejon 70kV line, Wheeler Ridge – San Bernard 70kV line, and San Bernard – Tejon 70kV line and replace the limiting disconnect switches. Mitigate thermal overloads on the Wheeler Ridge – Tejon 70kV line, Wheeler Ridge – San Bernard 70kV line, San Bernard – Tejon 70kV line caused by P3 overloads and additional loading at Tejon substation | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-15 | 72 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | 5.9 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5810186 | T.0010228 | Tejon Reinfor Wheeler Ridge-San Bernard | 3 | 60 | NA ¦ EX113705 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-12-02 | 2029-05-01 | 2028-04-28 | NA | NA | FALSE | $28,000 ¦ $56,000 | NA ¦ NA | 199.0303 | 14882.0359 | 0 | 0 | 0 | 0 | 160.4908 | 421.5451 | 7000 | 7000 | 300 | 0 | 160.4908 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
652 | Tejon Reinforce: Wheeler Ridge-Tejon |  |  | Kern | Reconductor of the Wheeler Ridge – Tejon 70kV line, Wheeler Ridge – San Bernard 70kV line, and San Bernard – Tejon 70kV line and replace the limiting disconnect switches. Mitigate thermal overloads on the Wheeler Ridge – Tejon 70kV line, Wheeler Ridge – San Bernard 70kV line, San Bernard – Tejon 70kV line caused by P3 overloads and additional loading at Tejon substation | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-04-03 | 50 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | 5 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5810187 | T.0010228 | Tejon Reinfor Wheeler Ridge-San Bernard | 3 | 60 | NA ¦ EX113705 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-03-03 | 2029-05-01 | 2027-04-30 | NA | NA | TRUE | $28,000 ¦ $56,000 | NA ¦ NA | 121.8298 | 15656.2021 | 0 | 0 | 0 | 0 | 73.315 | 1482.8871 | 306.1456 | 7000 | 100 | 0 | 73.315 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
653 | Tejon Reinforce: San Bernard-Tejon |  |  | Kern | Reconductor of the Wheeler Ridge – Tejon 70kV line, Wheeler Ridge – San Bernard 70kV line, and San Bernard – Tejon 70kV line and replace the limiting disconnect switches. Mitigate thermal overloads on the Wheeler Ridge – Tejon 70kV line, Wheeler Ridge – San Bernard 70kV line, San Bernard – Tejon 70kV line caused by P3 overloads and additional loading at Tejon substation | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-28 | 9 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | 7.1 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5810188 | T.0010228 | Tejon Reinfor Wheeler Ridge-San Bernard | 3 | 60 | NA ¦ EX113705 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-03-29 | 2029-05-01 | 2029-04-30 | NA | NA | FALSE | $28,000 ¦ $56,000 | NA ¦ NA | 110.0226 | 13949.0513 | 0 | 0 | 0 | 0 | 79.0527 | 269.9987 | 7000 | 6500 | 100 | 0 | 79.0526 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
654 | RIO OSO_W_SACRAMENTO 115KV LINE RECON |  |  | Arden-Arcade CDP, Sacramento ¦ Elverta CDP, Sacramento ¦ Rio Linda CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ West Sacramento, Yolo | Reconductoring Rio Oso – W. Sacramento 115 kV line as original re-rate of this line as a part of Vaca Dixon reinforcement project approved in 2017-18 TPP is no longer viable due to aging infrastructure. Addressing overloads and voltage criteria violations within the 115 kV and 60 kV transmission system connecting Vaca Dixon, Davis, Rio Oso, and Brighton substations under NERC Category P0 - P7 contingencies | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-25 | 88 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 43.55 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811552 | T.0010507 | Rio Oso_W_Sacramento 115KV Line Recon | 1 | 60 | NA ¦ EX113703 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-11-09 | 2030-05-01 | 2029-06-29 | NA | NA | FALSE | $48,700 ¦ $97,400 | NA ¦ NA | 358.738 | 100665.5378 | 0 | 0 | 0 | 0 | 292.4496 | 1135.3541 | 16113.747 | 49700.7215 | 32921.0124 | 376.454 | 292.4496 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
655 | Vaca-Plainfield 60 kV Line Reconductoring |  |  | Hartley CDP, Solano ¦ Monument Hills CDP, Yolo ¦ Solano ¦ Winters, Yolo ¦ Woodland, Yolo ¦ Yolo | Reconductor Vaca-Plainfield 60 kV (about 30 miles) to achieve minimum conductor rating of 635 AMPS for summer normal and 741 AMPS for summer emergency rating. Addressing the near-term overloads on the Vaca-Plainfield 60 kV line resulting from NERC Category P0 and P1 contingencies | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-14 | 66 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 30 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811564 | T.0010518 | Vaca-Plainfield 60KV Line Recond | 1 | 60 | NA ¦ EX113707 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-12-01 | 2030-12-01 | 2032-12-01 | Prioritization | NA | FALSE | $34,000 ¦ $68,000 | NA ¦ NA | 0 | 64000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 6000 | 14000 | 21000 | 21000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
656 | North Dublin-Vineyard Recond OH Seg 1 |  |  | Alameda ¦ Contra Costa ¦ Livermore, Alameda | Reconductor North Dublin -Vineyard 230 kV line with minimum summer emergency rating of 1350 AMPS or highest conductor feasible with existing structure and will include any other limiting elements upgrade to achieve the new line rating. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2025-08-22 | 20 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | 27.83 | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811681 | T.0010534 | North Dublin-Vineyard Recond Project | 3 | 60 | NA ¦ EX113670 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-09-25 | 2034-05-01 | 2031-02-28 | NA | NA | FALSE | $116,000 ¦ $233,000 | NA ¦ NA | 13.6562 | 47859.1417 | 0 | 0 | 0 | 0 | 0 | 525.8084 | 7333.3333 | 10000 | 10000 | 10000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
657 | North Dublin-Vineyard Recond UG Seg 1 |  |  | Alameda ¦ Livermore, Alameda ¦ Pleasanton, Alameda | Reconductor North Dublin -Vineyard 230 kV line with minimum summer emergency rating of 1350 AMPS or highest conductor feasible with existing structure and will include any other limiting elements upgrade to achieve the new line rating. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2026-01-06 | 20 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 4 | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811682 | T.0010534 | North Dublin-Vineyard Recond Project | 3 | 60 | NA ¦ EX113670 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-09-25 | 2034-05-01 | 2031-02-28 | NA | NA | FALSE | $116,000 ¦ $233,000 | NA ¦ NA | 10.9515 | 101748.4799 | 0 | 0 | 0 | 0 | 0 | 598.9749 | 7333.3333 | 10000 | 10000 | 10000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
658 | North Dublin-Vineyard Recond UG Seg 2&3 |  |  | Alameda ¦ Livermore, Alameda ¦ Pleasanton, Alameda | Reconductor North Dublin -Vineyard 230 kV line with minimum summer emergency rating of 1350 AMPS or highest conductor feasible with existing structure and will include any other limiting elements upgrade to achieve the new line rating. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2026-01-06 | 20 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | 7 | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811680 | T.0010534 | North Dublin-Vineyard Recond Project | 3 | 60 | NA ¦ EX113670 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-09-25 | 2034-05-01 | 2031-02-28 | NA | NA | FALSE | $116,000 ¦ $233,000 | NA ¦ NA | 118.0466 | 98974.2843 | 0 | 0 | 0 | 0 | 51.0217 | 695.4291 | 7333.3333 | 10000 | 10000 | 10000 | 51.0217 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
659 | Jefferson-Stanford Cable Replacement |  |  | Atherton, San Mateo ¦ Menlo Park, San Mateo ¦ San Mateo ¦ Stanford CDP, Santa Clara ¦ West Menlo Park CDP, San Mateo | Install temporary overhead shoo-fly transmission line to bypass existing underground cable section between Menlo Substation and SLAC 60 kV Tap for continuous electric customer service. Replace 0.9 mile of existing 800 kcmil AL underground cable with larger size cable of at least 1000 Amp. normal capacity | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-03 | 25 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.9 | NA | 60 | NA | NA | NA | NA | 3.0011 | Non-IGP | 5811838 | T.0010604 | Jefferson-Stanford Cable Replacement | 2 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2026 | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-12-03 | 2029-05-01 | 2028-02-29 | NA | NA | FALSE | 40000 | NA ¦ NA | 265.6062 | 37304.615 | 0 | 0 | 0 | 0 | 132.4368 | 2662.0988 | 32977.9653 | 0 | 0 | 0 | 132.4368 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
660 | Clearlake 60kV Reinforcemt |  |  | Lake ¦ Mendocino | The project scope of work involves the following: • Install a new 115/60 kV transformer bank at Middletown Substation with at least 100 MVA capacity. • Install two circuit breakers (115 kV and 60 kV) and associated disconnect switches at Middletown Substation to protect the new transformer. • Build a new 115 kV line from Lower Lake to Middletown substations with at least 345 Amps emergency capacity. This project is needed to provide transmission capacity to serve customers in the Humboldt Division. | Transmission Line/Substation | New | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-07-30 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | 21.5 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811929 | T.0010635 | Clear Lake 60kV Reinforcement | 4 | 60 | NA ¦ EX113216 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-12-10 | 2012-05-01 | 2028-06-26 | Prioritization | NA | FALSE | 30000 | NA ¦ NA | 330.0757 | 18163.7174 | 0 | 0 | 0 | 0 | 299.3942 | 531.3643 | 4858.389 | 5367.714 | 3604.603 | 3376.454 | 299.3941 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
661 | TESLA-NEWARK 230KV LINE NO 2 RECON |  |  | Alameda ¦ Fremont, Alameda ¦ Livermore, Alameda ¦ Sunol CDP, Alameda | Reconductor Tesla –Newark #2 230 kV line - From 024/148 to Newark (approximately 4.28 miles), with minimum summer emergency rating of 3428 AMPS, matching other sections of the line or highest conductor feasible with existing structure. Will also include any other limiting element upgrades to achieve this line rating. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2025-11-19 | 22 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | 4.28 | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811932 | T.0010636 | Tesla-Newark 230kV Line No 2 Recon | 3 | 60 | NA ¦ EX113706 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-02-26 | 2034-12-01 | 2035-02-05 | NA | NA | FALSE | $29,000 ¦ $58,000 | NA ¦ NA | 597.5845 | 44651.7457 | 0 | 0 | 0 | 0 | 501.2284 | 2150.5172 | 4000 | 8000 | 10000 | 10000 | 501.2285 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
662 | MARTIN-MILLBRAE 60KV AREA REINFORCEMENT |  |  | Brisbane, San Mateo ¦ Daly City, San Mateo ¦ San Bruno, San Mateo ¦ San Mateo ¦ South San Francisco, San Mateo | Reconductor 7.2 miles on the Martin-Sneath Lane 60 kV line and 2.5 miles on the Millbrae-Sneath Lane 60 kV line. Mitigate the thermal violations in the Martin-Millbrae 60 kV system under P1 contingencies. Increase the load serving capability and customer reliability in the area. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-25 | 101 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | 9.7 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811931 | T.0010637 | Martin-Millbrae 60kV Area Reinforcement | 4 | 60 | NA ¦ EX113701 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-11-03 | 2030-05-01 | 2030-05-31 | NA | NA | FALSE | $20,000 ¦ $40,000 | NA ¦ NA | 281.4212 | 45874.611 | 0 | 0 | 0 | 0 | 251.2964 | 1839.9006 | 4120.233 | 6311.025 | 20680.323 | 12471.833 | 251.2964 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
663 | CHCSS-Salinas-Soledad #1 |  |  | Monterey ¦ Prunedale CDP, Monterey ¦ Salinas, Monterey ¦ Soledad, Monterey | Re-conductor sections of CHCSS-Salinas-Soledad #1 and #2 115 kV lines. Reduce overloads on CHCSS-Natividad and Natividad-Salinas sections for a Mosslanding-Salinas #1 115 kV line | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004747 | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-03-31 | 126 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion ¦ Weather |  | 70.8 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811930 | T.0010638 | CHCSS-Salinas-Soledad 1 | 1 | 60 | NA ¦ EX113676 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-08-16 | 2030-12-01 | 2030-05-30 | NA | NA | FALSE | $54,000 ¦ $108,000 | NA ¦ NA | 355.6097 | 131881.9487 | 0 | 0 | 0 | 0 | 240.1901 | 1641.7588 | 5000 | 20000 | 35000 | 35000 | 240.19 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
664 | Camden-Kingsburg 70kV Line Reconductor |  |  | Fresno | Reconductor Camden-Kingsburg 70 kV and add 30 MVAR voltage support at Camden substation. | Transmission Line/Substation | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-02-18 | 74 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 14.9 | 1.2099 | 70 | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5812914 | T.0010712 | Camden: Install 30MVAR and 70kV Recond | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-05-11 | 2030-12-01 | 2028-10-13 | NA | NA | FALSE | $50,000 ¦ $100,000 | NA ¦ NA | 158.0637 | 56883.0085 | 0 | 0 | 0 | 0 | 78.2284 | 804.7801 | 15000 | 20000 | 17000 | 2000 | 78.2284 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
665 | Cortina #3 60 kV Reconductoring Project |  |  | Colusa ¦ Colusa, Colusa ¦ Williams, Colusa | Reconductor about 6.0 miles between the Cortina Substation and Wadham Jct on the Cortina #3 60 kV to achieve minimum conductor rating of 1014 AMPS for summer normal rating and 1127 AMPS for summer emergency rating. Reconductor about 1.5 miles between the Wadham Jct and Wescot (007/125) on the Cortina #3 60 kV to achieve minimum conductor rating of 1014 AMPS for summer normal rating and 1127 AMPS for summer emergency rating. Reconductor about 1.5 miles between the Wescot (007/125) and Willaims Substation on the Cortina #3 60 kV to achieve minimum conductor rating of 1014 AMPS for summer normal rating and 1127 AMPS for summer emergency rating. Install a 15 MVAR shunt capacitor at Meridian 60 kV substation. Upgrade any limiting components as necessary to achieve full conductor capacity | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-25 | 126 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 6 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5814977 | T.0011146 | Cortina #3 60 kV Reconductoring Project | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-08-01 | 2031-05-01 | 2032-02-06 | Customer action | NA | FALSE | 55500 | NA ¦ NA | 48.9169 | 39851.7579 | 0 | 0 | 0 | 0 | 24.8672 | 465.9437 | 0 | 0 | 0 | 1000 | 24.8672 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
666 | Konocti-Eagle Rock 60kV Recon-ETL.6861 |  |  | Lake ¦ Sonoma | Reconductor Konocti – Eagle Rock 60 kV Line and upgrade limiting elements to achieve full conductor capability | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-09-12 | 126 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 9.7 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815459 | T.0011250 | Konocti-Eagle Rock 60kV Recon | 1 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-12-20 | 2030-05-01 | 2030-05-31 | NA | NA | FALSE | 32500 | NA ¦ NA | 229.7744 | 22729.8713 | 0 | 0 | 0 | 0 | 127.8353 | 602.036 | 0 | 0 | 0 | 8000 | 127.8353 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
667 | Trimble-Montague 115kV Line upgrade |  |  | San Jose, Santa Clara | Reconductor ~ 0.58 circuit miles of Trimble-Charcot 115kV Line (from Trimble to Zanker Rd) with larger conductor to achieve at least 3000 Amps under summer emergency conditions. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0010908 | Load Growth | Line Reconductoring | NERC TPL Standards | NA | 2025-08-07 | 23 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.58 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815606 | T.0011274 | Montague-Trimble 115kV Reconductor | 1 | 60 | NA ¦ EX138958 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-09-18 | 2031-05-01 | 2030-10-15 | NA | NA | FALSE | 276000 | NA ¦ NA | 201.0672 | 15000 | 0 | 0 | 0 | 0 | 117.2956 | 1102.7824 | 0 | 0 | 0 | 0 | 117.2956 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
668 | Morgan Hill-Llagas 115kV Reconductor |  |  | Gilroy, Santa Clara ¦ Morgan Hill, Santa Clara ¦ Santa Clara | Reconductor ~ 10.84 circuit miles of Morgan Hill-Llagas 115kV Line with larger conductor to achieve at least 3000 Amps under summer emergency rating. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004271 | Load Growth | Line Reconductoring | NERC TPL Standards | NA | 2025-07-25 | 40 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | 10.84 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815659 | T.0011276 | Morgan Hill-Llagas 115kV Reconductor | 1 | 60 | NA ¦ EX138941 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-08-10 | 2031-05-01 | 2028-09-07 | NA | NA | FALSE | 155000 | NA ¦ NA | 351.5007 | 48895.587 | 0 | 0 | 0 | 0 | 228.9687 | 1807.8776 | 0 | 0 | 0 | 0 | 228.9687 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
669 | San Jose A-San Jose B 115kV Reconductor |  |  | San Jose, Santa Clara | Reconductor ~ 1.15 circuit miles of SJA-SJB #1 115kV Line with larger conductor to achieve at least 3000 Amps under summer emergency rating. Construct New ~1.372 circuit miles of SJA-SJB#2 115kV Line with conductor to achieve at least 3000 Amps under summer emergency rating. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0010465 | Load Growth | Line Reconductoring | NERC TPL Standards | NA | 2025-10-23 | 29 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Corrosion |  | 1.15 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815604 | T.0011286 | San Jose A-San Jose B 115kV T-Line UPGR | 4 | 60 | NA ¦ EX138932 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-01-25 | 2028-05-01 | 2028-06-29 | NA | NA | FALSE | 224000 | NA ¦ NA | 404.8153 | 33133.8661 | 0 | 0 | 0 | 0 | 187.1546 | 8463.17 | 0 | 0 | 0 | 0 | 187.1546 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
670 | Rebuild Sobrante-Grizzly-Claremont#2 |  |  | Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa | Rebuilding the two Sobrante-Grizzly-Claremont #1 and #2 115 kV lines into four lines, each with a summer normal rating of at least 1714 Amps. Two of these lines will bypass Claremont Substation and connect to Oakland D and Oakland L Substations through new underground (UG) cable sections. Rerouting the Moraga-Oakland X #4 line to bypass the Oakland X Substation and instead connect to Oakland C via a new UG cable section. Converting Oakland C to Gas-Insulated Switchgear (GIS). Replacing the Oakland C-Oakland X UG cable with a larger size cable. | Transmission Line - Multiple | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-17 | 55 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 78 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815585 | T.0011287 | North Oakland Reinforcement Project | 4 | 60 | NA ¦ EX138976 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-02-02 | 2032-05-01 | 2029-03-02 | NA | NA | FALSE | 1127000 | NA ¦ NA | 58.4423 | 58.4423 | 0 | 0 | 0 | 0 | 32.0209 | 26.4215 | 0 | 0 | 0 | 0 | 32.0208 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
671 | Rebuild Sobrante-Grizzly-Claremont#1 |  |  | Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa | Rebuilding the two Sobrante-Grizzly-Claremont #1 and #2 115 kV lines into four lines, each with a summer normal rating of at least 1714 Amps. Two of these lines will bypass Claremont Substation and connect to Oakland D and Oakland L Substations through new underground (UG) cable sections. Rerouting the Moraga-Oakland X #4 line to bypass the Oakland X Substation and instead connect to Oakland C via a new UG cable section. Converting Oakland C to Gas-Insulated Switchgear (GIS). Replacing the Oakland C-Oakland X UG cable with a larger size cable. | Transmission Line - Multiple | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-21 | 55 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 78 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815586 | T.0011287 | North Oakland Reinforcement Project | 4 | 60 | NA ¦ EX138976 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-03-07 | 2032-05-01 | 2029-04-03 | NA | NA | FALSE | 1127000 | NA ¦ NA | 5.5627 | 622937.0799 | 0 | 0 | 0 | 0 | 1.6382 | 2617.4356 | 0 | 0 | 0 | 0 | 1.6383 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
672 | San Jose B-Evergreen 115kV Reconductor |  |  | San Jose, Santa Clara | Reconductor ~ 5.66 circuit miles of San Jose B-Stone-Evergreen 115kV Line (from San Jose to Evergreen) with larger conductor to achieve at least 3000 Amps under summer emergency rating. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Load Growth | Line Reconductoring | NERC TPL Standards | NA | 2025-12-04 | 126 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 5.66 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815608 | T.0011288 | San Jose B-Evergreen 115kV Reconductor | 1 | 60 | NA ¦ EX138944 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-04-09 | 2030-05-01 | 2031-06-04 | Resources | NA | FALSE | 223000 | NA ¦ NA | 123.7393 | 13300 | 0 | 0 | 0 | 0 | 79.4956 | 1200.7799 | 0 | 0 | 0 | 0 | 79.4956 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
673 | Hellyer- Metcalf 115kV Reconductor |  |  | San Jose, Santa Clara ¦ Santa Clara | Reconductor ~ 4.5 circuit miles of Silver Creek-Metcalf 115kV Line with larger conductor to achieve at least 3000 Amps under summer emergency conditions. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0010903 | Load Growth | Line Reconductoring | NERC TPL Standards | NA | 2025-10-29 | 30 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 4.5 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815613 | T.0011290 | Hellyer-Metcalf 115kV Reconductor | 1 | 60 | NA ¦ EX138945 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-12-21 | 2030-05-01 | 2029-01-22 | NA | NA | FALSE | 223000 | NA ¦ NA | 353.8081 | 22500 | 0 | 0 | 0 | 0 | 241.5067 | 1360.1046 | 0 | 0 | 0 | 0 | 241.5067 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
674 | Moraga-San Leandro #1 115kV Reconductor |  |  | Alameda ¦ Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa ¦ San Leandro, Alameda | Reconductor the Moraga-San Leandro #1, #2, and #3 115 kV lines to achieve a minimum capacity of 2288 Amps or higher, reconductor the Moraga-Oakland J 115 kV line to achieve a minimum capacity of 2288 Amps or higher, reconductor the San Leandro-Oakland J 115 kV line to achieve a minimum capacity of 2288 Amps or higher. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-22 | 60 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 57.4 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815593 | T.0011294 | South Oakland Reinforcement Project | 6 | 60 | NA ¦ EX138977 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-04-10 | 2032-05-01 | 2029-05-07 | NA | NA | FALSE | 250000 | NA ¦ NA | 2.7619 | 189980.7481 | 0 | 0 | 0 | 0 | 1.0927 | 2012.7834 | 0 | 0 | 0 | 0 | 1.0926 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
675 | Moraga-San Leandro #2 115kV Reconductor |  |  | Alameda ¦ Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa ¦ San Leandro, Alameda | Reconductor the Moraga-San Leandro #1, #2, and #3 115 kV lines to achieve a minimum capacity of 2288 Amps or higher, reconductor the Moraga-Oakland J 115 kV line to achieve a minimum capacity of 2288 Amps or higher, reconductor the San Leandro-Oakland J 115 kV line to achieve a minimum capacity of 2288 Amps or higher. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-22 | 60 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 57.4 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815591 | T.0011294 | South Oakland Reinforcement Project | 6 | 60 | NA ¦ EX138977 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-06-04 | 2032-05-01 | 2029-07-02 | NA | NA | FALSE | 250000 | NA ¦ NA | 95.4054 | 95.4054 | 0 | 0 | 0 | 0 | 39.6277 | 55.7777 | 0 | 0 | 0 | 0 | 39.6277 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
676 | Eagle Rock-Fulton-Silverado 115kV Recon |  |  | Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma | Reconductor Eagle Rock-020/087A with minimum rating of 1236 Amps or higher and update any limiting components at the substation (if any). Reconductor 020/87A-037/191A with minimum rating of 1687 Amps or higher and update any limiting components at the substation (if any). | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Policy | Line Reconductoring | NERC TPL Standards | NA | 2025-06-04 | 126 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 28.6 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815800 | T.0011334 | Eagle Rock-Fulton-Silverado 115kV Recon | 2 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-12-02 | 2034-05-01 | 2028-04-03 | NA | NA | FALSE | 92900 | NA ¦ NA | 83.1245 | 18282.1659 | 0 | 0 | 0 | 0 | 47.3312 | 345.075 | 0 | 0 | 0 | 1000 | 47.3312 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
677 | Newark-Lockheed-Lawrence Loop |  |  | Fremont, Alameda ¦ Newark, Alameda ¦ San Jose, Santa Clara ¦ Sunnyvale, Santa Clara | This project will increase operational flexibility, load serving capability, customer reliability, and eliminate contingency overloads by performing the following scope: • Loop the Lockheed #1 Tap and 115kV Lockheed #2 Tap into the Newark-Lawrence 115kV Line creating the Newark-Lockheed-Lawrence loop. • Install new Tubular Steel Poles (TSP) and SCADA switches as needed to form the Newark-Lockheed-Lawrence loop configuration. • Line section from 006/046 to 007/049 on the Newark-Lawrence 115kV Line shall be kept in place for operational flexibility. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Load Growth | Line Reconductoring | NERC TPL Standards | NA | 2025-11-14 | 68 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | NA | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5816523 | T.0011626 | LC24-DA DeAnza T-line Capacity Upgrades | 3 | 60 | NA ¦ EX138936 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-06-23 | 2031-05-01 | 2028-12-28 | NA | NA | FALSE | 138000 | NA ¦ NA | 81.6434 | 3071.4611 | 0 | 0 | 0 | 0 | 53.7873 | 653.0779 | 0 | 0 | 0 | 0 | 53.7873 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
678 | Lockheed Tap 1 Reconductoring |  |  | Santa Clara ¦ Sunnyvale, Santa Clara | This project will increase operational flexibility, load serving capability, customer reliability, and eliminate contingency overloads by performing the following scope: • Loop the Lockheed #1 Tap and 115kV Lockheed #2 Tap into the Newark-Lawrence 115kV Line creating the Newark-Lockheed-Lawrence loop. • Install new Tubular Steel Poles (TSP) and SCADA switches as needed to form the Newark-Lockheed-Lawrence loop configuration. • Line section from 006/046 to 007/049 on the Newark-Lawrence 115kV Line shall be kept in place for operational flexibility. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0010873 | Load Growth | Line Reconductoring | NERC TPL Standards | NA | 2025-10-23 | 59 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 1.71 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5816521 | T.0011626 | LC24-DA DeAnza T-line Capacity Upgrades | 3 | 60 | NA ¦ EX138934 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-06-23 | 2031-05-01 | 2028-12-28 | NA | NA | FALSE | 138000 | NA ¦ NA | 90.2766 | 21541.9531 | 0 | 0 | 0 | 0 | 37.9617 | 654.0872 | 0 | 0 | 0 | 0 | 37.9617 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
679 | Lockheed Tap 2 Reconductoring |  |  | Sunnyvale, Santa Clara | This project will increase operational flexibility, load serving capability, customer reliability, and eliminate contingency overloads by performing the following scope: • Loop the Lockheed #1 Tap and 115kV Lockheed #2 Tap into the Newark-Lawrence 115kV Line creating the Newark-Lockheed-Lawrence loop. • Install new Tubular Steel Poles (TSP) and SCADA switches as needed to form the Newark-Lockheed-Lawrence loop configuration. • Line section from 006/046 to 007/049 on the Newark-Lawrence 115kV Line shall be kept in place for operational flexibility. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0010873 | Load Growth | Line Reconductoring | NERC TPL Standards | NA | 2025-11-05 | 68 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 1.3 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5816522 | T.0011626 | LC24-DA DeAnza T-line Capacity Upgrades | 3 | 60 | NA ¦ EX138935 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-07-17 | 2031-05-01 | 2029-01-22 | NA | NA | FALSE | 138000 | NA ¦ NA | 62.0788 | 21487.4997 | 0 | 0 | 0 | 0 | 29.6266 | 643.8268 | 0 | 0 | 0 | 0 | 29.6266 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
680 | Kern Oil-Live Oak 115kV Project |  |  | Kern ¦ Oildale CDP, Kern | The Project proposes to reconductor approximately 38 circuit miles of various 115 kV lines serving Bakersfield area in Kern County. The scope of the project include reconductoring 3.8 miles of the Kern PP-Westpark Nos. 1 and 2 115 kV Lines; 16.5 miles of the Kern-Magunden-Witco 115 kV Line; 3.5 miles of the Westpark-Magunden 115 kV Line; 5.0 miles of the Kern-Lamont 115 kV Line from Kern PP to Tevis Jct.; 5.0 miles of the Kern-Stockdale 115 kV line from Kern PP to Tevis Jct. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-10-22 | 77 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 4.6 | NA | 115 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 561 | 5.1001 | Non-IGP | 5774040 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 8 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2018 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-11-02 | 2016-03-01 | 2029-02-05 | Prioritization | NA | FALSE | $40,000 ¦ $65,000 | NA ¦ NA | 1091.0124 | 19491.0124 | 0 | 0 | 0 | 15.8311 | 26.6272 | 0 | 10400 | 1000 | 5000 | 1000 | 1091.0124 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
681 | Kern-Kern Oil 115kV Project |  |  | Bakersfield, Kern ¦ Kern ¦ Oildale CDP, Kern | The Project proposes to reconductor approximately 38 circuit miles of various 115 kV lines serving Bakersfield area in Kern County. The scope of the project include reconductoring 3.8 miles of the Kern PP-Westpark Nos. 1 and 2 115 kV Lines; 16.5 miles of the Kern-Magunden-Witco 115 kV Line; 3.5 miles of the Westpark-Magunden 115 kV Line; 5.0 miles of the Kern-Lamont 115 kV Line from Kern PP to Tevis Jct.; 5.0 miles of the Kern-Stockdale 115 kV line from Kern PP to Tevis Jct. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2025-11-20 | 77 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | 8.3 | NA | 115 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 519 | 5.1001 | Non-IGP | 5774039 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 8 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2018 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-04-26 | 2016-03-01 | 2029-08-23 | Prioritization | NA | FALSE | $40,000 ¦ $65,000 | NA ¦ NA | 2072.6776 | 24472.6776 | 0 | 0 | 0 | 22.4341 | 60.2879 | 0 | 10400 | 5000 | 5000 | 1000 | 2072.6776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
682 | GATE 500Kv: T-Line |  |  | Fresno | The reactive support study results noted above indicated that a +/- 800 MVAR dynamic reactive device at Gates Substation is required to address the high voltage and to improve dynamic performance. The recommendation is to approve installation of a total of +/-800 MVAR of dynamic reactive support on the Gates 500kV bus. Interconnect new Transmission Owner (TO) LS Power Grid California’s Orchard Substation STATCOM Facility to Gates 500kV Bus The scope of the proposed project is to install a minimum of two equally sized blocks of reactive devices independently connected to the 500kV system at PG&E’s Gates Substation to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power output over the complete range of the capability (unless the facility experiences a planned or forced outage). Sub-synchronous Resonance studies are required to be completed and any identified mitigation shall be implemented as part of this project. The project scope will include connecting two blocks of the STATCOM to two separate bays of Gates 500kV breaker-and-a-half (BAAH) bus. STATCOM connections will require both overhead and high-voltage underground cables. The high-level scope includes the following: • Install two 550kV, 4000 Amp 63KA breakers with associated switches and structures. • Relocate 500kV Bank 12 connection from BAAH Bay 2 to Bay 1 using GIB. • Build two transition stations (one inside the PG&E substation and one outside on PG&E property) to connect LS Power’s two STATCOM connections to PG&E 500kV bus. • Install overhead conductors, underground high-voltage cables and associated structures and switches to connect two STATCOMs • Relocate Bank 12 tertiary reactors controls and protection equipment from the 500kV control building to new Tertiary Reactors control building installed under Gates Bank 11 project. This is needed to create space in the 500kV control building for new breakers. • Install protection, controls, and IT equipment for new 500 kV breakers needed to support LS Power project. • Upgrade ground grid and grading as required. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-12 | 33 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.02 | 77.6619 | 500 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5795569 | T.0004672 | Gates: 500 kV Dynamic Voltage Support | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2019 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-05-08 | 2024-12-01 | 2025-01-28 | NA | NA | TRUE | $210,000 ¦ $250,000 | NA ¦ NA | 32851.6971 | 33019.5042 | 40.4213 | 1432.9869 | 23460.1952 | 7355.3214 | 540.2425 | 141.3659 | 48.2298 | 0.7413 | 0 | 0 | 32829.1673 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 32661.4875 | 22.403 | 0% ¦ LS Power, Gates: 500 kV Dynamic Voltage Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
683 | Cortina Sub: T-Line Work |  |  | Clearlake Oaks CDP, Lake ¦ Colusa ¦ Lake ¦ Lucerne CDP, Lake ¦ Mendocino ¦ Nice CDP, Lake | Replace the Cortina 230/115/60 kV Transformer 1 with one 230/115 kV and one 115/60 kV transformers. Upgrade bus differential relay, as needed. The annual reliability assessment identified thermal overload issues for NERC Category contingencies that involve loss of Cortina 230/115 kV Transformer 4. For an outage of Cortina 230/115 kV Transformer 4, Cortina 230/115/60 kV Transformer 1 will have to serve the Cortina 60 kV load and the Cortina 115 kV load and North Geysers area via Cortina 115/60 kV Transformer 5. The most severe of such contingencies may lead to loading of Cortina 230/115/60 kV Transformer 1 up to 137.5% of its summer emergency rating. Currently, there is an Operating Procedure to radialize the 60 kV and 115 kV loads by opening Cortina 115/60 KV Transformer 5 pre-contingency in order to prevent the Cortina 230/115/60 kV Transformer 1 overload post-contingency. However, planning and real time operating analysis show that opening Cortina 115/60 kV Bank 5 under normal condition could cause loss of generation violations, such as losing Wadham generator could overload Cortina 230/115/60 kV Transformer 1 up to 106.2% of its summer emergency rating. Therefore, this Operating Procedure cannot longer be used as a viable long-term solution under peak loading conditions. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0008218 | Reliability | Voltage Conversion | NERC TPL Standards | NA | 2025-08-18 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $40 Mil - $50 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 ¦ 115 ¦ 60 | NA | NA | NA | NA | 1.0001 | Non-IGP | 5810077 | T.0009531 | Cortina Replace Bank 1 with 2 banks | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-04-23 | 2027-12-01 | 2027-10-13 | NA | NA | FALSE | $21,000 ¦ $42,000 | NA ¦ NA | 0 | 1332 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1323 | 9 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
684 | Salinas-Spence Tline |  |  | Monterey ¦ Salinas, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Voltage Conversion | NERC TPL Standards | NA | 2025-11-20 | 58 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 11.6 | NA | 115 ¦ 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5811926 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-03-13 | TBD | 2031-04-09 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 102.7106 | 24390.5664 | 0 | 0 | 0 | 0 | 94.3057 | 142.0583 | 0 | 0 | 0 | 0 | 94.3057 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
685 | Salinas-Firestone-Spence |  |  | Monterey ¦ Salinas, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Voltage Conversion | NERC TPL Standards | NA | 2025-11-20 | 58 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1.66 | NA | 115 ¦ 60 | NA | NA | NA | NA | 1.0001 | Non-IGP | 5811927 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-03-06 | TBD | 2032-12-30 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 223.8171 | 86151.1527 | 0 | 0 | 0 | 0 | 213.8712 | 137.2815 | 1000 | 3800 | 17000 | 27000 | 213.8712 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
686 | 230 kV T-Line LOCKEFORD - NEW INDUSTRIAL |  |  | Lockeford CDP, San Joaquin | The Lockeford-Lodi Area 230 kV Development Project will loop the Brighton – Bellota 230 kV Line into Lockeford 230 kV Substation to bring a new 230 kV source into the area. A new 230 kV double circuit tower line will be constructed to connect the existing Lockeford 230 kV Substation to a new 230 kV switching to be constructed near the City of Lodi’s existing Industrial 60 kV Subsation. To accommodate the Brighton – Bellota loop-in and the new DCTL, the Lockeford 230 kV Bus will be upgraded to a four-bay breaker-and-a-half (BAAH) bus configuration. The City of Lodi will be constructing a new 230/60 kV Substation which will be connected to the new 230 kV switching station. | Transmission Line - Conductor | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Non-Wires - Large Scale Energy Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 32 | 10.2719 | 230 | NA | 45 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767239 | T.0000155 | Lockeford - Lodi Area 230 kV Development | 4 | 60 | NA ¦ 5752079 ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | PEA Deemed Complete | 2023-09-01 | EIR | NA | CPUC | NA | CPCN: A.23-09-001 | 2023-09-01 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 3 | 2029-11-12 | 2017-03-01 | 2031-06-02 | Prioritization | NA | FALSE | $80,000 ¦ $105,000 | TBD ¦ TBD | 21047.2773 | 60479.0718 | 1625.0271 | 2081.8356 | 1754.9182 | 1603.8079 | 2282.2442 | 7223.0348 | 10091.8728 | 10141.816 | 6189.2595 | 2466.7208 | 20709.8164 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
687 | LOOP IN BRIGHTON - BELLOTA INTO LOCKEFOR |  |  | Dogtown CDP, San Joaquin ¦ Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Herald CDP, Sacramento ¦ Lockeford CDP, San Joaquin ¦ Sacramento ¦ Sacramento, Sacramento ¦ San Joaquin ¦ Vineyard CDP, Sacramento ¦ Wilton CDP, Sacramento | The Lockeford-Lodi Area 230 kV Development Project will loop the Brighton – Bellota 230 kV Line into Lockeford 230 kV Substation to bring a new 230 kV source into the area. A new 230 kV double circuit tower line will be constructed to connect the existing Lockeford 230 kV Substation to a new 230 kV switching to be constructed near the City of Lodi’s existing Industrial 60 kV Subsation. To accommodate the Brighton – Bellota loop-in and the new DCTL, the Lockeford 230 kV Bus will be upgraded to a four-bay breaker-and-a-half (BAAH) bus configuration. The City of Lodi will be constructing a new 230/60 kV Substation which will be connected to the new 230 kV switching station. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2025-12-01 | 76 | Steady State Power Flow System Analysis | Non-Wires - Large Scale Energy Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 4 | NA | 230 | NA | 45 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767209 | T.0000155 | Lockeford - Lodi Area 230 kV Development | 4 | 60 | NA ¦ 5752079 ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | PEA Deemed Complete | 2023-09-01 | EIR | NA | CPUC | NA | CPCN: A.23-09-001 | 2023-09-01 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 3 | 2029-11-01 | 2017-03-01 | 2031-06-30 | Prioritization | NA | FALSE | $80,000 ¦ $105,000 | TBD ¦ TBD | 1561.3278 | 38042.694 | 747.3134 | 135.7591 | 103.8973 | 108.7883 | 112.9208 | 128.817 | 3606.2292 | 9179.8274 | 14048.2289 | 9537.1038 | 1540.9659 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
688 | RIPON SUB: BUILD 2ND 115 KV |  |  | Ripon, San Joaquin | Install a new 4.7-mile 115 kV transmission line from Ripon Substation to the Riverbank Switching Station – Manteca 115 kV Line, including the upgraded Ripon 115 kV Bus to a loop configuration .The Ripon Substation 115 kV Reliability Project will improve electric transmission reliability for customers served by Ripon Substation. The new 4.7-mile 115 kV transmission line will provide Ripon Substation with two sources to eliminate service interruptions for single contingency situations and limiting bus faults to only half the substation. | Transmission Line - Conductor | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2026-02-11 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 5 | 2.0603 | 115 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767284 | T.0000265 | RIPON NEW 115 KV LINE 2ND TAP RELIABILIT | 1 | 60 | NA ¦ 5752061 ¦ NA ¦ NA | FALSE | 2014 | Project Management Governance Standard | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5059-E | 2017-04-28 | Approved | 2017 | Operational | 1 | 2018-07-09 | 2015-05-31 | 2019-05-24 | Prioritization | NA | FALSE | $10,000 ¦ $15,000 | NA ¦ NA | 6849.4129 | 6849.4129 | 56.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6849.4129 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 53.2062 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
689 | Vierra 115 kV Looping (Tline) |  |  | Lathrop, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2026-02-06 | 14 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 2 | 1.355 | 115 | NA | 102 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5746744 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2014 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2020-10-16 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Operational | 1 | 2024-11-01 | 2014-05-01 | 2025-02-23 | Prioritization | NA | TRUE | $10,000 ¦ $15,000 | NA ¦ NA | 11977.7908 | 11989.7437 | 687.7113 | 612.6252 | 976.2231 | 4664.159 | 1229.4157 | 29.6612 | 0 | 0 | 0 | 0 | 11960.0825 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 11960.3965 | 17.7083 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
690 | Sanger Expansion T-Line |  |  | Fresno | Install a new seven bay 115 kV BAAH bus, two MPAC buildings, and relocate all associated 115 kV lines at Sanger Substation. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | T-Line Reliability | NA | NA | 2026-02-18 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 11.0513 | 115 | NA | 225 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5762399 | T.0000601 | Sanger Substation 115kV Bus Replacement | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2017-07-13 | IS/MND | NA | CPUC | NA | PTC: A.15-09-012 | 2015-09-30 | Approved | 2017 | Operational | 1 | 2019-06-03 | 2019-12-31 | 2020-11-30 | Prioritization | NA | FALSE | 55300 | NA ¦ NA | 5397.7331 | 5397.7331 | 718.5122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5397.7331 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 676.2041 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
691 | Santa Teresa Substation - T-Line Work |  |  | San Jose, Santa Clara ¦ Santa Clara | Construct a new substation on PG&E property at the Edenvale Service Center in San Jose, CA to serve three new data center loads and correct a normal deficiency on Edenvale Banks 2 and 4 | Transmission Line - Conductor | Relocate | NA | NA | Reliability | T-Line Capacity | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 79 | 8. Compliance/Commitments With Low Safety Risk | 85 | NA | NA | 5764801 | T.0001316 | SANTA TERESA SUB: NEW SUB | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2018 | 2021 | FALSE | 2021 | NA | https://www.caiso.com/Documents/BoardApproved2020-2021TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5601-E | 2019-07-29 | Approved | 2020 | Operational | 1 | 2020-10-14 | 2021-08-01 | 2021-12-13 | NA | NA | FALSE | 18000 | NA ¦ NA | 2827.0112 | 2827.0112 | 230.4599 | 10.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2827.0112 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 2636.6456 | 9.8031 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2020-2021TransmissionPlan.pdf
692 | TLINE - SPRING SUBSTATION TRANSFER |  |  | Gilroy, Santa Clara ¦ Morgan Hill, Santa Clara ¦ Santa Clara | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Transmission Line - Multiple | Upgrade/Retrofit | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2025-07-25 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5818331 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 10 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2025 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-12-01 | 2021-12-01 | 2025-12-31 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 2328.6767 | 2328.6767 | 0 | 0 | 0 | 0 | 2328.6767 | 0 | 0 | 0 | 0 | 0 | 2328.6767 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 2328.6767 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
693 | Gold Hill 230 kV T Line support |  |  | Folsom, Sacramento | A Bus section Fault (P2-1) overload on Missouri Flats – Gold Hill Lines 115 kV were identified in last year’s analysis and was addressed by switching load in the area. This year’s result show that given the load growth in the area, the P2-1 overload shows up in the long term. In order to mitigate the issue, the CAISO recommendeds the installation of a third 230/115 kV transformer at Gold Hill Substation | Transmission Line - Conductor | New | NA | T.0004920 ¦ EX138973 | Reliability | New T-Line | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 12.8702 | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5814895 | T.0004950 | Gold Hill: Installl 230/115 kV Txfmr | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-07-14 | 2022-12-31 | 2029-12-28 | Prioritization | NA | FALSE | 22000 | NA ¦ NA | 111.0995 | 421.0926 | 0 | 0 | 0 | 0 | 15.2074 | 102.654 | 0 | 0 | 0 | 0 | 15.2075 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
694 | Gold Hill 115 kV T Line support |  |  | Folsom, Sacramento | A Bus section Fault (P2-1) overload on Missouri Flats – Gold Hill Lines 115 kV were identified in last year’s analysis and was addressed by switching load in the area. This year’s result show that given the load growth in the area, the P2-1 overload shows up in the long term. In order to mitigate the issue, the CAISO recommendeds the installation of a third 230/115 kV transformer at Gold Hill Substation | Transmission Line - Conductor | New | NA | T.0004920 ¦ EX138973 | Reliability | New T-Line | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 12.8702 | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5814896 | T.0004950 | Gold Hill: Installl 230/115 kV Txfmr | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-07-14 | 2022-12-31 | 2029-12-28 | Prioritization | NA | FALSE | 22000 | NA ¦ NA | 64.2968 | 517.4516 | 0 | 0 | 0 | 0 | 25.8272 | 42.383 | 0 | 0 | 0 | 0 | 25.8272 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
695 | Gold Hill 60 kV T Line support |  |  | Folsom, Sacramento | A Bus section Fault (P2-1) overload on Missouri Flats – Gold Hill Lines 115 kV were identified in last year’s analysis and was addressed by switching load in the area. This year’s result show that given the load growth in the area, the P2-1 overload shows up in the long term. In order to mitigate the issue, the CAISO recommendeds the installation of a third 230/115 kV transformer at Gold Hill Substation | Transmission Line - Conductor | New | NA | T.0004920 ¦ EX138973 | Reliability | New T-Line | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 12.8702 | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5814897 | T.0004950 | Gold Hill: Installl 230/115 kV Txfmr | 5 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-07-14 | 2022-12-31 | 2029-12-28 | Prioritization | NA | FALSE | 22000 | NA ¦ NA | 56.6614 | 187.3832 | 0 | 0 | 0 | 0 | 1.4025 | 58.7076 | 0 | 0 | 0 | 0 | 1.4025 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
696 | LSPOWER FERN ROAD SUB_COMM YARD AND TLI |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Chico, Butte ¦ Cohasset CDP, Butte ¦ Round Mountain CDP, Shasta ¦ Shasta ¦ Tehama ¦ Whitmore CDP, Shasta | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Transmission Line - Multiple | New | NA | NA | Reliability | System Design Upgrade | NERC TPL Standards | NA | 2026-04-07 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | NA | 500 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5794601 | T.0006815 | LSPower Round Mountain Area 500kV Dynami | 9 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2020 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2024-10-25 | 2024-12-31 | 2026-06-12 | Customer Action | NA | TRUE | $160,000 ¦ $190,000 | NA ¦ NA | 23968.7923 | 28937.6998 | 320.226 | 646.9113 | 1502.4937 | 7726.9006 | 11357.3896 | 7187.0019 | 196.7766 | 0 | 0 | 0 | 21553.9213 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power, Round Mountain 500 kV Dynamic Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
697 | LSPower Fern Rd Transposition |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Butte Valley CDP, Butte ¦ Chico, Butte ¦ Cohasset CDP, Butte ¦ Manton CDP, Shasta ¦ Manton CDP, Tehama ¦ Paynes Creek CDP, Tehama ¦ Round Mountain CDP, Shasta ¦ Shasta ¦ Tehama ¦ Whitmore CDP, Shasta | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Transmission Line - Multiple | Relocate | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2026-04-07 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5818553 | T.0006815 | LSPower Round Mountain Area 500kV Dynami | 9 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2026 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2026-12-16 | 2024-12-31 | 2027-07-15 | Customer Action | NA | TRUE | $160,000 ¦ $190,000 | NA ¦ NA | 1.5094 | 6357.8647 | 0 | 0 | 0 | 0 | 0 | 1570.2486 | 4755.5703 | 32.0457 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power, Round Mountain 500 kV Dynamic Support | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
698 | RIO OSO GOLD HILL MOMENTUM SUB TLINE WRK |  |  | Folsom, Sacramento ¦ Granite Bay CDP, Placer ¦ Granite Bay CDP, Sacramento ¦ Orangevale CDP, Sacramento ¦ Placer ¦ Roseville, Placer ¦ Sacramento ¦ Sutter | To eliminate the deficiency and provide surplus distribution capacity to meet growing demand by installing two 230/21kV (75 MVA) distribution transformers at Momentum Substation(greenfield). Transmission Line Work (MWC 60): • Loop Rio Oso – Gold Hill or Rio Oso – Atlantic 230kV line in substation property Transmission Substation Work (MWC 61): • Build two rows of 230kV breaker and a half configuration bus arrangement, 6 breakers • Install MPAC building Distribution Substation Work to Install Fiddyment Bank 1 and 21kV Bus Structure (MWC 46): • Install one 230/21kV, 75 MVA LTC transformer, Fiddyment Bank 1. • Install one 21kV bank breaker • Install two 21kV feeder Breakers • Install one 21kV spare feeder bay Distribution Line Work to Fiddyment 2101 and 2102 Feeders (MWC 06): • Trench 1000 feet and install 6-1100Al EPR cables in two 6-inch conduits with one spare 6-inch conduit (for a future 2103 feeder) from Switchgear No. 1 to future PMI-9 SW 760956 (PM 35424031) on College Park Drive to create new Fiddyment 2101 and Fiddyment 2102 underground feeder outlets. These connect to feeders that are being constructed by the land developer on new business PM 35424031 (Placer One Backbone). • Switches may be installed as required for operational flexibility and efficiency. • Automated switches may be required and added to the project scope for FLISR. • Line work and equipment may be added or deleted upon completion of the final design and estimate. | Transmission Line - Conductor | New | NA | T.0008394 | Load Growth | New T-Line | NA | NA | 2025-07-21 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5808004 | T.0009604 | Momentum 230/21kV Substation | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7636-E | 2025-07-03 | Approved | 2025 | Engineering more than 50% complete | 3 | 2027-07-26 | 2028-12-29 | 2028-05-01 | NA | NA | FALSE | 26600 | NA ¦ NA | 176.482 | 5299.7006 | 0 | 0 | 0 | 1.5149 | 125.2581 | 209.9865 | 3804.5083 | 84.2811 | 0 | 0 | 126.773 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
699 | Inst New 70kV Line Poleline - Mercy Sprg |  |  | Merced | This project proposes to: • Install 230 kV partial bay at the new generation driven 230 kV switching station adjacent to Dos Amigos PP 230 kV Substation. • Add a new 70 kV Bus in the new generation driven 230 kV switching station, then it will be converted to a new 230/70 kV substation. • Install one 230/70 kV transformer at the new 230/70 kV substation. • Install a new 70 kV transmission line from new 70 kV Bus to Mercy Springs 70 kV Bus, and the new line is about one mile. • Install one breaker at Mercy Springs 70 kV Switching Station. | Transmission Line - Conductor | New | NA | T.0009177 | Reliability | New T-Line | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | 1 | 53.2803 | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5807500 | T.0009617 | Los Banos 70 kV Area Reinforcement | 3 | 60 | NA ¦ EX113235 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-08-22 | 2029-12-31 | 2030-11-21 | Workforce | Material | FALSE | 60000 | NA ¦ NA | 6.9498 | 5047.8071 | 0 | 0 | 0 | 0 | 4.9861 | 42.8209 | 500 | 1000 | 3000 | 500 | 4.9861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
700 | REEDLEY DINUBA LN REBUILD |  |  | Fresno | Add a double circuit between Reedley-Dinuba 70 kV line #2 and upgrade rating ofexisting Reedley-Dinuba 70 kV line #1 and upgrade Reedley 230/70 kV bank 4. | Transmission Line/Substation | New | NA | EX112722 | Reliability | New T-Line | NERC TPL Standards | NA | 2026-03-10 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 7.7 | 3.5939 | 70 | 230 ¦ 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5812199 | T.0010649 | REEDLEY-DINUBA LN REBUILD & TXFMER #4 | 3 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-07-02 | TBD | 2030-07-30 | NA | NA | FALSE | $49,000 ¦ $98,000 | NA ¦ NA | 73.3697 | 51271.3287 | 0 | 0 | 0 | 0 | 62.9181 | 1208.4106 | 5000 | 10000 | 15000 | 20000 | 62.9181 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
701 | New San Jose A-San Jose B 115kV Line |  |  | San Jose, Santa Clara | Reconductor ~ 1.15 circuit miles of SJA-SJB #1 115kV Line with larger conductor to achieve at least 3000 Amps under summer emergency rating. Construct New ~1.372 circuit miles of SJA-SJB#2 115kV Line with conductor to achieve at least 3000 Amps under summer emergency rating. | Transmission Line - Multiple | New | NA | T.0010465 | Load Growth | New T-Line | NERC TPL Standards | NA | 2025-10-23 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1.15 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815605 | T.0011286 | San Jose A-San Jose B 115kV T-Line UPGR | 4 | 60 | NA ¦ EX138931 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-04-20 | 2028-05-01 | 2028-06-29 | NA | NA | FALSE | 224000 | NA ¦ NA | 232.1978 | 57000 | 0 | 0 | 0 | 0 | 72.1129 | 12329.4366 | 0 | 0 | 0 | 0 | 72.1128 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
702 | SJA-SJB T-line Land Acquisition |  |  | San Jose, Santa Clara | Reconductor ~ 1.15 circuit miles of SJA-SJB #1 115kV Line with larger conductor to achieve at least 3000 Amps under summer emergency rating. Construct New ~1.372 circuit miles of SJA-SJB#2 115kV Line with conductor to achieve at least 3000 Amps under summer emergency rating. | Other | New | NA | NA | Load Growth | New T-Line | NERC TPL Standards | NA | 2025-10-23 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5565739 | T.0011286 | San Jose A-San Jose B 115kV T-Line UPGR | 4 | 60 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2026 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | NA | 2028-05-01 | 2028-06-29 | NA | NA | FALSE | 224000 | NA ¦ NA | 0 | 5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
703 | Distribution - Concord Naval Weapons Station - Tline work |  |  | Concord, Contra Costa | Extend existing 230kV Tline to potential new distribution substation (Avila) in Concord | Transmission Line - Multiple | Relocate | NA | NA | Load Growth | System Design Upgrade | NA | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.074522 | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5746582 | TBD | TBD | TBD | 60 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 11000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 3000 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
704 | Metcalf SPS Upgrade |  |  | Santa Clara | The project proposes to reconnect the 115 kV lines from Mountain View and Whisman Substations into the 115 kV bus at Ames Substation. The work will require protection upgrades at the substations and also will require circuit breaker replacement at Mountain and Whisman due to increased fault duty at those substations. This project was one of several projects that are needed to eliminate the need to have a reliability must run (RMR) contract with Calpine’s Metcalf Energy Center. Also, to address substation bus reliability issues at Ames Substation, the project will also install circuit breakers at Ames on the two 115 kV lines that serve the NASA Ames facility. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Reliability | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX130183 | T.0003920 | RMR - Mtn View-Whisman-Ames Project | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-12-01 | NA | 2027-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 2000 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
705 | Distribution - Lockeford Sub - Install Bk 5 |  |  | Lockeford CDP, San Joaquin | The project installs one new 115 kV transmission breaker and one new 75 MVA substation transformer in order to mitigate an Emergency Deficiency caused by removal of Transmission Bank 1 at Lockeford. | Substation - Circuit Breaker | New | NA | NA | Load Growth | Substation Capacity | NA | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 10.2719 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113198 | T.0005910 | Lockeford Sub, Replace Bank 1 | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | NA | 2027-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1325 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1325 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
706 | Sobrante 230/115 kV Transformer Bank Addition |  |  | Orinda, Contra Costa | New 230/115 kV Bank at Sobrante Substation with 420 MVA rating. It will also include any bus upgrades and limiting equipment upgrades to achieve this transformer rating. | Substation - Transformer | New | NA | NA | Policy | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 11.0767 | NA | 230 ¦ 115 kV | NA | NA | NA | 3.0011 | Non-IGP | EX113671 | T.0011859 | Sobrante 230/115 kV Transformer Bank Addition | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | 2034-12-01 | 2030-12-01 | NA | NA | FALSE | $20,000 ¦ $40,000 | NA ¦ NA | 0 | 11600 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 3000 | 3000 | 3000 | 2500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
707 | New Humboldt 115/115 kV Phase Shifter with 115 kV line to Humboldt 115kV Substation |  |  | Humboldt | Installation of a 115 kV phase shifting transformer to connect to the Humboldt 500 kV station with a 115k kV line to the Humboldt 115 kV substation. | Substation - Transformer | New | NA | NA | Policy | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.569 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | EX113672 | TBD | New Humboldt 115/115 kV Phase Shifter with 115 kV line to Humboldt 115kV Substation | TBD | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2033-12-01 | 2034-05-01 | 2034-12-01 | Prioritization | NA | FALSE | $40,000 ¦ $57,000 | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
708 | Distribution - Cloverdale - Install Bank 2, 1104 - Bank |  |  | Cloverdale, Sonoma | Install a new 115/12kV 30MVA transformer and 12kV distribution bus at Cloverdale substation. The project will create at least one distribution feeder needed to serve industrial and EV growth in the Santa Rosa area. | Substation - Circuit Breaker | New | NA | NA | Load Growth | Substation Capacity | NA | NA | 2026-02-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7377 | NA | 115 kV | NA | NA | NA | 4.01 | Non-IGP | EX113681 | TBD | TBD | TBD | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | NA | 2027-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2650 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 2650 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
709 | PLAINFIELD: AQUIRE LAND |  |  | Yolo | The California ISO’s 2018-2019 Transmission Planning Process (TPP) has identified the need for the Vaca – Dixon Area Reinforcement Project. This project will mitigate overloads and voltage criteria violations in the 115kV and 60kV transmission systems among Vaca Dixon, Davis, Rio Oso and Brighton Substations. The project will include the following work: 1. Install two 5.0 MVAR capacitor banks at Plainfield Substation. 2. Replace Vaca Dixon 115/60kV Bank 5 with a larger unit. 3. Replace the limiting elements on the 60kV equipment at Dixon Substation. 4. Re-rate the Woodland - Davis 115kV Line and the Rio Oso - West Sac 115kV Line. 5. Modify the existing special protection schemes (SPS) or add new SPS’s to trip load for select multiple contingencies. | Other | New | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.82985 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5554308 | T.0000007 | Vaca Dixon Area Reinforcement Project | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2024-07-17 | EIR | NA | CPUC | NA | PTC: A.24-06-008 | 2024-06-28 | Filed and Under Administrative Review | TBD | Programmatic Work | NA | NA | 2023-12-01 | OAI | NA | NA | TRUE | $70,000 ¦ $107,000 | NA ¦ NA | 32.121 | 332.121 | 0 | 0 | 22.4956 | 9.167 | 0.4585 | 300 | 0 | 0 | 0 | 0 | 32.121 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 31.6625 | 0.4585 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
710 | FULTON-FITCH: Reconductoring 60 kV |  |  | Sonoma | Reconductor approximately 8 miles of the Fulton-Hopland 60kV Line and 1.3 miles of the Geysers 12-Fulton 230kV Line, rerate another section of the Fulton-Hopland 60kV Line and Fitch Mountain #2 60kV Tap, and upgrade switches and associated equipment at Fitch Mountain Substation. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Reconductoring | NERC TPL Standards | NA | 2026-02-12 | 51 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1.3 | 0.53125 | NA | 60 kV | 490 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5741140 | T.0000039 | Fulton-Fitch Mtn 60kV Reconductor | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2016 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-10-11 | IS/MND | NA | CPUC | NA | PTC: A.15-12-005 | 2015-12-03 | Approved | 2017 | Operational | 1 | 2018-09-17 | 2013-05-01 | 2020-03-17 | Prioritization | NA | FALSE | 5000 | NA ¦ NA | 6783.6922 | 6783.6922 | 60.3741 | -14.8395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6783.6922 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 56.0471 | -13.7759 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil
711 | LAND PURCHASE FOR 70KV SUBSTATION |  |  | San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Other | New | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2026-03-02 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion ¦ Flooding |  | NA | 2.6839 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5553459 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Programmatic Work | NA | NA | 2019-05-01 | OAI | NA | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 449.3411 | 854.3411 | 0 | 0 | 400.9725 | 0 | 41.2919 | 412.0767 | 0 | 0 | 0 | 0 | 442.2644 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2025 ¦ 2026 | 0 | 0 | 400.9725 | 0 | 41.2919 | 7.0767 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
712 | NEW 230 kV INDUSTRIAL SWITCHING STATION |  |  | Lockeford CDP, San Joaquin | The Lockeford-Lodi Area 230 kV Development Project will loop the Brighton – Bellota 230 kV Line into Lockeford 230 kV Substation to bring a new 230 kV source into the area. A new 230 kV double circuit tower line will be constructed to connect the existing Lockeford 230 kV Substation to a new 230 kV switching to be constructed near the City of Lodi’s existing Industrial 60 kV Subsation. To accommodate the Brighton – Bellota loop-in and the new DCTL, the Lockeford 230 kV Bus will be upgraded to a four-bay breaker-and-a-half (BAAH) bus configuration. The City of Lodi will be constructing a new 230/60 kV Substation which will be connected to the new 230 kV switching station. | Substation - Multiple | New | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Non-Wires - Large Scale Energy Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 10.2719 | NA | 230 kV | 45 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767188 | T.0000155 | Lockeford - Lodi Area 230 kV Development | 4 | 61 | NA ¦ 5752080 ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | PEA Deemed Complete | 2023-09-01 | EIR | NA | CPUC | NA | CPCN: A.23-09-001 | 2023-09-01 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 3 | 2030-05-30 | 2017-03-01 | 2031-06-30 | Prioritization | NA | FALSE | $80,000 ¦ $105,000 | TBD ¦ TBD | 1492.0936 | 39596.5079 | 196.2828 | 147.2683 | 108.0446 | 101.7728 | 129.8818 | 261.1455 | 17124.0397 | 11905.6697 | 4411.2373 | 4426.1061 | 1468.3094 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
713 | SANTA TERESA SUB: T-SUB WORK |  |  | Santa Clara | Construct a new substation on PG&E property at the Edenvale Service Center in San Jose, CA to serve three new data center loads and correct a normal deficiency on Edenvale Banks 2 and 4 | Substation - Line Termination | New | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 115 kV | 79 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5782343 | T.0001316 | SANTA TERESA SUB: NEW SUB | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2019 | 2021 | FALSE | 2021 | NA | https://www.caiso.com/Documents/BoardApproved2020-2021TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5601-E | 2019-07-29 | Approved | 2020 | Operational | 1 | 2021-05-18 | 2021-08-01 | 2021-12-13 | NA | NA | FALSE | 18000 | NA ¦ NA | 9048.2514 | 9048.2514 | 7977.5224 | 203.6581 | 210.0896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9048.2514 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 8634.5038 | 203.6581 | 210.0895 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2020-2021TransmissionPlan.pdf
714 | Santa Teresa Project - Metcalf Work |  |  | Santa Clara | Construct a new substation on PG&E property at the Edenvale Service Center in San Jose, CA to serve three new data center loads and correct a normal deficiency on Edenvale Banks 2 and 4 | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | NA | NA | 5792897 | T.0001316 | SANTA TERESA SUB: NEW SUB | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2020 | 2021 | FALSE | 2021 | NA | https://www.caiso.com/Documents/BoardApproved2020-2021TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5601-E | 2019-07-29 | Approved | 2020 | Operational | 1 | 2021-08-16 | 2021-08-01 | 2021-12-13 | NA | NA | FALSE | 18000 | NA ¦ NA | 571.4974 | 571.4974 | 449.9423 | 29.0058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571.4974 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 537.8231 | 20.1371 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2020-2021TransmissionPlan.pdf
715 | Santa Teresa Project - Edenvale Work |  |  | San Jose, Santa Clara | Construct a new substation on PG&E property at the Edenvale Service Center in San Jose, CA to serve three new data center loads and correct a normal deficiency on Edenvale Banks 2 and 4 | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-03 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.3853 | NA | 115 kV | NA | NA | NA | NA | NA | 5792998 | T.0001316 | SANTA TERESA SUB: NEW SUB | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2020 | 2021 | FALSE | 2021 | NA | https://www.caiso.com/Documents/BoardApproved2020-2021TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5601-E | 2019-07-29 | Approved | 2020 | Operational | 1 | 2021-08-06 | 2021-08-01 | 2021-12-14 | NA | NA | FALSE | 18000 | NA ¦ NA | 945.014 | 945.014 | 754.7468 | 53.1615 | 0.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 945.014 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 891.6902 | 31.023 | 0.15843 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2020-2021TransmissionPlan.pdf
716 | Santa Teresa Project - IBM HR Work |  |  | Santa Clara | Construct a new substation on PG&E property at the Edenvale Service Center in San Jose, CA to serve three new data center loads and correct a normal deficiency on Edenvale Banks 2 and 4 | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | NA | NA | 5792999 | T.0001316 | SANTA TERESA SUB: NEW SUB | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2020 | 2021 | FALSE | 2021 | NA | https://www.caiso.com/Documents/BoardApproved2020-2021TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5601-E | 2019-07-29 | Approved | 2020 | Operational | 1 | 2021-08-12 | 2021-08-01 | 2021-12-14 | NA | NA | FALSE | 18000 | NA ¦ NA | 550.2998 | 550.2998 | 445.6298 | 26.1654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550.2998 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 524.1344 | 12.8407 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2020-2021TransmissionPlan.pdf
717 | Spring Substation Transfer |  |  | Morgan Hill, Santa Clara | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Substation - Multiple | Upgrade/Retrofit | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.8017 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5818332 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2025 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-12-01 | 2021-12-01 | 2025-12-31 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 10071.3525 | 10071.3525 | 0 | 0 | 0 | 0 | 10007.8081 | 63.5444 | 0 | 0 | 0 | 0 | 10007.8081 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
718 | SF A (Potrero):Install SF Potrero Bank 5 |  |  | San Francisco, San Francisco | The recommended scope of this project is to install a 115/12 kV, 75 MVA Bank 5 at a temporary location and 6-feeder switchgear. The new bank and switchgear will remain in place as temporary, and they will be relocated to the new location when Distribution portion of Potrero Substation rebuild, under Project T.0000557 is complete. Transmission Substation Work (MWC 61): • Install a new 115 kV GIS breaker and three 115 kV GIS disconnect switches inside the existing 115 kV GIS building. | Substation - Circuit Breaker | New | NA | T.0000557 | Load Growth | Substation Capacity | NA | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 5.647 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804784 | T.0009170 | SF A Potrero - Install SF Potrero Bank 4 | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-10-19 | 2027-12-30 | 2028-07-27 | Scope Change | NA | FALSE | 14200 | NA ¦ NA | 320.9769 | 27345.7705 | 0 | 0 | 0 | 3.6118 | 259.7467 | 595.4556 | 8918 | 2230 | 0 | 0 | 263.3586 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
719 | MOMENTUM SUB: 230KV BAAH |  |  | Placer | To eliminate the deficiency and provide surplus distribution capacity to meet growing demand by installing two 230/21kV (75 MVA) distribution transformers at Momentum Substation(greenfield). Transmission Line Work (MWC 60): • Loop Rio Oso – Gold Hill or Rio Oso – Atlantic 230kV line in substation property Transmission Substation Work (MWC 61): • Build two rows of 230kV breaker and a half configuration bus arrangement, 6 breakers • Install MPAC building Distribution Substation Work to Install Fiddyment Bank 1 and 21kV Bus Structure (MWC 46): • Install one 230/21kV, 75 MVA LTC transformer, Fiddyment Bank 1. • Install one 21kV bank breaker • Install two 21kV feeder Breakers • Install one 21kV spare feeder bay Distribution Line Work to Fiddyment 2101 and 2102 Feeders (MWC 06): • Trench 1000 feet and install 6-1100Al EPR cables in two 6-inch conduits with one spare 6-inch conduit (for a future 2103 feeder) from Switchgear No. 1 to future PMI-9 SW 760956 (PM 35424031) on College Park Drive to create new Fiddyment 2101 and Fiddyment 2102 underground feeder outlets. These connect to feeders that are being constructed by the land developer on new business PM 35424031 (Placer One Backbone). • Switches may be installed as required for operational flexibility and efficiency. • Automated switches may be required and added to the project scope for FLISR. • Line work and equipment may be added or deleted upon completion of the final design and estimate. | Substation - Multiple | New | NA | T.0008394 | Load Growth | New Substation | NA | NA | 2026-02-12 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3205 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5808038 | T.0009604 | Momentum 230/21kV Substation | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7636-E | 2025-07-03 | Approved | 2025 | Engineering more than 50% complete | 3 | 2027-05-10 | 2028-12-29 | 2027-12-21 | NA | NA | TRUE | 26600 | NA ¦ NA | 2886.359 | 16675.209 | 0 | 0 | 0 | 131.4523 | 916.6267 | 8245.0991 | 5387.0068 | 2035 | 0 | 0 | 1048.0791 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
720 | Salinas Area Reinf Spence Distr Line |  |  | Salinas, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Multiple | Upgrade/Retrofit | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.4966 | NA | 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5816052 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2026 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-02-01 | TBD | 2027-05-21 | NA | NA | TRUE | $226,100 ¦ $452,300 | NA ¦ NA | 0.198 | 16982.9336 | 0 | 0 | 0 | 0 | 0.1968 | 57.7701 | 10843.9062 | 0 | 0 | 0 | 0.1967 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
721 | Salinas Area Reinf - Spence - Firestone T-line |  |  | Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2025-12-01 | 58 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815904 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-06-09 | TBD | 2029-11-01 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 9.7744 | 16585.3542 | 0 | 0 | 0 | 0 | 8.8126 | 48.289 | 0 | 0 | 0 | 0 | 8.8126 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
722 | Salinas Area Reinf Soledad #1 T-line |  |  | Chualar CDP, Monterey ¦ Gonzales, Monterey ¦ Monterey ¦ Soledad, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2025-11-23 | 58 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815905 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-05-04 | TBD | 2029-12-10 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 31.6441 | 16778.6159 | 0 | 0 | 0 | 0 | 30.7398 | 49.5625 | 0 | 0 | 0 | 0 | 30.7398 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
723 | Salinas Area Reinf Soledad #2 T-line |  |  | Chualar CDP, Monterey ¦ Gonzales, Monterey ¦ Monterey ¦ Soledad, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2025-12-04 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815906 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-04-28 | TBD | 2030-03-25 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 3.5799 | 16948.4044 | 0 | 0 | 0 | 0 | 3.4681 | 48.7025 | 0 | 0 | 0 | 0 | 3.468 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
724 | Salinas Area Reinf Fresh Express Station |  |  | Salinas, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Multiple | Upgrade/Retrofit | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.4966 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815915 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-10-02 | TBD | 2030-04-18 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 7.0199 | 24071.1568 | 0 | 0 | 0 | 0 | 6.2622 | 54.371 | 0 | 0 | 0 | 0 | 6.2622 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
725 | Salinas Area Reinf Buena Vista Distr Lin |  |  | Salinas, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Multiple | Upgrade/Retrofit | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.4966 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815917 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2026 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-06-21 | TBD | 2027-10-12 | NA | NA | TRUE | $226,100 ¦ $452,300 | NA ¦ NA | 0.198 | 13453.15 | 0 | 0 | 0 | 0 | 0.1968 | 86.9956 | 7284.8971 | 0 | 0 | 0 | 0.1967 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
726 | Salinas Area Reinf Chualar Distr Line |  |  | Salinas, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Line Termination | New | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.4966 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815916 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2026 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-04-03 | TBD | 2028-07-26 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 0.198 | 13504.95 | 0 | 0 | 0 | 0 | 0.1968 | 86.9956 | 0 | 0 | 0 | 0 | 0.1967 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
727 | Salinas Area Reinf Salinas Substation |  |  | Salinas, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Multiple | New | NA | NA | Reliability | Voltage Conversion | NERC TPL Standards | NA | 2026-03-05 | 58 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.4966 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5816099 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-03-29 | TBD | 2028-08-11 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 57.8193 | 27709.5897 | 0 | 0 | 0 | 0 | 41.0603 | 192.2853 | 0 | 0 | 0 | 0 | 41.0603 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
728 | Salinas Area Reinf Firestone Switching |  |  | Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Multiple | Upgrade/Retrofit | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2026-02-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.14648 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815909 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-03-29 | TBD | 2028-08-11 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 14.3796 | 19580.2371 | 0 | 0 | 0 | 0 | 6.4569 | 146.2977 | 0 | 0 | 0 | 0 | 6.4569 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
729 | New Chualar substation |  |  | TBD | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Multiple | New | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | NA | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | TBD | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811925 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-08-08 | TBD | 2029-08-13 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 618.8672 | 56734.641 | 0 | 0 | 0 | 0 | 443.8142 | 1118.7338 | 800 | 500 | 500 | 500 | 443.8142 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
730 | Salinas Area Reinf Gonzales Decommission |  |  | Salinas, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Multiple | Removal | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.4966 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815926 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | NA | TBD | 2029-12-19 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 1.5866 | 9270.7073 | 0 | 0 | 0 | 0 | 1.331 | 112.9463 | 0 | 0 | 0 | 0 | 1.331 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
731 | Salinas Area Reinf Spence Substation |  |  | Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Multiple | New | NA | NA | Reliability | Voltage Conversion | NERC TPL Standards | NA | 2026-02-03 | 58 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.96235 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815908 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-20 | TBD | 2030-05-07 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 27.8441 | 23053.8609 | 0 | 0 | 0 | 0 | 14.0924 | 118.1907 | 0 | 0 | 0 | 0 | 14.0924 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
732 | Distribution - Concord Naval Weapons Station - High side work |  |  | Concord, Contra Costa | High Side protection work (230 kV) at the new Avila Substation in Concord | Substation - Circuit Breaker | New | NA | NA | Load Growth | Substation Capacity | NA | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.074522 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5746581 | TBD | TBD | TBD | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 11000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 3000 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
733 | COLEMAN-PH SUBSTATION |  |  | Cottonwood CDP, Shasta ¦ Shasta | This project is revised scope of the original Cottonwood-Red Bluff No. 2 60 kV Line Project & Red Bluff 230/60 kV Substation Project. The new revised scope includes: Reconductor Coleman - Red Bluff 60 kV Line, section from Coleman to Red Bluff (Approx 19 miles) with 730 Amps emergency rating or higher. Also, Install sectionalizing breaker at Cottonwood 60 kV Substation. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0005935 | Reliability | Line Termination | NERC TPL Standards | NA | 2025-10-21 | 85 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | NA | 60 kV | 137 | NA | NA | 5.1001 | Non-IGP | 5766751 | T.0000013 | Coleman - Red Bluff Project | 3 | 61 | NA ¦ 5738807 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7766-E | 2025-11-25 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-12-11 | 2021-12-01 | 2028-12-31 | Prioritization | NA | FALSE | $43,000 ¦ $57,000 | NA ¦ NA | 131.2831 | 1101.1176 | 47.5198 | 3.7781 | 4.4287 | 2.6489 | 39.963 | 614.795 | 0 | 0 | 0 | 0 | 103.8048 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
734 | UNION 70KV SUBSTATION |  |  | TBD | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Substation - Multiple | New | NA | NA | Reliability | New Substation | NERC TPL Standards | NA | NA | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | TBD | NA | 70 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767207 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 61 | NA ¦ 5737113 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering less than 50% complete | 4 | 2028-01-28 | 2019-05-01 | 2029-03-29 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 13604.6681 | 49749.093 | 24.4838 | 129.3569 | 10869.0958 | 982.4069 | 1068.4649 | 2710.6714 | 9559.0958 | 20734.1383 | 3351.6197 | 0.8448 | 13392.723 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
735 | CALIFORNIA FLATS: UPGRADE 230KV RELAY |  |  | Monterey | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.4097 | NA | 230 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | 26 | 5.1001 | Non-IGP | 5771721 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2019 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-10-27 | 2019-05-01 | 2028-02-09 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 53.0268 | 2116.8296 | 2.0283 | 4.1785 | 42.2238 | -3.4549 | 2.7887 | 350.0777 | 1402.0058 | 311.7194 | 0 | 0 | 53.0268 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
736 | MORRO BAY: UPGRADE 230KV RELAY |  |  | Morro Bay, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0010761 | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 12.614 | NA | 230 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | 10 | 5.1001 | Non-IGP | 5771722 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2019 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-10-26 | 2019-05-01 | 2028-02-09 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 46.0079 | 1882.706 | 0.2716 | 0.3421 | 48.137 | -6.7664 | 2.4213 | 396.0543 | 951.5876 | 489.0561 | 0 | 0 | 46.0079 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
737 | Kern PP 115kV Substation - Relay Upgrade |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Protection Relay | New | NA | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 10 | 5.1001 | Non-IGP | 5771733 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2019 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-10-03 | 2020-05-01 | 2030-12-27 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 74.5597 | 652.6666 | 0 | 0 | 0 | 12.7941 | 54.416 | 21.0023 | 23.6973 | 88.3228 | 74.0173 | 350.7762 | 73.6247 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
738 | Kern PP 230kV Substation - Relay Upgrade |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Protection Relay | New | NA | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 230 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 10 | 5.1001 | Non-IGP | 5771738 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2019 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2031-01-03 | 2020-05-01 | 2031-03-24 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 19.8495 | 615.3496 | 0 | 0 | 0 | 11.0545 | 1.5583 | 16.8351 | 22.6448 | 119.9108 | 98.8579 | 40.7751 | 19.2676 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
739 | Stockdale 230kV Substn Ampacity & Relay |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Line Termination | Upgrade/Retrofit | NA | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 230 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 11 | 5.1001 | Non-IGP | 5771739 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-11-04 | 2020-05-01 | 2033-04-20 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 934.3304 | 45088.6615 | 0 | 0 | 0 | 363.44 | 517.0986 | 158.4195 | 183.1286 | 4311.4016 | 1844.2969 | 6666.9782 | 892.5224 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
740 | CASA LOMA JUNCTION SUBSTATION |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Multiple | New | NA | T.0000220 ¦ T.0000144 | Reliability | New Substation | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 230 ¦ 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767199 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ 5756022 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2031-07-02 | 2020-05-01 | 2034-03-13 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 697.4275 | 90579.7372 | 0 | 0 | 0 | 160.2978 | 209.2645 | 262.331 | 387.8186 | 4187.9721 | 3611.5104 | 12024.0593 | 683.4038 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
741 | Lamont 115kV Substation - Relay Upgrade |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Protection Relay | New | NA | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 10 | 5.1001 | Non-IGP | 5771734 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2019 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2033-11-03 | 2020-05-01 | 2034-03-16 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 49.4974 | 2723.6871 | 0 | 0 | 0 | 10.8619 | 29.5142 | 9.3493 | 8.1876 | 157.3694 | 248.022 | 38.0008 | 46.7907 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
742 | CASA LOMA JCT SUBST_COMPETITIVE |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Multiple | New | NA | T.0000220 ¦ T.0000144 | Reliability | New Substation | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 230 ¦ 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767215 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ 5763622 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2031-07-02 | 2020-05-01 | 2034-03-30 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 858.8509 | 114969.5443 | 0 | 0 | 0 | 63.784 | 75.5394 | 118.4074 | 145.7957 | 24528.0514 | 3184.8649 | 13523.2055 | 848.0803 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
743 | Wheeler Ridge 230kV Station - New BAAH |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-11 | 115 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 8 | 5.1001 | Non-IGP | 5771737 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2020 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2033-08-03 | 2020-05-01 | 2034-04-28 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 172.2717 | 9723.5683 | 0 | 0 | 0 | 30.7901 | 132.7256 | 71.295 | 128.4191 | 1326.6136 | 558.5125 | 423.3023 | 169.9303 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
744 | Adobe 115kV Station Line & Relay Upgrade |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Protection Relay | New | NA | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 23 | 5.1001 | Non-IGP | 5771736 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2019 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2034-01-04 | 2020-05-01 | 2034-05-01 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 8.1047 | 495.0347 | 0 | 0 | 0 | 1.1099 | 0.4109 | 0.5277 | 0.674 | 98.6852 | 28.0827 | 9.601 | 8.1047 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
745 | WRJ COMPETITIVE_CPUC LIC/PER |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Other | New | NA | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.403 | NA | 230 ¦ 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767232 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ 5763622 ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-05-01 | 2020-05-01 | 2034-04-27 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 3917.8392 | 9431.8051 | 0 | 0 | 0 | 269.3011 | 541.8178 | 905.5155 | 1021.9309 | 692.4927 | 539.5379 | 515.3944 | 3813.7931 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
746 | Purchase Land New Substations Competitiv |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Other | New | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 10.403 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5523423 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2025 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Planning | 5 | NA | 2020-05-01 | 2028-12-20 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 0.1858 | 405.1858 | 0 | 0 | 0 | 0.1858 | 0 | 0 | 0 | 405 | 0 | 0 | 0.1858 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2028 | 0 | 0 | 0 | 0.18579 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
747 | Purchase Land New Substations Non-Compet |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Other | New | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 10.403 | NA | NA | 236 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.1001 | Non-IGP | 5523424 | T.0000156 | Wheeler Ridge Junction Substation | 19 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2025 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Planning | 5 | NA | 2020-05-01 | 2028-12-20 | ISO Action | NA | FALSE | $90,000 ¦ $140,000 | NA ¦ NA | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] PG&E was awarded competitive scope of this project. There is no outside developer.
748 | HERNDON SUB - NORTHERN FRESNO 115KV AREA |  |  | Fresno, Fresno | This project will sectionalize the 230kV buses at two key substations to ensure reliable electric service to customers in Fresno County. By installing 230kV bus sectionalizing breakers at Herndon and McCall substations, the project will reduce the likelihood of a 230kV bus or internal breaker fault causing 115kV overloads and voltage issues leading to load shedding and service interruptions to customers in the Fresno area. | Substation - Line Termination | New | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 13.3414 | NA | 115 kV | 428 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767191 | T.0000158 | Northern Fresno 115 kV Area Reinforcemnt | 1 | 61 | NA ¦ 5751201 ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-06-28 | 2018-05-01 | 2020-05-13 | Bundling Dependencies | NA | FALSE | $110,000 ¦ $190,000 | NA ¦ NA | 13727.9432 | 13727.9432 | 825.3714 | 74.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13727.9432 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 800.5071 | 71.7918 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - New Substation Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
749 | MARTIN SUB_230KV BUS EXT |  |  | Brisbane, San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Substation - Multiple | New | NA | T.0008764 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-12 | 53 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 230 kV | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | 5.1001 | Non-IGP | 5767214 | T.0000159 | Egbert 230kV Switching Station | 10 | 61 | NA ¦ 5763147 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Engineering more than 50% complete | 3 | 2027-02-02 | 2021-12-01 | 2028-10-12 | Prioritization | NA | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 50150.5712 | 157239.1825 | 5920.4821 | 16228.3266 | 16470.0052 | 4906.7885 | 4766.2958 | 27256.1713 | 6026.813 | 22986.322 | 27962.297 | 23094.674 | 49199.9722 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil
750 | MARTIN BUS EXT_CPUC LIC/PER |  |  | Brisbane, San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Other | New | NA | NA | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 230 kV | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | NA | NA | 5767220 | T.0000159 | Egbert 230kV Switching Station | 10 | 61 | NA ¦ 5763147 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2019 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Operational | 1 | NA | 2021-12-01 | 2021-01-04 | NA | NA | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 0.8809 | 0.8809 | 441.2028 | 684.4983 | -13089.9439 | -132.2422 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8809 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 12542.587 | 684.4983 | -13089.9439 | -129.9863 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil - $300 Mil ¦ Over $500 Mil
751 | LAND PURCHASE_MARTIN BUS EXTENSION |  |  | Brisbane, San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Other | New | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 18.2105 | NA | 230 kV | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | NA | NA | 5520825 | T.0000159 | Egbert 230kV Switching Station | 10 | 61 | NA ¦ 5763147 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Operational | 1 | NA | 2021-12-01 | 2021-01-28 | NA | NA | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 19036.9722 | 19036.9722 | 1849.0384 | -319.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19036.9722 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1849.0384 | -319.115 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil
752 | MARTIN BUS EXT MARTIN SUB PROT UPGRADES |  |  | Brisbane, San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0008764 | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 18.2105 | NA | 230 kV | 564 | 8. Compliance/Commitments With Low Safety Risk | 1126 | 5.1001 | Non-IGP | 5767645 | T.0000159 | Egbert 230kV Switching Station | 10 | 61 | NA ¦ 5763147 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Planning | 5 | 2028-05-30 | 2021-12-01 | 2028-10-12 | Prioritization | NA | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 354.1344 | 6661.4955 | 36.8994 | 194.1059 | 24.5206 | 35.2578 | 54.6305 | 625.18 | 147.7405 | 380.4424 | 704.2594 | 4162.9721 | 345.4142 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil
753 | SF RAS MODIFICATIONS @ C |  |  | San Francisco, San Francisco | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | T.0008764 | Reliability | Substation Reliability | NERC TPL Standards | NA | NA | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 1.2173 | NA | 230 kV | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | 5.1001 | Non-IGP | 5767648 | T.0000159 | Egbert 230kV Switching Station | 10 | 61 | NA ¦ 5763147 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2022 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Planning | 5 | 2028-05-30 | 2021-12-01 | 2028-10-27 | Prioritization | NA | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 30.7527 | 3440.3398 | 0 | 1.3345 | 1.5503 | 2.7675 | 20.7402 | 12.3826 | 47.4198 | 309.5549 | 344.3961 | 1501.6592 | 26.3925 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil
754 | MARTIN BUS EXT JEFFERSON PROT UPGRADES |  |  | San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0008764 | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.7091 | NA | 230 kV | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | 5.1001 | Non-IGP | 5767646 | T.0000159 | Egbert 230kV Switching Station | 10 | 61 | NA ¦ 5763147 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2016 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Planning | 5 | 2028-06-02 | 2021-12-01 | 2028-11-01 | Prioritization | NA | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 92.1119 | 5507.8753 | 15.6606 | 23.5376 | 10.0545 | 7.3803 | 29.9632 | 364.556 | 82.8762 | 163.7559 | 200.8916 | 4037.2736 | 87.2459 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil
755 | MARTIN BUS EXT EMBARCADERO PROT UPGRADE |  |  | San Francisco, San Francisco | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0008764 | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-03-21 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.55624 | NA | 230 kV | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | 5.1001 | Non-IGP | 5767647 | T.0000159 | Egbert 230kV Switching Station | 10 | 61 | NA ¦ 5763147 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Planning | 5 | 2028-07-03 | 2021-12-01 | 2028-11-13 | Prioritization | NA | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 124.6599 | 4166.8278 | 14.9511 | 52.312 | 12.1774 | 14.7481 | 27.4298 | 345.3099 | 121.9114 | 537.9793 | 418.8811 | 2516.7171 | 121.6184 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil
756 | VACA DIXON: Install 230 KV Smart Wires |  |  | Vacaville, Solano | The project scope is to install about 78 modular power flow control systems deployed on a dedicated bank structure at Vaca Dixon Substation (or adjacent property). Further scoping activities will finalize the substation location(s) to address potential new line overloads. The CAISO recently approved this project in their 2017-2018 Transmission Plan. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.725 | NA | 230 kV | 103 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5779290 | T.0003844 | Vaca-Dixon 230kV SmartWire Devices | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-06-23 | 2019-10-01 | 2028-01-25 | Prioritization | Project Design | FALSE | 11000 | NA ¦ NA | 3128.3204 | 48762.4375 | 1.8077 | 0 | 0 | 77.8365 | 230.5566 | 2224.1552 | 12000 | 10000 | 5000 | 400 | 3087.8828 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
757 | Midway-Temblor 115kV Recon & Voltage Sup |  |  | Kern | This project proposes to upgrade 14.5 miles of conductor and four (4) transmission switches (Nos. 137, 139, and 157) on the Midway – Temblor 115 kV Line, and install 39 MVAR shunt capacitors with 13 MVAR steps (a total of 3 steps), and convert existing 115kV bus at Temblor Substation to 5-element ring bus (expandable to 6-element in future). | Substation - Voltage Support Equipment | New | NA | T.0000423 | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-05 | 21 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 0.93942 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 20 | 5.1001 | Non-IGP | 5781146 | T.0004113 | Midway-Temblor 115kV Recon & Voltage Sup | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-08-16 | 2018-05-01 | 2029-11-12 | Prioritization | NA | FALSE | $25,000 ¦ $35,000 | NA ¦ NA | 913.2329 | 25727.8724 | 21.383 | 3.727 | 0 | 47.4085 | 459.3369 | 1280.9681 | 11100 | 4800 | 800 | 0 | 828.7922 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
758 | Castro Valley-Newark 230kV Line Capacity |  |  | Fremont, Alameda | The project scope of work involves upgrading the limiting substation equipment (jumper conductors and wave traps) on the Moraga-Castro Valley and Castro Valley-Newark 230 kV lines to utilize their full conductor ratings. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | 62 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | NA | 27.7611 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806179 | T.0004421 | Moraga-Castro Valley 230 kV Capacity | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-08-22 | 2013-05-01 | 2025-03-24 | Prioritization | NA | TRUE | $1,000 ¦ $5,000 | NA ¦ NA | 690.0088 | 690.0088 | 0 | 0 | 33.239 | 561.2673 | 100.9603 | -5.4579 | 0 | 0 | 0 | 0 | 695.4667 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 604.8388 | -4.7183 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
759 | Moraga-Castro Valley 230kV Line Capacity |  |  | Castro Valley CDP, Alameda | The project scope of work involves upgrading the limiting substation equipment (jumper conductors and wave traps) on the Moraga-Castro Valley and Castro Valley-Newark 230 kV lines to utilize their full conductor ratings. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-05 | 73 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 5.428 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806178 | T.0004421 | Moraga-Castro Valley 230 kV Capacity | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-01-10 | 2013-05-01 | 2025-04-07 | Prioritization | NA | TRUE | $1,000 ¦ $5,000 | NA ¦ NA | 958.615 | 958.615 | 0 | 0 | 33.9576 | 478.6882 | 444.9124 | 1.0568 | 0 | 0 | 0 | 0 | 957.5582 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 824.3536 | 0.90684 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
760 | Newark: HVDC Connection |  |  | Fremont, Alameda | The Newark – NRS HVDC project is modified to Newark – NRS 230 kV project. No HVDC converters or lines are required in the modified scope and the modified scope includes only a high capacity 230 kV AC line (1,000 MVA) from PG&E’s Newark substation to Silicon Valley Power’s (SVP’s) NRS substation. | Substation - Line Termination | New | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | 27.7611 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804787 | T.0009168 | Newark - HVDC Connection | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-18 | 2028-06-01 | 2027-05-28 | NA | NA | TRUE | $325,000 ¦ $510,000 | NA ¦ NA | 6080.376 | 22844.4906 | 0 | 0 | 345.0878 | 1188.6754 | 4342.5047 | 9365.6439 | 6996.5513 | 606.0276 | 0 | 0 | 5876.2679 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 1533.7632 | 5876.2679 | 6080.376 | 0% ¦ LS Power, San Jose Area HVDC 230 kV Line (Newark - NRS) | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
761 | METCALF -MORGAN HILL SECURITY FENCE |  |  | Morgan Hill, Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Substation - Other Equipment | New | NA | T.0003803 ¦ T.0005211 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 4.8017 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815774 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2025 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7391-E | 2024-10-10 | Approved | 2024 | Engineering less than 50% complete | 4 | 2026-05-29 | 2028-06-01 | 2026-07-28 | NA | NA | TRUE | $425,000 ¦ $615,000 | NA ¦ NA | 5240.9876 | 5972.1643 | 0 | 0 | 0 | 0 | 2183.6061 | 3788.5582 | 0 | 0 | 0 | 0 | 2183.6061 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 2183.6061 | 5240.9876 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
762 | San Jose B 230kV GIS |  |  | San Jose, Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Substation - Bus Arrangement | New | NA | T.0003803 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.1017 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813144 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7391-E | 2024-10-10 | Approved | 2024 | Engineering less than 50% complete | 4 | 2028-06-01 | 2030-06-01 | 2030-06-28 | NA | NA | FALSE | $425,000 ¦ $615,000 | NA ¦ NA | 249.8691 | 166472.1314 | 0 | 0 | 0 | 0 | 180.2107 | 13279.1754 | 32494.9049 | 32023.4015 | 69005.2057 | 19231.7945 | 180.2108 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2030 | 0 | 0 | 0 | 0 | 180.2107 | 249.8691 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
763 | San Jose B - HVDC - South Transition RE |  |  | San Jose, Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Substation - Multiple | New | NA | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-11 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5555161 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7391-E | 2024-10-10 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-06-15 | 2028-06-01 | 2027-12-30 | NA | NA | TRUE | $425,000 ¦ $615,000 | NA ¦ NA | 11.5117 | 454.7175 | 0 | 0 | 0 | 10.8109 | 0.7008 | 83.5674 | 215.5318 | 122.5521 | 21.5546 | 0 | 11.5117 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 10.8109 | 11.5117 | 11.5117 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
764 | San Jose B - HVDC - Trimble RE |  |  | San Jose, Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Substation - Multiple | New | NA | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-11 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807739 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7391-E | 2024-10-10 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-06-03 | 2028-06-01 | 2027-12-30 | NA | NA | TRUE | $425,000 ¦ $615,000 | NA ¦ NA | 83.809 | 2990.6821 | 0 | 0 | 0.7403 | 17.3429 | 41.6768 | 457.5361 | 2405.4593 | 67.9267 | 0 | 0 | 59.76 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 18.0832 | 59.7601 | 83.809 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
765 | San Jose B - HVDC - North Transition RE |  |  | San Jose, Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Substation - Multiple | New | NA | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-08 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.0642 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5555160 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7391-E | 2024-10-10 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-05-18 | 2028-06-01 | 2027-12-31 | NA | NA | TRUE | $425,000 ¦ $615,000 | NA ¦ NA | 13.5061 | 398.3254 | 0 | 0 | 0 | 10.1952 | 3.3109 | 48.0222 | 256.8728 | 79.9243 | 0 | 0 | 13.5061 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 10.1952 | 13.5061 | 13.5061 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
766 | Metcalf: 500kV HVDC Connection |  |  | Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Substation - Line Termination | New | NA | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804788 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7391-E | 2024-10-10 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-06-04 | 2028-06-01 | 2027-12-31 | NA | NA | TRUE | $425,000 ¦ $615,000 | NA ¦ NA | 3664.3611 | 71237.474 | 0 | 0 | 363.6569 | 1890.1419 | 1165.3476 | 21317.3977 | 13902.58 | 32598.3497 | 0 | 0 | 3419.1465 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 2253.7988 | 3419.1465 | 3664.3611 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
767 | San Jose B: HVDC Connection |  |  | San Jose, Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Substation - Line Termination | New | NA | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.1017 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804789 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7391-E | 2024-10-10 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-10-06 | 2028-06-01 | 2027-12-31 | NA | NA | TRUE | $425,000 ¦ $615,000 | NA ¦ NA | 35977.4844 | 219548.3471 | 0 | 0 | 329.67 | 13534.8854 | 16680.9805 | 69866.1743 | 65161.6213 | 21445.303 | 31246.9522 | 1282.7605 | 30545.5358 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 13864.5553 | 30545.5359 | 35977.4844 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
768 | San Jose B - HVDC - San Jose A RE |  |  | San Jose, Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Substation - Multiple | New | NA | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.1997 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807758 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7391-E | 2024-10-10 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-10-29 | 2028-06-01 | 2027-12-31 | NA | NA | TRUE | $425,000 ¦ $615,000 | NA ¦ NA | 85.1992 | 1676.3094 | 0 | 0 | 0.7403 | 79.6812 | 4.348 | 820.0666 | 201.7021 | 569.5477 | 0.2235 | 0 | 84.7695 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 80.4215 | 84.7695 | 85.1992 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
769 | San Jose B HVDC Land Acq |  |  | San Jose, Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Other | New | NA | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 2.1017 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5559139 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2025 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | 2028-06-01 | OAI | NA | NA | TRUE | $425,000 ¦ $615,000 | NA ¦ NA | 105.0707 | 8100.0707 | 0 | 0 | 0 | 0 | 0 | 4800.0707 | 0 | 3300 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 105.0707 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
770 | METCALF GC YARD RELOCATION LAND ACQUISIT |  |  | Santa Clara | The scope of the Metcalf – San Jose B HVDC project is modified as follows: a. Build a 1,000 MW HVDC link between Metcalf 500 kV and San Jose B 230 kV substation b. The voltage at the AC side of the San Jose B converter station is changed from 115 kV to 230 kV. c. A 230 kV switchyard and a 230/115 kV transformer will be required at San Jose B. | Other | New | NA | T.0003803 ¦ T.0005211 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 37.8815 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5561666 | T.0009169 | Metcalf HVDC Interconnection Project | 11 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2025 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2028-06-01 | OAI | NA | NA | TRUE | $425,000 ¦ $615,000 | NA ¦ NA | 16871.3796 | 28871.3796 | 0 | 0 | 0 | 0 | 16871.3796 | 12000 | 0 | 0 | 0 | 0 | 16871.3796 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 16871.3796 | 0 | 0% ¦ LS Power, San Jose Area HVDC 500 kV Line (Metcalf – San Jose) | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
771 | Collinsville New 500kV Sub Connection |  |  | Solano | This project will support connection of a new 500kV substation between Vaca Dixon and Tesla Substations to the PG&E electric system. The new 500kV substation (named Collinsville), to be installed by the third-party entity (LS Power), is needed to address a number of identified transmission constraints and provide an additional supply from the 500kV system into the northern Greater Bay Area, to increase reliability to the area and advance additional renewable generation in the northern area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Vaca Dixon – Tesla 500kV line into the new 500kV Collinsville substation and build the associated transmissioin line. • Modify Vaca Dixon 500kV Series Capacitor Bank 2 reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Connect two 230kV lines to Pittsburg 230kV bus in separate bus sections and install 115kV bus reactors in bus sections D&E. • Upgrade line protection of Tesla 500kV line at Tesla substation as needed | Substation - Multiple | New | NA | T.0004581 | Policy | Voltage Support | NERC TPL Standards | NA | 2026-03-25 | NA | Steady State Power Flow System Analysis | Wires - System Configuration Alternative | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804724 | T.0009189 | New Collinsville 500kV Sub Connection Pr | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-06-01 | 2028-01-01 | 2028-05-30 | NA | NA | FALSE | $475,000 ¦ $675,000 | NA ¦ NA | 958.6976 | 35568.169 | 0 | 0 | 45.4737 | 168.2413 | 705.3013 | 7978.704 | 16800.4039 | 7188.8949 | 2681.1499 | 0 | 919.0162 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 213.715 | 919.0163 | 958.6977 | 0% ¦ LS Power, New Collinsville 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
772 | Tesla: Upgrade system protection |  |  | Alameda | This project will support connection of a new 500kV substation between Vaca Dixon and Tesla Substations to the PG&E electric system. The new 500kV substation (named Collinsville), to be installed by the third-party entity (LS Power), is needed to address a number of identified transmission constraints and provide an additional supply from the 500kV system into the northern Greater Bay Area, to increase reliability to the area and advance additional renewable generation in the northern area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Vaca Dixon – Tesla 500kV line into the new 500kV Collinsville substation and build the associated transmissioin line. • Modify Vaca Dixon 500kV Series Capacitor Bank 2 reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Connect two 230kV lines to Pittsburg 230kV bus in separate bus sections and install 115kV bus reactors in bus sections D&E. • Upgrade line protection of Tesla 500kV line at Tesla substation as needed | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0004581 | Policy | Substation Reliability | NERC TPL Standards | NA | 2026-03-19 | NA | Steady State Power Flow System Analysis | Wires - System Configuration Alternative | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Heat Wave |  | NA | 69.382 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804802 | T.0009189 | New Collinsville 500kV Sub Connection Pr | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-08-17 | 2028-01-01 | 2028-05-30 | NA | NA | FALSE | $475,000 ¦ $675,000 | NA ¦ NA | 496.7935 | 8146.3811 | 0 | 0 | 37.658 | 104.6578 | 318.114 | 534.6377 | 5349.8911 | 1757.4137 | 44.0087 | 0 | 460.4299 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 142.3159 | 460.4299 | 496.7935 | 0% ¦ LS Power, New Collinsville 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
773 | Pittsburg: Connect 2 230 & inst bus reac |  |  | Pittsburg, Contra Costa | Add 18-ohm reactors in parallel between Bus D and E of the Pittsburg 115kV substation | Substation - Reactive Equipment | New | NA | T.0004581 | Policy | Voltage Support | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | Wires - System Configuration Alternative | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 28.8512 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804803 | T.0009189 | New Collinsville 500kV Sub Connection Pr | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2023 | TRUE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-06-29 | 2028-01-01 | 2028-05-26 | NA | NA | FALSE | 26000 | NA ¦ NA | 2699.5342 | 28963.6631 | 0 | 0 | 134.265 | 640.0182 | 1655.9587 | 2044.1579 | 15905.3672 | 7819.7799 | 764.1163 | 0 | 2430.242 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 774.2833 | 2430.2419 | 2699.5342 | 0% ¦ LS Power, New Collinsville 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
774 | MANNING SUB: MIDWAY PROTECTION UPGRADE |  |  | Buttonwillow CDP, Kern | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009550 | Policy | Substation Capacity | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804805 | T.0009194 | Manning New 500kV Sub Connection | 18 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-11-03 | 2028-01-01 | 2027-02-26 | NA | NA | TRUE | $325,000 ¦ $485,000 | NA ¦ NA | 357.4941 | 2079.1372 | 0 | 0 | 25.5257 | 92.1897 | 202.2863 | 621.9268 | 1137.2088 | 0 | 0 | 0 | 320.0016 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 117.7154 | 320.0016 | 357.4941 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
775 | MANNING SUB: TRANQUILITY BAAH |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Multiple | New | NA | T.0009550 | Policy | New Substation | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804813 | T.0009194 | Manning New 500kV Sub Connection | 18 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-05-15 | 2028-01-01 | 2028-04-21 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 1996.0083 | 22430.0693 | 0 | 0 | 64.1999 | 913.1347 | 831.6588 | 12395.7401 | 5001.4667 | 3223.8691 | 0 | 0 | 1808.9934 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 977.3346 | 1808.9934 | 1996.0083 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
776 | MANNING SUB: LOS BANOS PROTECTION UPGRAD |  |  | Merced | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009550 | Policy | Substation Capacity | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804804 | T.0009194 | Manning New 500kV Sub Connection | 18 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-07-08 | 2028-01-01 | 2028-04-27 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 720.2117 | 6236.5985 | 0 | 0 | 52.8413 | 172.066 | 373.7475 | 1214.6302 | 2844.9078 | 1578.4057 | 0 | 0 | 598.6548 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 224.9073 | 598.6548 | 720.2117 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
777 | MANNING SUB: GATES PROTECTION UPGRADE |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009550 | Policy | Substation Capacity | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804878 | T.0009194 | Manning New 500kV Sub Connection | 18 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2027-11-03 | 2028-01-01 | 2028-04-27 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 674.3294 | 3043.5577 | 0 | 0 | 147.1446 | 245.5821 | 212.7964 | 189.0227 | 830.9422 | 1418.0697 | 0 | 0 | 605.5231 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 392.7267 | 605.5231 | 674.3294 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
778 | Manning Sub: Las Aguilas Sw Sub |  |  | San Benito | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009550 | Policy | Substation Capacity | NERC TPL Standards | NA | 2026-02-10 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.0534 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5809978 | T.0009194 | Manning New 500kV Sub Connection | 18 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2028-03-06 | 2028-01-01 | 2028-04-28 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 339.7012 | 1980.5232 | 0 | 0 | 0 | 32.5037 | 275.3559 | 134.5203 | 647.3268 | 890.8165 | 0 | 0 | 307.8596 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 32.5037 | 307.8596 | 339.7012 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
779 | Manning Sub: Panoche Eng Centr |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009550 | Policy | Substation Capacity | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5809979 | T.0009194 | Manning New 500kV Sub Connection | 18 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2028-04-04 | 2028-01-01 | 2028-04-28 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 23.0757 | 23.0757 | 0 | 0 | 0 | 24.7645 | -1.6887 | 0 | 0 | 0 | 0 | 0 | 23.0757 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 24.7645 | 23.0757 | 23.0757 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
780 | Manning Sub: Manning Telecom and Testing |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009550 | Policy | Substation Capacity | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5809028 | T.0009194 | Manning New 500kV Sub Connection | 18 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7706-E | 2025-09-24 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-09-29 | 2028-01-01 | 2028-05-26 | NA | NA | FALSE | $325,000 ¦ $485,000 | NA ¦ NA | 969.9099 | 10543.8194 | 0 | 0 | 0 | 295.707 | 597.0237 | 7506.6674 | 1630.1607 | 514.2605 | 0 | 0 | 892.7308 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 295.707 | 892.7307 | 969.9099 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
781 | MANNING SUB: PANOCHE BAAH |  |  | Fresno | Replace 115 kV circuit breakers 132, 152, 102 and 162, install a new MPAC building for the 115 kV bus section, convert 230 kV Bus Section D to BAAH and replace overstressed breakers in Bus E to 63 kA at Panoche substation | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0009550 | Policy | Bus Upgrade | NERC TPL Standards | NA | 2026-03-03 | 25 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804806 | T.0009194 | Manning New 500kV Sub Connection | 18 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2023 | TRUE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-05-11 | 2028-01-01 | 2028-04-27 | NA | NA | FALSE | 184000 | NA ¦ NA | 7577.456 | 78264.2581 | 0 | 0 | 82.1099 | 3537.5552 | 3588.1592 | 37016.4945 | 24357.8651 | 9682.0743 | 0 | 0 | 7207.8242 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 3619.6651 | 7207.8242 | 7577.456 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
782 | STAGG: Install Special Protection Scheme |  |  | Stockton, San Joaquin | The project scope of work involves the following•Install a new 4.2 miles of 60 kV line between Stagg and Hammer substations •Install a new 60 kV circuit breaker at Stagg Substation•Upgrade the Hammer 60 kV bus to a six element ring bus•Upgrade associated substation equipment at Stagg and Hammer substations to accommodate the new 60 kV line, if necessary. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | Reliability | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.5909 | NA | 230 ¦ 60 kV | 102 | 8. Compliance/Commitments With Low Safety Risk | 7 | NA | NA | 5768693 | T.0000016 | Stagg-Hammer 60kV Line Install SPS | 2 | 61 | NA ¦ 5746743 ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2017 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-02-11 | 2021-04-21 | 2020-11-16 | NA | NA | FALSE | 2056 | NA ¦ NA | 1811.659 | 1811.659 | 32.8534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1811.659 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 32.8534 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
783 | SEMITROPIC-MIDWAY: Recond 115 KV Line |  |  | Kern | Reconductor 14.2 miles of the Semitropic-Midway No. 1 115kV Line. The project expects to improve service reliability in core operations by reconductoring the Semitropic-Midway No. 1 115kV Line that will improve system performance and reliability, which will reduce outages. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-12 | 52 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 14.2 | 2.2701 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 14 | NA | NA | 5767160 | T.0000143 | SEMITROPIC-MIDWAY 115KV LINE RECONDUCTOR | 4 | 61 | NA ¦ 5747849 ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-01 | 2016-12-01 | 2021-03-30 | Clearances | NA | FALSE | $15,000 ¦ $20,000 | NA ¦ NA | 5128.2809 | 5128.2809 | 2119.86 | -18.7167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5128.2809 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 4932.0462 | -17.8929 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Non-Wires - System DER Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
784 | LOCKEFORD SUBSTATION NEW 230 KV BAY |  |  | Lockeford CDP, San Joaquin | The Lockeford-Lodi Area 230 kV Development Project will loop the Brighton – Bellota 230 kV Line into Lockeford 230 kV Substation to bring a new 230 kV source into the area. A new 230 kV double circuit tower line will be constructed to connect the existing Lockeford 230 kV Substation to a new 230 kV switching to be constructed near the City of Lodi’s existing Industrial 60 kV Subsation. To accommodate the Brighton – Bellota loop-in and the new DCTL, the Lockeford 230 kV Bus will be upgraded to a four-bay breaker-and-a-half (BAAH) bus configuration. The City of Lodi will be constructing a new 230/60 kV Substation which will be connected to the new 230 kV switching station. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Non-Wires - Large Scale Energy Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 10.2719 | NA | 230 kV | 45 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5771389 | T.0000155 | Lockeford - Lodi Area 230 kV Development | 4 | 61 | NA ¦ 5752080 ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2018 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | PEA Deemed Complete | 2023-09-01 | EIR | NA | CPUC | NA | CPCN: A.23-09-001 | 2023-09-01 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 3 | 2030-11-15 | 2017-03-01 | 2031-06-30 | Prioritization | NA | FALSE | $80,000 ¦ $105,000 | TBD ¦ TBD | 346.0485 | 47317.6115 | 84.5839 | 39.954 | 20.2694 | 21.5602 | 14.2491 | 60.9171 | 2209.8691 | 9509.7112 | 12907.2514 | 22256.535 | 338.2276 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
785 | KERN PP: Upgrade 230 kV Bus |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-04 | 69 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 37.7504 | NA | 230 kV | 764 | NA | NA | NA | NA | 5767360 | T.0000204 | Kern 230kV Bus Upgrade | 13 | 61 | NA ¦ 5748540 ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-05-01 | 2013-05-01 | 2019-03-07 | Prioritization | NA | FALSE | $32,000 ¦ $44,000 | NA ¦ NA | 36997.1444 | 36997.1444 | 5.6904 | 7.6009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36997.1444 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 5.5939 | 7.472 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
786 | KERN: Repl 230 KV Bus Phase 2 |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-04 | 69 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 37.7504 | NA | 230 kV | 764 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5775225 | T.0000204 | Kern 230kV Bus Upgrade | 13 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-04-02 | 2013-05-01 | 2020-02-10 | Prioritization | NA | FALSE | $32,000 ¦ $44,000 | NA ¦ NA | 4198.2607 | 4198.2607 | 33.6794 | -0.2235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4198.2607 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 33.6794 | -0.2235 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
787 | KERN: Repl 230 KV Bus Phase 3 |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-04 | 69 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 37.7504 | NA | 230 kV | 764 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5775226 | T.0000204 | Kern 230kV Bus Upgrade | 13 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-06-01 | 2013-05-01 | 2021-03-01 | Prioritization | NA | FALSE | $32,000 ¦ $44,000 | NA ¦ NA | 4408.9848 | 4408.9848 | 2190.0309 | 34.5204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4408.9848 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 4374.4644 | 34.5204 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
788 | OAKLAND X SUB: 115kV BUS UPGRADE |  |  | Oakland, Alameda | The project proposes to replace the structures, conductors, and hardware in the same overhead alignment between Moraga Substation and California State Highway 13 and also to relocate the line sections between Highway 13, and Oakland X underground (UG) within city streets. By replacing the aging facilities PG&E can improve wildfire safety and public safety and increase path capacity into the Oakland area. The project scope of work includes: • Removal of 78 existing lattice steel transmission towers • Removal of approximately 20 circuit miles of conductor • Installation of approximately 60 new lattice steel transmission towers • Installation of approximately 11 miles of Aluminum Conductor Composite Reinforced (ACCR) conductor • Installation of three 115kV underground duct banks with 115kV transmission cables totaling approximately six miles • Installation of new 115kV circuit breakers and air switches at Moraga Substation • Upgrade the 115kV bus at Oakland X Substation to complement the higher capacity ACCR conductor | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2026-03-12 | 34 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 1.1294 | NA | 115 kV | NA | 5. Compliance/Commitments With Strong Safety Link | 55 | 5.1001 | Non-IGP | 5789521 | T.0000349 | Moraga-Oakland #1-#4 Rebuild | 12 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2024-12-12 | EIR | NA | CPUC | NA | PTC: A. 24-11-005 | 2024-11-15 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 3 | 2030-04-26 | 2025-07-31 | 2030-12-24 | Prioritization | NA | FALSE | 212000 | NA ¦ NA | 543.2084 | 14253.0758 | 78.6894 | 104.2516 | 105.8178 | 122.485 | 98.9701 | 210.6792 | 299.4724 | 318.7935 | 1448.8025 | 11105.5354 | 527.8859 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
789 | MORAGA SUB: 115KV TERMINAL UPGRADES |  |  | Orinda, Contra Costa | The project proposes to replace the structures, conductors, and hardware in the same overhead alignment between Moraga Substation and California State Highway 13 and also to relocate the line sections between Highway 13, and Oakland X underground (UG) within city streets. By replacing the aging facilities PG&E can improve wildfire safety and public safety and increase path capacity into the Oakland area. The project scope of work includes: • Removal of 78 existing lattice steel transmission towers • Removal of approximately 20 circuit miles of conductor • Installation of approximately 60 new lattice steel transmission towers • Installation of approximately 11 miles of Aluminum Conductor Composite Reinforced (ACCR) conductor • Installation of three 115kV underground duct banks with 115kV transmission cables totaling approximately six miles • Installation of new 115kV circuit breakers and air switches at Moraga Substation • Upgrade the 115kV bus at Oakland X Substation to complement the higher capacity ACCR conductor | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2026-03-03 | 63 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $250 Mil – $300 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 15.8714 | NA | 115 kV | NA | 5. Compliance/Commitments With Strong Safety Link | 55 | 5.1001 | Non-IGP | 5789522 | T.0000349 | Moraga-Oakland #1-#4 Rebuild | 12 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2024-12-12 | EIR | NA | CPUC | NA | PTC: A. 24-11-005 | 2024-11-15 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 3 | 2030-04-26 | 2025-07-31 | 2030-12-24 | Prioritization | NA | FALSE | 212000 | NA ¦ NA | 332.9074 | 13231.7657 | 33.6732 | 59.3722 | 39.1305 | 110.4441 | 78.7127 | 193.2854 | 309.9287 | 288.6281 | 1600.4808 | 10063.0687 | 321.8947 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
790 | Vierra 115 kV Reinforcement Phase 2 |  |  | Lathrop, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-02-06 | 16 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.355 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5805478 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2023 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Construction (50%-75%) | 2 | 2025-06-02 | 2014-05-01 | 2026-11-25 | Prioritization | NA | TRUE | $10,000 ¦ $15,000 | NA ¦ NA | 5340.921 | 7349.516 | 0 | 0 | 0 | 0.0302 | 4552.3242 | 2638.7559 | 137.8759 | 3.408 | 0 | 0 | 4552.3544 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
791 | VIERRA 115 KV BAAH |  |  | Lathrop, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-02-06 | 15 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.355 | NA | 115 kV | 102 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5746745 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2014 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Operational | 1 | 2024-05-21 | 2014-05-01 | 2025-05-21 | Prioritization | NA | TRUE | $10,000 ¦ $15,000 | NA ¦ NA | 22150.3472 | 22274.2858 | 167.2897 | 423.2744 | 3679.7011 | 10727.0871 | 5758.5612 | 198.0608 | 8.1096 | 0 | 0 | 0 | 22067.443 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 22067.531 | 82.9042 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
792 | GREEN VALLEY: Upgrade 115 kV Bus |  |  | Interlaken CDP, Santa Cruz | This project will replace the existing 115 kV bus with five bays of breaker-and-a-half (BAAH) configuration. The new 115 kV BAAH bus will be located in the existing substation yard, which will require sequential construction of the new BAAH bays and removal of sections of the existing 115 kV bus. The protection and controls of the new equipment will be moved to the new Modular Protection Automation and Control (MPAC) building | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2026-02-02 | 49 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | 428 | NA | NA | NA | NA | 5767951 | T.0000638 | Green Valley Substation Upgrade | 6 | 61 | NA ¦ 5744458 ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-04-04 | 2019-12-31 | 2018-09-20 | NA | NA | FALSE | 47000 | NA ¦ NA | 26400.222 | 26400.222 | 76.4141 | 22.2073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26400.222 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 69.3399 | 20.1514 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
793 | GREEN VALLEY: Upgd 115 kV BUS BAAH PH 2 |  |  | Interlaken CDP, Santa Cruz | This project will replace the existing 115 kV bus with five bays of breaker-and-a-half (BAAH) configuration. The new 115 kV BAAH bus will be located in the existing substation yard, which will require sequential construction of the new BAAH bays and removal of sections of the existing 115 kV bus. The protection and controls of the new equipment will be moved to the new Modular Protection Automation and Control (MPAC) building | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2026-02-02 | 49 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | 428 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5771880 | T.0000638 | Green Valley Substation Upgrade | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-09-23 | 2019-12-31 | 2019-12-20 | NA | NA | FALSE | 47000 | NA ¦ NA | 4379.949 | 4379.949 | 28.0383 | 3.9203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4379.949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 22.9785 | 3.2128 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
794 | GREEN VALLEY: Inst 115 KV SFCC PACI RAS |  |  | Interlaken CDP, Santa Cruz | This project will replace the existing 115 kV bus with five bays of breaker-and-a-half (BAAH) configuration. The new 115 kV BAAH bus will be located in the existing substation yard, which will require sequential construction of the new BAAH bays and removal of sections of the existing 115 kV bus. The protection and controls of the new equipment will be moved to the new Modular Protection Automation and Control (MPAC) building | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2026-02-02 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | 428 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767952 | T.0000638 | Green Valley Substation Upgrade | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-20 | 2019-12-31 | 2019-12-23 | NA | NA | FALSE | 47000 | NA ¦ NA | 385.4098 | 385.4098 | -16.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385.4098 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -16.0057 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
795 | GREEN VALLEY: Inst 115 KV VGCC PACI RAS |  |  | Interlaken CDP, Santa Cruz | This project will replace the existing 115 kV bus with five bays of breaker-and-a-half (BAAH) configuration. The new 115 kV BAAH bus will be located in the existing substation yard, which will require sequential construction of the new BAAH bays and removal of sections of the existing 115 kV bus. The protection and controls of the new equipment will be moved to the new Modular Protection Automation and Control (MPAC) building | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2026-02-02 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | 428 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767954 | T.0000638 | Green Valley Substation Upgrade | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-09-27 | 2019-12-31 | 2019-12-23 | NA | NA | FALSE | 47000 | NA ¦ NA | 718.8321 | 718.8321 | -16.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 718.8321 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -16.356 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
796 | GREEN VALLEY: Upgd 115 kV BUS BAAH PH 3 |  |  | Interlaken CDP, Santa Cruz | This project will replace the existing 115 kV bus with five bays of breaker-and-a-half (BAAH) configuration. The new 115 kV BAAH bus will be located in the existing substation yard, which will require sequential construction of the new BAAH bays and removal of sections of the existing 115 kV bus. The protection and controls of the new equipment will be moved to the new Modular Protection Automation and Control (MPAC) building | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2026-02-02 | 49 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | 428 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5771881 | T.0000638 | Green Valley Substation Upgrade | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-12-20 | 2019-12-31 | 2020-08-20 | Prioritization | NA | FALSE | 47000 | NA ¦ NA | 5582.8396 | 5582.8396 | 83.8647 | 994.8871 | 549.9734 | 47.5578 | 0 | 0 | 0 | 0 | 0 | 0 | 5582.8396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 81.1695 | 962.9159 | 532.2997 | 46.0296 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
797 | MONTA VISTA: Upgrade 230 kV Bus Phase 2 |  |  | Cupertino, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-03 | 21 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8314 | NA | 230 kV | 472 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5772060 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2018 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2021-08-17 | 2016-05-01 | 2028-05-30 | Prioritization | NA | FALSE | $10,000 ¦ $15,000 | NA ¦ NA | 32008.8337 | 50390.1645 | 7761.9947 | 6605.4205 | 2106.1482 | 4410.3476 | 7018.2452 | 7560.2037 | 100 | 0 | 0 | 0 | 31343.4904 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
798 | MONTA VISTA: Upgrade 230 kV Bus - Ph 1 |  |  | Cupertino, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-03 | 20 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8314 | NA | 230 kV | 472 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | Non-IGP | 5756027 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2016 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-06-18 | 2016-05-01 | 2019-02-19 | Prioritization | NA | FALSE | $10,000 ¦ $15,000 | NA ¦ NA | 14112.5022 | 14112.5022 | 35.9463 | 4.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14112.5022 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 35.8937 | 4.4565 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
799 | MONTEREY_INSTALL BUS AND BREAKERS P2 |  |  | Monterey, Monterey | The project scope of work includes following:60 kV bus•Remove existing 60kV bus in association with the bank replacement project •Install 60kV line breaker CB12, associated switch SW11, SW13 and bypass switch SW15. •Install 60kV line breaker CB32, associated switch SW31, SW33 and bypass switch SW35.•Install 3 – 1 phase 60kV line Potential Transformers (PTs) for 60kV Del Monte – Monterey line outside the disconnect SW13 towards the line side.•Install 3 – 1 phase 60kV line Potential Transformers (PTs) for 60kV Viejo – Monterey line outside the disconnect SW33 towards the line side.•Install one (1) 60kV bus sectionalizing breaker CB22, associated switch SW21, SW23, and bypass switch SW25.•Install one C phase bus PT in 60kV bus section D.•Install one C phase bus PT in 60kV bus section E.•Install the bus support insulators as needed for longer spans.•Install 2 x 1131 kcmil AL or equivalent conductor for 60kV incoming line, bus and 60kV station equipment connections. If required, one span of 3” AL SPS pipe will be installed from transformer circuit switcher to 60kV bus. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-03-04 | 78 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.29142 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5799060 | T.0000676 | MONTEREY Install 3-D-Banks & 60KV T BRKR | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2024-12-23 | 2020-12-15 | 2026-04-02 | Prioritization | NA | TRUE | 20200 | NA ¦ NA | 6009.1546 | 7212.5177 | 0 | 84.4498 | 22.015 | 2755.8302 | 2504.8193 | 1805.2649 | 40.1385 | 0 | 0 | 0 | 5367.1143 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $20 Mil - $30 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
800 | MONTEREY_REPLACE 60KV BUS AND CB12 |  |  | Monterey, Monterey | The project scope of work includes following:60 kV bus•Remove existing 60kV bus in association with the bank replacement project •Install 60kV line breaker CB12, associated switch SW11, SW13 and bypass switch SW15. •Install 60kV line breaker CB32, associated switch SW31, SW33 and bypass switch SW35.•Install 3 – 1 phase 60kV line Potential Transformers (PTs) for 60kV Del Monte – Monterey line outside the disconnect SW13 towards the line side.•Install 3 – 1 phase 60kV line Potential Transformers (PTs) for 60kV Viejo – Monterey line outside the disconnect SW33 towards the line side.•Install one (1) 60kV bus sectionalizing breaker CB22, associated switch SW21, SW23, and bypass switch SW25.•Install one C phase bus PT in 60kV bus section D.•Install one C phase bus PT in 60kV bus section E.•Install the bus support insulators as needed for longer spans.•Install 2 x 1131 kcmil AL or equivalent conductor for 60kV incoming line, bus and 60kV station equipment connections. If required, one span of 3” AL SPS pipe will be installed from transformer circuit switcher to 60kV bus. | Substation - Multiple | Upgrade/Retrofit | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-03-04 | 77 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.29142 | NA | 60 kV | NA | 6. Customer commitments | 17 | NA | NA | 5787939 | T.0000676 | MONTEREY Install 3-D-Banks & 60KV T BRKR | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-14 | 2020-12-15 | 2022-04-28 | Prioritization | NA | FALSE | 20200 | NA ¦ NA | 192.3473 | 192.3473 | 78.6391 | 87.0836 | 9.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192.3473 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 183.1192 | 9.228 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $20 Mil - $30 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
801 | Trinity: Inst Relays for Cottonwood |  |  | Weaverville CDP, Trinity | Project scope is to replace both 230/115kV transmission transformers which will address the 115kV high voltage issue and improve reliability of the North Valley transmission system. Installing the 115kV bus tie breakers will address NERC category P2 breaker fault of Cottonwood CB 102 or, a NERC category P4 nearby fault plus a CB 102 fault. The CAISO approved shunt reactors/transformer replacement to mitigate the high voltage issue and additionally the 115kV bus tie breakers to mitigate the P2 and P4 contingencies. The MPAC and breakers replacement will replace the deteriorated asset and capture the efficiency of upgrading protection and controls, avoid rework and multiple clearances. The high-level scope includes the following: • Replace the existing Banks 1 and 4 with 230/115kV 420MVA, with LTC and associated bus selector switches. • Install new bay and new 230kV breaker to connect new Bank 1 to 230kV bus. • Replace Bank 1 low-side breaker CB 172 and the associated switches. • Replace Bank 4 low-side CB 192 and the associated switches. • Expand existing 115kV MPAC to accommodate protection and controls. • Expand SPCC to accommodate increased oil quantity of new banks. • Install new sectionalizing CB’s 912 and 922 w/switches to sectionalize 115kV bus to Sections D and E. • Install new CB 132 with switches and relocate Trinity-Cottonwood 115kV line to Bus Section E. • Install new bus paralleling breaker CB 102 with switches in Bus Section E. • Install new bus paralleling breaker CB 902 with switches in Bus Section D. • Replace the existing OCBs 142 and 152 with non-SF6 breakers and the associated switches. • Replace six of the existing 230kV OCBs (CBs 222, 232, 272, 292, 522, and 542) with new 230kV 2000A gas circuit breakers, and the associated breaker and bus selector switches. • Install new 230kV 2000A bus paralleling breaker (CB 502) and associated switches in place of the existing Transformer 1 CB 512 position. • Replace switches 213, 357, 359, 367, and 369. • Install new MPAC Building to house the protection, automation, and control equipment for the 230kV Bus Sections “E” and “F”. | Substation - Protection Relay | New | NA | T.0004659 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-05 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 1.3227 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5787300 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2019 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-10-12 | 2028-04-30 | 2027-05-03 | NA | NA | TRUE | 51200 | NA ¦ NA | 260.6306 | 924.1656 | 3.5073 | 13.9738 | 28.1623 | 30.5328 | 139.7628 | 58.1137 | 598.2746 | 0 | 0 | 0 | 248.493 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
802 | Cottonwood:Inst 115kV Bus Sectionalizing |  |  | Cottonwood CDP, Shasta | Project scope is to replace both 230/115kV transmission transformers which will address the 115kV high voltage issue and improve reliability of the North Valley transmission system. Installing the 115kV bus tie breakers will address NERC category P2 breaker fault of Cottonwood CB 102 or, a NERC category P4 nearby fault plus a CB 102 fault. The CAISO approved shunt reactors/transformer replacement to mitigate the high voltage issue and additionally the 115kV bus tie breakers to mitigate the P2 and P4 contingencies. The MPAC and breakers replacement will replace the deteriorated asset and capture the efficiency of upgrading protection and controls, avoid rework and multiple clearances. The high-level scope includes the following: • Replace the existing Banks 1 and 4 with 230/115kV 420MVA, with LTC and associated bus selector switches. • Install new bay and new 230kV breaker to connect new Bank 1 to 230kV bus. • Replace Bank 1 low-side breaker CB 172 and the associated switches. • Replace Bank 4 low-side CB 192 and the associated switches. • Expand existing 115kV MPAC to accommodate protection and controls. • Expand SPCC to accommodate increased oil quantity of new banks. • Install new sectionalizing CB’s 912 and 922 w/switches to sectionalize 115kV bus to Sections D and E. • Install new CB 132 with switches and relocate Trinity-Cottonwood 115kV line to Bus Section E. • Install new bus paralleling breaker CB 102 with switches in Bus Section E. • Install new bus paralleling breaker CB 902 with switches in Bus Section D. • Replace the existing OCBs 142 and 152 with non-SF6 breakers and the associated switches. • Replace six of the existing 230kV OCBs (CBs 222, 232, 272, 292, 522, and 542) with new 230kV 2000A gas circuit breakers, and the associated breaker and bus selector switches. • Install new 230kV 2000A bus paralleling breaker (CB 502) and associated switches in place of the existing Transformer 1 CB 512 position. • Replace switches 213, 357, 359, 367, and 369. • Install new MPAC Building to house the protection, automation, and control equipment for the 230kV Bus Sections “E” and “F”. | Substation - Bus Arrangement | New | NA | T.0004659 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-19 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 26.1945 | NA | 115 kV | 1002 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5786464 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-04-01 | 2022-12-31 | 2028-10-10 | Prioritization | NA | FALSE | $8,500 ¦ $10,500 | NA ¦ NA | 1048.2653 | 6283.5728 | 30.2892 | 46.9034 | 92.9801 | 83.2805 | 693.5833 | 3016.9946 | 0 | 0 | 0 | 0 | 1026.407 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
803 | ORO LOMA: 115KV BAAH |  |  | Fresno | This project proposes to install a new 115 kilovolt (kV) BAAH bus at Oro Loma Substation. Completion of this project would increase reliability for the electric customers in Merced County and modernize the Oro Loma 115 kV bus for future expansion of the substation. This work is being done in conjunction with a Modular Protection Automation and Control (MPAC) installation project which will install a new MPAC building for the 115 kV protection and control equipment. | Substation - Bus Arrangement | New | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-02-10 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.8637 | NA | 115 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5769442 | T.0001473 | ORO LOMA BANK NO. 3 INSTALL PHASE | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-07-16 | 2019-07-10 | 2019-11-13 | NA | NA | FALSE | 5792 | NA ¦ NA | 7373.1658 | 7373.1658 | 19.7832 | 0.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7373.1658 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 16.8146 | 0.46496 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
804 | MARKHAM: Upgrade Relay |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0000147 | Reliability | Substation Reliability | NA | NA | 2026-02-05 | 29 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.3776 | NA | 115 kV | 579 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5776840 | T.0001685 | Evergreen Substation Upgrade | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2023-02-21 | 2018-12-20 | 2026-05-28 | Prioritization | NA | TRUE | 27200 | NA ¦ NA | 1264.5336 | 1329.4036 | 177.1129 | 144.4782 | 324.2052 | 136.8148 | 212.2531 | 94.0688 | 0 | 0 | 0 | 0 | 1235.3348 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
805 | EVERGREEN: Upgrade 115 KV Bus |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2026-02-05 | 33 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.3776 | NA | 115 kV | 179 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | Non-IGP | 5770124 | T.0001685 | Evergreen Substation Upgrade | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-06-25 | 2018-12-20 | 2023-06-02 | Prioritization | NA | FALSE | 27200 | NA ¦ NA | 31190.4094 | 31190.4094 | 8846.6389 | 9642.4386 | -2225.7581 | -202.6065 | 0 | 0 | 0 | 0 | 0 | 0 | 31190.4094 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 28589.8019 | -182.3459 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
806 | STONE: Upgrade Relay |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2026-02-06 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.68753 | NA | 115 kV | 579 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5770126 | T.0001685 | Evergreen Substation Upgrade | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-01 | 2018-12-20 | 2025-07-14 | Prioritization | NA | TRUE | 27200 | NA ¦ NA | 4288.4706 | 4343.5612 | 1231.0386 | 628.9345 | 647.9566 | 276.2694 | 615.6331 | 60.1376 | 0 | 0 | 0 | 0 | 4283.4235 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 4059.6942 | 4.7105 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
807 | SAN JOSE B: Upgrade Relay |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0011286 | Reliability | Substation Reliability | NA | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.1017 | NA | 115 kV | 579 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5770127 | T.0001685 | Evergreen Substation Upgrade | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-09-01 | 2018-12-20 | 2025-07-14 | Prioritization | NA | TRUE | 27200 | NA ¦ NA | 2428.6613 | 2472.6978 | 406.3647 | 235.0162 | 143.3442 | 137.5922 | 836.7459 | 92.1181 | 0 | 0 | 0 | 0 | 2380.5797 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 2255.1686 | 44.9706 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
808 | Evergreen Sub: Install 115kV Phase 2 |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0000147 | Reliability | Bus Upgrade | NA | NA | 2026-02-05 | 34 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.3776 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5805220 | T.0001685 | Evergreen Substation Upgrade | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-02-01 | 2018-12-20 | 2025-12-23 | Prioritization | NA | TRUE | 27200 | NA ¦ NA | 8878.2466 | 9317.4813 | 0 | 0 | 5680.6034 | 264.9948 | 2750.3953 | 610.0584 | 0 | 0 | 0 | 0 | 8695.9935 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 7968.5747 | 164.0278 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
809 | Legrand Substation Bus Upgrade |  |  | Merced | This project proposes to reconductor approximately 14 miles of the Wilson -LeGrand 115kV Line with 477 ACSS conductor or equivalent and replaces 146 wood poles with new light duty steel poles (LDSP). This project was recommended by the CAISO as a policy driven upgrade.. Completion of this project will provide additional transmission capacity to serve over 30,000 electric customers in Merced County. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Policy | Line Termination | NERC TPL Standards | NA | 2026-02-17 | 62 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.8754 | NA | 115 kV | NA | NA | NA | NA | NA | 5799444 | T.0002231 | Wilson-LeGrand | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2021 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5293-E | 2018-05-15 | Approved | 2018 | Operational | 1 | 2023-11-29 | 2020-12-31 | 2023-12-18 | Prioritization | NA | FALSE | 15000 | NA ¦ NA | 686.3803 | 686.3803 | 10.3989 | 189.1961 | 258.2828 | 228.5026 | 0 | 0 | 0 | 0 | 0 | 0 | 686.3803 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 413.1207 | 204.7278 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
810 | EMBARCADERO-POTRERO: Upgd SF RAS B at VG |  |  | San Francisco, San Francisco | The project will involve the construction of a new 230 kV underground transmission line between Embarcadero and Potrero Power Plant (P.P.) Substations, construction of a new 230 kV switchyard at Potrero, the installation of new 230/115 kV transformers at Potrero, and the interconnection of the Project into the Embarcadero 230 kV bus and Potrero P.P. 115 kV buses. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Reliability | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-21 | 23 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.55624 | NA | 230 kV | 564 | 8. Compliance/Commitments With Low Safety Risk | 9 | NA | NA | 5778325 | T.0003672 | NEW 230 KV SWITCHYARD AT POTRERO | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2012 | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-07-25 | 2015-12-31 | 2021-12-08 | Workforce | NA | FALSE | $130,000 ¦ $150,000 | NA ¦ NA | 2126.7081 | 2126.7081 | 321.0433 | 93.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2126.7081 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 2033.3421 | 93.709 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
811 | EMBARCADERO-POTRERO: Upgd SF RAS A at SF |  |  | San Francisco, San Francisco | The project will involve the construction of a new 230 kV underground transmission line between Embarcadero and Potrero Power Plant (P.P.) Substations, construction of a new 230 kV switchyard at Potrero, the installation of new 230/115 kV transformers at Potrero, and the interconnection of the Project into the Embarcadero 230 kV bus and Potrero P.P. 115 kV buses. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Reliability | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-21 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.55624 | NA | 230 kV | 564 | 8. Compliance/Commitments With Low Safety Risk | 9 | NA | NA | 5778434 | T.0003672 | NEW 230 KV SWITCHYARD AT POTRERO | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2012 | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2014-09-02 | 2015-12-31 | 2021-12-08 | Workforce | NA | FALSE | $130,000 ¦ $150,000 | NA ¦ NA | 2014.9352 | 2014.9352 | 341.757 | 10.3397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014.9352 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 2006.0985 | 10.3397 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
812 | Calflax: Add Bank 2 - Ring Bus |  |  | Fresno | This project proposes to install a new 70/12 kV 30 MVA transformer bank at Calflax Substation in order to prevent projected substantial overloads on Coalinga #2 Bank 1. To support the additional transformer bank at Calflax the existing 70 kV transmission tap that serves Calflax Bank 1 will be reconfigured into a four-element ring bus. In addition to the new transformer bank at Calflax Substation one new 12 kV circuit breaker and associated distribution work will be installed to serve the proposed additional 10 MW Tesla EV charging infrastructure load at Harris Ranch. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.68286 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5795019 | T.0003879 | Calflax Substation Bank 2 Installation | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-15 | 2023-02-08 | 2024-01-05 | Prioritization | NA | TRUE | 19400 | NA ¦ NA | 8145.8087 | 8155.4351 | 2102.5042 | 2649.9927 | 1963.3726 | 651.3023 | 778.6369 | 9.6263 | 0 | 0 | 0 | 0 | 8145.8087 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 7239.4276 | 763.7132 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
813 | Wilson 230 kV BAAH |  |  | Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0001381 ¦ T.0002231 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-04 | 71 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 22.8151 | NA | 230 kV | 58 | 8. Compliance/Commitments With Low Safety Risk | 7 | 5.1001 | Non-IGP | 5783618 | T.0004116 | WILSON: 115 kV ARP - BAAH | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2018 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-01-20 | 2015-05-01 | 2029-12-21 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 277.3368 | 38190.662 | 2.6271 | 0 | 0 | 0 | 102.6666 | 982.0334 | 2500 | 20500 | 2500 | 2500 | 253.2172 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
814 | WILSON: Reconfigure Bus to 115 KV BAAH |  |  | Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0001381 ¦ T.0002231 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-04 | 19 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 22.8151 | NA | 115 kV | 58 | 8. Compliance/Commitments With Low Safety Risk | 7 | 5.1001 | Non-IGP | 5781259 | T.0004116 | WILSON: 115 kV ARP - BAAH | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-04-25 | 2015-05-01 | 2028-12-26 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 1752.3855 | 103712.3382 | 18.8656 | 0 | 0 | 161.0489 | 537.2665 | 986.6973 | 19400 | 28800 | 19400 | 19400 | 1676.5764 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
815 | MORGAN HILL SUB: 115kV BAAH CONVERSION |  |  | Morgan Hill, Santa Clara | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | 5792891 ¦ T.0011276 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-02-04 | 18 | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.8017 | NA | 115 kV | 2135 | 8. Compliance/Commitments With Low Safety Risk | 50 | 5.1001 | Non-IGP | 5782117 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2019 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-06-15 | 2021-12-01 | 2028-05-30 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 7031.6757 | 79539.5825 | 7868.2695 | 995.6401 | 85.1211 | 2236.8434 | -8321.5861 | 3547.3903 | 35573.3233 | 4545.0005 | 906.0006 | 0 | 6844.4001 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
816 | GREEN VALLEY SUB: 115kV PROTECTION MODS |  |  | Interlaken CDP, Santa Cruz | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Substation - Protection Relay | Upgrade/Retrofit | NA | 5792891 | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-02-02 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 6.6121 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 50 | 5.1001 | Non-IGP | 5782114 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2020 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-03-01 | 2021-12-01 | 2028-05-30 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 57.319 | 1985.9412 | -0.8284 | 8.8608 | 0.3156 | 23.0578 | 7.2698 | 299.1514 | 160 | 611.0005 | 0 | 0 | 56.6002 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
817 | METCALF SUB: 115kV PROTECTION MODS |  |  | Santa Clara | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Substation - Protection Relay | Upgrade/Retrofit | NA | 5792891 | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 50 | 5.1001 | Non-IGP | 5782115 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2018 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-03-01 | 2021-12-01 | 2028-05-30 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 36.3719 | 2114.8816 | 0.5343 | 0.5785 | 0 | 22.6549 | 4.7288 | 343.9337 | 160 | 607.0003 | 0 | 0 | 35.9158 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
818 | LLAGAS SUB: 115kV PROTECTION MODS |  |  | Gilroy, Santa Clara | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Substation - Protection Relay | Upgrade/Retrofit | NA | 5792891 | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3037 | NA | 115 kV | NA | 8. Compliance/Commitments With Low Safety Risk | 50 | 5.1001 | Non-IGP | 5786319 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2019 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-03-01 | 2021-12-01 | 2028-05-30 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 75.5194 | 2008.0362 | 3.2671 | 11.0913 | 0.7227 | 13.2357 | 8.3984 | 311.9401 | 173.0004 | 690.0005 | 0 | 0 | 74.5723 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
819 | EM: KPP 70KV BUS LIMITING ELEMENT REPL |  |  | Bakersfield, Kern | Project will replace existing 70kV bus and conductors for the Bus Tie Circuit Breaker 62 to increase ampacity. Kern Power Plant consists of a 230kV, 115kV, 70kV, and 21kV yards. The 70kV bus at Kern PP is a double bus single breaker (DBSB) configuration with one bus tie breaker. HVCB 62 is a parallel breaker that could be used as a substitute breaker to do maintenance on other line breakers. However, due to HVCB 62 connections being rated close to 1200A, these connections are limiting use of HVCB 62 as substitute breaker. Installed conductors and SPS tubing does not meet required ampacity for 70kV voltage rating and is required to be replaced to avoid having a limiting element for operating purposes. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NA | NA | 2026-03-04 | 74 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 37.7504 | NA | 70 kV | NA | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5535602 | T.0004730 | KERN PP: 70KV BUS LIMITING ELEMENT REPL | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-08-12 | 2026-12-31 | 2027-10-12 | Clearances | NA | TRUE | 1984 | NA ¦ NA | 661.7836 | 1431.769 | 8.433 | 39.7789 | 23.2769 | 111.685 | 234.3836 | 29.9291 | 769.663 | 0 | 0 | 0 | 631.8545 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | -5.8622 | 37.2259 | 21.7828 | 104.5168 | 219.3404 | 28.0082 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
820 | JEFFERSON REMOTE END MARTINSUB |  |  | Brisbane, San Mateo | Extend the 230 kV bus at Jefferson substation and convert its configuration to Breaker and a Half. This project will allow for the interconnection of more bus elements. | Other - Operations Tech | New | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811101 | T.0004805 | Jefferson: 230 Kv Bus Upgrade | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-11-04 | 2022-12-31 | 2028-09-07 | Prioritization | NA | FALSE | $6,000 ¦ $11,000 | NA ¦ NA | 185.6842 | 4567.5718 | 0 | 0 | 0 | 18.066 | 117.11 | 1637.6476 | 0 | 0 | 0 | 0 | 135.176 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
821 | JEFFERSON 230 KV BUS UPGRADE |  |  | San Mateo | Extend the 230 kV bus at Jefferson substation and convert its configuration to Breaker and a Half. This project will allow for the interconnection of more bus elements. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-03 | 20 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.7091 | NA | 230 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 4 | 5.1001 | Non-IGP | 5785789 | T.0004805 | Jefferson: 230 Kv Bus Upgrade | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-12-16 | 2022-12-31 | 2028-09-08 | Prioritization | NA | FALSE | $6,000 ¦ $11,000 | NA ¦ NA | 427.189 | 6560.524 | 0 | 0 | 0 | 114.8687 | 288.6898 | 812.7534 | 1315.298 | 3416.299 | 9.358 | 0 | 403.5584 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
822 | Willow Pass Contra Costa Remote End |  |  | Antioch, Contra Costa | This project will provide the capacity increase required to meet the new business loads coming into the area. The project scope will: • Reconfigure the 115 kV high side bus to a ring bus. • Replace Bank 1 with a 115/21 kV 75 MVA transformer. • Relocate existing Bank 3, 115/21 kV 30 MVA transformer to a new foundation compatible with 75 MVA bank for future upgrades. • Install three 21 kV feeders. • Install two 21/12 kV, 7500 kVA auto banks. • Reconfigure the existing BART Bank on the new 115 kV ring bus at Willow Pass substation. • Install Supervisory Control and Data Acquisition system for the new substation bank and breakers. • Install one new 60 kV transmission switch to interconnect structure 000/006 on Willow Pass-Contra Costa 60 kV and structure 015/281 on Christie-Willow Pass 60 kV at the corner of Willow Pass Road and Port Chicago Highway. • Remove sections of Willow Pass-Contra Costa 60 kV and Christie-Willow Pass 60 kV from the structures towards Willow Pass substation. • Install a new Microwave system from Willow Pass to Pittsburg to comply with redundancy requirements for the Set A and Set B protection relays. Execution of this project will improve the future capacity expansion, operational flexibility, and reliability of the Willow Pass substation. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Load Growth | Substation Capacity | NA | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 15.1779 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561181 | T.0005844 | Willow Pass Sub_Repl Willow Pass Bk1 | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2026-02-11 | 2025-07-31 | 2026-03-11 | Scope Change | NA | TRUE | 42500 | NA ¦ NA | 134.7087 | 185.5058 | 0 | 0 | 0 | 0 | 51.2098 | 128.3999 | 5.8961 | 0 | 0 | 0 | 51.2098 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 51.2098 | 83.4989 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
823 | SAN MIGUEL SUB EXPANSION & 70KV RINGBUS |  |  | San Miguel CDP, San Luis Obispo | This project proposes to install a second transformer bank at San Miguel Substation to eliminate a forecasted 16 percent overload of San Miguel Transformer Bank 1, a 4 percent overload of the San Miguel 1104 distribution feeder, and a 13 percent overload of the Paso Robles 1107 distribution feeder. These overloads are forecasted to occur under normal conditions (N-0) during the summer months of 2024 and cannot be alleviated by load transfer because of depleted area capacity. Transmission Substation Work (MWC 61): • Expand the yard at San Miguel Substation for an ultimate 70kV six-breaker ring bus to accommodate a third distribution transformer, future 70kV transmission VAR support, and two 70kV line positions. • Modify the San Miguel 70kV bus and 70kV equipment to accommodate a second transformer . • The MWC 61 project will partially fund the yard expansion and creation of an Ultimate General Arrangement Outdoors Plan. | Substation - Bus Arrangement | New | NA | T.0000154 | Load Growth | Bus Upgrade | NA | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.77704 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5798129 | T.0006955 | San Miguel Install Bank 3 | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-02-11 | 2026-06-01 | 2025-12-14 | NA | NA | TRUE | 34300 | NA ¦ NA | 8453.5791 | 8527.5003 | 0 | 186.4175 | 150.8462 | 1734.6064 | 6176.5908 | 279.0393 | 0 | 0 | 0 | 0 | 8248.461 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 8011.8392 | 198.9201 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
824 | BANTA: INSTALL 115KV RING BUS |  |  | San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Substation - Bus Arrangement | New | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.54319 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5798130 | T.0006962 | Banta: Repl Bk 1 & Inst 115kV Ring Bus | 8 | 61 | NA ¦ EX113229 ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2022 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-09-11 | 2024-12-31 | 2027-12-01 | Prioritization | NA | TRUE | 17500 | NA ¦ NA | 1132.2813 | 14048.641 | 0 | 0 | 72.138 | 721.1449 | 301.1174 | 3136.1538 | 8791.3861 | 1100 | 0 | 0 | 1094.4004 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
825 | San Bernard Substation Install Bank 2 |  |  | Kern | This project proposes to install a second transformer bank at San Bernard Substation to eliminate a forecasted 9 percent normal overload of Arvin Transformer Bank 1 and a forecasted 10 percent normal overload of San Bernard Transformer Bank 1. These deficiencies are being caused by a sharp increase in water storage operations by the Arvin Edison Water Storage District that began in 2020. Although reduced by available load transfers, the overloads are expected to continue over the next two summers until capacity can be added in 2023. The installation of San Bernard Bank 2 will provide maximum load relief for San Bernard Bank 1, which is in very poor condition and recommended for replacement Transmission Substation Work (MWC 61): • Modify the San Bernard 70kV bus and 70kV equipment to accommodate a second transformer. | Substation - Structure | New | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | Wires - Location/Route Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.86468 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5798622 | T.0007229 | San Bernard Substation Install Bank 2 | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-02-20 | 2025-06-30 | 2025-05-02 | NA | NA | TRUE | 18300 | NA ¦ NA | 4281.8695 | 4298.5499 | 0 | 207.8821 | 1005.181 | 1614.0267 | 1445.1595 | 26.3005 | 0 | 0 | 0 | 0 | 4272.2493 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 4194.6845 | 9.4327 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
826 | FULTON BANK 5 TRANSMISSION WORK |  |  | Fulton CDP, Sonoma | Replace Fulton Bank 5 with a 3-phase 60MVA or 45 MVA 230/12 kV, LTC transformer (note that existing Bank 5 switchgear is limited to 4 breakers and 48 MVA of load). Recent new business applications of 16.3 MW will overload Fulton Bank 5 & Bank 6, Fulton 1101, Fulton 1105, and Fulton 1107. With these overloads and Fulton 1102 operating near full capacity, operational flexibility will be severely impacted. The end of line voltage on Fulton 1105 is expected to be 109.5V. This low voltage is exacerbated because a significant portion of the new business loads are located at the end of the line, 3 miles from the substation near the Sonoma County Airport. | Substation - Circuit Breaker | New | NA | NA | Load Growth | Substation Capacity | NA | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.4076 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5809042 | T.0007811 | Fulton Bank 5 Replacement | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-08-28 | 2028-01-13 | 2030-09-11 | Scope Change | NA | FALSE | 13000 | NA ¦ NA | 36.2416 | 11182.8942 | 0 | 0 | 0 | 1.5013 | 31.9782 | 110.4884 | 1954 | 25 | 0 | 0 | 33.4794 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
827 | HARDING: INST 60kV CB 32 |  |  | Stockton, San Joaquin | This project proposes to replace Bank 1 with a 16 MVA 60/12x4 kV dual winding transformer, enhance the ground grid, implement a Shakespeare Wall, install neutral reactors, deploy a 12 kV Shelter Aisle Switchgear, and complete necessary civil construction for the project. | Substation - Circuit Breaker | New | NA | NA | Load Growth | Substation Capacity | NA | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.14046 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811722 | T.0007980 | HARDING: REBUILD SUBSTATION | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-08-14 | 2028-02-29 | 2027-03-04 | NA | NA | TRUE | 35600 | NA ¦ NA | 498.9386 | 1836.4437 | 0 | 0 | 0 | 3.5293 | 474.3822 | 980.9135 | 348.3778 | 4.2359 | 0 | 0 | 477.9115 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
828 | Wheeler Ridge Sub: Install BAAH bay |  |  | Kern | This project proposes to install one new 230 kV breaker-and-a-half (BAAH) bay with two new 230 kV breakers, one 230/21 kV, 75 MVA three-phase transformer, one 21/12 kV 30 MVA autotransformer, one 2,000 ampere (A) rated 21 kV bus 1/bus 2 structure with six breaker bays, three 1,200 A 21 kV feeder breakers, one 2,000 A 21 kV bus tie breaker, three 21 kV distribution feeder outlets, and three new 21 kV underground distribution circuits from the substation to the customer site.This project will allow 50 MW of new electric vehicle (EV) charging load from Tesla Motors Company (Tesla) and future load from other EV customers to connect to the PG&E system. Transmission Substation Work (MWC 61): • Install one 230 kV BAAH bay • Install two 230 kV breakers in new BAAH bay • Extend 230 kV line north from new BAAH bay in 230 kV yard to location of new 230/21 kV transformer • Potential rearrangement of Wheeler Ridge-Adobe Switching Station 115 kV and Wheeler Ridge-San Bernard 70 kV lines within substation | Substation - Bus Arrangement | New | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5800046 | T.0008068 | Wheeler Ridge Sub: Install 21 kV bank | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-07-19 | NA | 2028-06-30 | NA | NA | FALSE | NA | NA ¦ NA | 2063.309 | 7208.0715 | 0 | 55.1259 | 13.7799 | 65.7444 | 1534.862 | 2003.5594 | 1929 | 1138 | 468 | 0 | 1669.5121 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
829 | Panoche Sub: Install 230 kV breaker |  |  | Fresno | This project proposes to install one new 230 kV breaker, one 230/21 kV, 75 MVA three-phase transformer, one 21/12 kV, 30 MVA autotransformer, one new 2000 Ampere-rated 21 kV bus 1/bus 2 structure with six breaker bays, three feeder breakers and one bus tie breaker, three new 21 kV distribution feeder outlets, and three new 21 kV underground distribution circuits from the substation to the customer site. This project will allow 45 MW of new Electric Vehicle (EV) charging load from Tesla and future load from other EV customers to connect to the PG&E system. Transmission Substation Work (MWC 61): Note that Panoche 230 kV has ten 230 kV lines and three substation transformers. Per Standard 073131, if this substation were rebuilt, the desired 230 kV bus configuration would be Breaker-and-a-Half (BAAH). Conversion of Panoche Substation to BAAH is not expected at this time and an extension of the existing Bus 1/Bus 2 arrangement is assumed. • Extend existing 230 kV Bus 1/Bus 2 to accommodate one 230 kV double-bus bay • Install one 230 kV breaker in new bay • Extend 230 kV line south from new breaker in 230 kV yard to distribution substation portion of yard | Substation - Bus Arrangement | New | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5800044 | T.0008070 | Panoche Sub: Install 12 kV bank | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2024-12-09 | 2026-04-30 | 2026-12-22 | Material | NA | TRUE | 44900 | NA ¦ NA | 8538.616 | 10059.12 | 0 | 50.4276 | 195.4706 | 1183.5391 | 6683.7232 | 1739.4054 | 206.554 | 0 | 0 | 0 | 8113.1605 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
830 | Manning: Panoche Sub Replace CB 102, 132 |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | T.0009550 | Policy | Bus Upgrade | NERC TPL Standards | NA | 2026-03-03 | 24 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5808684 | T.0009194 | Manning New 500kV Sub Connection | 18 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2023 | TRUE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-01-08 | 2028-01-01 | 2028-04-28 | NA | NA | FALSE | 184000 | NA ¦ NA | 218.9128 | 6226.859 | 0 | 0 | 0 | 29.2655 | 144.6092 | 2328.2623 | 3283.0902 | 441.6318 | 0 | 0 | 173.8746 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 29.2655 | 173.8747 | 218.9128 | 0% ¦ LS Power, New Manning 500 kV substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive and Construction Work in Progress Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
831 | Los Banos: 500kV Path Rating Upgrade |  |  | Merced | Upgrade substation terminals at Gates, Los Banos, and Midway for 500 kV Path 15 and Midway for 500 kV Path 26 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Capacity | NERC TPL Standards | NA | 2026-03-06 | 64 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 500 kV | NA | NA | NA | 5.1001 | NA | 5805119 | T.0009205 | Gates Los Banos Midway Path Rating Upg | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-03-01 | 2024-05-31 | 2024-05-03 | NA | NA | FALSE | 2100 | NA ¦ NA | 328.1858 | 328.1858 | 0 | 0 | 119.0827 | 209.1031 | 0 | 0 | 0 | 0 | 0 | 0 | 328.1858 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 328.1858 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
832 | Midway: 500kV Path Rating Upgrade |  |  | Buttonwillow CDP, Kern | Upgrade substation terminals at Gates, Los Banos, and Midway for 500 kV Path 15 and Midway for 500 kV Path 26 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Capacity | NERC TPL Standards | NA | 2026-03-03 | 64 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 500 kV | NA | NA | NA | 5.1001 | NA | 5805120 | T.0009205 | Gates Los Banos Midway Path Rating Upg | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-04-01 | 2024-05-31 | 2024-05-17 | NA | NA | FALSE | 2100 | NA ¦ NA | 1021.602 | 1021.602 | 0 | 0 | 128.5406 | 893.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.602 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 1021.602 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
833 | Gates: 500kV Path Rating Upgrade |  |  | Fresno | Upgrade substation terminals at Gates, Los Banos, and Midway for 500 kV Path 15 and Midway for 500 kV Path 26 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Capacity | NERC TPL Standards | NA | 2026-03-12 | 64 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | NA | NA | NA | 5.1001 | NA | 5805118 | T.0009205 | Gates Los Banos Midway Path Rating Upg | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-05-07 | 2024-05-31 | 2024-06-01 | NA | NA | FALSE | 2088.777 | NA ¦ NA | 1473.6052 | 1473.6052 | 0 | 0 | 149.2278 | 1324.3774 | 0 | 0 | 0 | 0 | 0 | 0 | 1473.6052 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1473.6052 | -1e-05 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
834 | Round Mountain:500kV Path Rating Upgrade |  |  | Round Mountain CDP, Shasta | Upgrade substation terminals at Round Mountain, Table Mountain, and Vaca-Dixon for 500 kV Path 66 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NA | NA | 2026-03-09 | 58 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | 29.1389 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5805121 | T.0009211 | ROUND TABLE VACA MOUNTAIN 500KV PATH RAT | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-02-27 | 2024-05-31 | 2024-05-20 | NA | NA | TRUE | 5165 | NA ¦ NA | 2002.6249 | 2002.6249 | 0 | 0 | 127.2214 | 1058.5743 | 807.7578 | 9.0714 | 0 | 0 | 0 | 0 | 1993.5535 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1185.7957 | 807.7578 | 9.0714 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
835 | Table Mountain:500kV Path Rating Upgrade |  |  | Butte | Upgrade substation terminals at Round Mountain, Table Mountain, and Vaca-Dixon for 500 kV Path 66 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NA | NA | 2026-03-20 | 58 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Subsidence |  | NA | 47.516 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5805122 | T.0009211 | ROUND TABLE VACA MOUNTAIN 500KV PATH RAT | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-03-05 | 2024-05-31 | 2024-06-18 | NA | NA | FALSE | 5165 | NA ¦ NA | 1439.1886 | 1439.1886 | 0 | 0 | 103.1011 | 1292.7173 | 43.3702 | 0 | 0 | 0 | 0 | 0 | 1439.1886 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1395.8184 | 43.3702 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
836 | Vaca Dixonn: 500kV Path Rating Upgrade |  |  | Solano | Upgrade substation terminals at Round Mountain, Table Mountain, and Vaca-Dixon for 500 kV Path 66 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NA | NA | 2026-03-25 | 61 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5805123 | T.0009211 | ROUND TABLE VACA MOUNTAIN 500KV PATH RAT | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-03-18 | 2024-05-31 | 2024-06-18 | NA | NA | FALSE | 5165 | NA ¦ NA | 1587.1066 | 1587.1066 | 0 | 0 | 82.3829 | 1465.0891 | 39.6346 | 0 | 0 | 0 | 0 | 0 | 1587.1066 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1547.472 | 39.6346 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
837 | TESLA_RECONFIGURE 115 KV BUS |  |  | Alameda | This project will convert the Tesla 115kV bus from DBSB to BAAH. Below is the high-level scope of this project: 1. Install five bays of folded bus design BAAH bays to connect the existing elements 2. Install new MPAC building with protection and controls 3. Upgrade ground grid as needed The project will mitigate the system collapse issue due to the NERC Category P2-4 contingency. Even though load shedding is allowed under P2-4 contingency, the alternative of using RAS to shed load is not recommended due to loss of large amount of loads (about 300 MW in the 2032 study case), complexity of the RAS design and high requirement on the RAS reaction time. As a result, converting the Tesla 115 kV bus from DBSB to BAAH is recommended as shown in Figure 2. With the BAAH configuration, only two elements would be tripped when there is fault on the bay middle breaker, and there is no system collapse issue post any of the middle breaker faults. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0007754 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-19 | 51 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Heat Wave |  | NA | 69.382 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806787 | T.0009526 | Tesla_Reconfigure 115 kV bus | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-02-17 | 2030-12-31 | 2028-09-21 | NA | NA | FALSE | 55000 | NA ¦ NA | 351.2779 | 30077.2191 | 0 | 0 | 1.0183 | 0.9376 | 248.0672 | 2327.1961 | 5000 | 12000 | 10000 | 500 | 250.023 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
838 | Patterson: Upgrade Tesla Remote End |  |  | San Joaquin | This project will convert the Tesla 115kV bus from DBSB to BAAH. Below is the high-level scope of this project: 1. Install five bays of folded bus design BAAH bays to connect the existing elements 2. Install new MPAC building with protection and controls 3. Upgrade ground grid as needed The project will mitigate the system collapse issue due to the NERC Category P2-4 contingency. Even though load shedding is allowed under P2-4 contingency, the alternative of using RAS to shed load is not recommended due to loss of large amount of loads (about 300 MW in the 2032 study case), complexity of the RAS design and high requirement on the RAS reaction time. As a result, converting the Tesla 115 kV bus from DBSB to BAAH is recommended as shown in Figure 2. With the BAAH configuration, only two elements would be tripped when there is fault on the bay middle breaker, and there is no system collapse issue post any of the middle breaker faults. | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0007754 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-02-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.2961 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5563800 | T.0009526 | Tesla_Reconfigure 115 kV bus | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-01-26 | 2030-12-31 | 2028-08-29 | NA | NA | FALSE | 55000 | NA ¦ NA | 9.7135 | 6518.2303 | 0 | 0 | 0 | 0 | 4.5273 | 971.2961 | 0 | 0 | 0 | 0 | 4.5273 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
839 | Salado: Upgrade Tesla Remote End |  |  | Stanislaus | This project will convert the Tesla 115kV bus from DBSB to BAAH. Below is the high-level scope of this project: 1. Install five bays of folded bus design BAAH bays to connect the existing elements 2. Install new MPAC building with protection and controls 3. Upgrade ground grid as needed The project will mitigate the system collapse issue due to the NERC Category P2-4 contingency. Even though load shedding is allowed under P2-4 contingency, the alternative of using RAS to shed load is not recommended due to loss of large amount of loads (about 300 MW in the 2032 study case), complexity of the RAS design and high requirement on the RAS reaction time. As a result, converting the Tesla 115 kV bus from DBSB to BAAH is recommended as shown in Figure 2. With the BAAH configuration, only two elements would be tripped when there is fault on the bay middle breaker, and there is no system collapse issue post any of the middle breaker faults. | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0007754 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-02-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.5796 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5563801 | T.0009526 | Tesla_Reconfigure 115 kV bus | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-01-26 | 2030-12-31 | 2028-08-29 | NA | NA | FALSE | 55000 | NA ¦ NA | 9.6097 | 6518.1265 | 0 | 0 | 0 | 0 | 5.0145 | 970.7052 | 0 | 0 | 0 | 0 | 5.0144 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
840 | Manteca: Upgrade Tesla Remote End |  |  | Manteca, San Joaquin | This project will convert the Tesla 115kV bus from DBSB to BAAH. Below is the high-level scope of this project: 1. Install five bays of folded bus design BAAH bays to connect the existing elements 2. Install new MPAC building with protection and controls 3. Upgrade ground grid as needed The project will mitigate the system collapse issue due to the NERC Category P2-4 contingency. Even though load shedding is allowed under P2-4 contingency, the alternative of using RAS to shed load is not recommended due to loss of large amount of loads (about 300 MW in the 2032 study case), complexity of the RAS design and high requirement on the RAS reaction time. As a result, converting the Tesla 115 kV bus from DBSB to BAAH is recommended as shown in Figure 2. With the BAAH configuration, only two elements would be tripped when there is fault on the bay middle breaker, and there is no system collapse issue post any of the middle breaker faults. | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0007754 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-14 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.8539 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5563802 | T.0009526 | Tesla_Reconfigure 115 kV bus | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-01-26 | 2030-12-31 | 2028-08-29 | NA | NA | FALSE | 55000 | NA ¦ NA | 9.9382 | 6518.4549 | 0 | 0 | 0 | 0 | 5.0145 | 971.0336 | 0 | 0 | 0 | 0 | 5.0145 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
841 | Borden: Borden BK 1 Capacity Increase |  |  | Madera | This project proposes to replace Borden Bank 1 breaker and upgrade 70kV bus to match the capability of the Borden Bank 1. 1. Upgrade Bank Breaker CB 52 and associated switches to match the Transformer Bank # 1’s full capacity (200 N/220 E MVA) 2. Upgrade Borden 70 kV Bus Section “D” to match the Transformer Bank # 1’s full capacity. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-16 | 21 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 7.1874 | NA | 230 ¦ 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806920 | T.0009562 | Borden Borden BK 1 Capacity Increase | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-11-20 | 2025-07-17 | 2029-03-30 | Prioritization | NA | FALSE | $11,500 ¦ $23,000 | NA ¦ NA | 306.5975 | 13412.0728 | 0 | 0 | 0 | 76.7837 | 156.6324 | 3247.1117 | 8974.903 | 956.642 | 0 | 0 | 233.4161 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
842 | RAVENSWOOD 230 115KV BK 1 LIMITING FACIL |  |  | Menlo Park, San Mateo | This project proposes to improve the operational flexibility by upgrading limiting equipment associated with the 230/115kV Bank 1 at Ravenswood substation. | Substation - Transformer | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-05 | 59 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5554629 | T.0009570 | Ravenswood 230 115kV Bk 1 Limiting Facility Upgrade | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Cancelled | 4 | 2028-09-06 | 2019-12-01 | 2029-03-14 | Prioritization | Project Design | FALSE | $100 ¦ $200 | NA ¦ NA | 21.9082 | 3426.2097 | 0 | 0 | 0 | 18.0234 | 4.8499 | 28.817 | 0 | 0 | 0 | 0 | 22.8734 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Project Status] Project cancelled in CAISO 2024-2025 Transmission Plan
843 | NEWARK DIST_82N_INSTALL NEWARK BANK 23 |  |  | Fremont, Alameda | The project scope of work includes following: Substation Work: T.0010142.01: MAT 10R, Planning Order 5809764, OAA 74059542 Install Newark Bank 23, Extend 21 kV outdoor bus, Install 2112, 2113 and 2114 Circuit Breakers • Install Newark Bank 23, 75 MVA, 230/21kV substation transformer • Extend and build 21 kV bus structure • Install 21 kV, 1200A, 25kA feeder Breaker 2112 with protection package • Install 21 kV, 1200A, 25kA feeder Breaker 2113 with protection package • Install 21 kV, 1200A, 25kA feeder Breaker 2114 with protection package • Install 21 kV, 2000A, 25kA bank/bus tie Breaker 2200/2 with protection package • Required by 6/30/2026 T.0010142.02: MAT 82N, Planning Order 5809765, OAA 74059543 • Install new 230 kV circuit breaker • Required by 6/30/2026 Distribution Work: MAT 10Q Install Newark 2112, 2113 and 2114 circuits and extend circuits to three Primary Metering Sites • Required by Q2 2026 – Q2 2028 Associated switches and primary meters to be installed on New Business Orders 35486286, 35553914 and 35552721 Newark 2112 circuit: PO 5810760, OAA 35564690 - • Trench and install approximately 5,500 Feet of new 1100 AL cables in new 6’’conduits • Install 2 subsurface 3-Way, 3-Way switched 600A switches with new #7 enclosures Newark 2113 circuit: PO 5810761, • Trench and install approximately 12,000 Feet of new 1100 AL cables in new 6’’conduits • Install approximately 2,000 Feet of new 1100 AL cables in existing 6’’conduits • Install 4 subsurface 3-Way, 3-Way switched 600A switches with new #7 enclosures Newark 2114 circuit: PO 5810762, OAA 35564692 - • Trench and install approximately 6,500 Feet of new 1100 AL cables in new 6’’conduits • Install 4 subsurface 3-Way, 3-Way switched 600A switches with new #7 enclosures | Substation - Circuit Breaker | New | NA | NA | Load Growth | Substation Capacity | NA | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.2008 | NA | 230 kV | NA | NA | NA | 5.211 | Non-IGP | 5809765 | T.0010142 | NEWARK DIST_INSTALL NEWARK BANK 23 | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-09-29 | 2026-06-30 | 2026-06-30 | NA | NA | TRUE | 63700 | NA ¦ NA | 4118.6892 | 9195.0389 | 0 | 0 | 0 | 226.387 | 3461.9389 | 4806.7129 | 700 | 0 | 0 | 0 | 3688.3259 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
844 | Cloverdale Bank 2 Install |  |  | Cloverdale, Sonoma | Install Bank 2, reconfigure high side projection into ring bus configuration (install 2 Circuit Breakers), install 2 new 12 Kilovolt (kV) feeder. There is one new business (NB) load (EV) application for a total of 4.5 MW which will overload Cloverdale bank by 9% in 2026. The Cloverdale 1102 feeder will be overloaded by 13% in 2027. In addition, Cloverdale 1102 is projected to experience a 19% overload on 3/0Al conductor by 2028. | Substation - Circuit Breaker | New | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-02-12 | NA | Steady State Power Flow System Analysis | Wires - Location/Route Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7377 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5816698 | T.0010246 | CLOVERDALE INSTALL BK 2 AND NEW FEEDERS | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-07 | 2028-05-31 | 2028-05-31 | NA | NA | FALSE | 15000 | NA ¦ NA | 58.0175 | 10191.9785 | 0 | 0 | 0 | 0 | 15.3717 | 459.7766 | 0 | 0 | 0 | 0 | 15.3717 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
845 | SAN JOSE A - SUBSTATION REBUILD BUS UPG |  |  | San Jose, Santa Clara | This project proposes to rebuild San Jose A Substation into a substation capable of serving new load. The rebuild calls for one 115kV Breaker-and-a-Half (BAAH) GIS (Gas Insulated Switchgear) with fifteen (15) transmission circuit breakers. It will install two (2) distribution transformers, two (2) distribution switchgears, three (3) new 21kV feeders, and five (5) 12kV feeders. This AA will fund all pre-construction activities, including detailed engineering and cost estimating, substation design, project team meetings, job walkdowns and field verifications, contract execution support, permit applications, traffic control, long lead time materials, and civil site preparation. | Substation - Multiple | Upgrade/Retrofit | NA | T.0011286 | Load Growth | Bus Upgrade | NA | NA | 2026-03-03 | 69 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.1997 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811207 | T.0010465 | San Jose A -Substation rebuild | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-11-01 | NA | 2028-11-07 | NA | NA | FALSE | NA | NA ¦ NA | 17395.677 | 208312.6596 | 0 | 0 | 0 | 203.4629 | 11762.3356 | 27623.305 | 75000 | 90623.556 | 3000 | 100 | 11965.7986 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
846 | French Camp: Rebuild Sub |  |  | San Joaquin | Loop French Camp substation into Bellota-Tesla #2 230 kV line to add a new 230 kV bus at French Camp. The total length of transmission circuit is about 4.4 miles. Addressing overloads at Weber 60 kV line #2 (Weber - French Camp) starting in the near-term under NERC Category P1 contingencies | Substation - Multiple | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-02-04 | 76 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 0.85162 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5812672 | T.0010675 | French Camp Reinforcement | 2 | 61 | NA ¦ EX113699 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2032-10-24 | 2030-06-01 | 2036-04-05 | Prioritization | NA | FALSE | $42,100 ¦ $84,200 | NA ¦ NA | 271.1797 | 108636.8315 | 0 | 0 | 0 | 0 | 216.5727 | 238.81 | 1800 | 3600 | 8100 | 9000 | 216.5727 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
847 | DIXON LANDING:61G_REPLACE BANK 3 |  |  | Fremont, Alameda | This project proposes to upgrade existing Dixon Landing Bank 3 from 45 MVA bank to new 115/21 kV, 75 MVA bank; and extend the existing idled 21 kV Distribution feeder, Dixon Landing 2110. Dixon Landing Bank 2 is projected to be overloaded in 2027 by 6.5% (2.9 MW) due to ~20 MW of total requested load increases from multiple New Businesses in the City of Fremont. Upgrading Dixon Landing Bank 3 with a 75 MVA bank and extending the existing Dixon Landing 2110 feeder, will alleviate the overload on Dixon Landing Bank 2 and increase new capacity to serve future customers in the City of Fremont area. It will also improve service reliability, operating flexibility and allow for more emergency capacity. | Substation - Transformer | Upgrade/Retrofit | NA | NA | Load Growth | Transformer Addition/Replacement | NA | NA | 2026-03-03 | 29 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.79979 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811302 | T.0010801 | DIXON LANDING 46 and 61 Repl BK 3_FDRS | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-08-02 | NA | 2027-09-27 | NA | NA | TRUE | NA | NA ¦ NA | 16.3868 | 5866.2647 | 0 | 0 | 0 | 0 | 4.5354 | 561.7291 | 4090.8876 | 2650 | 0 | 0 | 4.5355 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
848 | Tulare Lake -install 70kV breaker |  |  | Kings | This project proposes to install one new 70 kilovolt (kV) and one new 12kV circuit breaker at the Tulare Lake Substation. Additionally, it includes upgrading the existing autotransformer outside the substation fence and install new feeder to serve Electric Vehicle (EV) charging load at Greenlane facility located at the intersection of I-5 and SR 41 in the Fresno Division. This work is essential to prevent a 13 megawatt (MW) overload of the existing Arco-Tulare 70kV transmission line and serve new business growth in Kettleman Distribution Planning Area (DPA). | Substation - Circuit Breaker | New | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.0391 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5814785 | T.0010842 | TULARE LAKE Install New Feeder 1105 | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-04-20 | NA | 2028-09-05 | NA | NA | FALSE | NA | NA ¦ NA | 5.2419 | 1453.4072 | 0 | 0 | 0 | 0 | 3.9018 | 66.9538 | 0 | 0 | 0 | 0 | 3.9018 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
849 | North Dublin: Install BK 2 |  |  | Contra Costa | This project proposes to install a new North Dublin Bank 2, 230/21 kV, 75 MVA bank; and install a new 21 kV Distribution feeder, North Dublin 2105. Vineyard 2110 is projected to be overloaded in 2028 by 17.3% (3.67 MW) and North Dublin 2101 is projected to be overloaded in 2028 by 10.4% (2.2 MW) due to ~8.3 MW of total requested load increases from multiple New Businesses in the City of Dublin. Installing new 75 MVA North Dublin Bank 2 and the new North Dublin 2105 feeder will alleviate the overloads on Vineyard 2110 and North Dublin 2101 and increase new capacity to serve future customers in the City of Dublin area. It will also improve service reliability, operating flexibility and allow for more emergency capacity. Substation 61G • Reconfigure Bus work if required • 1- 230kV Breaker | Substation - Circuit Breaker | New | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-02-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.373 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5814040 | T.0010863 | N DUBLIN SUB:INSTALL BK 2 AND 21KV FDR | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-03-02 | NA | 2028-05-03 | NA | NA | FALSE | NA | NA ¦ NA | 1.2201 | 10934.729 | 0 | 0 | 0 | 0 | 0 | 201.8987 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
850 | Lammers - Install CB 132 and CB 142 |  |  | San Joaquin | This project was initiated to eliminate the following distribution system overload at Lammers Substation in Tracy which cannot be eliminated by load transfer because of depleted area capacity: Lammers 1101 Distribution Feeder 9.03 MW (72%) Normal Overload in 2026 The forecasted overload is the direct result of a 14.4 MW new business application by Prologis, Inc. for an EV charging facility for semitrucks at their existing facility at 5902 Hopkins Road in Tracy. To prevent the forecasted distribution feeder overload, this project proposes to install a new Transformer Bank 3, 12 kV indoor switchgear and a new 1109 distribution feeder at Lammers Substation and perform distribution line work outside of the substation to serve the new EV facility Transmission Line (MWC 60) Lammers Transmission Substation Scope – Ring Bus: 2028 – Install 2-115 kV circuit breakers to complete 6-breaker ring bus | Substation - Circuit Breaker | New | NA | NA | Load Growth | Bus Upgrade | NA | NA | 2026-02-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.6805 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5817259 | T.0011052 | Lammers - Install Bank 3 | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-06-13 | NA | 2029-12-11 | NA | NA | FALSE | NA | NA ¦ NA | 4.8475 | 4005.0041 | 0 | 0 | 0 | 0 | 0 | 68.4489 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
851 | Convert Oakland C Subst to GIS |  |  | Oakland, Alameda | Rebuilding the two Sobrante-Grizzly-Claremont #1 and #2 115 kV lines into four lines, each with a summer normal rating of at least 1714 Amps. Two of these lines will bypass Claremont Substation and connect to Oakland D and Oakland L Substations through new underground (UG) cable sections. Rerouting the Moraga-Oakland X #4 line to bypass the Oakland X Substation and instead connect to Oakland C via a new UG cable section. Converting Oakland C to Gas-Insulated Switchgear (GIS). Replacing the Oakland C-Oakland X UG cable with a larger size cable. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-04 | 90 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.8705 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815581 | T.0011287 | North Oakland Reinforcement Project | 4 | 61 | NA ¦ EX138976 ¦ NA ¦ 60 | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-01-07 | 2032-05-01 | 2030-05-21 | NA | NA | FALSE | 1127000 | NA ¦ NA | 0 | 114506.2371 | 0 | 0 | 0 | 0 | 0 | 276.4725 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
852 | Moraga: 230kV Bus Upgrade |  |  | Orinda, Contra Costa | Add sectionalizing breakers and a bus tie breaker to Moraga 230 kV bus | Substation - Bus Arrangement | New | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8714 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815744 | T.0011323 | Moraga: 230kV Bus Upgrade | 1 | 61 | NA ¦ 5792051 ¦ T.0006159 ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-04-06 | 2024-05-01 | 2029-10-10 | Prioritization | NA | FALSE | 17000 | NA ¦ NA | 18.2087 | 14194 | 0 | 0 | 0 | 0 | 5.6376 | 189.0424 | 0 | 0 | 0 | 0 | 5.6377 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
853 | Sobrante: 230kV Bus Upgrade |  |  | Orinda, Contra Costa | Expand Sobrante 230 kV bus and split to two sections, section D and section E by adding two sectionalizing breakers and one bus-tie breaker. | Substation - Bus Arrangement | New | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.0767 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815745 | T.0011324 | Sobrante: 230kV Bus Upgrade | 1 | 61 | NA ¦ EX138984 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-01-07 | 2033-05-01 | 2028-07-13 | NA | NA | FALSE | 15000 | NA ¦ NA | 29.9298 | 3760.5001 | 0 | 0 | 0 | 0 | 0 | 274.6215 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
854 | Distribution - Oak Park - Repl Bk with 60/12kV |  |  | Stockton, San Joaquin | Oak Park distribution transformer replacement and add new 60kV CB. | Substation - Transformer | Upgrade/Retrofit | NA | NA | Load Growth | Transformer Addition/Replacement | NA | NA | 2026-03-03 | 74 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.14572 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | EX139352 | TBD | TBD | TBD | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-12-01 | NA | 2028-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2650 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1325 | 1325 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
855 | Distribution - Shepherd Install Bk2 |  |  | Clovis, Fresno | Shepherd Bank 2 replacement and add new 115kV CB in existing ring bus | Substation - Transformer | Upgrade/Retrofit | NA | NA | Load Growth | Transformer Addition/Replacement | NA | NA | 2026-03-13 | 29 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.5202 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX139357 | TBD | TBD | TBD | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-12-01 | NA | 2028-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2650 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1325 | 1325 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
856 | Distribution - New sub - Mariposa Rd |  |  | TBD | New sub high side work (230 kV), scope TBD | Substation - Multiple | New | NA | NA | Load Growth | New Substation | NA | NA | NA | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | TBD | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX139354 | TBD | TBD | TBD | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 11000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 3000 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
857 | Distribution - New sub - Johnson Canyon |  |  | TBD | New sub high side work (115 kV), scope TBD | Substation - Multiple | New | NA | NA | Load Growth | New Substation | NA | NA | NA | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | TBD | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX139356 | TBD | TBD | TBD | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 11000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 3000 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
858 | Distribution - New substation - S Fresno |  |  | TBD | New sub high side work (115 kV), scope TBD | Substation - Multiple | New | NA | NA | Load Growth | New Substation | NA | NA | NA | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | TBD | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX139359 | TBD | TBD | TBD | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 11000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 3000 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
859 | TEMPLETON SUB-INSTALL REVERSE POWER RELA |  |  | San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-02 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.6839 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5805698 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-10-27 | 2019-05-01 | 2028-02-09 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 26.031 | 1305.7297 | 0 | 0 | 29.9809 | -5.3417 | 1.3917 | 253.0201 | 727.6955 | 298.9832 | 0 | 0 | 26.031 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
860 | MOSHER: Inst Special Protection Scheme |  |  | Stockton, San Joaquin | The project scope of work involves the following•Install a new 4.2 miles of 60 kV line between Stagg and Hammer substations •Install a new 60 kV circuit breaker at Stagg Substation•Upgrade the Hammer 60 kV bus to a six element ring bus•Upgrade associated substation equipment at Stagg and Hammer substations to accommodate the new 60 kV line, if necessary. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | Reliability | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.5909 | NA | 230 ¦ 60 kV | 102 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5780820 | T.0000016 | Stagg-Hammer 60kV Line Install SPS | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2019 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-07-19 | 2021-04-21 | 2020-11-16 | NA | NA | FALSE | 2056 | NA ¦ NA | 924.5943 | 924.5943 | 24.7057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 924.5943 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 24.7057 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
861 | Five Points SS DTT |  |  | Fresno | This project proposes to install a new 70/12 kV 30 MVA transformer bank at Calflax Substation in order to prevent projected substantial overloads on Coalinga #2 Bank 1. To support the additional transformer bank at Calflax the existing 70 kV transmission tap that serves Calflax Bank 1 will be reconfigured into a four-element ring bus. In addition to the new transformer bank at Calflax Substation one new 12 kV circuit breaker and associated distribution work will be installed to serve the proposed additional 10 MW Tesla EV charging infrastructure load at Harris Ranch. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Load Growth | Substation Capacity | NA | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.68286 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5795145 | T.0003879 | Calflax Substation Bank 2 Installation | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-06 | 2023-02-08 | 2024-01-05 | Prioritization | NA | FALSE | 19400 | NA ¦ NA | 284.9708 | 284.9708 | 24.7282 | 96.857 | 92.5151 | 41.1269 | 29.7436 | 0 | 0 | 0 | 0 | 0 | 284.9708 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 252.0389 | 29.3436 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
862 | Ames-Mtn View-Whisman Proj (SPS Work) |  |  | Mountain View, Santa Clara | The project proposes to reconnect the 115 kV lines from Mountain View and Whisman Substations into the 115 kV bus at Ames Substation. The work will require protection upgrades at the substations and also will require circuit breaker replacement at Mountain and Whisman due to increased fault duty at those substations. This project was one of several projects that are needed to eliminate the need to have a reliability must run (RMR) contract with Calpine’s Metcalf Energy Center. Also, to address substation bus reliability issues at Ames Substation, the project will also install circuit breakers at Ames on the two 115 kV lines that serve the NASA Ames facility. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Reliability | Special Protection Scheme | NERC TPL Standards | NA | 2026-02-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.8814 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5787398 | T.0003920 | RMR - Mtn View-Whisman-Ames Project | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-17 | NA | 2028-11-20 | NA | NA | FALSE | NA | NA ¦ NA | 15.712 | 2748.3163 | 0 | 0 | 0 | 0 | 13.4585 | 143.0335 | 0 | 0 | 0 | 0 | 13.4585 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
863 | El Capitan 115kv Protection Upgrade |  |  | Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0001381 ¦ T.0002231 | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.954 | NA | 115 kV | 462 | 5. Compliance/Commitments With Strong Safety Link | 11 | 5.1001 | Non-IGP | 5787806 | T.0004116 | WILSON: 115 kV ARP - BAAH | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-06-07 | 2022-08-12 | 2029-07-26 | Prioritization | NA | FALSE | 66700 | NA ¦ NA | 47.8292 | 1333.7802 | 0.6863 | 0 | 0 | 3.5165 | 3.8026 | 156.1547 | 0 | 0 | 0 | 0 | 46.6574 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
864 | Moraga U: RAS Project |  |  | Orinda, Contra Costa | Modify the existing San Leandro U Substation, which will include all the necessary requirements, including time of day and seasonal setting changes, iterative tripping, and ability to accommodate bypass scenarios. The main driver for this RAS is the ISO planning standard that does not allow for load tripping in Greater Bay Area as a high population density area. The New RAS will monitor the outages and flows on five critical lines in Moraga-Oakland J area and take corrective actions to resolve any overloads on these lines without dropping the load. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.8714 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5791839 | T.0004580 | San Leandro U: Ras Project | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-01-05 | 2022-09-30 | 2026-09-30 | Prioritization | NA | TRUE | 4000 | NA ¦ NA | 2106.1539 | 6284.4965 | 74.2202 | 127.1494 | 410.4164 | 67.2875 | 282.0594 | 2605.9985 | 20.7336 | 0 | 0 | 0 | 961.1329 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
865 | San Leandro U: RAS project |  |  | San Leandro, Alameda | Modify the existing San Leandro U Substation, which will include all the necessary requirements, including time of day and seasonal setting changes, iterative tripping, and ability to accommodate bypass scenarios. The main driver for this RAS is the ISO planning standard that does not allow for load tripping in Greater Bay Area as a high population density area. The New RAS will monitor the outages and flows on five critical lines in Moraga-Oakland J area and take corrective actions to resolve any overloads on these lines without dropping the load. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2372 | NA | 115 kV | NA | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5534504 | T.0004580 | San Leandro U: Ras Project | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2022-05-13 | 2022-09-30 | 2026-09-30 | Prioritization | NA | TRUE | 4000 | NA ¦ NA | 5889.269 | 7605.5483 | 656.7866 | 2509.3148 | 338.395 | 1506.2676 | 713.3025 | 1520.0111 | 59.006 | 0 | 0 | 0 | 5855.5372 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 656.7866 | 2509.3148 | 338.395 | 1506.2676 | 713.3025 | 33.7318 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
866 | Oakland J U: RAS Project |  |  | Oakland, Alameda | Modify the existing San Leandro U Substation, which will include all the necessary requirements, including time of day and seasonal setting changes, iterative tripping, and ability to accommodate bypass scenarios. The main driver for this RAS is the ISO planning standard that does not allow for load tripping in Greater Bay Area as a high population density area. The New RAS will monitor the outages and flows on five critical lines in Moraga-Oakland J area and take corrective actions to resolve any overloads on these lines without dropping the load. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Special Protection Scheme | NERC TPL Standards | NA | 2026-02-09 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.5059 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5791857 | T.0004580 | San Leandro U: Ras Project | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-01 | 2022-09-30 | 2026-09-30 | Prioritization | NA | TRUE | 4000 | NA ¦ NA | 1328.9084 | 4695.0051 | 120.2907 | 142.5106 | 373.0508 | 217.1887 | 423.7442 | 1607.3691 | 12.1649 | 0 | 0 | 0 | 1276.785 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
867 | CHCSS-Salinas-Soledad SPS Project |  |  | Monterey ¦ Prunedale CDP, Monterey ¦ Salinas, Monterey ¦ Soledad, Monterey | The project scope of work will install a new remedial action scheme (RAS) at Salinas Substation to detect overloads on the Crazy Horse Canyon Switching Station (CHCSS) – Salinas – Soledad 115 kV Lines following a double-circuit towerline (DCTL) outage of the Moss Landing – Salinas 115 kV Lines. The RAS will then trip distribution loads at Salinas to eliminate the overloads. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | EX113219 | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-31 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Corrosion |  | NA | NA | NA | 115 kV | 120 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5785510 | T.0004747 | Chcss-Salinas-Soledad Sps Project | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-02-03 | NA | 2028-02-16 | NA | NA | FALSE | NA | NA ¦ NA | 30.3478 | 4801.3983 | 1 | 1 | 8 | 10 | 10 | 271.0505 | 4000 | 500 | 0 | 0 | 30.3478 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
868 | LSPOWER PACIRAS 500KV VGCC - FERN ROAD |  |  | Round Mountain CDP, Shasta | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-03-09 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5798639 | T.0006815 | LSPower Round Mountain Area 500kV Dynami | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2024-12-12 | 2024-12-31 | 2026-06-12 | Construction Delays | NA | TRUE | $160,000 ¦ $190,000 | NA ¦ NA | 440.886 | 1275.7326 | 0 | 1.0104 | 3.2596 | 128.3549 | 234.0952 | 909.0124 | 0 | 0 | 0 | 0 | 366.7202 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power, Round Mountain 500 kV Dynamic Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
869 | LSPOWER PACIRAS 500KV RGCC - FERN ROAD |  |  | Round Mountain CDP, Shasta | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | Reliability | Substation Reliability | NERC TPL Standards | NA | 2026-03-09 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5798638 | T.0006815 | LSPower Round Mountain Area 500kV Dynami | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-05-21 | 2024-12-31 | 2026-06-12 | Construction Delays | NA | TRUE | $160,000 ¦ $190,000 | NA ¦ NA | 229.3447 | 586.2865 | 0 | 2.5198 | 4.7566 | 14.0824 | 138.2543 | 426.6735 | 0 | 0 | 0 | 0 | 159.6129 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power, Round Mountain 500 kV Dynamic Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
870 | BIRDS LANDING REMOTE END |  |  | Solano | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-18 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 3.4512 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5549722 | T.0008048 | Contra Costa PP Line Swaps | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-12-06 | 2025-05-01 | 2025-05-30 | NA | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 2309.9751 | 2309.9751 | 0 | 8.8244 | 145.5417 | 684.064 | 1471.545 | 0 | 0 | 0 | 0 | 0 | 2309.9751 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 154.366 | 654.117 | 1418.9846 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
871 | LONE TREE REMOTE END |  |  | Antioch, Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-03 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | 2.3791 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5549723 | T.0008048 | Contra Costa PP Line Swaps | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-01-28 | 2025-05-01 | 2025-05-30 | NA | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 1322.4436 | 1322.4436 | 0 | 13.938 | 174.3722 | 512.561 | 599.7053 | 21.8671 | 0 | 0 | 0 | 0 | 1300.5765 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 188.3102 | 512.561 | 565.4056 | 21.2904 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
872 | Table Mtn 230 kV Redundant Relay |  |  | Butte | This project proposes to improve the electric transmission grid reliability and operational flexibility by installing redundant Bus Differential relays on the 230kV Bus at Table Mountain substation. | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-20 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807179 | T.0009530 | Table Mtn: Install new 500kV Bank and 23 | 2 | 61 | NA ¦ EX113250 ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-07-20 | 2029-12-10 | 2027-12-24 | NA | NA | TRUE | 35800 | NA ¦ NA | 333.1334 | 14424.9681 | 0 | 0 | 0.3394 | 182.7438 | 128.8437 | 2200.2638 | 11118.263 | 100 | 0 | 0 | 311.9269 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
873 | Kasson: Upgrade 115kV bus diff protect |  |  | San Joaquin | This project proposes to install a redundant set of 115kV bus protection and replace the 115kV CB 132 to resolve the thermal overloading on three (3) 60kV and two (2) 115kV lines in the near term under the circumstances of the existing bus protection failure. • Replace the CB 132 and associated switches. Foundations/ structures might need to be replaced as well. • Add a “set B” bus overcurrent relay and connect the 115kV line CBs CT to the new relay. | Substation - Protection Relay | New | NA | 5756036 | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-31 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.1988 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806846 | T.0009533 | KASSON: Repl CB 132 & Add Set B Bus Rly | 1 | 61 | NA ¦ EX113246 ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-11-05 | 2027-03-31 | 2027-01-14 | NA | NA | TRUE | 3500 | NA ¦ NA | 900.8591 | 2818.6896 | 0 | 0 | 0 | 151.7765 | 709.6835 | 1457.2295 | 324.9358 | 0 | 0 | 0 | 861.46 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
874 | Los Banos: Replace 230kV CBs 212 & 222 |  |  | Merced | Based on 2022 Short Circuit Analysis results and study plan , Los Banos 230 kV CBs 212, 222, 252, and 262 will be overstressed in 2030. Planning analyses show that the Los Banos 230 kV CBs 212, 222, 252 and 262 are projected to overload in 2030. Manning 500 kV Project has been added to 2023 TPP project list that contributes overstressed to Los Banos 230 kV CBs. • Replace 230 kV CBs 212, 222 in place with 3,000 Amps, 63 kA CBs, new SMP Relays. Foundations/structures may need to be replaced. • Replace 230 kV CBs 252, 262 with two (2) new BAAH Bays in the new BAAH bus section to meet the ultimate plan. New CBs will be 3,000 Amps, 63 kA CBs. Need T line relocations into new BAAH positions. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | T.0009177 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-06 | 33 | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 53.2803 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806918 | T.0009550 | Los Banos: 230kV CB Overstress | 4 | 61 | NA ¦ EX113236 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-09-30 | 2032-12-31 | 2028-12-28 | NA | NA | FALSE | 66000 | NA ¦ NA | 862.5319 | 8111.9882 | 0 | 0 | 0 | 244.3667 | 582.6822 | 1984.9394 | 5300 | 0 | 0 | 0 | 827.0488 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
875 | Los Banos: Replace 230kV CBs 252 & 262 |  |  | Merced | Based on 2022 Short Circuit Analysis results and study plan , Los Banos 230 kV CBs 212, 222, 252, and 262 will be overstressed in 2030. Planning analyses show that the Los Banos 230 kV CBs 212, 222, 252 and 262 are projected to overload in 2030. Manning 500 kV Project has been added to 2023 TPP project list that contributes overstressed to Los Banos 230 kV CBs. • Replace 230 kV CBs 212, 222 in place with 3,000 Amps, 63 kA CBs, new SMP Relays. Foundations/structures may need to be replaced. • Replace 230 kV CBs 252, 262 with two (2) new BAAH Bays in the new BAAH bus section to meet the ultimate plan. New CBs will be 3,000 Amps, 63 kA CBs. Need T line relocations into new BAAH positions. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | T.0009177 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-06 | 33 | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806919 | T.0009550 | Los Banos: 230kV CB Overstress | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-09-30 | 2032-12-31 | 2028-12-28 | NA | NA | FALSE | 66000 | NA ¦ NA | 336.6052 | 32160.5585 | 0 | 0 | 0 | 131.7719 | 167.0166 | 1761.77 | 10000 | 13000 | 6600 | 500 | 298.7885 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
876 | PANOCHE UPGRADE LOS BANOS REMOTE END |  |  | Fresno | Based on 2022 Short Circuit Analysis results and study plan , Los Banos 230 kV CBs 212, 222, 252, and 262 will be overstressed in 2030. Planning analyses show that the Los Banos 230 kV CBs 212, 222, 252 and 262 are projected to overload in 2030. Manning 500 kV Project has been added to 2023 TPP project list that contributes overstressed to Los Banos 230 kV CBs. • Replace 230 kV CBs 212, 222 in place with 3,000 Amps, 63 kA CBs, new SMP Relays. Foundations/structures may need to be replaced. • Replace 230 kV CBs 252, 262 with two (2) new BAAH Bays in the new BAAH bus section to meet the ultimate plan. New CBs will be 3,000 Amps, 63 kA CBs. Need T line relocations into new BAAH positions. | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0009177 | Reliability | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811878 | T.0009550 | Los Banos: 230kV CB Overstress | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-09-22 | 2032-12-31 | 2028-12-28 | NA | NA | FALSE | 66000 | NA ¦ NA | 35.5427 | 1392.5597 | 0 | 0 | 0 | 0 | 33.4552 | 66.4424 | 0 | 0 | 0 | 0 | 33.4551 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
877 | Los Esteros:115kV Bus1&2 Redundant Relay |  |  | San Jose, Santa Clara | Install redundant Bus Differential Relays for 115kV Bus 1 & 2 at Los Esteros substation. Los Esteros 115kV fault duty is about 52 kA. Existing one level of bus protection relies on remote tripping for a single contingency of bus differential protection failure to trip for a bus fault. Remote tripping is not high speed, typically each takes 0.3 to 0.8 second. Stability issues may arise as a result of the slow fault clearing and subsequent compromise on transmission network connectivity. Los Esteros 115kV bus interconnects with Calpine Generation at 115kV and it is not desirable to rely on Calpine relays to clear PG&E bus faults. Besides, outage can result in loss of 293MW generation import. With only one level of bus differential protection, there is a need to force open all the breakers on that bus section when bus differential protection is cut-out (for testing etc.). Under this condition, fault on any circuit connected to the remaining bus section could disconnect the other circuit on the same bay and fault on the remaining bus will result in station loss. This can be an operational concern. Los Esteros substation is a critical facility serving Silicon Valley. Considering Reliability and operating flexibility and to address the operational concern, the California Independent System Operator(CAISO) is recommending approval of adding 115kV low impedance Bus Differential Set B relays for Bus 1 & 2 at Los Esteros substation. | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-09 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807123 | T.0009560 | Los Esteros_115kV Bus1&2 Redundant Relay | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-09-03 | NA | 2026-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 568.9092 | 1874.9988 | 0 | 0 | 0 | 28.6076 | 513.0758 | 1179.42 | 153.8954 | 0 | 0 | 0 | 541.6834 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
878 | Gates: 230kV Bus SecD&E Redundant Relay |  |  | Fresno | Install Gates Section D & E 230 KV Redundant Bus Differential Relay to resolve P5 issues. | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807128 | T.0009583 | Gates 230kV Bus SecD&E Redundant Relay | 1 | 61 | NA ¦ EX113245 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-05-07 | NA | 2026-09-15 | NA | NA | TRUE | NA | NA ¦ NA | 842.8314 | 3854.3261 | 0 | 0 | 0 | 116.3642 | 700.1861 | 2384.8402 | 652.9356 | 0 | 0 | 0 | 816.5503 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
879 | McCall: 115kV Bus#1&#2 Redundant Relay |  |  | Fresno | Install MCCALL 115KV BAAH BUS #1&2 redundant relay to resolve P5 issues. | Substation - Protection Relay | New | NA | EX112724 ¦ T.0003305 | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 16.2494 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807127 | T.0009584 | McCall_115kV Bus#1&#2 Redundant Relay | 1 | 61 | NA ¦ Tx000749 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-05-18 | NA | 2027-04-12 | NA | NA | TRUE | NA | NA ¦ NA | 612.0572 | 3460.1563 | 0 | 0 | 0 | 158.2425 | 429.5927 | 2458.303 | 414.0181 | 0 | 0 | 0 | 587.8352 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
880 | Humboldt: 115kV Redundant Bus Diff Rly |  |  | Humboldt | Install Humboldt 115 kV Redundant Bus Differential Relay to resolve P5 issues. | Substation - Protection Relay | New | NA | T.0006372 ¦ EX111032 | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.569 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807201 | T.0009597 | Humboldt_115kV Redundant Bus Diff Rly | 1 | 61 | NA ¦ EX113248 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-03-17 | NA | 2027-04-27 | NA | NA | TRUE | NA | NA ¦ NA | 254.4791 | 6158.3451 | 0 | 0 | 0 | 121.9368 | 110.1626 | 926.2457 | 967.8438 | 0 | 0 | 0 | 232.0994 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
881 | Lakeville: 230kV Redundant Bus Diff Rly |  |  | Sonoma | Install Lakeville 230 kV Redundant Bus Differential Relay to resolve P5 issues. | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-13 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 14.7021 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807202 | T.0009598 | Lakeville_230kV Redundant Bus Diff Rly | 1 | 61 | NA ¦ EX113244 ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-09-27 | 2029-06-08 | 2029-02-21 | NA | NA | FALSE | 3950 | NA ¦ NA | 416.7123 | 6577.5449 | 0 | 0 | 0 | 113.2555 | 263.474 | 1076.1889 | 0 | 0 | 0 | 0 | 376.7295 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
882 | Mesa 230kV BAAH Bus1 Bus2 Redundant Rly |  |  | Nipomo CDP, San Luis Obispo | Install Mesa 230 kV BAAH Bus #1 and #2 Redundant Relay to resolve P5 issues. | Substation - Protection Relay | New | NA | T.0000588 ¦ T.0009596 | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-09 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 10.5414 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807203 | T.0009599 | Mesa 230kV BAAH Bus1 Bus2 Redundant Rly | 1 | 61 | NA ¦ EX113249 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-09-23 | NA | 2027-03-19 | NA | NA | TRUE | NA | NA ¦ NA | 707.1596 | 2119.242 | 0 | 0 | 0 | 121.9931 | 552.4526 | 935.5872 | 493.0759 | 0 | 0 | 0 | 674.4457 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
883 | Morro Bay SW Sta:230kV Bus Redundant Rly |  |  | Morro Bay, San Luis Obispo | Replace existing 230kV high impedance bus differential protection with low Impedance (Set A) Bus Differential Protection and Control • Install new low impedance Bus Differential protection and control (Set B relays) for 230kV Bus • Install standalone/slip-on CTs if required as bus differential requires its own CTs • Install new control cables from CCVTs & existing breakers to control building for relays | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0000154 | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Relay Upgrades | NERC TPL Standards | NA | 2026-03-03 | 35 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 12.614 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813218 | T.0010761 | Morro Bay SW Sta 230kV Bus Redundant Rly | 1 | 61 | NA ¦ EX112241 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-08-02 | NA | 2028-12-15 | NA | NA | FALSE | NA | NA ¦ NA | 15.3826 | 2192.1909 | 0 | 0 | 0 | 0 | 0 | 192.1908 | 2000 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
884 | Round Mtn Bus 1 and 2 Sec E 230 Red Rlys |  |  | Round Mountain CDP, Shasta | Adding redundant bus relay for Round Mountain Bus 1 and Bus 2 Section E 230 kV buses | Substation - Protection Relay | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-09 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | 29.1389 | NA | 230 kV | NA | NA | NA | 3.0011 | Non-IGP | 5816306 | T.0011582 | Round Mtn Bus 1 and 2 Sec E 230 Red Rlys | 1 | 61 | NA ¦ EX112244 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-03-30 | NA | 2028-08-14 | NA | NA | FALSE | NA | NA ¦ NA | 11.3943 | 2905.9673 | 0 | 0 | 0 | 0 | 2.2094 | 151.1027 | 0 | 0 | 0 | 0 | 2.2094 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
885 | Caribou SPS#2 Upgrade |  |  | Plumas | Modify scheme to be triggered by any contingency on the Caribou – Table Mountain 230kV line, including opening a line section without a fault to comply with TPL-001-4 P2-1. The project scope is to add monitoring element (breaker 242) to the Caribou PH Generation Shedding Scheme#2 (Caribou SPS#2). | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | T.0007887 ¦ T.0010888 ¦ T.0003628 ¦ T.0007507 | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 2.2068 | NA | 230 kV | NA | NA | NA | 3.0011 | Non-IGP | 5816304 | T.0011583 | Caribou SPS#2 Upgrade | 1 | 61 | NA ¦ EX112246 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-05 | NA | 2028-09-20 | NA | NA | FALSE | NA | NA ¦ NA | 18.7092 | 2912.8858 | 0 | 0 | 0 | 0 | 4.7508 | 148.3954 | 0 | 0 | 0 | 0 | 4.7508 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
886 | Bellota RAS (original project:Bellota 230 kV Bus Upgrade) |  |  | San Joaquin | Resolve the voltage collapse issue under P2-4 contingency (losing two Bellota 230/115 kV transformer banks) | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Special Protection Scheme | NERC TPL Standards | NA | 2026-03-14 | 21 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5812359 | TBD | TBD | TBD | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-10-01 | NA | 2027-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1100 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1000 | 100 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
887 | Eagle Rock 115 kV Redundant Bus Differential Relay |  |  | Sonoma | Add redundant protection relays for Eagle Rock 115kV Bus 1&2; This is a capacity project proposed to mitigate overloads identified for P5 contingency. | Substation - Protection Relay | New | NA | T.0007732 | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Substation Reliability | NERC TPL Standards | NA | 2026-03-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.8266 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113669 | TBD | TBD | TBD | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-12-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 500 | 1500 | 3000 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
888 | CAPACITOR BANK AT PLAINFIELD SS |  |  | Solano | The California ISO’s 2018-2019 Transmission Planning Process (TPP) has identified the need for the Vaca – Dixon Area Reinforcement Project. This project will mitigate overloads and voltage criteria violations in the 115kV and 60kV transmission systems among Vaca Dixon, Davis, Rio Oso and Brighton Substations. The project will include the following work: 1. Install two 5.0 MVAR capacitor banks at Plainfield Substation. 2. Replace Vaca Dixon 115/60kV Bank 5 with a larger unit. 3. Replace the limiting elements on the 60kV equipment at Dixon Substation. 4. Re-rate the Woodland - Davis 115kV Line and the Rio Oso - West Sac 115kV Line. 5. Modify the existing special protection schemes (SPS) or add new SPS’s to trip load for select multiple contingencies. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-25 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 42.1076 | NA | 60 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 16 | 5.1001 | Non-IGP | 5766696 | T.0000007 | Vaca Dixon Area Reinforcement Project | 7 | 61 | NA ¦ 5738814 ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2024-07-17 | EIR | NA | CPUC | NA | PTC: A.24-06-008 | 2024-06-28 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 3 | 2027-01-04 | 2023-12-01 | 2028-06-30 | Prioritization | NA | FALSE | $70,000 ¦ $107,000 | NA ¦ NA | 5446.3603 | 32664.1882 | 136.6514 | 386.1143 | 941.8825 | 1090.3737 | 2053.0331 | 13046.6281 | 3746.2531 | 9.7594 | 0 | 0 | 4993.7966 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
889 | DAVIS: 115KV LINE TERMINAL UPDATE |  |  | Davis, Yolo | The California ISO’s 2018-2019 Transmission Planning Process (TPP) has identified the need for the Vaca – Dixon Area Reinforcement Project. This project will mitigate overloads and voltage criteria violations in the 115kV and 60kV transmission systems among Vaca Dixon, Davis, Rio Oso and Brighton Substations. The project will include the following work: 1. Install two 5.0 MVAR capacitor banks at Plainfield Substation. 2. Replace Vaca Dixon 115/60kV Bank 5 with a larger unit. 3. Replace the limiting elements on the 60kV equipment at Dixon Substation. 4. Re-rate the Woodland - Davis 115kV Line and the Rio Oso - West Sac 115kV Line. 5. Modify the existing special protection schemes (SPS) or add new SPS’s to trip load for select multiple contingencies. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-03 | 123 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 1.7115 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5560573 | T.0000007 | Vaca Dixon Area Reinforcement Project | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2025 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7542-E | 2025-03-12 | Approved | 2025 | Operational | 1 | 2025-11-03 | 2023-12-01 | 2025-11-13 | Bundling Dependencies | Clearances | TRUE | $70,000 ¦ $107,000 | NA ¦ NA | 42.5843 | 72.1955 | 0 | 0 | 0 | 0 | 35.0442 | 37.1513 | 0 | 0 | 0 | 0 | 35.0443 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 35.0442 | 7.54 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
890 | WOODLAND: 115KV LINE TERMINAL UPDATE |  |  | Woodland, Yolo | The California ISO’s 2018-2019 Transmission Planning Process (TPP) has identified the need for the Vaca – Dixon Area Reinforcement Project. This project will mitigate overloads and voltage criteria violations in the 115kV and 60kV transmission systems among Vaca Dixon, Davis, Rio Oso and Brighton Substations. The project will include the following work: 1. Install two 5.0 MVAR capacitor banks at Plainfield Substation. 2. Replace Vaca Dixon 115/60kV Bank 5 with a larger unit. 3. Replace the limiting elements on the 60kV equipment at Dixon Substation. 4. Re-rate the Woodland - Davis 115kV Line and the Rio Oso - West Sac 115kV Line. 5. Modify the existing special protection schemes (SPS) or add new SPS’s to trip load for select multiple contingencies. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-04 | 123 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 1.8386 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5560779 | T.0000007 | Vaca Dixon Area Reinforcement Project | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2025 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7542-E | 2025-03-12 | Approved | 2025 | Operational | 1 | 2025-11-03 | 2023-12-01 | 2025-11-13 | Bundling Dependencies | Clearances | TRUE | $70,000 ¦ $107,000 | NA ¦ NA | 71.7932 | 95.9597 | 0 | 0 | 0 | 0 | 64.2775 | 31.6822 | 0 | 0 | 0 | 0 | 64.2776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 64.2775 | 7.5156 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
891 | Table Mountain 115 kV RAS |  |  | Chico, Butte | Install a Special Protection System (SPS) to monitor load follows on the three 115 kV lines at the Table Mount end and drop up to 45 MWs of load from Sycamore Creek 115 kV, Nord 115 kV, and Chico B 115 kV Substations beyond certain flow on these lines | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Special Protection Scheme | NERC TPL Standards | NA | 2026-02-11 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.5676 | NA | 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 5 | 5.1001 | Non-IGP | 5746692 | T.0000021 | Table Mountain-Sycamore Creek 115kV | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-10-12 | NA | 2029-04-30 | NA | NA | FALSE | NA | NA ¦ NA | 760.7749 | 11154.2333 | 41.9103 | 45.3864 | 0 | 21.1377 | 60.4497 | 168.9397 | 500 | 1000 | 2000 | 0 | 750.8993 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
892 | Fitch Mtn: Replace limiting term equip |  |  | Sonoma | Reconductor approximately 8 miles of the Fulton-Hopland 60kV Line and 1.3 miles of the Geysers 12-Fulton 230kV Line, rerate another section of the Fulton-Hopland 60kV Line and Fitch Mountain #2 60kV Tap, and upgrade switches and associated equipment at Fitch Mountain Substation. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-12 | 51 | Steady State Power Flow System Analysis | Wires - System Configuration Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.53125 | NA | 60 kV | NA | NA | NA | NA | NA | 5795387 | T.0000039 | Fulton-Fitch Mtn 60kV Reconductor | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2021 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-10-11 | IS/MND | NA | CPUC | NA | PTC: A.15-12-005 | 2015-12-03 | Approved | 2017 | Operational | 1 | 2021-07-23 | 2013-05-01 | 2021-09-15 | Prioritization | NA | FALSE | 5000 | NA ¦ NA | 34.2259 | 34.2259 | 33.8536 | 0.3723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.2259 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 30.7725 | 0.33794 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
893 | WARNERVILLE-BELLOTA: Rec 230 KV Line |  |  | San Joaquin | Reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations. Key construction elements are as follows: • Replace 22.5 miles of the Bellota-Warnerville 230 kV circuit • Replace 19.9 miles of the Bellota-Cottle 230 kV circuit • Replace 2.5 miles of the Cottle-Melones 230 kV circuit • Replace 0.1 mile of the Warnerville-Wilson 230 kV circuit • Upgrade transmission line terminals at Bellota, Cottle, and Warnerville substations | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Policy | Line Termination | NERC TPL Standards | NA | 2026-03-14 | 93 | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | 318 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5756037 | T.0000043 | Bellota-Warnerville 230kV Reinforcement | 8 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2014 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6047-E | 2021-01-06 | Approved | 2021 | Operational | 1 | 2023-01-10 | 2024-12-31 | 2023-04-28 | NA | NA | FALSE | 28000 | NA ¦ NA | 1876.9192 | 1876.9192 | 159.1196 | 557.2565 | 931.845 | 25.6478 | 0.131 | 0 | 0 | 0 | 0 | 0 | 1876.9192 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 1604.3074 | 22.0209 | 0.11252 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
894 | Cottle: Replace Limiting Components |  |  | Oakdale, Stanislaus | Reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations. Key construction elements are as follows: • Replace 22.5 miles of the Bellota-Warnerville 230 kV circuit • Replace 19.9 miles of the Bellota-Cottle 230 kV circuit • Replace 2.5 miles of the Cottle-Melones 230 kV circuit • Replace 0.1 mile of the Warnerville-Wilson 230 kV circuit • Upgrade transmission line terminals at Bellota, Cottle, and Warnerville substations | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Policy | Line Termination | NERC TPL Standards | NA | 2026-02-05 | 11 | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.1 | NA | 115 kV | 318 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5786047 | T.0000043 | Bellota-Warnerville 230kV Reinforcement | 8 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2020 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6047-E | 2021-01-06 | Approved | 2021 | Operational | 1 | 2023-10-30 | 2025-05-01 | 2024-03-31 | NA | NA | FALSE | 28000 | NA ¦ NA | 242.4596 | 242.4596 | 48.1328 | 19.4092 | 105.6335 | 25.1433 | 0.2421 | 0 | 0 | 0 | 0 | 0 | 242.4596 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 238.7806 | 0.23821 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
895 | EDES: Reconduct Fiber Interconnect |  |  | Oakland, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0004580 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-04 | 20 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 2.4009 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 425 | 5.1001 | Non-IGP | 5778946 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E ¦ AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020 ¦ 2022 | Construction (over 75%) | 2 | 2021-11-01 | 2015-03-01 | 2026-04-30 | Project Design | NA | TRUE | $15,000 ¦ $30,000 | NA ¦ NA | 14832.6267 | 15397.2527 | 3307.1917 | 3364.9645 | 2281.3533 | 641.1168 | 2614.7028 | 2051.8901 | 0 | 0 | 0 | 0 | 13345.3625 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil
896 | EASTSHORE: Reconductoring 115 KV |  |  | Hayward, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-04 | 13 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 9.9849 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 425 | NA | NA | 5769866 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E ¦ AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020 ¦ 2022 | Operational | 1 | 2021-11-01 | 2015-03-01 | 2023-08-10 | Prioritization | NA | FALSE | $15,000 ¦ $30,000 | NA ¦ NA | 1935.7122 | 1935.7122 | 741.0506 | 761.8701 | 248.5133 | 0.1613 | 0 | 0 | 0 | 0 | 0 | 0 | 1935.7122 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 1785.6568 | 0.1471 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil
897 | OAKLAND J: Install 115 kV Reconductor |  |  | San Leandro, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-05 | 55 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 1.6572 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 425 | NA | NA | 5767558 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 61 | NA ¦ 5747764 ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E ¦ AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020 ¦ 2022 | Operational | 1 | 2021-09-27 | 2015-03-01 | 2023-09-14 | Prioritization | NA | FALSE | $15,000 ¦ $30,000 | NA ¦ NA | 5282.0588 | 5282.0588 | 1710.2883 | 2272.3859 | 758.5508 | 0.5466 | 0 | 0 | 0 | 0 | 0 | 0 | 5282.0588 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 4952.349 | 0.5076 | -2e-05 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil
898 | GRANT: Support 115 KV Reconductoring |  |  | San Leandro, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-05 | 23 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 1.6572 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 425 | 5.1001 | Non-IGP | 5778947 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E ¦ AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020 ¦ 2022 | Operational | 1 | 2021-09-16 | 2015-03-01 | 2023-10-31 | Project Design | NA | FALSE | $15,000 ¦ $30,000 | NA ¦ NA | 4069.0529 | 4069.0529 | 1947.9742 | 565.0001 | 935.7042 | 88.5793 | 45.8867 | 78.7541 | 0 | 0 | 0 | 0 | 3990.2988 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 3855.8328 | 88.5793 | 45.8867 | 78.7541 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil
899 | SEMITROPIC: Install Bypass |  |  | Kern | Reconductor 14.2 miles of the Semitropic-Midway No. 1 115kV Line. The project expects to improve service reliability in core operations by reconductoring the Semitropic-Midway No. 1 115kV Line that will improve system performance and reliability, which will reduce outages. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-12 | 52 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.2701 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5777099 | T.0000143 | SEMITROPIC-MIDWAY 115KV LINE RECONDUCTOR | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-11-01 | 2016-12-01 | 2020-12-28 | Clearances | NA | FALSE | $15,000 ¦ $20,000 | NA ¦ NA | 239.4286 | 239.4286 | 37.6847 | 3.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.4286 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 31.0364 | 2.5388 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Non-Wires - System DER Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
900 | TERMINAL UPGRADES PASO ROBLES SUB |  |  | El Paso de Robles, San Luis Obispo | This project will construct a new 230/70kV substation (owned and operated by HWT) and an adjacent 70kV substation (owned by PG&E) approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles DPA. Key project elements for the scope include: Competitive Scope (230kV): Awarded to HWT • Construct 230kV portion of Estrella Substation, including one new 230/70kV transformer. • Acquire land rights and permits for substation. • Complete rough grading for both the 230kV and 70kV stations. Non-competitive Scope (70kV): • Construct the 70kV Union substation. • Construct 230kV transmission lines to loop the Cal Flats-Morro Bay 230kV into Estrella Substation. • Construct one (1)-double circuit 70kV line from Union Substation to a tie-in point with the San MiguelPaso Robles 70kV line (10.5 miles). The line includes a common neutral conductor and fiber optic cable. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70kV line between the tie-in point and Paso Robles Substation (six miles). Add a common neutral conductor and fiber optic cable. • Acquire land rights and permits for the 70kV substation and transmission lines connecting to the substation and perfect easements for certain portions of the reconductoring work on the San Miguel-Paso Robles 70kV line. • Build 230kV remote end upgrades at Morro Bay and Cal Flats substations to coordinate with the new Estrella Substation. • Install reverse power relays at Templeton and Union/Estrella substations to avoid reverse power flow from the 70kV system to the 230kV system during certain system conditions. • Install a new dead-end structure and associated switches at Paso Robles Substation to accommodate new conductor size and terminate a new fiber optic cable within the control building. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | New T-Line | NERC TPL Standards | NA | 2026-03-03 | 54 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.6272 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5805506 | T.0000154 | Estrella 230 kV Transmission Substation | 20 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-11-03 | 2019-05-01 | 2027-03-31 | Prioritization | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 452.3815 | 1307.9929 | 0 | 0 | 25.9901 | 9.8753 | 399.545 | 377.841 | 494.7414 | 0 | 0 | 0 | 435.4105 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra, Estrella 230 kV Transmission Substation | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
901 | MERCY SPRINGS & CANAL SS UPGRADES |  |  | Los Banos, Merced | The Oro Loma 70 kV Area Reinforcement project will reconductor 70 kV lines in the Oro Loma area to help ensure reliable electric service to customers in the Merced County. The project will reconductor 2.4 miles of the Los Banos - Livingston Jct – Canal 70 kV Line, from Los Banos to Santa Nella substations and 10.8 miles of the Mercy Springs SW STA – Canal – Oro Loma 70 kV Line, from Mercy Springs SW STA to Canal Substation. The conductor should be capable of handling at least 825 Amps and 975 Amps during summer normal and emergency conditions, respectively. Associated substation terminal equipment will be upgraded as needed to meet the ratings of the new line conductor. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2025-10-01 | 41 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.7007 | NA | 70 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5767200 | T.0000157 | Oro Loma 70kV Reinforcement | 7 | 61 | NA ¦ 5746747 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-10-12 | 2015-05-01 | 2027-12-30 | Prioritization | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 87.2628 | 1971.897 | 0 | 0 | 0 | 0 | 9.8159 | 397.7081 | 1402.1925 | 1000 | 0 | 0 | 74.1889 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
902 | LOS BANOS & SANTE NELLA SS UPGRADES |  |  | Fresno | The Oro Loma 70 kV Area Reinforcement project will reconductor 70 kV lines in the Oro Loma area to help ensure reliable electric service to customers in the Merced County. The project will reconductor 2.4 miles of the Los Banos - Livingston Jct – Canal 70 kV Line, from Los Banos to Santa Nella substations and 10.8 miles of the Mercy Springs SW STA – Canal – Oro Loma 70 kV Line, from Mercy Springs SW STA to Canal Substation. The conductor should be capable of handling at least 825 Amps and 975 Amps during summer normal and emergency conditions, respectively. Associated substation terminal equipment will be upgraded as needed to meet the ratings of the new line conductor. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-10 | 73 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 3.8637 | NA | 70 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5777179 | T.0000157 | Oro Loma 70kV Reinforcement | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-02-16 | 2015-05-01 | 2028-05-23 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 2754.7634 | 4847.7911 | 1595.3007 | 14.5047 | 0 | 16.7943 | 200.2535 | 292.034 | 1300 | 200 | 0 | 0 | 2714.5349 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
903 | SANTA NELLA SUB UPGRADES |  |  | Santa Nella CDP, Merced | The Oro Loma 70 kV Area Reinforcement project will reconductor 70 kV lines in the Oro Loma area to help ensure reliable electric service to customers in the Merced County. The project will reconductor 2.4 miles of the Los Banos - Livingston Jct – Canal 70 kV Line, from Los Banos to Santa Nella substations and 10.8 miles of the Mercy Springs SW STA – Canal – Oro Loma 70 kV Line, from Mercy Springs SW STA to Canal Substation. The conductor should be capable of handling at least 825 Amps and 975 Amps during summer normal and emergency conditions, respectively. Associated substation terminal equipment will be upgraded as needed to meet the ratings of the new line conductor. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-04 | 41 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.1314 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813982 | T.0000157 | Oro Loma 70kV Reinforcement | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-02-16 | 2015-05-01 | 2028-05-23 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 9.6985 | 9.6985 | 0 | 0 | 0 | 0 | 0.901 | 8.7975 | 0 | 0 | 0 | 0 | 0.901 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
904 | HERNDON SUB: REPL230kV SW267,269,201,203 |  |  | Fresno, Fresno | Replace Switch Nos. 267, 269, 201 and 203 at Herndon Substation, to provide additional transmission capacity | Substation - Switch | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-12 | 58 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 13.3414 | NA | 230 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5756014 | T.0000252 | HERNDON: REPL 230KV SW 267,269,201,203 | 1 | 61 | NA ¦ 5767970 ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2014 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-10-21 | 2015-05-31 | 2020-01-24 | Project Design | NA | FALSE | $1,000 ¦ $2,000 | NA ¦ NA | 1258.6064 | 1258.6064 | 133.8655 | -6.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1258.6064 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 124.0673 | -5.7406 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
905 | SOUTH OF PALERMO - PALERMO SUB |  |  | Palermo CDP, Butte | This project will reinforce 80.3 circuit miles of the 115kV transmission lines between Palermo, Pease, Bogue, and Rio Oso substations with 477 kcmil steel-supported aluminum conductors with emergency capability of 970 Amps. This includes the installation of five Supervisory Control and Data Acquisition (SCADA) controlled transmission line switches on the Palermo – Pease, Pease – Rio Oso, Palermo – Bogue, and Bogue – Rio Oso 115kV lines to improve reliability and service restoration time. Key construction elements are as follows:  Replacement of 238 steel electric transmission lattice towers with 238 new hybrid tubular steel poles (HTSP), which include a concrete foundation and steel pole on top  Replacement of 21 steel electric transmission lattice towers with 21 tubular steel poles (TSP).  Replacement of 45 steel electric transmission lattice steel poles with new lattice steel poles.  Replacement of 2 steel electric transmission lattice towers with new steel lattice towers.  Reinforcement of 61 steel electric transmission lattice tower foundations with screw anchors.  Reinforcement of 23 steel electric transmission lattice towers with 19 top or waist cage extensions.  Upgrade 8 transmission relay terminals at 4 surrounding substations. This project has been divided into three construction phases as follows:  Phase 1: Rio Oso Substation to Pease Junction  Phase 2: Pease Substation to Palermo Substation  Phase 3: Bogue Substation to Bogue Junction | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-13 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.0464 | NA | 115 kV | 180 | NA | NA | NA | NA | 5767550 | T.0000450 | South of Palermo 115kV Reinforcement | 8 | 61 | NA ¦ 5763937 ¦ NA ¦ NA | FALSE | 2016 | Project Management Governance Standard | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-11-01 | 2014-05-01 | 2019-04-25 | Prioritization | NA | FALSE | $80,000 ¦ $100,000 | NA ¦ NA | 1817.9 | 1817.9 | 5.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1817.9 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 5.0049 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
906 | POTRERO A-X #2 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | NA | 2026-03-12 | 76 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5798619 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-04-27 | 2025-06-20 | 2030-09-30 | Prioritization | NA | FALSE | 191100 | NA ¦ NA | 62.8801 | 1504.4514 | 0.708 | 39.8149 | 7.9864 | 1.5644 | 0.9522 | 168.0004 | 0 | 0 | 0 | 0 | 51.026 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
907 | MISSION A-X #2 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | NA | 2026-02-05 | 76 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.83366 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5798620 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-04-27 | 2025-06-20 | 2030-09-30 | Prioritization | NA | FALSE | 191100 | NA ¦ NA | 36.6269 | 1478.1982 | 0.708 | 21.2856 | 3.5921 | 0.9083 | 0.4992 | 165.7801 | 0 | 0 | 0 | 0 | 26.9931 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
908 | LARKIN A-Y #3 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | NA | 2026-02-03 | 56 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 1.0478 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5798621 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-04-27 | 2025-06-20 | 2030-09-30 | Prioritization | NA | FALSE | 191100 | NA ¦ NA | 37.6158 | 1479.1871 | 1.4266 | 21.9261 | 3.4823 | 0.9527 | 0.5072 | 165.4672 | 0 | 0 | 0 | 0 | 28.2949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
909 | POTRERO A-Y #3 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | NA | 2026-03-12 | 56 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5801471 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-04-27 | 2025-06-20 | 2030-09-30 | Prioritization | NA | FALSE | 191100 | NA ¦ NA | 79.1038 | 1520.6751 | 0 | 8.9742 | 58.1951 | 2.3907 | 0 | 165.69 | 0 | 0 | 0 | 0 | 69.5601 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
910 | MISSION X-Y #2 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | NA | 2026-02-05 | 76 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.83366 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5801472 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-04-27 | 2025-06-20 | 2030-09-30 | Prioritization | NA | FALSE | 191100 | NA ¦ NA | 19.0959 | 1460.6672 | 0 | 6.6395 | 0.7987 | 0.2647 | 0 | 167.5392 | 0 | 0 | 0 | 0 | 7.703 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
911 | LARKIN X-Y #2 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | NA | 2026-02-03 | 76 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 1.0478 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5801473 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-04-27 | 2025-06-20 | 2030-09-30 | Prioritization | NA | FALSE | 191100 | NA ¦ NA | 33.6163 | 1475.1876 | 0 | 6.0017 | 17.7943 | 0.8469 | 0 | 165.1196 | 0 | 0 | 0 | 0 | 24.643 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
912 | Kern 115kV Reinforce-Magunden CB122 |  |  | East Niles CDP, Kern | The Project proposes to reconductor approximately 38 circuit miles of various 115 kV lines serving Bakersfield area in Kern County. The scope of the project include reconductoring 3.8 miles of the Kern PP-Westpark Nos. 1 and 2 115 kV Lines; 16.5 miles of the Kern-Magunden-Witco 115 kV Line; 3.5 miles of the Westpark-Magunden 115 kV Line; 5.0 miles of the Kern-Lamont 115 kV Line from Kern PP to Tevis Jct.; 5.0 miles of the Kern-Stockdale 115 kV line from Kern PP to Tevis Jct. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-09 | 32 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 15.2256 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5784620 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 8 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-11-06 | 2016-03-01 | 2030-09-19 | Prioritization | NA | FALSE | $40,000 ¦ $65,000 | NA ¦ NA | 59.276 | 1209.276 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 100 | 50 | 0 | 59.276 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
913 | BAKERSFIELD SUB: UPGRADE 230KV |  |  | Bakersfield, Kern | This project will loop the Bakersfield 230kV Substation onto the Midway-Kern No. 2 230kV Line and reconductor approximately 14 circuit miles of the Bakersfield Nos. 1 and 2 230kV Tap Lines to provide operational flexibility and service reliability in the area. The project scope of work includes the following: o Loop Bakersfield 230kV substation onto the Midway – Kern No. 2 230kV line; o Upgrade terminal equipment at Bakersfield Substation, as necessary, to accommodate the rating of the transmission line conductor; o Reconductor 14 circuit miles of the Bakersfield Nos. 1 and 2 230kV Taps; o Upgrade distribution equipment to accommodate transmission work; o Install protection and telecommunication upgrades | Substation - Line Termination | Upgrade/Retrofit | NA | T.0000220 ¦T.0001650 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | 44 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.6195 | NA | 230 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.101 | Non-IGP | 5767357 | T.0003202 | Bakersfield-Kern Taps 1&2 230kV Recon | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2017 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5924-E | 2020-08-19 | Approved | 2020 | Engineering more than 50% complete | 3 | 2027-07-27 | 2019-05-01 | 2028-08-17 | Prioritization | NA | FALSE | $60,000 ¦ $90,000 | NA ¦ NA | 1012.0743 | 7751.8217 | 0.3879 | 0 | 0 | 202.4627 | 51.5296 | 484.0493 | 4247.667 | 1735.24 | 0 | 0 | 978.034 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ NA
914 | Bakersfield Sub: Upgrade 230KV |  |  | Bakersfield, Kern | This project will loop the Bakersfield 230kV Substation onto the Midway-Kern No. 2 230kV Line and reconductor approximately 14 circuit miles of the Bakersfield Nos. 1 and 2 230kV Tap Lines to provide operational flexibility and service reliability in the area. The project scope of work includes the following: o Loop Bakersfield 230kV substation onto the Midway – Kern No. 2 230kV line; o Upgrade terminal equipment at Bakersfield Substation, as necessary, to accommodate the rating of the transmission line conductor; o Reconductor 14 circuit miles of the Bakersfield Nos. 1 and 2 230kV Taps; o Upgrade distribution equipment to accommodate transmission work; o Install protection and telecommunication upgrades | Substation - Line Termination | Upgrade/Retrofit | NA | T.0000220 ¦T.0001650 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.6195 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5809170 | T.0003202 | Bakersfield-Kern Taps 1&2 230kV Recon | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2024 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5924-E | 2020-08-19 | Approved | 2020 | Engineering more than 50% complete | 3 | 2027-06-29 | 2019-05-01 | 2029-01-25 | Prioritization | Project Design | FALSE | $60,000 ¦ $90,000 | NA ¦ NA | 1.1771 | 637.2478 | 0 | 0 | 0 | 1.1701 | 0.007 | 36.7608 | 0 | 0 | 0 | 0 | 1.1771 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ NA
915 | RMR: SAN JOSE B: EM REPL: TRIMBLE-SJ B L |  |  | San Jose, Santa Clara | The project scope is to install modular power flow control systems deployed on a dedicated bank structure at Vaca Dixon Substation (or adjacent property). The project submitted by Smart Wire entail installing modular power flow control system devices electrically in series with the Vaca Dixon – Lakeville and Vaca Dixon – Tulucay 230 kV lines on PG&E property at Vaca Dixon Substation. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0010902 ¦ T.0010873 ¦ T.0010874 ¦ T.0010875 ¦ T.0010908 | Economic | Line Termination | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.1017 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5779598 | T.0003876 | Trimble-San Jose B 115 kV Line Rerate | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2018 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-10-16 | 2018-05-01 | 2019-02-25 | Prioritization | NA | FALSE | 250 | NA ¦ NA | 2647.422 | 2647.422 | 457.3456 | 1.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2647.422 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 391.256 | 1.1905 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
916 | RMR: NASA-AMES 115KV LINE #1 CB INSTALL |  |  | Mountain View, Santa Clara | The project proposes to reconnect the 115 kV lines from Mountain View and Whisman Substations into the 115 kV bus at Ames Substation. The work will require protection upgrades at the substations and also will require circuit breaker replacement at Mountain and Whisman due to increased fault duty at those substations. This project was one of several projects that are needed to eliminate the need to have a reliability must run (RMR) contract with Calpine’s Metcalf Energy Center. Also, to address substation bus reliability issues at Ames Substation, the project will also install circuit breakers at Ames on the two 115 kV lines that serve the NASA Ames facility. | Substation - Circuit Breaker | New | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-05 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.8814 | NA | 115 kV | 137 | NA | NA | 5.1001 | Non-IGP | 5781026 | T.0003920 | RMR - Mtn View-Whisman-Ames Project | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2019 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-02-19 | 2019-05-31 | 2019-04-26 | NA | NA | TRUE | 14100 | NA ¦ NA | 1837.0685 | 1863.9368 | 127.0634 | 54.8234 | 11.3285 | 25.7418 | 17.0499 | 27.2502 | 0 | 0 | 0 | 0 | 1836.6866 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 124.0746 | 53.5337 | 11.0618 | 25.1363 | 16.6487 | 0.37289 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
917 | RMR: NASA-AMES 115KV LINE #2 CB INSTALL |  |  | Mountain View, Santa Clara | The project proposes to reconnect the 115 kV lines from Mountain View and Whisman Substations into the 115 kV bus at Ames Substation. The work will require protection upgrades at the substations and also will require circuit breaker replacement at Mountain and Whisman due to increased fault duty at those substations. This project was one of several projects that are needed to eliminate the need to have a reliability must run (RMR) contract with Calpine’s Metcalf Energy Center. Also, to address substation bus reliability issues at Ames Substation, the project will also install circuit breakers at Ames on the two 115 kV lines that serve the NASA Ames facility. | Substation - Circuit Breaker | New | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-05 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.8814 | NA | 115 kV | 137 | NA | NA | NA | NA | 5781027 | T.0003920 | RMR - Mtn View-Whisman-Ames Project | 6 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2019 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-04-29 | 2019-05-31 | 2019-06-24 | NA | NA | FALSE | 14100 | NA ¦ NA | 1195.5181 | 1195.5181 | 4.9562 | 10.8232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.5181 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 4.8427 | 10.5754 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
918 | RAVENSWOOD: Repl T-Line Structure |  |  | Menlo Park, San Mateo | The project will replace the two line termination dead-end structures and associated switches at Ravenswood Substation for the Ravenswood – Cooley Landing 115 kV Lines. This will eliminate a potential failure of either structure, which could result in an extended outage of the line and could impact personnel safety in the substation. This work will also enable the structures to support the new conductor to be installed on the lines as part of the Ravenswood – Cooley Landing 115 kV Reconductoring Project, which is expected to start work in Fall 2020. The substation project is expected to be released to operations by June 30, 2020. | Substation - Structure | Upgrade/Retrofit | NA | NA | Asset Condition | Line Termination | NA | NA | 2026-03-05 | 62 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | NA | 230 kV | 21 | 8. Compliance/Commitments With Low Safety Risk | 11 | NA | NA | 5782143 | T.0004285 | Ravenswood T-Line Structure Replacement | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-02 | 2020-06-22 | 2021-11-17 | Prioritization | NA | FALSE | 2300 | NA ¦ NA | 2191.726 | 2191.726 | 727.9613 | 134.7235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2191.726 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1825.2846 | 118.2158 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
919 | PINEDALE SUB: RECONDUCTOR 115KV LINE |  |  | Fresno, Fresno | This project proposes to reconductor roughly 8 circuit miles (4 miles of double circuit transmission line) between Pinedale Jct and Bullard Substation on the Herndon - Bullard Nos. 1 and 2 115 kV lines. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0003307 ¦ T.0003310 ¦ T.0003306 ¦ T.0003309 ¦ T.0003311 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-10 | 18 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.2566 | NA | 115 kV | 69 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5787498 | T.0004347 | Herndon - Bullard Nos. 1 and 2 115 kV RC | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-14 | 2021-01-01 | 2027-11-02 | Prioritization | NA | TRUE | $6,000 ¦ $8,000 | NA ¦ NA | 73.7827 | 996.9926 | 2.8017 | 3.0339 | 0 | 0 | 25.3655 | 80.199 | 846.6872 | 0 | 0 | 0 | 70.1063 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
920 | BULLARD SUB: RECONDUCTOR 115KV LINE |  |  | Fresno, Fresno | This project proposes to reconductor roughly 8 circuit miles (4 miles of double circuit transmission line) between Pinedale Jct and Bullard Substation on the Herndon - Bullard Nos. 1 and 2 115 kV lines. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0003307 ¦ T.0003310 ¦ T.0003306 ¦ T.0003309 ¦ T.0003311 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | 18 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.363 | NA | 115 kV | 69 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5787499 | T.0004347 | Herndon - Bullard Nos. 1 and 2 115 kV RC | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-07-27 | 2021-01-01 | 2027-12-17 | Prioritization | NA | TRUE | $6,000 ¦ $8,000 | NA ¦ NA | 124.3149 | 1677.4483 | 5.5659 | 6.024 | 0 | 1.3643 | 29.2978 | 102.0899 | 1454.1443 | 0 | 0 | 0 | 119.4967 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
921 | Moraga-Casto Valley 230 kV Line Cap In |  |  | Orinda, Contra Costa | The project scope of work involves upgrading the limiting substation equipment (jumper conductors and wave traps) on the Moraga-Castro Valley and Castro Valley-Newark 230 kV lines to utilize their full conductor ratings. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | 72 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 15.8714 | NA | 230 kV | 180 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.1001 | Non-IGP | 5747775 | T.0004421 | Moraga-Castro Valley 230 kV Capacity | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2014 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-08-27 | 2013-05-01 | 2025-03-26 | Prioritization | NA | TRUE | $1,000 ¦ $5,000 | NA ¦ NA | 1318.9962 | 1318.9962 | 14.5695 | 58.3383 | 289.616 | 542.9682 | 304.3439 | 11.7583 | 0 | 0 | 0 | 0 | 1307.2379 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1183.4538 | 10.5613 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
922 | South of Mesa Upgrade - Sisquoc Sub |  |  | Santa Barbara | This project proposes to upgrade approximately 21.3 miles of conductor on the Sisquoc – Santa Ynez SW STA 115 kV Line, install 20 Mega Volt-ampere reactive (MVAR) shunt capacitors at Cabrillo Substation and install Remedial Action Scheme (RAS) (formerly known as Special Protection Scheme (SPS)) on the Sisquoc – Santa Ynez SW STA 115 kV Line. Completion of this project is needed to improve the electric transmission system reliability and operational flexibility in the Santa Barbara County. This project will be funded under Major Work Category (MWC) 60, Electric Transmission Line Capacity and 61, Electric Transmission Substation Capacity. The project has a Risk Informed Budget Allocation (RIBA) score of 137. The RIBA score is based on the impact and frequency of three risk categories: safety, reliability and environmental. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-03 | 37 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.9084 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5792241 | T.0004832 | South Of Mesa Upgrade Project | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-08-02 | 2023-12-31 | 2027-12-02 | Prioritization | NA | TRUE | $29,600 ¦ $59,200 | NA ¦ NA | 26.2698 | 919.9089 | 1.0059 | 0 | 0 | 0 | 2.468 | 89.6269 | 797.8087 | 6.793 | 0 | 0 | 25.6803 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
923 | South of Mesa Upgrade - Santa Ynez SS |  |  | Santa Barbara | This project proposes to upgrade approximately 21.3 miles of conductor on the Sisquoc – Santa Ynez SW STA 115 kV Line, install 20 Mega Volt-ampere reactive (MVAR) shunt capacitors at Cabrillo Substation and install Remedial Action Scheme (RAS) (formerly known as Special Protection Scheme (SPS)) on the Sisquoc – Santa Ynez SW STA 115 kV Line. Completion of this project is needed to improve the electric transmission system reliability and operational flexibility in the Santa Barbara County. This project will be funded under Major Work Category (MWC) 60, Electric Transmission Line Capacity and 61, Electric Transmission Substation Capacity. The project has a Risk Informed Budget Allocation (RIBA) score of 137. The RIBA score is based on the impact and frequency of three risk categories: safety, reliability and environmental. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-04 | 37 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.40907 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5792240 | T.0004832 | South Of Mesa Upgrade Project | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-06-22 | 2023-12-31 | 2028-07-14 | Prioritization | NA | FALSE | $29,600 ¦ $59,200 | NA ¦ NA | 75.5439 | 12311.64 | 0.3794 | 0 | 0 | 0 | 5.574 | 74.2848 | 1053.3585 | 11110.0155 | 0 | 0 | 73.9811 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
924 | Shoofly for Willow Pass 115KV Pittsburg |  |  | Pittsburg, Contra Costa | This project will provide the capacity increase required to meet the new business loads coming into the area. The project scope will: • Reconfigure the 115 kV high side bus to a ring bus. • Replace Bank 1 with a 115/21 kV 75 MVA transformer. • Relocate existing Bank 3, 115/21 kV 30 MVA transformer to a new foundation compatible with 75 MVA bank for future upgrades. • Install three 21 kV feeders. • Install two 21/12 kV, 7500 kVA auto banks. • Reconfigure the existing BART Bank on the new 115 kV ring bus at Willow Pass substation. • Install Supervisory Control and Data Acquisition system for the new substation bank and breakers. • Install one new 60 kV transmission switch to interconnect structure 000/006 on Willow Pass-Contra Costa 60 kV and structure 015/281 on Christie-Willow Pass 60 kV at the corner of Willow Pass Road and Port Chicago Highway. • Remove sections of Willow Pass-Contra Costa 60 kV and Christie-Willow Pass 60 kV from the structures towards Willow Pass substation. • Install a new Microwave system from Willow Pass to Pittsburg to comply with redundancy requirements for the Set A and Set B protection relays. Execution of this project will improve the future capacity expansion, operational flexibility, and reliability of the Willow Pass substation. | Transmission Line - Conductor | New | NA | NA | Load Growth | Line Termination | NA | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 0.72358 | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5815498 | T.0005844 | Willow Pass Sub_Repl Willow Pass Bk1 | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-11-18 | 2025-07-31 | 2025-12-15 | NA | NA | FALSE | 42500 | NA ¦ NA | 38.9259 | 38.9259 | 0 | 0 | 0 | 0 | 36.0136 | 2.9124 | 0 | 0 | 0 | 0 | 36.0135 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
925 | Wilson-Oro Loma 115 kV Reconductoring |  |  | Fresno | Reconductor approximately 9 circuit miles between Wilson and El Nido on the Wilson-Oro Loma 115 kV Line with a larger conductor to achieve at least 650 Amps of summer emergency rating. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-10 | 77 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.8637 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5791342 | T.0006016 | Wilson-Oro Loma 115 kV Reconductoring | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2022 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-11-04 | 2026-12-31 | 2028-03-17 | Project Design | NA | FALSE | $11,300 ¦ $22,700 | NA ¦ NA | 7.3462 | 961.2185 | 0 | 0 | 0 | 0 | 4.503 | 156.7157 | 800 | 0 | 0 | 0 | 4.5029 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
926 | East Shore: Reconfigure 230 kV Bus |  |  | Hayward, Alameda | Reroute Russell City-East Shore and San Mateo-East Shore 230 kV lines at PG&E's East Shore 230 kV Substation | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0004581 ¦ T.0006960 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-04 | 13 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 9.9849 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5791251 | T.0006021 | East Shore - Reconfigure 230 kV Bus | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2022 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-05-07 | 2024-12-31 | 2027-08-04 | Prioritization | NA | FALSE | $2,000 ¦ $4,000 | NA ¦ NA | 0 | 4311 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 4308 | 3 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
927 | Newark: Add CB to Bank 7 |  |  | Fremont, Alameda | Add a second high side circuit breaker to the Newark 230/115 kV transformer bank #7 | Substation - Transformer | New | NA | T.0003446 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | 27.7611 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5791252 | T.0006022 | Newark - Add CB to Bank 7 | 1 | 61 | NA ¦ EX113211 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-04-15 | 2024-12-31 | 2027-07-13 | Prioritization | NA | TRUE | $3,000 ¦ $6,000 | NA ¦ NA | 130.0448 | 2569.5015 | 0 | 0 | 0 | 2.2501 | 112.8559 | 490.5719 | 1935.5837 | 35 | 0 | 0 | 115.1059 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
928 | CONTROL BLDG BATTERY BDLG DESIGN |  |  | Antioch, Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence ¦ Corrosion |  | NA | 19.1042 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5551485 | T.0008048 | Contra Costa PP Line Swaps | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-11 | 2025-05-01 | 2025-03-12 | NA | NA | FALSE | $5,000 ¦ $10,000 | NA ¦ NA | 912.6503 | 912.6503 | 0 | 1.1957 | 391.6311 | 437.7946 | 64.0891 | 17.9397 | 0 | 0 | 0 | 0 | 894.7106 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 392.8268 | 437.7946 | 64.0891 | 17.9397 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
929 | CONTRA COSTA PP SW STA PHASE 1 |  |  | Antioch, Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | 61 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence ¦ Corrosion |  | NA | 19.1042 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5800033 | T.0008048 | Contra Costa PP Line Swaps | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-12-06 | 2025-05-01 | 2025-05-30 | NA | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 24096.7429 | 24363.2093 | 0 | 201.321 | 2604.3292 | 14966.2223 | 6222.6758 | 368.6609 | 0 | 0 | 0 | 0 | 23994.5483 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 23549.4142 | 100.1845 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
930 | CONTRA COSTA PP SW STA PHASE 2 |  |  | Antioch, Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 19.1042 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5803600 | T.0008048 | Contra Costa PP Line Swaps | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-06-09 | 2025-05-01 | 2026-02-24 | Clearances | Workforce | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 4914.434 | 7130.3997 | 0 | 0 | 7.8747 | 416.6472 | 3643.7944 | 3062.0835 | 0 | 0 | 0 | 0 | 4068.3162 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 4740.6469 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
931 | Valley Home: Sub Terminal Line Eq |  |  | San Joaquin | This project will increase operating flexibility, load serving capability, customer reliability, eliminate contingency overloads, and harden the transmission system by performing the following scope: • Reconductor 1.3 circuit miles between Riverbank Junction Switching Station and Structure 035/212 of the Stanislaus – Melones Switching Station–Riverbank Junction Switching Station 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Reconductor 1.8 circuit miles between Riverbank Junction Switching Station and Valley Home Tap (038/233) of the Riverbank Switching Station – Ripon 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Reconductor 3.1 circuit miles between Stanislaus - Manteca #2 035/212 and Stanislaus - Manteca #2 038/233 of the Stanislaus - Manteca #2 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Design for OPGW and install OPGW Peaks (do not install OPGW at this time) • Include all open maintenance tags within the project scope where applicable (including replacing Bellota-Riverbank Junction SW-179, Notification 121744057) • Replace structures, all insulators and insulator hardware to accommodate the increase in conductor size | Substation - Line Termination | Upgrade/Retrofit | NA | T.0004301 ¦ T.0007979 ¦ T.0004515 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-04 | 90 | Steady State Power Flow System Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3993 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5563819 | T.0008743 | Riverbank-Ripon - Line Reconductor | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2026 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7732-E | 2025-10-15 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-06-01 | 2028-05-01 | 2026-06-10 | NA | NA | TRUE | $6,800 ¦ $13,600 | NA ¦ NA | 2.6202 | 26.1202 | 0 | 0 | 0 | 0 | 0 | 26.1202 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
932 | Riverbank Jct SWSTA: Terminal Line Equip |  |  | Stanislaus | This project will increase operating flexibility, load serving capability, customer reliability, eliminate contingency overloads, and harden the transmission system by performing the following scope: • Reconductor 1.3 circuit miles between Riverbank Junction Switching Station and Structure 035/212 of the Stanislaus – Melones Switching Station–Riverbank Junction Switching Station 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Reconductor 1.8 circuit miles between Riverbank Junction Switching Station and Valley Home Tap (038/233) of the Riverbank Switching Station – Ripon 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Reconductor 3.1 circuit miles between Stanislaus - Manteca #2 035/212 and Stanislaus - Manteca #2 038/233 of the Stanislaus - Manteca #2 115kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating • Design for OPGW and install OPGW Peaks (do not install OPGW at this time) • Include all open maintenance tags within the project scope where applicable (including replacing Bellota-Riverbank Junction SW-179, Notification 121744057) • Replace structures, all insulators and insulator hardware to accommodate the increase in conductor size | Substation - Line Termination | Upgrade/Retrofit | NA | T.0004301 ¦ T.0007979 ¦ T.0004515 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-05 | 90 | Steady State Power Flow System Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.80994 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5817003 | T.0008743 | Riverbank-Ripon - Line Reconductor | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2026 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7732-E | 2025-10-15 | Approved | 2025 | Operational | 1 | 2025-12-08 | 2028-05-01 | 2025-12-15 | NA | NA | TRUE | $6,800 ¦ $13,600 | NA ¦ NA | 12.0769 | 12.7749 | 0 | 0 | 0 | 0 | 0.0929 | 12.6819 | 0 | 0 | 0 | 0 | 0.0929 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
933 | MORMON: Terminal Upgrades |  |  | San Joaquin | The project will increase operating flexibility, load serving capability, customer reliability, eliminate normal overloads and improve asset health by performing the following scope: • Rebuild 6.2 circuit miles between Weber (000/004) and Mormon (006/103) of the Weber - Mormon Jct. 60 kV Line and conductor with a larger conductor to achieve at least 742 Amps of summer interior emergency rating. • New poles will be sized to accommodate future distribution under build conductor. • Upgrade substation terminal equipment to achieve full conductor capacity, if needed. • Include all open maintenance tags within the project scope where applicable. • When replacing structures, all insulators and insulator hardware should be replaced. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-02 | 126 | Steady State Power Flow System Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.3132 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5563496 | T.0008749 | Weber-Mormon Jct Reconductor | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7813-E | 2026-01-15 | Approved | 2026 | Engineering more than 50% complete | 3 | 2026-06-01 | 2027-05-01 | 2026-06-15 | NA | NA | TRUE | $9,300 ¦ $18,600 | NA ¦ NA | 31.4918 | 56.8005 | 0 | 0 | 0 | 0 | 21.4313 | 35.3692 | 0 | 0 | 0 | 0 | 21.4313 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
934 | Borden Sub: Line Termination |  |  | Madera | This project proposes to reconductor roughly 13 circuit miles of the Borden - Coppermine 70 kV Line and to install a voltage support device in the area. This will provide additional transmission capacity to serve electric customers in Madera and Fresno Counties. The project scope of work includes following: •Reconductor roughly 9.5 circuit miles of line between Borden and Cassidy Substations (from Pole 19/10A to Cassidy Substation) on the Borden-Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 700 Amps during summer normal conditions •Reconductor roughly 3.6 circuit miles of line between Cassidy and Coppermine Substations (from Pole 03/07 to Coppermine Substation) on the Borden - Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 500 Amps during summer normal conditions. •Remove any limiting components to achieve the full conductor capability •Install 20 MVar voltage support device at Coppermine Substation. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-16 | 63 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 7.1874 | NA | 70 kV | NA | NA | NA | 5.101 | Non-IGP | 5815738 | T.0008870 | Coppermine 70 kV Reinforcement Project | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-01-04 | 2027-05-01 | 2027-05-11 | NA | NA | FALSE | $15,800 ¦ $31,600 | NA ¦ NA | 35.1845 | 35.1845 | 0 | 0 | 0 | 0 | 31.4485 | 3.736 | 0 | 0 | 0 | 0 | 31.4485 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
935 | Coppermine 70 kV Reinforcement Sub |  |  | Madera | This project proposes to reconductor roughly 13 circuit miles of the Borden - Coppermine 70 kV Line and to install a voltage support device in the area. This will provide additional transmission capacity to serve electric customers in Madera and Fresno Counties. The project scope of work includes following: •Reconductor roughly 9.5 circuit miles of line between Borden and Cassidy Substations (from Pole 19/10A to Cassidy Substation) on the Borden-Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 700 Amps during summer normal conditions •Reconductor roughly 3.6 circuit miles of line between Cassidy and Coppermine Substations (from Pole 03/07 to Coppermine Substation) on the Borden - Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 500 Amps during summer normal conditions. •Remove any limiting components to achieve the full conductor capability •Install 20 MVar voltage support device at Coppermine Substation. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-16 | 63 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 7.1874 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5803380 | T.0008870 | Coppermine 70 kV Reinforcement Project | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-11-18 | 2027-05-01 | 2028-05-16 | Material | NA | FALSE | $15,800 ¦ $31,600 | NA ¦ NA | 150.7654 | 2786.9984 | 0 | 0 | 0 | 0 | 132.2828 | 816.7049 | 400 | 0 | 0 | 0 | 132.2828 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
936 | BORDEN-CASSIDY: LINE TERMINATION |  |  | Fresno ¦ Fresno, Fresno ¦ Madera ¦ Madera Ranchos CDP, Madera ¦ Rolling Hills CDP, Madera | This project proposes to reconductor roughly 13 circuit miles of the Borden - Coppermine 70 kV Line and to install a voltage support device in the area. This will provide additional transmission capacity to serve electric customers in Madera and Fresno Counties. The project scope of work includes following: •Reconductor roughly 9.5 circuit miles of line between Borden and Cassidy Substations (from Pole 19/10A to Cassidy Substation) on the Borden-Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 700 Amps during summer normal conditions •Reconductor roughly 3.6 circuit miles of line between Cassidy and Coppermine Substations (from Pole 03/07 to Coppermine Substation) on the Borden - Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 500 Amps during summer normal conditions. •Remove any limiting components to achieve the full conductor capability •Install 20 MVar voltage support device at Coppermine Substation. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2025-09-12 | 63 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | 70 kV | NA | NA | NA | 1.0001 | Non-IGP | 5815045 | T.0008870 | Coppermine 70 kV Reinforcement Project | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-11-23 | 2027-05-01 | 2028-05-16 | Material | NA | FALSE | $15,800 ¦ $31,600 | NA ¦ NA | 58.8241 | 2048.6747 | 0 | 0 | 0 | 0 | 40.8866 | 1149.6195 | 400 | 0 | 0 | 0 | 40.8866 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
937 | Cortina Switch Replacement |  |  | Colusa | The Delevan – Cortina 230 kV transmission line, located in Colusa county, is 18.0 miles long and supported by 122 structures. The Delevan – Cortina 230 kV line is a critical component of the 230 kV corridor in the North Valley connecting the Round Mountain and Vaca-Dixon substations. This project will help facilitate the delivery of an additional 437 MW of renewable generation and energy storage to PG&E’s local grid. The project scope of work includes: • Reconductor approximately 17.7 miles of the Delevan – Cortina 230 kV Line with a conductor able to achieve at least 1517 Amps of summer interior emergency rating. The use of Aluminum conductor composite reinforced (ACCR) or Aluminum conductor composite core (ACCC) conductors will be investigated to minimize unnecessary structure replacement. • Conduct a field verification to determine if the existing structures will need to be replaced, repaired or recoated. • Replace all insulators and insulator hardware. When reinsulating and reconductoring on double circuit structures, the scope is limited to insulators and hardware on the subject line. • Upgrade terminal equipment at Delevan and Cortina substations, as needed, to accommodate transmission line conductor capacity. • Include all open maintenance tags within the project scope where applicable. | Substation - Switch | Upgrade/Retrofit | NA | NA | Policy | Line Termination | NERC TPL Standards | NA | 2026-03-06 | 13 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.7436 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5809984 | T.0009013 | Delevan - Cortina Line Reconductoring | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-11-01 | 2028-12-01 | 2027-12-28 | NA | NA | TRUE | $17,700 ¦ $35,400 | NA ¦ NA | 284.4544 | 1859.6862 | 0 | 0 | 0 | 45.9487 | 211.8048 | 295.3291 | 1247.2464 | 0 | 0 | 0 | 257.7536 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
938 | Dixon Landing: Newark-Dixon Lnding 115kV |  |  | Fremont, Alameda | The revised scope aims to reconductor the following 115 kV lines using advanced conductors to achieve a summer emergency rating of 3,000 Amps or higher: Piercy-Metcalf, Swift-Metcalf, Newark-Dixon Landing, and McKee-Piercy. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0003803 ¦ T.0005211 ¦ T.0009571 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | 30 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.79979 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561379 | T.0009536 | Dixon Landing 115 kV Upgrade | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-10 | 2008-12-31 | 2028-07-25 | Scope Change | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 28.9464 | 15597.1834 | 0 | 0 | 0 | 0 | 14.4449 | 861.9428 | 8109.3361 | 0 | 0 | 0 | 14.4449 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
939 | Piercy: Metcalf-Piercy 115kV Line Upgra |  |  | San Jose, Santa Clara | The revised scope aims to reconductor the following 115 kV lines using advanced conductors to achieve a summer emergency rating of 3,000 Amps or higher: Piercy-Metcalf, Swift-Metcalf, Newark-Dixon Landing, and McKee-Piercy. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0003803 ¦ T.0005211 ¦ T.0009571 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-03 | 30 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3509 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561388 | T.0009536 | Dixon Landing 115 kV Upgrade | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-10 | 2008-12-31 | 2028-07-25 | Scope Change | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 31.5821 | 14994.9025 | 0 | 0 | 0 | 0 | 9.6757 | 622.6339 | 8366.4844 | 0 | 0 | 0 | 9.6756 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
940 | McKee: McKee-Piercy 115kV Line Upgra |  |  | San Jose, Santa Clara | The revised scope aims to reconductor the following 115 kV lines using advanced conductors to achieve a summer emergency rating of 3,000 Amps or higher: Piercy-Metcalf, Swift-Metcalf, Newark-Dixon Landing, and McKee-Piercy. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0003803 ¦ T.0005211 ¦ T.0009571 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-03 | 30 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7628 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561358 | T.0009536 | Dixon Landing 115 kV Upgrade | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-10 | 2008-12-31 | 2028-07-26 | Scope Change | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 26.8725 | 47226.2616 | 0 | 0 | 0 | 0 | 11.6049 | 435.0734 | 18188.6576 | 0 | 0 | 0 | 11.6049 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
941 | Newark: Newark- Dixon Landing 115 kV Upg |  |  | Fremont, Alameda | The revised scope aims to reconductor the following 115 kV lines using advanced conductors to achieve a summer emergency rating of 3,000 Amps or higher: Piercy-Metcalf, Swift-Metcalf, Newark-Dixon Landing, and McKee-Piercy. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0003803 ¦ T.0005211 ¦ T.0009571 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | 30 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 27.7611 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561380 | T.0009536 | Dixon Landing 115 kV Upgrade | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-10 | 2008-12-31 | 2028-07-26 | Scope Change | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 35.1054 | 4173.0322 | 0 | 0 | 0 | 0 | 17.1486 | 340.8812 | 2443.5012 | 0 | 0 | 0 | 17.1486 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
942 | Swift: Swift-Metcalf 115 kV Line Upgra |  |  | San Jose, Santa Clara | The revised scope aims to reconductor the following 115 kV lines using advanced conductors to achieve a summer emergency rating of 3,000 Amps or higher: Piercy-Metcalf, Swift-Metcalf, Newark-Dixon Landing, and McKee-Piercy. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0003803 ¦ T.0005211 ¦ T.0009571 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-06 | 30 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.1012 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561381 | T.0009536 | Dixon Landing 115 kV Upgrade | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-10 | 2008-12-31 | 2028-07-26 | Scope Change | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 31.0332 | 11110.8227 | 0 | 0 | 0 | 0 | 15.3909 | 453.577 | 5411.02 | 0 | 0 | 0 | 15.3909 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
943 | Metcalf: Metcalf-Piercy 115kV Line Upgra |  |  | Santa Clara | The revised scope aims to reconductor the following 115 kV lines using advanced conductors to achieve a summer emergency rating of 3,000 Amps or higher: Piercy-Metcalf, Swift-Metcalf, Newark-Dixon Landing, and McKee-Piercy. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0003803 ¦ T.0005211 ¦ T.0009571 | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-05 | 30 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561389 | T.0009536 | Dixon Landing 115 kV Upgrade | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-10 | 2008-12-31 | 2028-07-26 | Scope Change | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 46.8796 | 1528.8131 | 0 | 0 | 0 | 0 | 11.9796 | 110.0471 | 823.1348 | 0 | 0 | 0 | 11.9795 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
944 | Newark-Milpitas 115kV Line Upgrade |  |  | Fremont, Alameda | This project proposes to remove the limiting substation equipment on the Newark-Milpitas #1 115kV line at Newark substation. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | 98 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 27.7611 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5554623 | T.0009561 | Newark-Milpitas 115kV Line Upgrade | 2 | 61 | NA ¦ EX113212 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-08-11 | 2019-06-01 | 2026-12-04 | Prioritization | Project Design | TRUE | $1,500 ¦ $2,000 | NA ¦ NA | 387.5227 | 905.1724 | 0 | 0 | 0 | 81.1165 | 296.8291 | 488.3801 | 38.8466 | 0 | 0 | 0 | 377.9456 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 81.1165 | 278.5856 | 9.1148 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
945 | Milpitas: Newark-Milpitas Line #1 Upgd |  |  | Milpitas, Santa Clara | This project proposes to remove the limiting substation equipment on the Newark-Milpitas #1 115kV line at Newark substation. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-02 | 98 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.3452 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5558294 | T.0009561 | Newark-Milpitas 115kV Line Upgrade | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-08-11 | 2019-06-01 | 2026-12-28 | Prioritization | Project Design | TRUE | $1,500 ¦ $2,000 | NA ¦ NA | 170.2829 | 1127.772 | 0 | 0 | 0 | 0 | 147.9368 | 879.8351 | 35.9765 | 0 | 0 | 0 | 147.9368 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 147.9368 | 22.3461 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
946 | Jarvis: Newark-Jarvis #1 115kV Line Upgd |  |  | Union City, Alameda | This project proposes to remove the limiting substation equipment on the Monta Vista-Wolfe 115kV, Metcalf-El Patio #1 and Newark-Jarvis #1 115kV lines at Jarvis, Metcalf and Wolfe substations. • At Wolfe substation, upgrade the line termination conductor and any other limiting element to have summer emergency rating of 1104 Amps. • At Metcalf Substation, upgrade the line termination conductor and any other limiting element to achieve a summer emergency rating of 1144 Amps. • At Jarvis Substation, replace the 600 Amps line switch and any other limiting element to achieve a summer emergency rating of 802 Amps. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0009536 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-03 | 54 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | 1.9821 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5554628 | T.0009571 | South Bay Area Limiting Element Upgrade | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-08-18 | 2027-12-31 | 2026-09-10 | NA | NA | TRUE | 11000 | NA ¦ NA | 446.6295 | 2071.5336 | 0 | 0 | 0 | 79.3235 | 193.6121 | 1574.3284 | 205.2537 | 0 | 0 | 0 | 272.9356 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 79.3235 | 193.6121 | 173.6939 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
947 | Metcalf-El Patio #1 115kV Line Upgd |  |  | Santa Clara | This project proposes to remove the limiting substation equipment on the Monta Vista-Wolfe 115kV, Metcalf-El Patio #1 and Newark-Jarvis #1 115kV lines at Jarvis, Metcalf and Wolfe substations. • At Wolfe substation, upgrade the line termination conductor and any other limiting element to have summer emergency rating of 1104 Amps. • At Metcalf Substation, upgrade the line termination conductor and any other limiting element to achieve a summer emergency rating of 1144 Amps. • At Jarvis Substation, replace the 600 Amps line switch and any other limiting element to achieve a summer emergency rating of 802 Amps. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-05 | 52 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | 5.1001 | NA | 5554627 | T.0009571 | South Bay Area Limiting Element Upgrade | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2024 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-06-01 | 2027-12-31 | 2024-06-04 | NA | NA | FALSE | 11000 | NA ¦ NA | 348.3002 | 348.3002 | 0 | 0 | 0 | 348.3002 | 0 | 0 | 0 | 0 | 0 | 0 | 348.3002 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 348.3002 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
948 | Momentum: Upgrade Rio Oso remote end |  |  | Sutter | To eliminate the deficiency and provide surplus distribution capacity to meet growing demand by installing two 230/21kV (75 MVA) distribution transformers at Momentum Substation(greenfield). Transmission Line Work (MWC 60): • Loop Rio Oso – Gold Hill or Rio Oso – Atlantic 230kV line in substation property Transmission Substation Work (MWC 61): • Build two rows of 230kV breaker and a half configuration bus arrangement, 6 breakers • Install MPAC building Distribution Substation Work to Install Fiddyment Bank 1 and 21kV Bus Structure (MWC 46): • Install one 230/21kV, 75 MVA LTC transformer, Fiddyment Bank 1. • Install one 21kV bank breaker • Install two 21kV feeder Breakers • Install one 21kV spare feeder bay Distribution Line Work to Fiddyment 2101 and 2102 Feeders (MWC 06): • Trench 1000 feet and install 6-1100Al EPR cables in two 6-inch conduits with one spare 6-inch conduit (for a future 2103 feeder) from Switchgear No. 1 to future PMI-9 SW 760956 (PM 35424031) on College Park Drive to create new Fiddyment 2101 and Fiddyment 2102 underground feeder outlets. These connect to feeders that are being constructed by the land developer on new business PM 35424031 (Placer One Backbone). • Switches may be installed as required for operational flexibility and efficiency. • Automated switches may be required and added to the project scope for FLISR. • Line work and equipment may be added or deleted upon completion of the final design and estimate. | Other - Operations Tech | New | NA | T.0008394 | Load Growth | Line Termination | NA | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.3219 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5560143 | T.0009604 | Momentum 230/21kV Substation | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7636-E | 2025-07-03 | Approved | 2025 | Engineering more than 50% complete | 3 | 2027-08-19 | 2028-12-29 | 2028-02-16 | NA | NA | TRUE | 26600 | NA ¦ NA | 32.7541 | 1324.214 | 0 | 0 | 0 | 0.1212 | 32.6329 | 212.169 | 753.9208 | 4.8527 | 0 | 0 | 32.7541 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
949 | Momentum: Upgrade Gold Hill Remote end |  |  | Folsom, Sacramento | To eliminate the deficiency and provide surplus distribution capacity to meet growing demand by installing two 230/21kV (75 MVA) distribution transformers at Momentum Substation(greenfield). Transmission Line Work (MWC 60): • Loop Rio Oso – Gold Hill or Rio Oso – Atlantic 230kV line in substation property Transmission Substation Work (MWC 61): • Build two rows of 230kV breaker and a half configuration bus arrangement, 6 breakers • Install MPAC building Distribution Substation Work to Install Fiddyment Bank 1 and 21kV Bus Structure (MWC 46): • Install one 230/21kV, 75 MVA LTC transformer, Fiddyment Bank 1. • Install one 21kV bank breaker • Install two 21kV feeder Breakers • Install one 21kV spare feeder bay Distribution Line Work to Fiddyment 2101 and 2102 Feeders (MWC 06): • Trench 1000 feet and install 6-1100Al EPR cables in two 6-inch conduits with one spare 6-inch conduit (for a future 2103 feeder) from Switchgear No. 1 to future PMI-9 SW 760956 (PM 35424031) on College Park Drive to create new Fiddyment 2101 and Fiddyment 2102 underground feeder outlets. These connect to feeders that are being constructed by the land developer on new business PM 35424031 (Placer One Backbone). • Switches may be installed as required for operational flexibility and efficiency. • Automated switches may be required and added to the project scope for FLISR. • Line work and equipment may be added or deleted upon completion of the final design and estimate. | Other - Operations Tech | New | NA | T.0008394 | Load Growth | Line Termination | NA | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 12.8702 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5560144 | T.0009604 | Momentum 230/21kV Substation | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7636-E | 2025-07-03 | Approved | 2025 | Engineering more than 50% complete | 3 | 2027-08-26 | 2028-12-29 | 2028-02-24 | NA | NA | TRUE | 26600 | NA ¦ NA | 32.3912 | 1333.0151 | 0 | 0 | 0 | 0.1212 | 32.27 | 214.7741 | 758.4814 | 6 | 0 | 0 | 32.3912 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
950 | Mercy Springs SW STA: Connect 70kV Line |  |  | Merced | This project proposes to: • Install 230 kV partial bay at the new generation driven 230 kV switching station adjacent to Dos Amigos PP 230 kV Substation. • Add a new 70 kV Bus in the new generation driven 230 kV switching station, then it will be converted to a new 230/70 kV substation. • Install one 230/70 kV transformer at the new 230/70 kV substation. • Install a new 70 kV transmission line from new 70 kV Bus to Mercy Springs 70 kV Bus, and the new line is about one mile. • Install one breaker at Mercy Springs 70 kV Switching Station. | Substation - Transformer | New | NA | T.0009177 | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 53.2803 | NA | 230 ¦ 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807502 | T.0009617 | Los Banos 70 kV Area Reinforcement | 3 | 61 | NA ¦ EX113343 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-08-01 | 2029-12-31 | 2029-12-14 | NA | NA | FALSE | 60000 | NA ¦ NA | 12.0927 | 34553.263 | 0 | 0 | 0 | 0 | 6.7808 | 46.4822 | 2500 | 10000 | 20000 | 2000 | 6.7808 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
951 | Northeast Kern - Rio Bravo Sub |  |  | Kern | This project proposes to: • Reconductor ~13.6 circuit miles of Midway – Shafter 115 kV Line • Reconductor ~8.3 circuit miles on the Shafter-Rio Bravo 115 kV • Reconductor ~3.9 circuit miles on the Midway-Tupman-Rio Bravo-Renfro 115 kV (between Rio Bravo and Renfro Junction From 11/62 To Rio Bravo Sub) • Reconductor ~3.5 circuit miles on the Lerdo-Kern Oil-7th Standard 115 kV Line (between Lerdo J and Kern Oil, from 023/005 To Kern Oil Sub) • Reconductor ~6.8 circuit miles on the Smyrna-Semitropic-Midway 115 kV Line (between Midway and Ganso from Midway to 081/634 and from 081/634 to Ganso) • Reconductor ~14.1 circuit miles on the Semitropic-Midway #1 115 kV Line (between Midway and Semitropic_E) • Convert the existing control point to a summer setup to open line section from Wasco to McFarland 70 kV line. • Convert the existing control point to a summer setup to open line section from Famoso to Cawelo C 115 kV line. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-06 | 78 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.6401 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5814512 | T.0009633 | NorthEast Kern 115kV Reconductor | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Planning | 5 | 2027-12-01 | 2032-12-31 | 2028-02-01 | NA | NA | FALSE | 256000 | NA ¦ NA | 0 | 2600 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1500 | 1000 | 100 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
952 | Cortina #1 Sub Upgrades |  |  | Colusa | The Cortina #1 60 kV transmission line, located in Colusa County, is approximately 26.2 miles long and supported by 447 structures. The Arbuckle, Harrington and Dunnigan 60 kV substations are radially served by the Cortina #1 60 kV line with the Cortina #2 60 kV line serving as an alternate source with normally open switches. This project will help facilitate the delivery of an additional 10 MW to serve increased load in the Cortina area due to the addition of Tesla charging banks. The project scope of work includes: • Reconductor approximately 26.2 miles of the Cortina #1 60 kV Line between Cortina Substation and Dunnigan Substation with a conductor able to achieve at least 818 Amps of summer interior normal rating. • If new structures are required, they will be sized to accommodate a future distribution underbuild conductor of 715 AAC. • Existing distribution underbuild will be relocated to new transmission structures. • Removal of the idle Drake Substation tap and Switch 25. • Upgrade substation terminal equipment to achieve full conductor capacity. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-06 | 126 | Steady State Power Flow System Analysis | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.7436 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811724 | T.0009641 | Cortina #1 60 kV Line Reconductoring | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7836-E | 2026-02-11 | Approved | 2026 | Engineering more than 50% complete | 3 | 2026-12-09 | 2028-06-01 | 2027-01-14 | NA | NA | TRUE | $47,100 ¦ $94,300 | NA ¦ NA | 171.6952 | 1610.659 | 0 | 0 | 0 | 4.2038 | 130.0176 | 476.4376 | 357.4782 | 1000 | 0 | 0 | 134.2214 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
953 | Borden-Storey 230 kV 1 & 2 Recond |  |  | Chowchilla, Madera ¦ Madera ¦ Madera Acres CDP, Madera ¦ Merced ¦ Merced, Merced ¦ Parksdale CDP, Madera | Reconductoring the Borden – Storey section(s) of the Wilson – Borden #1 and #2 230 kV lines | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Policy | Line Termination | NERC TPL Standards | NA | 2025-08-21 | 20 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807524 | T.0009662 | Borden-Storey Project | 4 | 61 | NA ¦ EX113344 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-11-02 | 2032-12-31 | 2029-12-17 | NA | NA | FALSE | 50000 | NA ¦ NA | 2.2587 | 1405.6084 | 0 | 0 | 0 | 0 | 0 | 79.4473 | 500 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-F-Board-Approved_2022-2023_Transmission-Plan.pdf
954 | SAN RAFAEL SUB UPGRADES |  |  | San Rafael, Marin | Reconductor Ignacio - San Rafael No. 1 115 kV Line, Ignacio - Alto 60 kV Line, and Ignacio - San Rafael No. 3 115 kV Line section from Ignacio - Las Gallinas as well as upgrade limiting equipment on lines. Add a 10 MVAR shunt capacitor at Greenbrae 60 kV Substation and associated substation upgrades to accommodate this installation | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-02 | 65 | Steady State Power Flow System Analysis | Wires - Location/Route Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.2052 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5814487 | T.0009719 | Ignacio Area Upgrade | 6 | 61 | NA ¦ EX113201 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2012 ¦ 2018 | FALSE | 2012 ¦ 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-11-09 | 2023-12-01 | 2028-06-08 | Prioritization | NA | FALSE | 37000 | NA ¦ NA | 82.5035 | 28347.1859 | 0 | 0 | 0 | 0 | 75.3665 | 249.0374 | 11522.7821 | 12000 | 3500 | 500 | 75.3664 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
955 | Manteca: Repl SWs 163 and 173 |  |  | Manteca, San Joaquin | This project proposes to replace four (4) 115kV switches that are currently limiting the line rating on Manteca-Vierra 115kV line. • Replace four (4) 115kV Switches 163 & 173 with higher continuous current (CC) rating (currently 600 Amps; 1949-vintage A.B. Chance) (Note that existing switch 163 has one set of switch on each side of CB 164 and will be renumbered as 161 and 163 respectively, existing switch 173 has one set of switch on each side of CB 174 and will be renumbered as 171 and 173 respectively) • Foundation and structure might require modification. | Substation - Switch | Upgrade/Retrofit | NA | NA | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | T-Line Capacity | NERC TPL Standards | NA | 2026-03-14 | 76 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 9.8539 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5555289 | T.0009928 | Manteca: Repl Switches 163 and 173 | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-02-28 | NA | 2028-06-05 | NA | NA | TRUE | NA | NA ¦ NA | 146.5837 | 4603.537 | 0 | 0 | 0 | 50.3062 | 77.7171 | 2975.5138 | 19.5326 | 0 | 0 | 0 | 128.0233 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 45.2758 | 69.9455 | 16.7044 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
956 | Menlo: Jefferson-Stanford UG Cable Rplc |  |  | West Menlo Park CDP, San Mateo | Install temporary overhead shoo-fly transmission line to bypass existing underground cable section between Menlo Substation and SLAC 60 kV Tap for continuous electric customer service. Replace 0.9 mile of existing 800 kcmil AL underground cable with larger size cable of at least 1000 Amp. normal capacity | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-09 | 25 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | 0.37098 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5564267 | T.0010604 | Jefferson-Stanford Cable Replacement | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2026 | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-03-01 | 2029-05-01 | 2028-02-29 | NA | NA | FALSE | 40000 | NA ¦ NA | 8.9495 | 265.3132 | 0 | 0 | 0 | 0 | 2.4843 | 142.8289 | 100 | 0 | 0 | 0 | 2.4842 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
957 | CLEARLAKE SUBSTATION TERMINAL UPGRADE |  |  | Lake | The project scope of work involves the following: • Install a new 115/60 kV transformer bank at Middletown Substation with at least 100 MVA capacity. • Install two circuit breakers (115 kV and 60 kV) and associated disconnect switches at Middletown Substation to protect the new transformer. • Build a new 115 kV line from Lower Lake to Middletown substations with at least 345 Amps emergency capacity. This project is needed to provide transmission capacity to serve customers in the Humboldt Division. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-13 | 78 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 0.60404 | NA | 115 kV | NA | NA | NA | 5.101 | Non-IGP | 5813639 | T.0010635 | Clear Lake 60kV Reinforcement | 4 | 61 | NA ¦ EX113216 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-03-21 | 2012-05-01 | 2028-06-09 | Prioritization | NA | FALSE | 30000 | NA ¦ NA | 0.9287 | 1919.9246 | 0 | 0 | 0 | 0 | 0 | 94.4069 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
958 | Middletown Substation Terminal Upgrade |  |  | Lake | The project scope of work involves the following: • Install a new 115/60 kV transformer bank at Middletown Substation with at least 100 MVA capacity. • Install two circuit breakers (115 kV and 60 kV) and associated disconnect switches at Middletown Substation to protect the new transformer. • Build a new 115 kV line from Lower Lake to Middletown substations with at least 345 Amps emergency capacity. This project is needed to provide transmission capacity to serve customers in the Humboldt Division. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-09 | 56 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 0.77804 | NA | 115 kV | NA | NA | NA | 5.101 | Non-IGP | 5814511 | T.0010635 | Clear Lake 60kV Reinforcement | 4 | 61 | NA ¦ EX113216 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-02-07 | 2012-05-01 | 2028-06-13 | Prioritization | NA | FALSE | 30000 | NA ¦ NA | 18.1417 | 1823.4234 | 0 | 0 | 0 | 0 | 13.6076 | 207.0441 | 0 | 0 | 0 | 0 | 13.6076 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
959 | Hopland Substation Terminal Upgrade |  |  | Mendocino | The project scope of work involves the following: • Install a new 115/60 kV transformer bank at Middletown Substation with at least 100 MVA capacity. • Install two circuit breakers (115 kV and 60 kV) and associated disconnect switches at Middletown Substation to protect the new transformer. • Build a new 115 kV line from Lower Lake to Middletown substations with at least 345 Amps emergency capacity. This project is needed to provide transmission capacity to serve customers in the Humboldt Division. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-13 | 78 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 0.63377 | NA | 115 kV | NA | NA | NA | 5.101 | Non-IGP | 5814510 | T.0010635 | Clear Lake 60kV Reinforcement | 4 | 61 | NA ¦ EX113216 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-01-18 | 2012-05-01 | 2029-07-03 | Prioritization | NA | FALSE | 30000 | NA ¦ NA | 0.8778 | 1880.9346 | 0 | 0 | 0 | 0 | 0 | 34.0359 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
960 | TESLA SUBSTATION TERMINAL UPGRADE |  |  | San Joaquin | Reconductor Tesla –Newark #2 230 kV line - From 024/148 to Newark (approximately 4.28 miles), with minimum summer emergency rating of 3428 AMPS, matching other sections of the line or highest conductor feasible with existing structure. Will also include any other limiting element upgrades to achieve this line rating. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Policy | Line Termination | NERC TPL Standards | NA | 2026-02-05 | 22 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.2961 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813638 | T.0010636 | Tesla-Newark 230kV Line No 2 Recon | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-12-17 | 2034-12-01 | 2034-12-26 | NA | NA | FALSE | $29,000 ¦ $58,000 | NA ¦ NA | 15.0686 | 5823.4772 | 0 | 0 | 0 | 0 | 6.3683 | 910.1253 | 0 | 0 | 0 | 0 | 6.3684 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
961 | Newark Substation Terminal Upgrade |  |  | Fremont, Alameda | Reconductor Tesla –Newark #2 230 kV line - From 024/148 to Newark (approximately 4.28 miles), with minimum summer emergency rating of 3428 AMPS, matching other sections of the line or highest conductor feasible with existing structure. Will also include any other limiting element upgrades to achieve this line rating. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Policy | Line Termination | NERC TPL Standards | NA | 2026-03-03 | 22 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | 27.7611 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5817422 | T.0010636 | Tesla-Newark 230kV Line No 2 Recon | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-12-22 | 2034-12-01 | 2034-12-29 | NA | NA | FALSE | $29,000 ¦ $58,000 | NA ¦ NA | 25.659 | 5845.1215 | 0 | 0 | 0 | 0 | 15.3726 | 913.4749 | 0 | 0 | 0 | 0 | 15.3726 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
962 | SNEATH LANE SUBSTATION TERMINAL UPGRADE |  |  | San Bruno, San Mateo | Reconductor 7.2 miles on the Martin-Sneath Lane 60 kV line and 2.5 miles on the Millbrae-Sneath Lane 60 kV line. Mitigate the thermal violations in the Martin-Millbrae 60 kV system under P1 contingencies. Increase the load serving capability and customer reliability in the area. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-10 | 101 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.3131 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813640 | T.0010637 | Martin-Millbrae 60kV Area Reinforcement | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-03-07 | 2030-05-01 | 2030-05-31 | NA | NA | FALSE | $20,000 ¦ $40,000 | NA ¦ NA | 10.5952 | 9201.6419 | 0 | 0 | 0 | 0 | 5.1088 | 897.5444 | 0 | 0 | 0 | 0 | 5.1088 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
963 | Martin Substation Terminal Upgrade |  |  | Brisbane, San Mateo | Reconductor 7.2 miles on the Martin-Sneath Lane 60 kV line and 2.5 miles on the Millbrae-Sneath Lane 60 kV line. Mitigate the thermal violations in the Martin-Millbrae 60 kV system under P1 contingencies. Increase the load serving capability and customer reliability in the area. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-12 | 101 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5817629 | T.0010637 | Martin-Millbrae 60kV Area Reinforcement | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-03-07 | 2030-05-01 | 2030-05-31 | NA | NA | FALSE | $20,000 ¦ $40,000 | NA ¦ NA | 8.9194 | 9202.7622 | 0 | 0 | 0 | 0 | 4.301 | 899.2535 | 0 | 0 | 0 | 0 | 4.301 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
964 | Millbrae Substation Terminal Upgrade |  |  | Millbrae, San Mateo | Reconductor 7.2 miles on the Martin-Sneath Lane 60 kV line and 2.5 miles on the Millbrae-Sneath Lane 60 kV line. Mitigate the thermal violations in the Martin-Millbrae 60 kV system under P1 contingencies. Increase the load serving capability and customer reliability in the area. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-09 | 101 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.0501 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5817630 | T.0010637 | Martin-Millbrae 60kV Area Reinforcement | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-03-07 | 2030-05-01 | 2030-05-31 | NA | NA | FALSE | $20,000 ¦ $40,000 | NA ¦ NA | 9.6332 | 9203.7951 | 0 | 0 | 0 | 0 | 4.301 | 900.1043 | 0 | 0 | 0 | 0 | 4.301 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
965 | CORTINA #3 MERIDIAN SUB LINE TERM |  |  | Colusa | Reconductor about 6.0 miles between the Cortina Substation and Wadham Jct on the Cortina #3 60 kV to achieve minimum conductor rating of 1014 AMPS for summer normal rating and 1127 AMPS for summer emergency rating. Reconductor about 1.5 miles between the Wadham Jct and Wescot (007/125) on the Cortina #3 60 kV to achieve minimum conductor rating of 1014 AMPS for summer normal rating and 1127 AMPS for summer emergency rating. Reconductor about 1.5 miles between the Wescot (007/125) and Willaims Substation on the Cortina #3 60 kV to achieve minimum conductor rating of 1014 AMPS for summer normal rating and 1127 AMPS for summer emergency rating. Install a 15 MVAR shunt capacitor at Meridian 60 kV substation. Upgrade any limiting components as necessary to achieve full conductor capacity | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-06 | 126 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.7436 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815239 | T.0011146 | Cortina #3 60 kV Reconductoring Project | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-07-23 | 2031-05-01 | 2032-01-14 | Customer action | NA | FALSE | 55500 | NA ¦ NA | 51.7968 | 6244.644 | 0 | 0 | 0 | 0 | 49.0808 | 520.569 | 0 | 0 | 0 | 0 | 49.0808 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
966 | San Jose B Sub Terminal Upgrade |  |  | San Jose, Santa Clara | Reconductor ~ 1.15 circuit miles of SJA-SJB #1 115kV Line with larger conductor to achieve at least 3000 Amps under summer emergency rating. Construct New ~1.372 circuit miles of SJA-SJB#2 115kV Line with conductor to achieve at least 3000 Amps under summer emergency rating. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0010465 | Load Growth | Line Termination | NERC TPL Standards | NA | 2026-02-04 | 29 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.1017 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815699 | T.0011286 | San Jose A-San Jose B 115kV T-Line UPGR | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2026 | 2026 | FALSE | 2026 | NA | https://stakeholdercenter.caiso.com/InitiativeDocuments/Draft-2025-2026-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-03-31 | 2028-05-01 | 2027-05-18 | NA | NA | TRUE | 224000 | NA ¦ NA | 0 | 960.5229 | 0 | 0 | 0 | 0 | 0 | 458.9087 | 395.0347 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | Type 4 | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://stakeholdercenter.caiso.com/RecurringStakeholderProcesses/2025-2026-Transmission-planning-process
967 | Silverado: Eagle Rock-Fulton-Slvrdo 115 |  |  | Saint Helena, Napa | Reconductor Eagle Rock-020/087A with minimum rating of 1236 Amps or higher and update any limiting components at the substation (if any). Reconductor 020/87A-037/191A with minimum rating of 1687 Amps or higher and update any limiting components at the substation (if any). | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Policy | Line Termination | NERC TPL Standards | NA | 2026-02-02 | 126 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.7884 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5563879 | T.0011334 | Eagle Rock-Fulton-Silverado 115kV Recon | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-10-03 | 2034-05-01 | 2029-04-28 | NA | NA | FALSE | 92900 | NA ¦ NA | 0.2671 | 3327.9849 | 0 | 0 | 0 | 0 | 0.2671 | 0 | 342.3594 | 0 | 0 | 0 | 0.2671 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
968 | STOCKDALE SUB 230KV UPGRADES |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.3735 | NA | 230 kV | 764 | NA | NA | NA | NA | 5774238 | T.0000204 | Kern 230kV Bus Upgrade | 13 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-10-16 | 2013-05-01 | 2018-12-18 | Bundling Dependencies | NA | FALSE | $32,000 ¦ $44,000 | NA ¦ NA | 3397.1034 | 3397.1034 | 291.2012 | 45.3817 | 0.5654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3397.1034 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 281.696 | 43.9004 | 0.54693 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
969 | BAKERSFIELD SUB 230KV UPGRADES |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.6195 | NA | 230 kV | 764 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5774239 | T.0000204 | Kern 230kV Bus Upgrade | 13 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-10-01 | 2013-05-01 | 2020-02-07 | Prioritization | NA | FALSE | $32,000 ¦ $44,000 | NA ¦ NA | 2379.1395 | 2379.1395 | 14.3856 | 3.2364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2379.1395 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 13.7513 | 3.0937 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
970 | WHEELER RIDGE: Inst 75 MVAR Capacitors |  |  | Kern | Install three 75 Mega Volt-Ampere reactive (MVAR) steps of mechanically switched capacitors, upgrade the 230kV bus to breaker-and-a-half (BAAH), and add an MPAC building at Wheeler Ridge Substation, | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-11 | 9 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 230 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767969 | T.0000662 | WHEELER RIDGE 230kV VOLTAGE SUPPORT | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-04-15 | 2016-12-01 | 2021-02-01 | Prioritization | NA | FALSE | $25,000 ¦ $40,000 | NA ¦ NA | 36547.9267 | 36547.9267 | 5707.5285 | 64.7646 | 14.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36547.9267 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 35822.4888 | 63.5454 | 14.6385 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
971 | MIDWAY: INSTALL TEMP RELAYS |  |  | Buttonwillow CDP, Kern | Install three 75 Mega Volt-Ampere reactive (MVAR) steps of mechanically switched capacitors, upgrade the 230kV bus to breaker-and-a-half (BAAH), and add an MPAC building at Wheeler Ridge Substation, | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 94.5324 | NA | 230 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5783316 | T.0000662 | WHEELER RIDGE 230kV VOLTAGE SUPPORT | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-01-04 | 2016-12-01 | 2021-02-01 | Prioritization | NA | FALSE | $25,000 ¦ $40,000 | NA ¦ NA | 332.1616 | 332.1616 | 212.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.1616 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 324.4703 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
972 | Wheeler Ridge: Votlage Support Phase 2 |  |  | Kern | Install three 75 Mega Volt-Ampere reactive (MVAR) steps of mechanically switched capacitors, upgrade the 230kV bus to breaker-and-a-half (BAAH), and add an MPAC building at Wheeler Ridge Substation, | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-11 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5785918 | T.0000662 | WHEELER RIDGE 230kV VOLTAGE SUPPORT | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2020 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-05-03 | 2016-12-01 | 2021-07-02 | Prioritization | NA | FALSE | $25,000 ¦ $40,000 | NA ¦ NA | 2436.3076 | 2436.3076 | 2138.355 | 55.6184 | 240.7467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2436.3076 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1886.2186 | 48.9863 | 212.0392 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
973 | MARYSVILLE: Convert to Ring BUS |  |  | Marysville, Yuba | Upgrade the Marysville 60kV Bus to a five-circuit-breaker ring bus configuration. This project will resolve current configuration issues, address reliability concerns, and replace deteriorating equipment at Marysville Substation. The upgrades will also position the substation for future system reinforcement or interconnection projects, and provide enhanced automation and additional controls of PG&E’s transmission system. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2026-02-11 | 31 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.73781 | NA | 60 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767818 | T.0000911 | MARYSVILLE 60kV Bus Upgrade | 1 | 61 | NA ¦ 5766635 ¦ NA ¦ NA | TRUE | 2015 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-08-01 | 2018-02-08 | 2020-04-29 | Workforce | NA | FALSE | 20340 | NA ¦ NA | 21938.2652 | 21938.2652 | 241.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21938.2652 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 286.7925 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
974 | COTTONWOOD: Replace Bank |  |  | Cottonwood CDP, Shasta | Project scope is to replace both 230/115kV transmission transformers which will address the 115kV high voltage issue and improve reliability of the North Valley transmission system. Installing the 115kV bus tie breakers will address NERC category P2 breaker fault of Cottonwood CB 102 or, a NERC category P4 nearby fault plus a CB 102 fault. The CAISO approved shunt reactors/transformer replacement to mitigate the high voltage issue and additionally the 115kV bus tie breakers to mitigate the P2 and P4 contingencies. The MPAC and breakers replacement will replace the deteriorated asset and capture the efficiency of upgrading protection and controls, avoid rework and multiple clearances. The high-level scope includes the following: • Replace the existing Banks 1 and 4 with 230/115kV 420MVA, with LTC and associated bus selector switches. • Install new bay and new 230kV breaker to connect new Bank 1 to 230kV bus. • Replace Bank 1 low-side breaker CB 172 and the associated switches. • Replace Bank 4 low-side CB 192 and the associated switches. • Expand existing 115kV MPAC to accommodate protection and controls. • Expand SPCC to accommodate increased oil quantity of new banks. • Install new sectionalizing CB’s 912 and 922 w/switches to sectionalize 115kV bus to Sections D and E. • Install new CB 132 with switches and relocate Trinity-Cottonwood 115kV line to Bus Section E. • Install new bus paralleling breaker CB 102 with switches in Bus Section E. • Install new bus paralleling breaker CB 902 with switches in Bus Section D. • Replace the existing OCBs 142 and 152 with non-SF6 breakers and the associated switches. • Replace six of the existing 230kV OCBs (CBs 222, 232, 272, 292, 522, and 542) with new 230kV 2000A gas circuit breakers, and the associated breaker and bus selector switches. • Install new 230kV 2000A bus paralleling breaker (CB 502) and associated switches in place of the existing Transformer 1 CB 512 position. • Replace switches 213, 357, 359, 367, and 369. • Install new MPAC Building to house the protection, automation, and control equipment for the 230kV Bus Sections “E” and “F”. | Substation - Transformer | Upgrade/Retrofit | NA | T.0004659 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-19 | 68 | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 26.1945 | NA | 230 ¦ 115 kV | 1002 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.1001 | Non-IGP | 5768471 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2018 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-11-20 | 2022-12-31 | 2028-11-20 | Prioritization | NA | FALSE | 15000 | NA ¦ NA | 9186.7618 | 32525.103 | 104.7318 | 62.7034 | 137.8143 | 186.851 | 5780.104 | 12255.1651 | 5101 | 2254 | 0 | 0 | 6919.3352 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
975 | LOS ESTEROS: Install Shunt Reactors |  |  | San Jose, Santa Clara | Install three 85 MVar shunt reactors on the 230kV buses at Los Esteros Substation to help control system voltages. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-09 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 230 kV | 1007 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5768542 | T.0001130 | Los Esteros Shunt Reactor Project | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2018 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-12-02 | 2020-05-01 | 2021-03-18 | Prioritization | NA | FALSE | $24,000 ¦ $36,000 | NA ¦ NA | 18616.0457 | 18616.0457 | 1937.364 | 105.8186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18616.0457 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 18510.2306 | 105.8186 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
976 | Wilson 115kV STATCOM |  |  | Merced, Merced | Install a 115kV +100/-100 Mega Volt-Ampere reactive (MVAR) voltage control system (STATCOM) at Wilson Substation. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 22.8151 | NA | 115 kV | 318 | 8. Compliance/Commitments With Low Safety Risk | 7 | NA | Non-IGP | 5768820 | T.0001381 | Wilson 115kv STATCOM | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2018 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-08-03 | 2020-05-01 | 2021-05-10 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 37248.4511 | 37248.4511 | 8434.6808 | 652.2538 | 56.5171 | -251.5877 | -123.4261 | 0 | 0 | 0 | 0 | 0 | 37248.4511 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 35633.2248 | 628.1203 | 54.4259 | -242.279 | -118.8589 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
977 | RIO OSO: SVC |  |  | Sutter | Install a 230kV +200/-260 Mega Volt-Ampere reactive (MVAR) SVC at Rio Oso Substation | Substation - Voltage Support Equipment | New | NA | T.0000614 | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | Wires - System Configuration Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 9.3219 | NA | 230 kV | 1002 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5770538 | T.0001739 | RIO OSO Substation 230kV SVC | 1 | 61 | NA ¦ 5725553 ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2018 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-02-02 | 2016-05-01 | 2026-10-30 | Workforce | NA | TRUE | $35,000 ¦ $45,000 | NA ¦ NA | 45283.9429 | 58132.469 | 3758.1703 | 7006.1151 | 5190.1307 | 22698.1128 | 3359.8795 | 11872.5085 | 1764.925 | 0 | 0 | 0 | 44495.0354 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
978 | DELEVAN: Install 200 MVAR Shunt Reactor |  |  | Colusa | Install three steps for a total of 202 MVar shunt reactors1 at Delevan 230kV Substation to help control system voltages | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.7615 | NA | 230 kV | 1002 | 8. Compliance/Commitments With Low Safety Risk | 22 | NA | NA | 5771160 | T.0001991 | DELEVAN Substation 230kV Shunt Reactor | 1 | 61 | NA ¦ 5768472 ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2018 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-01-27 | 2020-05-01 | 2020-10-08 | NA | NA | FALSE | $19,000 ¦ $28,000 | NA ¦ NA | 16957.2187 | 16957.2187 | 124.5794 | 37.6812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16957.2187 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 124.5369 | 37.6683 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
979 | LIVE OAK: Upgrade 115 KV Line |  |  | Live Oak, Sutter | The Project proposes to reconductor approximately 38 circuit miles of various 115 kV lines serving Bakersfield area in Kern County. The scope of the project include reconductoring 3.8 miles of the Kern PP-Westpark Nos. 1 and 2 115 kV Lines; 16.5 miles of the Kern-Magunden-Witco 115 kV Line; 3.5 miles of the Westpark-Magunden 115 kV Line; 5.0 miles of the Kern-Lamont 115 kV Line from Kern PP to Tevis Jct.; 5.0 miles of the Kern-Stockdale 115 kV line from Kern PP to Tevis Jct. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-02-11 | 64 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 0.39793 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5776125 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 8 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-01-10 | 2016-03-01 | 2028-04-03 | Prioritization | NA | FALSE | $40,000 ¦ $65,000 | NA ¦ NA | 33.6369 | 3283.6369 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 2000 | 1000 | 50 | 33.6369 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
980 | KERN OIL: Upgrade 115 KV Line |  |  | Oildale CDP, Kern | The Project proposes to reconductor approximately 38 circuit miles of various 115 kV lines serving Bakersfield area in Kern County. The scope of the project include reconductoring 3.8 miles of the Kern PP-Westpark Nos. 1 and 2 115 kV Lines; 16.5 miles of the Kern-Magunden-Witco 115 kV Line; 3.5 miles of the Westpark-Magunden 115 kV Line; 5.0 miles of the Kern-Lamont 115 kV Line from Kern PP to Tevis Jct.; 5.0 miles of the Kern-Stockdale 115 kV line from Kern PP to Tevis Jct. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NERC TPL Standards | NA | 2026-03-06 | 64 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.2122 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5776126 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 8 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-01-10 | 2016-03-01 | 2028-04-03 | Prioritization | NA | FALSE | $40,000 ¦ $65,000 | NA ¦ NA | 51.3909 | 5248.1606 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 1000 | 1000 | 50 | 51.3909 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
981 | OCEI - Oakland X 115kV Bus Upgrade |  |  | Oakland, Alameda | The project will install one bus-sectionalizing circuit breakers and associated switches on the 115kV bus at Oakland X Substation, which will improve the reliability and operational flexibility of the buses. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-12 | 31 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 1.1294 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 5 | NA | NA | 5784219 | T.0004590 | OCEI -Oakland X 115kV Bus Upgrade | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-08-03 | 2023-03-01 | 2022-06-24 | NA | NA | FALSE | $56,000 ¦ $76,000 | NA ¦ NA | 7305.3813 | 7305.3813 | 3308.2185 | 3340.2826 | 74.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7305.3813 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 7023.5139 | 72.5163 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $300 Mil - $350 Mil ¦ Over $500 Mil ¦ $300 Mil - $350 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
982 | OCEI Moraga Bank 3 Switch Repl |  |  | Orinda, Contra Costa | The project will replace Bank 3 115kV switches 771, 773, 777, 779, 791, 793, & 795 which will improve the reliability and operational flexibility of the buses. | Substation - Switch | Upgrade/Retrofit | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-03 | 60 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 15.8714 | NA | 115 kV | NA | 8. Compliance/Commitments With Low Safety Risk | 1 | NA | NA | 5789153 | T.0004650 | OCEI-MORAGA 115KV BUS UPGRADE & BK 3 SWI | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-03 | 2022-04-17 | 2022-06-30 | NA | NA | FALSE | $56,000 ¦ $76,000 | NA ¦ NA | 2211.8949 | 2211.8949 | 778.6613 | 1383.4136 | 13.1324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2211.8949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 1951.8856 | 11.6127 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $300 Mil - $350 Mil ¦ Over $500 Mil ¦ $300 Mil - $350 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
983 | OCEI - Moraga 115kV Bus Upgrade |  |  | Orinda, Contra Costa | The project will install two bus-sectionalizing circuit breakers and one bus-tie breaker on the 115 kV buses at Moraga Substation, which will improve the reliability and operational flexibility of the buses. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-03-03 | 62 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 15.8714 | NA | 115 kV | NA | 8. Compliance/Commitments With Low Safety Risk | 1 | 5.1001 | Non-IGP | 5783340 | T.0004650 | OCEI-MORAGA 115KV BUS UPGRADE & BK 3 SWI | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-16 | 2022-04-17 | 2025-06-28 | Project Design | Materials | TRUE | $56,000 ¦ $76,000 | NA ¦ NA | 20506.3548 | 21155.3494 | 3341.7659 | 5653.5159 | 3720.9188 | 3741.6034 | 3819.664 | 652.6346 | 55.9 | 0 | 0 | 0 | 20446.8148 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 19513.7462 | 56.3781 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $300 Mil - $350 Mil ¦ Over $500 Mil ¦ $300 Mil - $350 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
984 | Gates 500kV DRS- LB-Gates #3 Convert |  |  | Fresno | The reactive support study results noted above indicated that a +/- 800 MVAR dynamic reactive device at Gates Substation is required to address the high voltage and to improve dynamic performance. The recommendation is to approve installation of a total of +/-800 MVAR of dynamic reactive support on the Gates 500kV bus. Interconnect new Transmission Owner (TO) LS Power Grid California’s Orchard Substation STATCOM Facility to Gates 500kV Bus The scope of the proposed project is to install a minimum of two equally sized blocks of reactive devices independently connected to the 500kV system at PG&E’s Gates Substation to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power output over the complete range of the capability (unless the facility experiences a planned or forced outage). Sub-synchronous Resonance studies are required to be completed and any identified mitigation shall be implemented as part of this project. The project scope will include connecting two blocks of the STATCOM to two separate bays of Gates 500kV breaker-and-a-half (BAAH) bus. STATCOM connections will require both overhead and high-voltage underground cables. The high-level scope includes the following: • Install two 550kV, 4000 Amp 63KA breakers with associated switches and structures. • Relocate 500kV Bank 12 connection from BAAH Bay 2 to Bay 1 using GIB. • Build two transition stations (one inside the PG&E substation and one outside on PG&E property) to connect LS Power’s two STATCOM connections to PG&E 500kV bus. • Install overhead conductors, underground high-voltage cables and associated structures and switches to connect two STATCOMs • Relocate Bank 12 tertiary reactors controls and protection equipment from the 500kV control building to new Tertiary Reactors control building installed under Gates Bank 11 project. This is needed to create space in the 500kV control building for new breakers. • Install protection, controls, and IT equipment for new 500 kV breakers needed to support LS Power project. • Upgrade ground grid and grading as required. | Substation - Other Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5555267 | T.0004672 | Gates: 500 kV Dynamic Voltage Support | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2024 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-08-21 | 2024-12-01 | 2024-09-05 | NA | NA | FALSE | $210,000 ¦ $250,000 | NA ¦ NA | 202.1697 | 202.1697 | 0 | 0 | 0 | 189.2645 | 12.9051 | 0 | 0 | 0 | 0 | 0 | 202.1697 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 173.088 | 11.8022 | 0 | 0% ¦ LS Power, Gates: 500 kV Dynamic Voltage Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
985 | Gates 500kV DRS- LB-Gates #3 Convert t |  |  | Merced | The reactive support study results noted above indicated that a +/- 800 MVAR dynamic reactive device at Gates Substation is required to address the high voltage and to improve dynamic performance. The recommendation is to approve installation of a total of +/-800 MVAR of dynamic reactive support on the Gates 500kV bus. Interconnect new Transmission Owner (TO) LS Power Grid California’s Orchard Substation STATCOM Facility to Gates 500kV Bus The scope of the proposed project is to install a minimum of two equally sized blocks of reactive devices independently connected to the 500kV system at PG&E’s Gates Substation to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power output over the complete range of the capability (unless the facility experiences a planned or forced outage). Sub-synchronous Resonance studies are required to be completed and any identified mitigation shall be implemented as part of this project. The project scope will include connecting two blocks of the STATCOM to two separate bays of Gates 500kV breaker-and-a-half (BAAH) bus. STATCOM connections will require both overhead and high-voltage underground cables. The high-level scope includes the following: • Install two 550kV, 4000 Amp 63KA breakers with associated switches and structures. • Relocate 500kV Bank 12 connection from BAAH Bay 2 to Bay 1 using GIB. • Build two transition stations (one inside the PG&E substation and one outside on PG&E property) to connect LS Power’s two STATCOM connections to PG&E 500kV bus. • Install overhead conductors, underground high-voltage cables and associated structures and switches to connect two STATCOMs • Relocate Bank 12 tertiary reactors controls and protection equipment from the 500kV control building to new Tertiary Reactors control building installed under Gates Bank 11 project. This is needed to create space in the 500kV control building for new breakers. • Install protection, controls, and IT equipment for new 500 kV breakers needed to support LS Power project. • Upgrade ground grid and grading as required. | Substation - Other Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 53.2803 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5555282 | T.0004672 | Gates: 500 kV Dynamic Voltage Support | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2024 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-08-21 | 2024-12-01 | 2024-09-05 | NA | NA | FALSE | $210,000 ¦ $250,000 | NA ¦ NA | 326.8812 | 326.8812 | 0 | 0 | 0 | 270.9218 | 55.7614 | 0.198 | 0 | 0 | 0 | 0 | 326.6832 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 244.1843 | 50.2583 | 0.17845 | 0% ¦ LS Power, Gates: 500 kV Dynamic Voltage Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
986 | Gates:500kV Dynamic Voltage Support |  |  | Fresno | The reactive support study results noted above indicated that a +/- 800 MVAR dynamic reactive device at Gates Substation is required to address the high voltage and to improve dynamic performance. The recommendation is to approve installation of a total of +/-800 MVAR of dynamic reactive support on the Gates 500kV bus. Interconnect new Transmission Owner (TO) LS Power Grid California’s Orchard Substation STATCOM Facility to Gates 500kV Bus The scope of the proposed project is to install a minimum of two equally sized blocks of reactive devices independently connected to the 500kV system at PG&E’s Gates Substation to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power output over the complete range of the capability (unless the facility experiences a planned or forced outage). Sub-synchronous Resonance studies are required to be completed and any identified mitigation shall be implemented as part of this project. The project scope will include connecting two blocks of the STATCOM to two separate bays of Gates 500kV breaker-and-a-half (BAAH) bus. STATCOM connections will require both overhead and high-voltage underground cables. The high-level scope includes the following: • Install two 550kV, 4000 Amp 63KA breakers with associated switches and structures. • Relocate 500kV Bank 12 connection from BAAH Bay 2 to Bay 1 using GIB. • Build two transition stations (one inside the PG&E substation and one outside on PG&E property) to connect LS Power’s two STATCOM connections to PG&E 500kV bus. • Install overhead conductors, underground high-voltage cables and associated structures and switches to connect two STATCOMs • Relocate Bank 12 tertiary reactors controls and protection equipment from the 500kV control building to new Tertiary Reactors control building installed under Gates Bank 11 project. This is needed to create space in the 500kV control building for new breakers. • Install protection, controls, and IT equipment for new 500 kV breakers needed to support LS Power project. • Upgrade ground grid and grading as required. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 500 kV | NA | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5784840 | T.0004672 | Gates: 500 kV Dynamic Voltage Support | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2019 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-04-03 | 2024-12-01 | 2024-09-25 | NA | NA | TRUE | $210,000 ¦ $250,000 | NA ¦ NA | 50861.3424 | 51699.1043 | 564.8449 | 4474.5306 | 22504.2552 | 18895.784 | 4024.4549 | 1078.4431 | 0 | 0 | 0 | 0 | 50620.6612 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 45156.5978 | 3891.1901 | 232.7114 | 0% ¦ LS Power, Gates: 500 kV Dynamic Voltage Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
987 | TESLA: 230KV BUS REACTORS D - E |  |  | Alameda | This project proposes to replace the existing bus series reactors (8&16 ohms) in 230kV bus sections C, D & E with 36 ohms reactors and make the necessary connection changes. The proposed project will limit the fault duty to commonly used standard equipment in the industry to 63KA and comply with BES Transmission System Reliability and NERC requirements. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-19 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | 230 kV | NA | 8. Compliance/Commitments With Low Safety Risk | 9 | NA | NA | 5784841 | T.0004673 | Tesla 230 kV Series Reactor Replacement | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-19 | 2023-12-31 | 2023-06-14 | NA | NA | FALSE | $24,000 ¦ $29,000 | NA ¦ NA | 16942.7732 | 16942.7732 | 1586.1892 | 9991.8688 | 4955.7861 | 139.5394 | 10.6475 | 0 | 0 | 0 | 0 | 0 | 16942.7732 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 16023.1518 | 132.7277 | 10.1278 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
988 | TESLA: 230KV BUS REACTORS C - D |  |  | Alameda | This project proposes to replace the existing bus series reactors (8&16 ohms) in 230kV bus sections C, D & E with 36 ohms reactors and make the necessary connection changes. The proposed project will limit the fault duty to commonly used standard equipment in the industry to 63KA and comply with BES Transmission System Reliability and NERC requirements. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-19 | 57 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5793942 | T.0004673 | Tesla 230 kV Series Reactor Replacement | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-06-15 | 2023-12-31 | 2024-03-25 | NA | NA | TRUE | $24,000 ¦ $29,000 | NA ¦ NA | 9524.8489 | 9524.8489 | 22.0468 | 3746.2333 | 3223.6406 | 2313.2964 | 211.921 | 0 | 0 | 0 | 0 | 0 | 9524.8489 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 8727.7438 | 197.7261 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
989 | Pease: Inst Capacitors |  |  | Sutter | This project will entail the following: 1.Loop the Pease – Marysville 60 kV Line into E. Marysville Substation. 2.Install a 200MVA, 115/60kV (LTC) transformer at E. Marysville Substation. 3.Upgrade the terminal equipment at E. Marysville Substation. 4.Install 25 MVAR of voltage support at the Pease Substation 115 kV bus. | Substation - Voltage Support Equipment | New | NA | NA | Economic | Voltage Support | NERC TPL Standards | NA | 2026-02-10 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 4.6809 | NA | 115 kV | NA | 8. Compliance/Commitments With Low Safety Risk | 14 | 5.1001 | Non-IGP | 5785382 | T.0004728 | East Marysville 115/60 kV Project | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-03-07 | 2022-12-31 | 2029-04-03 | Prioritization | NA | FALSE | $26,000 ¦ $32,000 | NA ¦ NA | 103.0538 | 16755.7066 | -0.235 | 4.6211 | 5.082 | 2.5996 | 25.8212 | 78.3477 | 4000 | 500 | 0 | 0 | 101.6502 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
990 | South of Mesa Upgrade - Sub Voltage Sup |  |  | Lompoc, Santa Barbara | This project proposes to upgrade approximately 21.3 miles of conductor on the Sisquoc – Santa Ynez SW STA 115 kV Line, install 20 Mega Volt-ampere reactive (MVAR) shunt capacitors at Cabrillo Substation and install Remedial Action Scheme (RAS) (formerly known as Special Protection Scheme (SPS)) on the Sisquoc – Santa Ynez SW STA 115 kV Line. Completion of this project is needed to improve the electric transmission system reliability and operational flexibility in the Santa Barbara County. This project will be funded under Major Work Category (MWC) 60, Electric Transmission Line Capacity and 61, Electric Transmission Substation Capacity. The project has a Risk Informed Budget Allocation (RIBA) score of 137. The RIBA score is based on the impact and frequency of three risk categories: safety, reliability and environmental. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-02-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.3073 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 14 | 5.1001 | Non-IGP | 5785938 | T.0004832 | South Of Mesa Upgrade Project | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-10-03 | 2023-12-31 | 2029-05-07 | Prioritization | NA | FALSE | $29,600 ¦ $59,200 | NA ¦ NA | 356.1455 | 20739.5769 | -0.3342 | 0 | 0 | 0 | 0 | 80.9718 | 1559.1312 | 12620.6558 | 6127.4897 | 0 | 351.3284 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
991 | San Ardo: Install 60kV Voltage Support |  |  | Monterey | The project scope of work includes following: Install a 10 Mvar Shunt Capacitor at San Ardo Substation. This location has been revised due to space limitation at Oil Fields Substation. Convert San Ardo 60 kV bus into a ring-bus configuration; loop Coburn - Oil Fields #1 & #2 lines into the new ring bus and install the capacitor bank. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.44363 | NA | 60 kV | 76 | 5. Compliance/Commitments With Strong Safety Link | 19 | 5.1001 | Non-IGP | 5790100 | T.0004889 | San Ardo: Oil Fields Voltage Support | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2030-02-22 | 2022-05-01 | 2031-09-05 | Prioritization | NA | FALSE | $7,000 ¦ $10,000 | NA ¦ NA | 755.5213 | 25863.3203 | 47.5603 | 0 | 0 | 0 | 4.9179 | 118.2744 | 1000 | 8000 | 15000 | 1000 | 745.0459 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
992 | LSPower Round Mtn:Modify SC4 |  |  | Round Mountain CDP, Shasta | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-09 | 24 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 29.1389 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5816260 | T.0006815 | LSPower Round Mountain Area 500kV Dynami | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2025 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-02-03 | 2024-12-31 | 2027-07-15 | Customer Action | NA | TRUE | $160,000 ¦ $190,000 | NA ¦ NA | 8138.6957 | 15967.6224 | 0 | 0 | 0 | 0 | 8018.5738 | 6586.7162 | 1358.4923 | 3.8401 | 0 | 0 | 8018.5738 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power, Round Mountain 500 kV Dynamic Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
993 | LSPOWER TABLE MTN:MODIFY 500KV SERIES CAPS |  |  | Round Mountain CDP, Shasta | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-09 | 23 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | 29.1389 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5793954 | T.0006815 | LSPower Round Mountain Area 500kV Dynami | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2020 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-02-03 | 2024-12-31 | 2027-03-24 | Customer Action | NA | TRUE | $160,000 ¦ $190,000 | NA ¦ NA | 9760.9465 | 20294.9807 | 287.7999 | 268.3997 | 8809.1949 | 3909.7443 | -3810.6913 | 10069.7446 | 760.7886 | 0 | 0 | 0 | 9464.4475 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power, Round Mountain 500 kV Dynamic Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
994 | LSPOWER TABLE MTN:MODIFY 500KV SERIES CAPS |  |  | Butte | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-20 | 24 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5793953 | T.0006815 | LSPower Round Mountain Area 500kV Dynami | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2020 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2023-02-15 | 2024-12-31 | 2026-04-23 | Customer Action | NA | TRUE | $160,000 ¦ $190,000 | NA ¦ NA | 42134.2599 | 44073.1426 | 240.0967 | 13447.4834 | 21073.7509 | 29512.1512 | -23308.0877 | 3085.1538 | 22.5944 | 0 | 0 | 0 | 40965.3945 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power, Round Mountain 500 kV Dynamic Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
995 | LSPOWER TABLE MTN MODIFY SC2 |  |  | Butte | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-20 | 24 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 47.516 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5816258 | T.0006815 | LSPower Round Mountain Area 500kV Dynami | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2025 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2023-02-15 | 2024-12-31 | 2026-04-30 | Customer Action | NA | TRUE | $160,000 ¦ $190,000 | NA ¦ NA | 36439.884 | 40774.8927 | 0 | 0 | 0 | 0 | 35935.0865 | 4839.8063 | 0 | 0 | 0 | 0 | 35935.0864 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power, Round Mountain 500 kV Dynamic Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
996 | LSPower Table Mtn: Modify 500kV CB722 |  |  | Butte | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-20 | 23 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 47.516 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5816259 | T.0006815 | LSPower Round Mountain Area 500kV Dynami | 9 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2025 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-09-26 | 2024-12-31 | 2026-01-14 | Customer Action | NA | TRUE | $160,000 ¦ $190,000 | NA ¦ NA | 3178.1232 | 11202.1814 | 0 | 0 | 0 | 0 | 1768.749 | 7439.3938 | 26.6758 | 1967.3628 | 0 | 0 | 1768.749 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 2870.2153 | 0% ¦ LS Power, Round Mountain 500 kV Dynamic Support | NA ¦ NA | NA | NA ¦ NA | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
997 | LOS ESTEROS-NORTECH 115KV SERIES REACTOR |  |  | San Jose, Santa Clara | To address the near-term critical, category P1 contingency driven issues, the ISO is recommending approval of adding series compensation devices on the Los Esteros-Nortech 115 kV line. As part of this scope, 2 Ohms reactor will be added on the Los Esteros-Nortech 115kV Line at Los Esteros Substation. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-09 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5802781 | T.0008698 | Los Esteros-Nortech 115kV Series Reactor | 3 | 61 | NA ¦ Ex112231 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-02-23 | 2023-06-01 | 2026-06-01 | Prioritization | NA | TRUE | $10,000 ¦ $15,000 | NA ¦ NA | 12566.6682 | 19897.8847 | 0 | 0 | 172.3946 | 3275.0319 | 7582.9772 | 8857.6209 | 9.86 | 0 | 0 | 0 | 11030.4037 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
998 | Nortech Los Esteros Line Upgrade |  |  | San Jose, Santa Clara | To address the near-term critical, category P1 contingency driven issues, the ISO is recommending approval of adding series compensation devices on the Los Esteros-Nortech 115 kV line. As part of this scope, 2 Ohms reactor will be added on the Los Esteros-Nortech 115kV Line at Los Esteros Substation. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-02-08 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.6495 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5808476 | T.0008698 | Los Esteros-Nortech 115kV Series Reactor | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-02-23 | 2023-06-01 | 2026-06-01 | Prioritization | NA | TRUE | $10,000 ¦ $15,000 | NA ¦ NA | 660.4482 | 2720.8501 | 0 | 0 | 0 | 112.312 | 316.2506 | 2292.2875 | 0 | 0 | 0 | 0 | 428.5626 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
999 | Coppermine 70 kV Reinforcement Caps |  |  | Fresno | This project proposes to reconductor roughly 13 circuit miles of the Borden - Coppermine 70 kV Line and to install a voltage support device in the area. This will provide additional transmission capacity to serve electric customers in Madera and Fresno Counties. The project scope of work includes following: •Reconductor roughly 9.5 circuit miles of line between Borden and Cassidy Substations (from Pole 19/10A to Cassidy Substation) on the Borden-Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 700 Amps during summer normal conditions •Reconductor roughly 3.6 circuit miles of line between Cassidy and Coppermine Substations (from Pole 03/07 to Coppermine Substation) on the Borden - Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 500 Amps during summer normal conditions. •Remove any limiting components to achieve the full conductor capability •Install 20 MVar voltage support device at Coppermine Substation. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.0827 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5803381 | T.0008870 | Coppermine 70 kV Reinforcement Project | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-09-20 | 2027-05-01 | 2030-04-04 | Material | NA | FALSE | $15,800 ¦ $31,600 | NA ¦ NA | 486.8435 | 46017.0154 | 0 | 0 | 0 | 0 | 467.6294 | 1137.7444 | 800 | 700 | 14100 | 3800 | 467.6294 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
1000 | Moss Landing-Las Aguilas Series Reactor |  |  | San Benito | Install 10 Ohms series reactor on the Moss Landing-Las Aguilas 230kV Line at Las Aguilas Substation. CAISO recommended the Moss Landing-Las Aguilas 230kV series reactor(10 Ohm) project in 2021-2022 Transmission plan. The series reactor can mitigate the transmission congestion on Moss Landing-Las Aguilas path during summer high solar generation hours in Fresno area. Based on CAISO's economic analysis, the economic benefit to be brought by Moss Landing to Las Aguilas series reactor project will be 3 to 4 times of the project cost. This project will bring net saving and benefit the ratepayers. To address the transmission congestion on Moss Landing-Las Aguilas path, the CAISO is recommending approval of adding series compensation devices on the Moss Landing-Las Aguilas 230kV line. Current studies show that adding about 10 Ohm reactor on the Moss Landing-Las Aguilas 230kV line would be an optimal solution. | Substation - Voltage Support Equipment | New | NA | NA | Economic | Voltage Support | NERC TPL Standards | NA | 2026-02-10 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.0534 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807121 | T.0009559 | Moss Landing-Las Aguilas Series Reactor | 1 | 61 | NA ¦ EX112240 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-04-16 | 2026-01-01 | 2027-08-24 | Prioritization | NA | TRUE | $30,000 ¦ $40,000 | NA ¦ NA | 255.3329 | 14657.1337 | 0 | 0 | 0 | 22.7903 | 228.4815 | 275.7357 | 14112.2059 | 0 | 0 | 0 | 251.2718 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
1001 | Lone Tree-Cayetano-Newark Series Reactor |  |  | Alameda ¦ Antioch, Contra Costa ¦ Brentwood, Contra Costa ¦ Contra Costa | Add 6 SmartValve units (2 SmartValve 10-1800 units per phase) to the Cayetano – Lone Tree 230 kV line Add 6 SmartValves units (2 SmartValve 10-1800 units per phase) to the Las Positas - Newark 230 kV Line | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2025-08-26 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | NA | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807124 | T.0009573 | Lone Tree_Cayetano-Newark Series Reactor | 2 | 61 | NA ¦ EX113233 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-04-17 | 2027-12-31 | 2028-08-30 | Scope Change | NA | FALSE | 25000 | NA ¦ NA | 241.1029 | 22963.5021 | 0 | 0 | 0 | 1.3965 | 221.4346 | 292.3937 | 7506.58 | 190.35 | 0 | 0 | 222.831 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
1002 | IGNACIO AREA UPGRADE_ GRENBRAE SUB |  |  | Larkspur, Marin | Reconductor Ignacio - San Rafael No. 1 115 kV Line, Ignacio - Alto 60 kV Line, and Ignacio - San Rafael No. 3 115 kV Line section from Ignacio - Las Gallinas as well as upgrade limiting equipment on lines. Add a 10 MVAR shunt capacitor at Greenbrae 60 kV Substation and associated substation upgrades to accommodate this installation | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-02-09 | NA | Steady State Power Flow System Analysis | Wires - Location/Route Alternative | Over $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.0901 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807462 | T.0009719 | Ignacio Area Upgrade | 6 | 61 | NA ¦ EX113201 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2012 ¦ 2018 | FALSE | 2012 ¦ 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-12-18 | 2023-12-01 | 2029-03-20 | Prioritization | NA | FALSE | 37000 | NA ¦ NA | 302.3962 | 24385.6591 | 0 | 0 | 0 | 44.9267 | 196.1652 | 207.742 | 144.3075 | 11000 | 3500 | 500 | 241.0919 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
1003 | Mesa: Install 115kV Shunt Reactors |  |  | Nipomo CDP, San Luis Obispo | Add 120 Mvar shunt reactor (3X40 MVAR or 4X30 MVAR) and removal of one or two shunt capacitor steps at Mesa 115 kV. Mitigate high-voltages observed in real time around or right after midnight, during low demand and zero solar output periods at Diablo Canyon 230 kV substation | Substation - Reactive Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-09 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.5414 | NA | 230 kV | NA | NA | NA | 1.0001 | Non-IGP | 5811258 | T.0010474 | Mesa: Install 115kV Shunt Reactors | 1 | 61 | NA ¦ EX113677 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-04-14 | 2027-05-01 | 2029-01-12 | Prioritization | NA | FALSE | $35,000 ¦ $70,000 | NA ¦ NA | 778.3915 | 51200.7829 | 0 | 0 | 0 | 27.7671 | 619.7418 | 1903.2741 | 11600 | 37000 | 50 | 0 | 647.5088 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
1004 | SALINAS AREA REINF BUENA VISTA SUB |  |  | Salinas, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-02-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.111 | NA | 60 kV | NA | NA | NA | 1.0001 | Non-IGP | 5811922 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-05-25 | TBD | 2028-10-10 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 72.1279 | 29642.3349 | 0 | 0 | 0 | 0 | 58.524 | 128.3429 | 700 | 500 | 500 | 500 | 58.5239 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
1005 | SALINAS AREA REINF INDUSTRIAL ACRE |  |  | Salinas, Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.19612 | NA | 60 kV | NA | NA | NA | 1.0001 | Non-IGP | 5811923 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-07-05 | TBD | 2032-12-31 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 39.7564 | 22819.9191 | 0 | 0 | 0 | 0 | 32.6692 | 141.814 | 1250 | 5000 | 1000 | 1000 | 32.6692 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
1006 | SALINAS AREA REINF FIRESTONE SUB |  |  | Monterey | The project scope of work for the Salinas Area Reinforcement includes following: • Build a new Chualar 115 kV Substation with two distribution transformers to serve the load from Gonzales 60 kV Substation. The Gonzales 60 kV substation will be decommissioned. • Rebuild the existing 60 kV lines from Salinas-Spence, Salinas-Firestone and Firestone-Spence to 115 kV to achieve minimum rating of 1400 A for the Salinas-Buena Vista and Salinas-Sanborn Jct sections, and 800 A for the Buena Vista-Firestone-Spence and Sanborn Jct-Spence Jct-Spence sections • Maintain the existing bus configuration at Spence after 115 kV conversion. • Supply Chualar 115 kV Substation from Spence with 115 kV lines normally closed. Normally close Buena Vista – Industrial Acres and loop-in the existing line into Industrial Acres. • Spence-Chualar and Spence Jct-Chualar Jct-Chualar sections should achieve minimum rating of 500 A, and Sanborn Jct-Industrial Acres-Buena Vista sections should achieve minimum rating of 950 A • Replace the transformers and other high voltage side equipment at the following substations to allow 115 kV operation: Industrial Acres, Spence, Buena Vista, Fresh Express and Firestone. • Terminate two lines (Salinas-Spence, Salinas-Firestone) at Salinas 115 kV bus to convert and operate the Salinas - Chualar system at 115 kV. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-02-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.14648 | NA | 60 kV | NA | NA | NA | 1.0001 | Non-IGP | 5811924 | T.0010623 | Salinas Area Reinf Chualar Sub | 17 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-07-05 | TBD | 2032-12-31 | NA | NA | FALSE | $226,100 ¦ $452,300 | NA ¦ NA | 52.9381 | 20852.8682 | 0 | 0 | 0 | 0 | 44.398 | 139.8813 | 1250 | 5000 | 1000 | 1000 | 44.398 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
1007 | Camden: Install 30MVAR Voltage Support |  |  | Fresno | Reconductor Camden-Kingsburg 70 kV and add 30 MVAR voltage support at Comden substation. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-02-18 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.2099 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5812915 | T.0010712 | Camden: Install 30MVAR and 70kV Recond | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-12-15 | 2030-12-01 | 2030-03-15 | NA | NA | FALSE | $50,000 ¦ $100,000 | NA ¦ NA | 119.9306 | 18394.6093 | 0 | 0 | 0 | 1.2609 | 75.1003 | 858.2325 | 0 | 0 | 0 | 0 | 76.3612 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
1008 | KINGSBURG SUB: VOLTAGE SUPPORT |  |  | Fresno | Reconductor Camden-Kingsburg 70 kV and add 30 MVAR voltage support at Camden substation. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | NA | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.37 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5564703 | T.0010712 | Camden: Install 30MVAR and 70kV Recond | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-12-15 | 2030-12-01 | 2030-03-15 | NA | NA | FALSE | $50,000 ¦ $100,000 | NA ¦ NA | 4.203 | 15209.1828 | 0 | 0 | 0 | 0 | 2.7752 | 70.3806 | 0 | 0 | 0 | 0 | 2.7752 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
1009 | CORTINA #3 MERIDIAN SUB VOLTAGE SUPPORT |  |  | Meridian CDP, Sutter | Reconductor about 6.0 miles between the Cortina Substation and Wadham Jct on the Cortina #3 60 kV to achieve minimum conductor rating of 1014 AMPS for summer normal rating and 1127 AMPS for summer emergency rating. Reconductor about 1.5 miles between the Wadham Jct and Wescot (007/125) on the Cortina #3 60 kV to achieve minimum conductor rating of 1014 AMPS for summer normal rating and 1127 AMPS for summer emergency rating. Reconductor about 1.5 miles between the Wescot (007/125) and Willaims Substation on the Cortina #3 60 kV to achieve minimum conductor rating of 1014 AMPS for summer normal rating and 1127 AMPS for summer emergency rating. Install a 15 MVAR shunt capacitor at Meridian 60 kV substation. Upgrade any limiting components as necessary to achieve full conductor capacity | Substation - Line Termination | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-02-18 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.98054 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815747 | T.0011146 | Cortina #3 60 kV Reconductoring Project | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | 2025 | NA | https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2031-07-21 | 2031-05-01 | 2032-04-08 | Customer action | NA | FALSE | 55500 | NA ¦ NA | 20.1128 | 6254.2617 | 0 | 0 | 0 | 0 | 16.3776 | 426.4671 | 0 | 0 | 0 | 0 | 16.3776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/iso-board-approved-2024-2025-transmission-plan.pdf
1010 | COVELO: INSTALL 60KV VOLTAGE SUPPORT |  |  | Covelo CDP, Mendocino | Install a 10 MVAR Shunt Capacitor at Covelo 60 kV due to P1 low voltages starting 2025 at Covelo 60 kV substation. | Substation - Voltage Support Equipment | New | NA | NA | Reliability | Voltage Support | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.65904 | NA | 60 kV | NA | NA | NA | 4.01 | Non-IGP | 5816337 | T.0011512 | COVELO: INSTALL 60KV VOLTAGE SUPPORT | 1 | 61 | NA ¦ EX113675 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-06-05 | 2030-12-01 | 2028-09-12 | NA | NA | FALSE | $11,000 ¦ $22,000 | NA ¦ NA | 24.6056 | 16579 | 0 | 0 | 0 | 0 | 6.6267 | 571.83 | 0 | 0 | 0 | 0 | 6.6267 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
1011 | PEASE: Install BK 5 |  |  | Sutter | Install a second 115/60kV transformer and upgrade the 115kV and 60kV buses at Pease Substation. | Substation - Transformer | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-02-10 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.6809 | NA | 115 ¦ 60 kV | 76 | 8. Compliance/Commitments With Low Safety Risk | 14 | NA | NA | 5756140 | T.0000598 | Pease Transformer Add & Bus Upgrade | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2015 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-09-07 | 2016-05-31 | 2020-12-08 | Material | NA | FALSE | $25,000 ¦ $35,000 | NA ¦ NA | 12874.8154 | 12874.8154 | 885.5154 | 492.6064 | 562.2293 | 1.804 | 0 | 0 | 0 | 0 | 0 | 0 | 12874.8154 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 879.0681 | 472.8102 | 539.6354 | 1.7316 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $50 Mil – $75 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1012 | PEASE: Reconfigure 115 KV Bus to BAAH |  |  | Sutter | Install a second 115/60kV transformer and upgrade the 115kV and 60kV buses at Pease Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NERC TPL Standards | NA | 2026-02-10 | 10 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.6809 | NA | 115 kV | 76 | 8. Compliance/Commitments With Low Safety Risk | 14 | NA | NA | 5768208 | T.0000598 | Pease Transformer Add & Bus Upgrade | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-07-25 | 2016-05-31 | 2020-12-10 | Workforce | NA | FALSE | $25,000 ¦ $35,000 | NA ¦ NA | 31602.6289 | 31602.6289 | 2322.647 | 1122.319 | 1995.9522 | 377.4101 | 0 | 0 | 0 | 0 | 0 | 0 | 31602.6289 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 2184.7926 | 1072.9739 | 1908.1959 | 360.8165 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $50 Mil – $75 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1013 | RIO OSO: Install BK 1 and BK 2 |  |  | Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Transformer | Upgrade/Retrofit | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-04 | 70 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.3219 | NA | 230 ¦ 115 kV | 318 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5726234 | T.0000614 | Rio Oso Substation Upgrade | 12 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2014 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-07-05 | 2009-05-01 | 2025-05-02 | Prioritization | NA | TRUE | $10,000 ¦ $20,000 | NA ¦ NA | 17498.9222 | 18751.2642 | 5866.8701 | -2159.2006 | 2104.3251 | 2411.9903 | 1446.3159 | 860.9342 | 634.069 | 0 | 0 | 0 | 17256.2611 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 16775.0973 | 233.5232 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1014 | CASCADE: Install BK 2 Phase 1 |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Transformer | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-02-16 | 23 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | NA | 115 ¦ 60 kV | 58 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.1001 | Non-IGP | 5777641 | T.0000651 | Cascade Substation Upgrade | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-07-09 | 2014-03-01 | 2025-01-23 | Prioritization | Clearances | TRUE | $20,000 ¦ $30,000 | NA ¦ NA | 21160.2366 | 22156.1948 | 4609.8332 | 1073.484 | 1173.9983 | 2748.997 | 3932.5303 | 1169.3605 | 0 | 0 | 0 | 0 | 20986.8343 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 20758.2509 | 171.0309 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1015 | CASCADE: Install BK 2 Phase 2 |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Transformer | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-02-16 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | NA | 115 ¦ 60 kV | 58 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.1001 | Non-IGP | 5777642 | T.0000651 | Cascade Substation Upgrade | 10 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-03 | 2014-03-01 | 2025-08-01 | Prioritization | NA | TRUE | $20,000 ¦ $30,000 | NA ¦ NA | 4019.1113 | 4634.6869 | 1236.1694 | 235.5049 | 238.5812 | 260.2907 | 1429.8504 | 677.7064 | 0 | 0 | 0 | 0 | 3956.9805 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 3661.2667 | 56.5034 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1016 | GLENN: Replace BK 1 |  |  | Glenn | This project will replace GLENN Bank 1 with a new 230/60 kV, 200 MVA transformer with a Load Tap Changer (LTC) and parallel scheme under MWC-61 | Substation - Transformer | Upgrade/Retrofit | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-16 | 61 | Steady State Power Flow System Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.7152 | NA | 230 ¦ 60 kV | 45 | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5757478 | T.0000817 | Glenn: Replace 230/60kV Bank 1 | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2016 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-04-30 | 2018-03-01 | 2024-03-28 | Workforce | NA | TRUE | $5,000 ¦ $10,000 | NA ¦ NA | 20208.8224 | 20284.7585 | 2151.6674 | 745.3453 | 1038.8603 | 2380.8066 | 841.1971 | 85.0743 | 0 | 0 | 0 | 0 | 20199.6843 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 18712.0349 | 807.4593 | 8.7716 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1017 | PITTSBURG: Install 230/115KV BK14 Phase3 |  |  | Pittsburg, Contra Costa | This project proposes to add a third Pittsburg 230/115 kV Transformer with a rating of 420 MVA. Completion of this project will provide adequate transmission capacity to enable safe and reliable electric service to electric customers served by Pittsburg Substation | Substation - Transformer | New | NA | T.0004581 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 28.8512 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813499 | T.0000946 | PITTSBURG: Install 230/115KV TRANSFORMER | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-04-24 | 2011-05-01 | 2028-10-12 | Prioritization | NA | FALSE | $10,000 ¦ $20,000 | NA ¦ NA | 53.9181 | 31997.1531 | 0 | 0 | 0 | 0 | 39.9747 | 768.8875 | 0 | 0 | 0 | 0 | 39.9747 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1018 | PITTSBURG: Install 230/115KV BK14 Phase2 |  |  | Pittsburg, Contra Costa | This project proposes to add a third Pittsburg 230/115 kV Transformer with a rating of 420 MVA. Completion of this project will provide adequate transmission capacity to enable safe and reliable electric service to electric customers served by Pittsburg Substation | Substation - Transformer | New | NA | T.0004581 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.72358 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813447 | T.0000946 | PITTSBURG: Install 230/115KV TRANSFORMER | 4 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-12-07 | 2011-05-01 | 2028-05-01 | Prioritization | NA | FALSE | $10,000 ¦ $20,000 | NA ¦ NA | 1296.7239 | 19125.2692 | 0 | 0 | 0 | 189.9798 | 800.8026 | 801.8274 | 0 | 0 | 0 | 0 | 990.7825 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1019 | PITTSBURG: Install 230/115KV TRANSFORMER |  |  | Pittsburg, Contra Costa | This project proposes to add a third Pittsburg 230/115 kV Transformer with a rating of 420 MVA. Completion of this project will provide adequate transmission capacity to enable safe and reliable electric service to electric customers served by Pittsburg Substation | Substation - Transformer | New | NA | T.0004581 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-06 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.72358 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 14 | 5.1001 | Non-IGP | 5768148 | T.0000946 | PITTSBURG: Install 230/115KV TRANSFORMER | 4 | 61 | NA ¦ 5738798 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2019 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-02-01 | 2011-05-01 | 2025-06-27 | Prioritization | NA | FALSE | $10,000 ¦ $20,000 | NA ¦ NA | 3789.3571 | 62000 | 975.1644 | 223.7535 | 315.6961 | 282.5169 | 138.322 | 15.7728 | 15000 | 30000 | 12000 | 5000 | 3773.5843 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 3773.6398 | 15.7728 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1020 | GATES: Repl 500/230 KV BAAH #2 |  |  | Fresno | Installing three bays of new 230kV BAAH bus will improve system reliability, allow for interconnection of new generation, and improve maintenance and operational flexibility of the Gates Substation. PG&E owns enough land at Gates Substation to install future bays. The ultimate plan is to install 15 bays of 230kV BAAH at the substation. Specific components of the project include: • Build a new greenfield three-bay 230kV BAAH Bus Section F, with provision for future expansion; • Connect the new Bus Section F to the existing Bus Section E; • Install two sectionalizing breakers between the bus sections; • Transfer the four line and one transformer connections from Bus Section E to the new Bus Section F; • Install a new 230kV MPAC building; • Construct an access road to the new BAAH Bus Section F; • Build approximately 0.5 mile of security fence and extend concrete security wall (5,180 ft.); and • Upgrade terminal equipment at Midway, Arco, and Mustang Switching Stations, as needed. | Substation - Transformer | Upgrade/Retrofit | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-12 | 71 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 ¦ 230 kV | 318 | NA | NA | NA | NA | 5768213 | T.0000960 | Gates 230kV Bus Upgrade | 4 | 61 | NA ¦ 5751202 ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-01-09 | 2019-04-30 | 2018-12-11 | NA | NA | FALSE | 70000 | NA ¦ NA | 38690.8409 | 38690.8409 | 35.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38690.8409 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 34.5947 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1021 | Bridgeville: Inst Relays for Cottonwood |  |  | Humboldt | Project scope is to replace both 230/115kV transmission transformers which will address the 115kV high voltage issue and improve reliability of the North Valley transmission system. Installing the 115kV bus tie breakers will address NERC category P2 breaker fault of Cottonwood CB 102 or, a NERC category P4 nearby fault plus a CB 102 fault. The CAISO approved shunt reactors/transformer replacement to mitigate the high voltage issue and additionally the 115kV bus tie breakers to mitigate the P2 and P4 contingencies. The MPAC and breakers replacement will replace the deteriorated asset and capture the efficiency of upgrading protection and controls, avoid rework and multiple clearances. The high-level scope includes the following: • Replace the existing Banks 1 and 4 with 230/115kV 420MVA, with LTC and associated bus selector switches. • Install new bay and new 230kV breaker to connect new Bank 1 to 230kV bus. • Replace Bank 1 low-side breaker CB 172 and the associated switches. • Replace Bank 4 low-side CB 192 and the associated switches. • Expand existing 115kV MPAC to accommodate protection and controls. • Expand SPCC to accommodate increased oil quantity of new banks. • Install new sectionalizing CB’s 912 and 922 w/switches to sectionalize 115kV bus to Sections D and E. • Install new CB 132 with switches and relocate Trinity-Cottonwood 115kV line to Bus Section E. • Install new bus paralleling breaker CB 102 with switches in Bus Section E. • Install new bus paralleling breaker CB 902 with switches in Bus Section D. • Replace the existing OCBs 142 and 152 with non-SF6 breakers and the associated switches. • Replace six of the existing 230kV OCBs (CBs 222, 232, 272, 292, 522, and 542) with new 230kV 2000A gas circuit breakers, and the associated breaker and bus selector switches. • Install new 230kV 2000A bus paralleling breaker (CB 502) and associated switches in place of the existing Transformer 1 CB 512 position. • Replace switches 213, 357, 359, 367, and 369. • Install new MPAC Building to house the protection, automation, and control equipment for the 230kV Bus Sections “E” and “F”. | Substation - Protection Relay | New | NA | T.0004659 | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-02-04 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 1.1134 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5788601 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2021 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-05-03 | 2028-04-30 | 2027-08-09 | NA | NA | TRUE | 51200 | NA ¦ NA | 307.1843 | 1384.1443 | 2.2138 | 0.7326 | 7.3608 | 25.4665 | 263.8549 | 80.0167 | 963.4199 | 0 | 0 | 0 | 299.6286 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1022 | GATES REPL BK 12 500/230 KV TRANSFORMER |  |  | Fresno | Installing the Gates 500/230 kV Transformer No. 2 is needed to provide deliverability to renewable generation in the Fresno area and additional flexibility for pumping operations at HPSP. The scope of work includes the following: • Install Gates 500/230 kV Transformer No. 2; • Install half-bay (two breakers and disconnect switches) on the existing 500 kV BAAH bus; • Connect transformer to 500 kV and 230 kV BAAH buses; • Upgrade overstressed circuit breakers and terminal equipment, as needed; and install low-side reactors; • Repair collapsed trench and associated work. | Substation - Bus Arrangement | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 ¦ 230 kV | 318 | 5a. Mitigates System Wide Failure Risk | NA | NA | NA | 5768212 | T.0003388 | GATES 500kV Bank 12 Installation | 3 | 61 | NA ¦ 5751202 ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-01-31 | 2017-05-01 | 2019-11-13 | Prioritization | NA | FALSE | $75,000 ¦ $85,000 | NA ¦ NA | 4330.3387 | 4330.3387 | 388.2181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4330.3387 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 388.2181 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1023 | GATES BK 12 500/230KV TRANSFORMER |  |  | Fresno | Installing the Gates 500/230 kV Transformer No. 2 is needed to provide deliverability to renewable generation in the Fresno area and additional flexibility for pumping operations at HPSP. The scope of work includes the following: • Install Gates 500/230 kV Transformer No. 2; • Install half-bay (two breakers and disconnect switches) on the existing 500 kV BAAH bus; • Connect transformer to 500 kV and 230 kV BAAH buses; • Upgrade overstressed circuit breakers and terminal equipment, as needed; and install low-side reactors; • Repair collapsed trench and associated work. | Substation - Transformer | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 500 ¦ 230 kV | 318 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5787467 | T.0003388 | GATES 500kV Bank 12 Installation | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-01-31 | 2017-05-01 | 2020-04-22 | Prioritization | NA | FALSE | $75,000 ¦ $85,000 | NA ¦ NA | 46452.7778 | 46452.7778 | -8.2474 | 0 | 0 | 770.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 46452.7778 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 ¦ 2026 | -8.2474 | 0 | 0 | 770.8019 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1024 | WILSON: Install 115 KV Transformer |  |  | Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Transformer | New | NA | T.0001381 ¦ T.0002231 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-04 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 22.8151 | NA | 115 kV | 58 | 8. Compliance/Commitments With Low Safety Risk | 7 | 5.1001 | Non-IGP | 5781260 | T.0004116 | WILSON: 115 kV ARP - BAAH | 7 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-09-12 | 2015-05-01 | 2030-06-28 | Prioritization | NA | FALSE | $35,000 ¦ $45,000 | NA ¦ NA | 145.0447 | 40486.9812 | 3.5219 | 0 | 0 | 25.2694 | 17.0225 | 303.6995 | 1900 | 11200 | 1900 | 1900 | 140.8958 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1025 | East Marysville: Inst Transformer |  |  | Marysville, Yuba | This project will entail the following: 1.Loop the Pease – Marysville 60 kV Line into E. Marysville Substation. 2.Install a 200MVA, 115/60kV (LTC) transformer at E. Marysville Substation. 3.Upgrade the terminal equipment at E. Marysville Substation. 4.Install 25 MVAR of voltage support at the Pease Substation 115 kV bus. | Substation - Transformer | New | NA | NA | Economic | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-02-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 1.8811 | NA | 115 ¦ 60 kV | NA | 8. Compliance/Commitments With Low Safety Risk | 14 | 5.1001 | Non-IGP | 5785381 | T.0004728 | East Marysville 115/60 kV Project | 2 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-04-06 | 2022-12-31 | 2030-03-25 | Prioritization | NA | FALSE | $26,000 ¦ $32,000 | NA ¦ NA | 428.9771 | 40793.5142 | 25.3737 | 20.3285 | 22.356 | 23.9033 | 60.8752 | 180.7499 | 6000 | 7000 | 1000 | 0 | 406.918 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1026 | Gold Hill: Add 230/115 kV Transformer |  |  | Folsom, Sacramento | A Bus section Fault (P2-1) overload on Missouri Flats – Gold Hill Lines 115 kV were identified in last year’s analysis and was addressed by switching load in the area. This year’s result show that given the load growth in the area, the P2-1 overload shows up in the long term. In order to mitigate the issue, the CAISO recommendeds the installation of a third 230/115 kV transformer at Gold Hill Substation | Substation - Transformer | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 12.8702 | NA | 230 ¦ 115 kV | NA | 8. Compliance/Commitments With Low Safety Risk | NA | 5.1001 | Non-IGP | 5787179 | T.0004950 | Gold Hill: Installl 230/115 kV Txfmr | 5 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-06-20 | 2022-12-31 | 2029-12-27 | Prioritization | NA | FALSE | 22000 | NA ¦ NA | 542.9336 | 42148.1842 | 1.3221 | 0.4802 | 0.5281 | 100.6991 | 355.2099 | 1794.466 | 1080.5168 | 1761.2577 | 22902.2305 | 8.7576 | 463.5186 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
1027 | REPLACE VACA DIXON BANK #5 |  |  | Solano | This project will replace Vaca Dixon Bank 5, existing four single-phase transformers, with one three-phase 115/60 kV, 200 MVA, as well as reconductoring the low-side all the way to the 60 kV bus to support up to 3000 A and installing two 60 kV single-phase station service voltage transformers and removal of 115/60 kV single-phase transformers, lattice structures, 60 kV breakers, and switches. | Substation - Transformer | Upgrade/Retrofit | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-25 | 21 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 115 ¦ 60 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 4 | 5.1001 | Non-IGP | 5782080 | T.0005914 | Vaca Dixon - Replace Bank 5 | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-07-26 | 2023-12-01 | 2022-08-11 | NA | NA | FALSE | 15000 | NA ¦ NA | 14023.4242 | 14023.4242 | 6781.8064 | 5883.8701 | 129.6684 | 78.7113 | 28.908 | 0.6568 | 0 | 0 | 0 | 0 | 14022.7674 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 13006.3693 | 122.1557 | 74.151 | 27.2331 | 0.61873 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1028 | Mountain View: Repl SW 157 & 159 w/CBs |  |  | Mountain View, Santa Clara | This project proposes to replace existing substation transformer Bank 1 in order to eliminate a growing deficiency on both Mountain View Bank 1 and Mountain View Bank 3. Replace two existing 115 kV motor-operated switches (157 and 159) with circuit breakers. Presently any bus or bank fault will trip both existing 115 kV breakers CB 112 & CB 122. By adding two additional 115 kV circuit breakers, only the faulted bus or bank would experience an outage. This additional scope will improve the looped bus, provide a logical path to an ultimate five-element 115 kV ring bus, improve bank clearances and increase reliability by reducing momentary outages to the 39,141 existing customers on Mountain View Substation. Transmission Substation Work (MWC 61): • Replace 115 kV circuit switchers 159 and 157 with 115 kV circuit breakers. • Extend existing control building will to accommodate the new relays for the breakers. with 115 kV circuit breakers. • Replace existing CB 112 with new circuit breaker/disconnect switches. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Load Growth | Substation Capacity | NA | NA | 2026-02-04 | 61 | Steady State Power Flow System Analysis | Wires - Replacement Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8224 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5798023 | T.0005971 | Mountain View - Replace Bank 1 | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2025-11-17 | 2028-12-06 | 2027-07-02 | NA | NA | TRUE | 22100 | NA ¦ NA | 2143.5844 | 7059.6298 | 36.571 | 166.6344 | 44.46 | 418.3417 | 998.7547 | 2742.5471 | 2651.9682 | 0 | 0 | 0 | 1664.7619 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1029 | GV INSTALL HIGH SIDE BREAKER & SW |  |  | Interlaken CDP, Santa Cruz | This project proposes to install one new 115/21 kV, 45 MVA three-phase transformer, one new 21 kV bus 1/bus 2 structure with four breaker bays, one bus-tie breaker and two feeder breakers, two new 21 kV distribution feeder outlets, two new Green Valley distribution circuits outside of the substation by installing new lines, reconductoring existing 21 kV sections and voltage conversion of existing 4 kV circuits. This work will eliminate a 14 percent overload of Green Valley Bank 2 and a 11 percent overload of Green Valley Bank 3. These overloads are forecasted to occur by summer 2024 and are the result of multiple new business applications, including 18 large cannabis cultivation greenhouses to be built on available agricultural land surrounding the City of Watsonville Transmission Substation Work (MWC 61) • Install one 115kV breaker and two switches at existing Bay #2 of the existing Breaker-and-a-Half (BAAH) 115 kV bus at Green Valley Substation to complete the BAAH arrangement | Substation - Circuit Breaker | New | NA | NA | Load Growth | Transformer Addition/Replacement | NA | NA | 2026-02-02 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5799591 | T.0007278 | Green Valley_Replace Bank 4 | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-11-03 | 2027-01-15 | 2026-12-02 | NA | NA | TRUE | 46000 | NA ¦ NA | 2395.6784 | 4468.6645 | 0 | 130.177 | 32.2844 | 481.2105 | 1493.7105 | 2101.4937 | 204.0805 | 0 | 0 | 0 | 2137.3824 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1030 | Metcalf: Install 230/115kV Bank CBs |  |  | Santa Clara | To address the near-term critical, category P2 contingency driven issues, the ISO is recommending approval of adding parallel breakers to each of the 230/115kV bank 1, 2 & 3 at Metcalf 230kV Substation so that the three Metcalf 230/115 kV transformer banks can connect to both Metcalf 230kV Bus1 and Bus 2. | Substation - Circuit Breaker | New | NA | NA | Reliability | Substation Capacity | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5803919 | T.0008980 | Metcalf Install 230 115kV Bank CBs | 1 | 61 | NA ¦ EX113230 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-10-13 | 2026-12-31 | 2028-02-09 | Prioritization | NA | FALSE | $900 ¦ $1,350 | NA ¦ NA | 384.7765 | 9245.3029 | 0 | 0 | 15.8875 | 168.3758 | 186.8865 | 3283.9591 | 1500 | 150 | 0 | 0 | 371.1498 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
1031 | Atlantic: Install 230/60 kV Bank |  |  | Roseville, Placer | This project will install a 200 MVA, 3-phase 230/60 kV transformer with LTC. Below is the high-level scope of this project: 1. Install a 200 MVA, 3-phase 230/60 kV transformer with LTC 2. Connect the new transformer to 230kV BAAH. This will require one new 230kV breaker and relocating other 230kV connections. 3. Install 60kV breaker to connect the new transformer. Modify 60kV bus as necessary to connect the new bank. 4. Modify the protection scheme as necessary to support this project. 5. Upgrade SPCC and the ground grid as necessa This project would mitigate the Atlantic 60 kV system high voltage issue. It will also increase operating flexibility, load serving capability, and customer reliability. | Substation - Transformer | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 10.7 | NA | 230 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806786 | T.0009529 | Atlantic Install 230 60 kV Bank | 1 | 61 | NA ¦ EX113210 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-03-02 | 2029-05-01 | 2029-01-10 | NA | NA | FALSE | $20,000 ¦ $40,000 | NA ¦ NA | 615.2183 | 39428.6248 | 0 | 0 | 0 | 182.2522 | 382.477 | 1191.7757 | 4165.266 | 15235.0521 | 39.0335 | 0 | 564.7292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
1032 | Table Mtn: Install second 500/230kV Bank |  |  | Butte | This project will support installation of the second 500/230kV transformer at Table Mountain substation. The second 500/230kV transformer is needed to address the 230kV high voltage issue in the North-Valley region. The proposed high-level scope of work for this project includes: • Install three single-phase 374MVA transformers and the associated structures. • Relocate terminal connections as necessary to connect both 500kV banks in separate bays. • Install tertiary shunt reactors for the new bank as required. • Install Bus tie breaker in Bus Section E. • Upgrade protection scheme as required to implement the project scope. • Modify RAS scheme if required. Additional studies may be required to determine this. | Substation - Transformer | New | NA | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-20 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806785 | T.0009530 | Table Mtn: Install new 500kV Bank and 23 | 2 | 61 | NA ¦ EX112236 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-06-28 | 2027-01-01 | 2029-05-25 | Prioritization | NA | FALSE | $38,400 ¦ $76,800 | NA ¦ NA | 454.8564 | 59331.9656 | 0 | 0 | 0 | 165.5046 | 251.525 | 2046.4762 | 24500 | 20200 | 7400 | 0 | 417.0296 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
1033 | Cortina: Replace Bank 1 with 2 banks |  |  | Colusa | Replace the Cortina 230/115/60 kV Transformer 1 with one 230/115 kV and one 115/60 kV transformers. Upgrade bus differential relay, as needed. The annual reliability assessment identified thermal overload issues for NERC Category contingencies that involve loss of Cortina 230/115 kV Transformer 4. For an outage of Cortina 230/115 kV Transformer 4, Cortina 230/115/60 kV Transformer 1 will have to serve the Cortina 60 kV load and the Cortina 115 kV load and North Geysers area via Cortina 115/60 kV Transformer 5. The most severe of such contingencies may lead to loading of Cortina 230/115/60 kV Transformer 1 up to 137.5% of its summer emergency rating. Currently, there is an Operating Procedure to radialize the 60 kV and 115 kV loads by opening Cortina 115/60 KV Transformer 5 pre-contingency in order to prevent the Cortina 230/115/60 kV Transformer 1 overload post-contingency. However, planning and real time operating analysis show that opening Cortina 115/60 kV Bank 5 under normal condition could cause loss of generation violations, such as losing Wadham generator could overload Cortina 230/115/60 kV Transformer 1 up to 106.2% of its summer emergency rating. Therefore, this Operating Procedure cannot longer be used as a viable long-term solution under peak loading conditions. | Substation - Transformer | Upgrade/Retrofit | NA | T.0008218 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-06 | 56 | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.7436 | NA | 230 ¦ 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806847 | T.0009531 | Cortina Replace Bank 1 with 2 banks | 3 | 61 | NA ¦ EX112148 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-09-04 | 2027-12-01 | 2027-05-24 | NA | NA | TRUE | $21,000 ¦ $42,000 | NA ¦ NA | 914.4074 | 20712.4251 | 0 | 0 | 0 | 141.7862 | 619.4555 | 4815.6654 | 15112.4334 | 8 | 0 | 0 | 761.2417 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
1034 | CORTINA REPLACE BANK 1 230/115kV |  |  | Colusa | Replace the Cortina 230/115/60 kV Transformer 1 with one 230/115 kV and one 115/60 kV transformers. Upgrade bus differential relay, as needed. The annual reliability assessment identified thermal overload issues for NERC Category contingencies that involve loss of Cortina 230/115 kV Transformer 4. For an outage of Cortina 230/115 kV Transformer 4, Cortina 230/115/60 kV Transformer 1 will have to serve the Cortina 60 kV load and the Cortina 115 kV load and North Geysers area via Cortina 115/60 kV Transformer 5. The most severe of such contingencies may lead to loading of Cortina 230/115/60 kV Transformer 1 up to 137.5% of its summer emergency rating. Currently, there is an Operating Procedure to radialize the 60 kV and 115 kV loads by opening Cortina 115/60 KV Transformer 5 pre-contingency in order to prevent the Cortina 230/115/60 kV Transformer 1 overload post-contingency. However, planning and real time operating analysis show that opening Cortina 115/60 kV Bank 5 under normal condition could cause loss of generation violations, such as losing Wadham generator could overload Cortina 230/115/60 kV Transformer 1 up to 106.2% of its summer emergency rating. Therefore, this Operating Procedure cannot longer be used as a viable long-term solution under peak loading conditions. | Substation - Transformer | Upgrade/Retrofit | NA | T.0008218 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-06 | 56 | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.7436 | NA | 230 ¦ 115 ¦ 60 kV | NA | NA | NA | 1.0001 | Non-IGP | 5810098 | T.0009531 | Cortina Replace Bank 1 with 2 banks | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-09-04 | 2027-12-01 | 2027-12-20 | NA | NA | TRUE | $21,000 ¦ $42,000 | NA ¦ NA | 2122.3398 | 14851.5692 | 0 | 0 | 0 | 844.8987 | 879.86 | 1153.4112 | 2947.807 | 5283 | 0 | 0 | 1724.7587 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
1035 | Henrietta: Henrietta BK 3 Replacement |  |  | Kings | Replace Henrietta 230/115 kV Bank 3 | Substation - Transformer | Replace | NA | NA | Policy | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-06 | 20 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 7.0079 | NA | 230 ¦ 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5806921 | T.0009553 | Henrietta_Henrietta BK 3 Replacement | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-07-16 | 2032-12-31 | 2028-04-28 | NA | NA | FALSE | 20000 | NA ¦ NA | 240.7996 | 15751.7753 | 0 | 0 | 0 | 59.1724 | 159.1952 | 2643.7368 | 12022.74 | 866.931 | 0 | 0 | 218.3675 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-F-Board-Approved_2022-2023_Transmission-Plan.pdf
1036 | Mesa: 230/115kV Spare Transformer |  |  | Nipomo CDP, San Luis Obispo | This project proposes to install a new 420Mva 230/115kV spare transformer to provide capacity to perform maintenance on existing Transformers 2 and 3, the Morro Bay-Mesa, and the Diablo Canyon PP 230kV lines | Substation - Transformer | New | NA | T.0009582 ¦ T.0000588 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-09 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 10.5414 | NA | 230 ¦ 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5807200 | T.0009596 | Mesa_230_15kV Spare Transformer | 1 | 61 | NA ¦ EX113238 ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-10-18 | 2032-12-31 | 2030-07-11 | NA | NA | FALSE | 24000 | NA ¦ NA | 223.5573 | 21572.4735 | 0 | 0 | 0 | 86.5078 | 111.3156 | 211.197 | 2500 | 2500 | 5000 | 2000 | 197.8234 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
1037 | Pole Line: Inst BK1 |  |  | Merced | This project proposes to: • Install 230 kV partial bay at the new generation driven 230 kV switching station adjacent to Dos Amigos PP 230 kV Substation. • Add a new 70 kV Bus in the new generation driven 230 kV switching station, then it will be converted to a new 230/70 kV substation. • Install one 230/70 kV transformer at the new 230/70 kV substation. • Install a new 70 kV transmission line from new 70 kV Bus to Mercy Springs 70 kV Bus, and the new line is about one mile. • Install one breaker at Mercy Springs 70 kV Switching Station. | Substation - Transformer | New | NA | T.0009177 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-03 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.8847 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807501 | T.0009617 | Los Banos 70 kV Area Reinforcement | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-01-04 | 2029-12-31 | 2032-01-27 | Workforce | Material | FALSE | 60000 | NA ¦ NA | 43.713 | 29197.3414 | 0 | 0 | 0 | 5.2968 | 27.0912 | 54.4198 | 0 | 0 | 0 | 0 | 32.388 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
1038 | Redwd City Area Reinf: Ravenswood Sub |  |  | Menlo Park, San Mateo | The scope of this project is to install a new 230/115 kV Transformer at Ravenswood Substation, and reconductor 6.5 circuit miles of the San Mateo - Belmont 115 kV Line and 7.5 circuit miles of the Ravenswood - Bair 115 kV Line #1. | Substation - Transformer | New | NA | T.0002156 ¦ T.0002155 ¦T.0006509 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807539 | T.0009638 | Redwd City Area Reinf Projects | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-10-06 | 2030-12-31 | 2029-06-22 | NA | NA | FALSE | 110800 | NA ¦ NA | 100.6351 | 13427.7365 | 0 | 0 | 0 | 41.8092 | 52.8847 | 294.1229 | 0 | 0 | 0 | 0 | 94.6939 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1039 | Reedley Txfmer #4 |  |  | Fresno | Add a double circuit between Reedley-Dinuba 70 kV line #2 and upgrade rating ofexisting Reedley-Dinuba 70 kV line #1 and upgrade Reedley 230/70 kV bank 4. | Substation - Transformer | Upgrade/Retrofit | NA | EX112722 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-10 | 21 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.5939 | NA | 230 ¦ 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5812198 | T.0010649 | REEDLEY-DINUBA LN REBUILD & TXFMER #4 | 3 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-06-14 | TBD | 2028-08-30 | NA | NA | FALSE | $49,000 ¦ $98,000 | NA ¦ NA | 20.1592 | 20.1592 | 0 | 0 | 0 | 0 | 2.0812 | 18.0781 | 0 | 0 | 0 | 0 | 2.0811 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
1040 | Gates: Install New 230/70kV Bank |  |  | Fresno | This project proposes to Install a new 3phase 230/70kV 200MVA transformer at Gates substation. 1. Install new 3 phase 230/70kV 200MVA transformer and connect it to the 230kV bus section D at Gates substation. 2. Install New breaker on the Gates 230kV bus section D. 3. Install New breaker on the Gates 70kV bus. | Substation - Transformer | New | NA | T.0003540 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | NA | 2026-03-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 ¦ 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5812902 | T.0010700 | Gates: Install New 230/70kV Bank | 1 | 61 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | 2024 | NA | https://www.caiso.com/documents/iso-board-approved-2023-2024-transmission-plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-03-28 | 2030-12-01 | 2030-03-20 | NA | NA | FALSE | $36,000 ¦ $72,000 | NA ¦ NA | 21.2092 | 41021.2092 | 0 | 0 | 0 | 0 | 2 | 18.5111 | 5000 | 15000 | 15000 | 3000 | 2.6981 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/documents/appendix-c-board-approved-2023-2024-transmission-plan.pdf
1041 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | NA | Other [See Notes] | NERC CIP Compliance | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5786102 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2014 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-04-28 | 2020-06-12 | 2021-01-06 | Workforce | NA | FALSE | 549 | NA ¦ NA | 1188.3913 | 1188.3913 | 16.3089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1188.3913 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 1188.3913 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 2 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1042 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | NA | Other [See Notes] | NERC CIP Compliance | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5788426 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2014 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2021-01-19 | NA | NA | FALSE | NA | NA ¦ NA | 3967.4371 | 3967.4371 | 15.3249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3967.4371 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 3967.4371 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 6 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1043 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.51 | Non-IGP | 5799031 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2022-01-01 | NA | 2026-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 4877.7158 | 11091.9892 | 9.628 | 777.0494 | 1425.399 | 1987.5296 | 549.2687 | 838.982 | 499.5512 | 500 | 1500 | 1500 | 4748.8747 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 4199.606 | -114.566 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1044 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 975 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5775350 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2023-03-03 | NA | NA | FALSE | NA | NA ¦ NA | 8142.786 | 8142.786 | 2049.0964 | 1640.1073 | 288.1272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8142.786 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1148.9258 | 243.8808 | 6749.9581 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1045 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5544571 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-02-19 | 2022-11-30 | 2022-11-30 | NA | NA | FALSE | NA | NA ¦ NA | 1196.4973 | 12250 | 364.553 | 799.1749 | 32.7694 | 0 | 0 | 0 | 0 | 0 | 0 | 5250 | 1196.4973 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 1196.4972 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1046 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5547904 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-01 | 2022-12-01 | 2022-12-01 | NA | NA | FALSE | 1200 | NA ¦ NA | 1180.1634 | 1180.1634 | 0 | 1161.1628 | 19.0007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1180.1634 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 468.1573 | 712.0061 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1047 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5795758 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-04-01 | 2020-12-30 | 2022-03-29 | Project Design | NA | FALSE | 1858 | NA ¦ NA | 1495.9747 | 1495.9747 | 781.5098 | 86.6684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1495.9747 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 1495.9747 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1048 | ET PI - Phase 1 |  |  | NA | A data warehouse named ET DW was built as the work output of this Planning Order. The ET DW helps improve Transmission Operations processes to minimize customer outage and to mitigate wildfire risk. It also helps to improve planning and asset strategy processes that ultimately leads to lower cost of operation and reduced wildfire risk. The ET DW also helps with meeting compliance requirements such as FERC Order 881. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5788320 | NA | NA | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2023-07-19 | NA | NA | FALSE | NA | NA ¦ NA | 1781.0577 | 1781.0577 | 758.6595 | 215.6293 | 62.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1781.0577 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 1781.0577 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1049 | SP&P Data ET - CAP |  |  | NA | Bucket for ET PI Data Analytics | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3201 | Non-IGP | 5792856 | NA | NA | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 15823.2144 | 19333.1503 | 674.5554 | 2357.5174 | 4595.1239 | 6845.9862 | 1147.0832 | 1212.8843 | 499.9999 | 500 | 500 | 500 | 15620.266 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 11196.3237 | 3822.1945 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1050 | T-SCADA/Congruitive |  |  | NA | Bucket for Transmission SCADA | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5805507 | NA | NA | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1981.1423 | 1981.1423 | 0 | 0 | 901.2399 | 1108.2764 | -28.3739 | 0 | 0 | 0 | 0 | 0 | 1981.1423 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 548.2044 | 1430.8763 | 2.0616 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1051 | SYNCHROPHASOR SUSTAINMNT AND PI APP PROJ |  |  | NA | Bucket for the Synchrophasor PI Project, which puts into service the next phase of evolution for PG&E’s synchrophasor system to more effectively support the growing needs of PG&E’s Phasor Data community. This project will implement a synchrophasor data archival system leveraging OSIsoft PI, a standard industry software tool which PG&E is already fully licensed. The ability to leverage synchrophasor data has been requested by several PG&E consumers, to be used for multiple business applications relating to compliance and operational integrity, such as: • NERC PRC-002-2 R5 - PMUs fulfill the role of DDRs (Dynamic Data Recorders) for post-event analysis required at specific locations within the transmission grid • NERC MOD-033 – Requires the Transmission Operator to provide transmission system recorded data for post-event analysis upon request • CPUC Advice Letter 5571-E – Requires frequency monitoring and quarterly reporting to determine frequency impacts on operation of inverter-based resources • Asset Performance Center – Provide PMU data for APC use cases such as equipment monitoring for preventive maintenance, big data analytics, and others | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 45 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5780185 | NA | NA | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-07-01 | 2021-07-31 | 2021-07-31 | NA | NA | FALSE | 896 | NA ¦ NA | 1335.8018 | 1335.8018 | 368.6261 | 35.9549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1335.8018 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 1335.8018 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1052 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 45 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5504279 | P.11210 | Electric Transmission Operations Upgrade | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-01-01 | 2021-07-01 | 2021-07-01 | NA | NA | FALSE | NA | NA ¦ NA | 4167.4346 | 4167.4346 | 334.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4167.4346 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 2702.1497 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1053 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 741 | NA | NA | NA | NA | 5752873 | T.0004406 | Electric Transmission Operations Upgrade | 2 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2015 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2015-10-15 | 2018-12-01 | 2018-12-01 | NA | NA | FALSE | 9826 | NA ¦ NA | 17974.9969 | 17974.9969 | 322.2714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17974.9969 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 322.2714 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1054 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5795759 | T.0004406 | Electric Transmission Operations Upgrade | 2 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-11-01 | 2020-12-31 | 2022-01-28 | Project Design | NA | FALSE | 5022 | NA ¦ NA | 7047.2061 | 7047.2061 | 1511.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7047.2061 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 5936.5689 | 1110.6372 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1055 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 16 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.21 | Non-IGP | 5763262 | TBD | Electric Transmission Operations Upgrade | TBD | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 16078 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 6178 | 7550 | 2100 | 250 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support
1056 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | T.0009554 ¦ 5531415 | Other [See Notes] | System Operations | NA | NA | NA | 27 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.42 | Non-IGP | 5560199 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2028-06-01 | OAI | NA | NA | TRUE | 213700 | NA ¦ NA | 12456.1582 | 267174.1615 | 0 | 0 | 0 | 0 | 10954.8411 | 21319.3204 | 53500 | 69500 | 65900 | 23000 | 10954.8411 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 10954.8411 | 1501.3171 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Alternative Solutions and Costs - Solutions] Other - Status Quo ¦ Non-Wires ¦ Non-Wires [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ $200 Mil - $250 Mil ¦ $200 Mil - $250 Mil [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1057 | TSRP-NORTH BAY SIERRA ET NEW CO |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | NA | NA | 5777398 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-07-10 | 2020-03-27 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 3195.9789 | 3195.9789 | 26.0868 | 4.3083 | 1.5511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3195.9789 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 24.8862 | 4.11 | 1.4797 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1058 | TSRP-NORTH BAY SIERRA ET NEW CO |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | NA | NA | 5777400 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-07-10 | 2020-03-27 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 3503.4937 | 3503.4937 | 55.6639 | 20.8576 | 10.1885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3503.4937 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 53.1875 | 19.9297 | 9.7352 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1059 | TSRP-NORTH BAY SIERRA ET COMM- |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | NA | NA | 5777404 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-07-10 | 2020-03-27 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 2130.5004 | 2130.5004 | 24.7454 | 2.3067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2130.5004 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 24.0363 | 2.2406 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1060 | TSRP-NORTH BAY SIERRA ET MPAC/H |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | NA | NA | 5777402 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-07-10 | 2020-11-30 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 1760.3055 | 1760.3055 | 16.3922 | 24.2266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1760.3055 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 15.8243 | 23.3873 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1061 | TSRP NBS IT T-Line Switches |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | NA | NA | 5778581 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-07-10 | 2022-03-22 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 2162.2337 | 2162.2337 | 169.7272 | 33.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2162.2337 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 2145.79 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1062 | TSRP NBS IT Cross Connects |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5777377 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-06-18 | 2024-01-10 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 1795.867 | 1795.867 | 282.8784 | 243.6013 | 200.1293 | 5.5398 | 0 | 0 | 0 | 0 | 0 | 0 | 1795.867 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 1785.4367 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1063 | TSRP NBS IT VSAT |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5777403 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-07-10 | 2024-01-10 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 1633.3884 | 1633.3884 | 167.1893 | 151.763 | 123.4326 | 4.784 | 0 | 0 | 0 | 0 | 0 | 0 | 1633.3884 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 1621.8939 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1064 | TSRP NBS IT Other Sites |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5778582 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-07-10 | 2024-01-10 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 4108.7603 | 4108.7603 | 334.92 | 330.4898 | 349.9442 | 33.5766 | 0 | 0 | 0 | 0 | 0 | 0 | 4108.7603 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 4084.8189 | 0.00015 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1065 | TSRP NS - IT OTHER SITES |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5782304 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-07-10 | 2024-01-10 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 5615.375 | 5615.375 | 849.2666 | 482.3716 | 500.288 | 16.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 5615.375 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 5615.375 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1066 | TSRP NS - IT CROSS CONNECTS |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5783801 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-12-01 | 2019-07-10 | 2024-01-10 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 693.0173 | 693.0173 | 97.3632 | 86.9165 | 362.723 | 7.1288 | 0 | 0 | 0 | 0 | 0 | 0 | 693.0173 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 693.0173 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1067 | TSRP NS - IT NEW MPLS |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5783802 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-07-10 | 2024-01-10 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 2624.4966 | 2624.4966 | 602.8265 | 428.5147 | 227.4815 | 10.8164 | 0 | 0 | 0 | 0 | 0 | 0 | 2624.4966 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 2624.4966 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1068 | TSRP NS - IT VSAT |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5783803 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-06-18 | 2024-01-10 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 1055.7362 | 1055.7362 | 157.528 | 120.4581 | 152.9266 | 5.4282 | 0 | 0 | 0 | 0 | 0 | 0 | 1055.7362 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 1055.7362 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1069 | TSRP NBS IT New MPLS |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5777401 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 13 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-05 | 2019-07-10 | 2024-12-31 | Workforce | NA | FALSE | 225000 | NA ¦ NA | 4180.146 | 4180.146 | 313.657 | 333.686 | 319.8999 | 12.2507 | 0 | 0 | 0 | 0 | 0 | 0 | 4180.146 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 4153.3304 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1070 | TSRP PMO |  |  | NA | Provide program management support for TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5536661 | T.0004903 | TSRP PMO | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2021-12-31 | NA | NA | FALSE | NA | NA ¦ NA | 10367.6914 | 10367.6914 | 3885.7761 | -5137.4379 | 3582.0723 | 1331.5721 | 2945.5693 | 290.0929 | 0 | 0 | 0 | 0 | 10077.5985 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 1942.8881 | -2568.7197 | 1791.0358 | 665.7853 | 1472.7862 | 145.0464 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1071 | TSRP_NS_SUB_MAPLE CREEK |  |  | Humboldt | TSRP work on Maple Creek: Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS e-terra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, with system-wide migration by December 2029, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover installation of new IT equipment, EMS database development and testing. Scope does not cover removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring change to this premise will require scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-02 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.27362 | NA | 60 kV | NA | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5787009 | T.0004997 | TSRP_NS_SUB_MAPLE CREEK | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-07-21 | 2022-12-31 | 2026-01-21 | Prioritization | NA | TRUE | 603 | NA ¦ NA | 1386.3368 | 1386.3368 | 33.8308 | 100.0718 | 372.5871 | 475.9925 | 160.1673 | 17.1396 | 0 | 0 | 0 | 0 | 1369.1972 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1072 | TSRP_NS_SUB_COTTONWOOD |  |  | Cottonwood CDP, Shasta | Migrate off of the existing SCADA platform and onto the existing EMS to improve ET operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within ET Transmission System Operators currently use both RTscada and EMS. The use of two control consoles for RTscada and EMS increases unsafe conditions for field personnel and customers because the existing processes and safeguards are inadequate for operation of two independent SCADA control systems. The current interaction between RTscada and EMS requires completely manual processes to ensure that the separate databases are aligned. Alignment between the two databases is critical, as this is the only way to ensure that the correct device operates in the field when a System Operator initiates a SCADA control. Moving to a single system will reduce the risk of inadvertent operation of field devices due to database misalignment. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-19 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 26.1945 | NA | NA | NA | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5786934 | T.0005015 | TSRP_NS_SUB_COTTONWOOD | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-03-01 | 2022-12-31 | 2024-02-15 | Prioritization | NA | FALSE | 1600 | NA ¦ NA | 2179.9856 | 2179.9856 | 26.8221 | 85.4558 | 1418.3395 | 338.306 | 45.619 | 0 | 0 | 0 | 0 | 0 | 2179.9856 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1959.2031 | 41.6166 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1073 | TSRP_NS_SUB_CORTINA |  |  | Colusa | Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS e-terra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, with system-wide migration by December 2029, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover installation of new IT equipment, EMS database development and testing. Scope does not cover removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring change to this premise will require scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-06 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.7436 | NA | NA | NA | 3. Emergency Preparedness | 2 | 5.3 | Non-IGP | 5786915 | T.0005033 | TSRP_NS _SUB_CORTINA | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-09-21 | 2024-03-31 | 2024-01-30 | NA | NA | TRUE | 629 | NA ¦ NA | 1228.7921 | 1229.9139 | 478.9771 | 85.7174 | 194.1906 | 111.8658 | 24.427 | 36.8644 | 0 | 0 | 0 | 0 | 1193.0495 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1086.8983 | 22.4375 | 32.8315 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1074 | TSRP_NS_SUB_TABLE MOUNTAIN |  |  | Butte | TSRP will migrate off of the current Supervisory Control and Data Acquisition (SCADA) system and onto the existing Energy Management System (EMS). Migrate off of the existing SCADA platform and onto the existing EMS to improve ET operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within ET. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-20 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | NA | NA | 3. Emergency Preparedness | 5 | 5.3 | Non-IGP | 5786910 | T.0005084 | TSRP_NS_SUB_TABLE MOUNTAIN | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-01-04 | 2024-12-31 | 2023-10-20 | NA | NA | FALSE | 1600 | NA ¦ NA | 1500.8863 | 1500.8863 | 272.8298 | 487.7439 | 308.0108 | 305.8678 | 2.869 | 0 | 0 | 0 | 0 | 0 | 1500.8863 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 1119.7021 | 285.3079 | 2.6762 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1075 | TSRP SV - IT CROSS CONNECTS |  |  | NA | As part of the Transmission SCADA Replacement Program (TSRP) scope, the program needs to assure a secure, reliable, TCP/IP connection from all substations into PG&E’s secure data network. “TSRP SV - IT CROSS CONNECTS” addresses those substations in the South Valley (SV) of PG&E’s service territory (Fresno and Kern Divisions.) Specifically, this order supports those substations within SV that already have TCP/IP communications path including routers and switches installed. TSRP SV - IT CROSS CONNECTS scope includes installing communication cabling and ancillary IT equipment within these substations to assure reliable data flow from the SCADA monitoring/control devices with the substation out to PG&Es secure data network. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5787478 | T.0005137 | Tsrp Sv - It Cross Connects | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1293.465 | 1293.465 | 84.2114 | 509.883 | 383.106 | 204.1781 | 85.2693 | 0 | 0 | 0 | 0 | 0 | 1293.465 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1076 | TSRP SV - IT NEW MPLS |  |  | NA | Upgrade communications infrastructure in South Valley (Midway, Fresno jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5787479 | T.0005138 | Tsrp Sv - It New Mpls | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-02 | NA | 2024-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 1929.8044 | 1929.8044 | 39.8787 | 959.3022 | 420.3891 | 279.8309 | 144.7926 | 24.2012 | 0 | 0 | 0 | 0 | 1905.6032 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1077 | TSRP_SV_SUB_TIVY VALLEY |  |  | Fresno | Electric Operations (EO) has requested the migration of six Electric Transmission (ET) operating jurisdictions of existing SCADA platform onto the existing EMS – E-Terra to enhance ET operability, efficiency, security, and safety. Initiated October 2014, with system-wide migration by March 2026, this program identified as Transmission SCADA Replacement Program (TSRP) have been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture; provide telecommunication circuits connections to EMS via SCADA RTU, and addition of T-line switch data and control. Once completed, Electric Transmission Operations will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Tivy Valley Substation is a 70KV looped station with two (2) transmission circuit breakers, one distribution transformer Tx1115/12KV, TB 1 3-phase regulator and two (2) 12KV circuit breakers. Tivy Valley substation currently reports to RTSCADA on PGE protocol via modem on 4-wire lease line. Existing D20M++ RTU is not LAN capable. TSRP will replace the RTU with EATON SG-4260 so the planned IT solution which is LAN based is a viable solution. This requires retesting for RTSCADA as well while testing to EMS. The LAN link will carry both RTSCADA and EMS connectivity. This scope covers only the substation component of the overall TSRP program of which the goal is to support ISTS’s plan for installing EMS’s telecommunication paths. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-02-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.75891 | NA | NA | NA | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5788154 | T.0005258 | TSRP_SV_SUB_TIVY VALLEY | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-09-15 | 2022-07-30 | 2024-12-20 | Prioritization | Workforce | FALSE | 982 | NA ¦ NA | 1093.1903 | 1093.1903 | 252.9142 | 191.3477 | 263.6474 | 243.7761 | 102.7922 | 0.357 | 0 | 0 | 0 | 0 | 1092.8333 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 966.8822 | 99.9915 | 0.34725 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1078 | Video Wall Controller Upgrade |  |  | NA | Bucket for Video Wall Controller Upgrade | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5788318 | T.0005299 | TSRP_SV_SUB_KERN OIL | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-05-01 | 2020-10-01 | 2022-12-01 | Prioritization | NA | FALSE | 1035 | NA ¦ NA | 2115.8721 | 2115.8721 | 355.9005 | 64.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2115.8721 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 2115.8721 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1079 | TSRP_SV_SUB_MAGUNDEN |  |  | East Niles CDP, Kern | Electric Operations (EO) has requested the migration of six Electric Transmission (ET) operating jurisdictions of existing SCADA platform onto the existing EMS – E-Terra to enhance ET operability, efficiency, security, and safety. Initiated October 2014, with system-wide migration by March 2026, this program identified as Transmission SCADA Replacement Program (TSRP) have been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture; provide telecommunication circuits connections to EMS via SCADA RTU, and addition of T-line switch data and control. Once completed, Electric Transmission Operations will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. South Valley is one of the six operating jurisdictions and is chosen to undergo this TSRP SCADA migration plan. Targeted are various substations that currently possess a form of legacy telecommunication circuit connection to RTSCADA, with transmission equipment assets. Among these targeted substations is Renfro Substation. Magunden Substation is a 115KV looped station with two (2) transmission 115kV circuit breakers, two (2) distribution transformers T1 - 115/12KV, T3 – 115/12kV, seven (7) – 12kV Distribution Breakers and two (2) –12kV Bank Breakers. Magunden Substation currently reports to RTSCADA via serial connection using PG&E Protocol. Existing D20ME RTU is not equipped with EME / BIN MIC Kit hence not LAN capable. A new D20MX will be acquired for the ethernet connection to new Cisco Switch 2520. This requires retesting for RTSCADA as well while testing to EMS. The LAN link will carry both RTSCADA and EMS connectivity. This scope covers only the substation component of the overall TSRP program of which the goal is to support ISTS’s plan for installing EMS’s telecommunication paths. | Other - Operations Tech | New | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-02-09 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.2256 | NA | NA | NA | 3. Emergency Preparedness | 11 | 5.3 | Non-IGP | 5788119 | T.0005309 | TSRP_SV_SUB_MAGUNDEN | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-02-01 | 2022-07-01 | 2025-07-22 | Prioritization | NA | TRUE | 913 | NA ¦ NA | 1079.5666 | 1079.5666 | 183.3701 | 237.3228 | 229.5799 | 350.8115 | 30.1902 | 0 | 0 | 0 | 0 | 0 | 1079.5666 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1080 | TSRP_SV_SUB_MC CALL |  |  | Fresno | Electric Operations (EO) has requested the migration of six Electric Transmission (ET) operating jurisdictions of existing SCADA platform onto the existing EMS – E-Terra to enhance ET operability, efficiency, security, and safety. Initiated October 2014, with system-wide migration by March 2026, this program identified as Transmission SCADA Replacement Program (TSRP) have been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture; prove telecommunication circuits connections to EMS via SCADA RTU, and addition of T-Line switch data and control. Once completed, Electric Transmission OPS will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. South Valley is one of the six operation jurisdictions and is chosen to undergo this TSRP SCADA migration plan. Targeted are various substations that currently possess a form of legacy telecommunication circuit connection to RTSCADA, with transmission equipment assets. Among these targeted substations is Tranquility Switching Station. Targeted are substations with Human – Machine Interface platform (HMI). For these stations, each HMI platform within the station will require the installation of (2) new Eaton SG-4260 devices which will replace the existing DELL servers and successfully migrate all devices to the new Eaton SG-4260. These requirements cover the work associated with TSRP at McCall Substation. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-06 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 16.2494 | NA | NA | NA | 5a. Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5788123 | T.0005313 | TSRP_SV_SUB_MC CALL | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-30 | 2022-06-30 | 2024-12-12 | Workforce | NA | FALSE | 743 | NA ¦ NA | 1798.9704 | 1798.9704 | 108.7374 | 337.8508 | 719.4248 | 586.8483 | 46.1091 | 0 | 0 | 0 | 0 | 0 | 1798.9704 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1699.7963 | 44.5557 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1081 | TSRP_NBS_SUB_VACA DIXON |  |  | Solano | TSRP will migrate off of the current Supervisory Control and Data Acquisition (SCADA) system and onto the existing Energy Management System (EMS). Migrate off of the existing SCADA platform and onto the existing EMS to improve ET operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within ET. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-25 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 42.1076 | NA | 500 ¦ 230 ¦ 115 ¦ 60 kV | NA | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5788839 | T.0005544 | TSRP_NBS_SUB_VACA DIXON | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-09-06 | 2020-12-31 | 2021-11-17 | Prioritization | NA | TRUE | 1400 | NA ¦ NA | 1885.8531 | 1886.5085 | 389.1974 | 12.7649 | 5.3078 | 2.8249 | 74.3087 | 12.5496 | 0 | 0 | 0 | 0 | 1873.9589 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 1642.9946 | 4.8294 | 2.5703 | 67.6105 | 10.822 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1082 | TSRP_NBS_SUB_LAKEVILLE |  |  | Sonoma | TSRP will migrate off of the current Supervisory Control and Data Acquisition (SCADA) system and onto the existing Energy Management System (EMS). Migrate off of the existing SCADA platform and onto the existing EMS to improve ET operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within ET. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-13 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 14.7021 | NA | 230 ¦ 115 ¦ 60 kV | NA | 3. Emergency Preparedness | NA | NA | NA | 5788814 | T.0005547 | TSRP_NBS_SUB_LAKEVILLE | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-09-06 | 2020-12-31 | 2020-12-15 | NA | NA | FALSE | 1600 | NA ¦ NA | 2106.7652 | 2106.7652 | 47.9046 | 24.2084 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2106.7652 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 43.7228 | 22.0845 | 0.19155 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1083 | TSRP_NBS_SUB_HIGHWAY |  |  | American Canyon, Napa | TSRP work on Highway: Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS e-terra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, with system-wide migration by December 2029, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover installation of new IT equipment, EMS database development and testing. Scope does not cover removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring change to this premise will require scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-02-02 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.71048 | NA | NA | NA | 3. Emergency Preparedness | 9 | 5.3 | Non-IGP | 5788810 | T.0005573 | TSRP_NBS_SUB_HIGHWAY | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-15 | 2022-03-31 | 2025-02-11 | Prioritization | NA | TRUE | 312 | NA ¦ NA | 1079.4867 | 1079.4867 | 104.8009 | 262.2198 | 209.2937 | 336.1904 | 43.9193 | 10.209 | 0 | 0 | 0 | 0 | 1069.2777 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1040.9164 | 9.892 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1084 | TSRP_NBS_SUB_IGNACIO |  |  | Novato, Marin | TSRP will migrate off of the current Supervisory Control and Data Acquisition (SCADA) system and onto the existing Energy Management System (EMS). Migrate off of the existing SCADA platform and onto the existing EMS to improve ET operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within ET. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-05 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.9486 | NA | 230 ¦ 115 ¦ 60 kV | NA | 3. Emergency Preparedness | NA | NA | NA | 5788812 | T.0005575 | TSRP_NBS_SUB_IGNACIO | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-09-06 | 2020-12-17 | 2020-12-17 | NA | NA | FALSE | 1100 | NA ¦ NA | 1058.2387 | 1058.2387 | 77.3 | 8.7959 | 6.2544 | 2.8229 | 0 | 0 | 0 | 0 | 0 | 0 | 1058.2387 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 953.3274 | 8.0392 | 5.7164 | 2.58 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1085 | TSRP_CV_IT NEW MPLS |  |  | Fresno, Fresno | Upgrade communications infrastructure in Central Valley in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Heat Wave ¦ Weather |  | NA | 2.5149 | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5791642 | T.0006074 | TSRP_CV_IT NEW MPLS | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-07-01 | 2025-06-30 | 2026-01-06 | Resources | NA | FALSE | 900 | NA ¦ NA | 1090.1463 | 1090.1463 | 0.0033 | 98.6634 | 61.4529 | 715.6488 | 210.8809 | 3.4503 | 0 | 0 | 0 | 0 | 1086.696 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 1090.1463 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1086 | TSRP_CV_SUB_TESLA |  |  | Alameda | Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS e-terra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provides telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover the installation of new IT equipment, EMS database development, and testing. The scope does not cover the removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring a change to this premise will require a scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-19 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5792364 | T.0006305 | TSRP_CV_SUB_TESLA | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2022-11-04 | 2024-01-24 | 2027-12-03 | Prioritization | NA | TRUE | 977 | NA ¦ NA | 543.6779 | 1234.3299 | 86.7157 | 131.4374 | 104.8302 | 200.8889 | 17.0604 | 33.2079 | 591.5398 | 0 | 0 | 0 | 543.6779 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1087 | TSRP_SV_T-LINE_AUBERRY |  |  | Auberry CDP, Fresno ¦ Fresno | Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS e-terra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, with system-wide migration by December 2029, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover installation of new IT equipment, EMS database development and testing. Scope does not cover removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring change to this premise will require scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2025-04-02 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5542081 | T.0006703 | TSRP_SV_T-LINE_AUBERRY | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-11-08 | 2024-12-01 | 2023-11-08 | NA | NA | FALSE | 965 | NA ¦ NA | 1633.229 | 1633.229 | 0 | 12.8575 | 1620.1427 | 0.2289 | 0 | 0 | 0 | 0 | 0 | 0 | 1633.229 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 12.8575 | 1620.1427 | 0.22891 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1088 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5548665 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-03-01 | 2022-12-01 | 2023-05-16 | NA | NA | FALSE | 908 | NA ¦ NA | 1227.7169 | 25500 | 0 | 1006.0584 | 221.6585 | 0 | 0 | 0 | 4750 | 4750 | 3500 | 5500 | 1227.7169 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 1227.7169 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1089 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5801898 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-07-25 | 2023-11-01 | 2024-06-30 | Scope Change | NA | FALSE | 784 | NA ¦ NA | 1377.2938 | 1377.2938 | 0 | 849.3666 | 504.3501 | 23.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 1377.2938 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 703.1053 | 674.1885 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1090 | Electric Transmission Operations Upgrade |  |  |  |  | Other | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5555503 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2026-05-31 | OAI | NA | NA | FALSE | 1100 | NA ¦ NA | 1035.2011 | 1035.2011 | 0 | 0 | 0 | 202.8414 | 737.6411 | 94.7186 | 0 | 0 | 0 | 0 | 940.4825 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 202.8414 | 0 | 225.1866 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1091 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Relocate | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 14 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5791860 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-07-13 | 2022-12-31 | 2025-02-28 | Material | Scope Change | TRUE | 2873 | NA ¦ NA | 7184.2256 | 7184.2256 | 870.0172 | 940.7095 | 2393.213 | 1463.107 | 940.7209 | 134.6156 | 0 | 0 | 0 | 0 | 7049.61 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 134.2036 | 0 | 7050.022 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1092 | CAISO Control Return |  |  | NA | The main driver for this project is to meet our obligations to CAISO and support their compliance with NERC standard BAL-003-1.1, however there are benefits to PG&E such as situational awareness improvements that can be made for PG&E’s Grid Operations team. The PMU data must be brought into the Energy Management System (EMS) where it can be utilized for situational awareness displays, state estimation, and as backups to existing real-time data that can improve PG&E’s compliance to TOP-001-5 and TOP-010-1(i). | Other - Operations Tech | New | NA | NA | Other [See Notes] | System Operations | NERC BAL Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5555923 | TBD | TBD | TBD | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1000 | 1000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [NERC/WECC/CAISO Standard/Requirement/Contingency] BAL-003-1.1 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1093 | FERC 881 Phase 2A |  |  | NA | The project will provide the initial engineering scoping for EMS software enhancements and capability expansion. Mission critical emergent work/real-time needs for Control Center assets and support associated with compliance, safety, PSPS, grid reliability, wildfire safety support and situational awareness | Other - Operations Tech | New | NA | NA | Other [See Notes] | System Operations | Other [See Notes] | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5555502 | NA | NA | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2026-05-29 | OAI | NA | NA | FALSE | 1850 | NA ¦ NA | 1390.1701 | 20390.1701 | 0 | 0 | 0 | 105.3179 | 1099.5731 | 185.2791 | 0 | 5000 | 2000 | 5000 | 1204.891 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 105.3179 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [NERC/WECC/CAISO Standard/Requirement/Contingency] FERC 881 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1094 | FERC Order 881 |  |  | NA | This project provides compliance for FERC NOPR 881 and Improved transmission capability due to Ambient-Adjusted ratings based on ambient temperature and other weather related measurements. Improved real-time situational awareness because EMS tools would be utilizing highly accurate, near real-time determined facility ratings, needed for safe and reliable management of the PG&E Transmission Grid | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | Other [See Notes] | NA | NA | 6 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5800498 | NA | NA | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-04-01 | 2024-12-01 | 2024-12-01 | NA | NA | FALSE | 3390 | NA ¦ NA | 4454.0815 | 4454.0815 | 0 | 4.1093 | 3135.5247 | 1063.6794 | 250.7682 | 0 | 0 | 0 | 0 | 0 | 4454.0815 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 2338.5852 | 1864.7282 | 250.7682 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [NERC/WECC/CAISO Standard/Requirement/Contingency] FERC 881 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1095 | Enterprise FERC 881 |  |  | NA | The Federal Energy Regulatory Commission (FERC) requires public utility transmission providers to implement ambient-adjusted ratings on the transmission lines over which they provide transmission services (FERC Order 881). This work consists of implementation of the technology, and procedures to comply with the FERC 881 Order. The project consists of multiple workstreams including Electric System Operations, Asset Management (Transmission and Substation Standards, and Strategic Governance), IT and Compliance. The work will also include the implementation of GE’s Digital Dynamic Line Rating (DDLR) product to generate Ambient Adjusted Ratings (AAR). The PG&E work will also be coordinated with the CAISO. This Project will develop, build, test, and place into production the systems, data, and procedures needed for PG&E to comply with the FERC Order 881. | Other - Operations Tech | New | NA | NA | Other [See Notes] | System Operations | Other [See Notes] | NA | NA | 6 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5555924 | NA | NA | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-08-01 | 2025-07-31 | 2025-07-31 | NA | NA | TRUE | 12364 | NA ¦ NA | 15686.6291 | 15686.6291 | 0 | 0 | 0 | 4090.3959 | 11594.1829 | 2.0503 | 0 | 0 | 0 | 0 | 15684.5788 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 15684.5788 | 2.0503 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [NERC/WECC/CAISO Standard/Requirement/Contingency] FERC 881 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1096 | PMU_CAISO_BELLOTA |  |  | San Joaquin | The scope of the project includes installation of PMUs at Bellota for tie lines to external Balancing authorities, testing, validation of data quality and availability at CAISO, and integration of PMU data into the Energy Management System (EMS) to be utilized for situational awareness displays, state estimation, and as backups to existing real-time data. The transmission lines to be monitored include Malin – Round Mountain #1 and Malin - Round Mountain #2 500kV lines. The installation of the PMUs will provide CAISO with improved data that will support system frequency response assessments and their compliance with BAL-003-1.1. In addition, PG&E has objectives to achieve through the implementation of these PMUs. PG&E’s objectives include an improved model validation process as well as enhanced situational awareness data and tools for use in Transmission Operations. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | System Operations | NERC BAL Compliance | NA | 2026-03-14 | 10 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5800633 | T.0008257 | PMU_CAISO_BELLOTA | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-05-13 | 2020-12-01 | 2024-10-11 | Prioritization | NA | FALSE | 11000 | NA ¦ NA | 1150.8815 | 1150.8815 | 0 | 37.9507 | 235.061 | 873.6508 | 4.2191 | 0 | 0 | 0 | 0 | 0 | 1150.8815 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1146.6624 | 4.2191 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] BAL-003-1.1 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1097 | PMU_CAISO_ROUND MOUNTAIN |  |  | Round Mountain CDP, Shasta | The scope of the project includes installation of PMUs at Round Mountain for tie lines to external Balancing authorities, testing, validation of data quality and availability at CAISO, and integration of PMU data into the Energy Management System (EMS) to be utilized for situational awareness displays, state estimation, and as backups to existing real-time data. The transmission lines to be monitored include Malin – Round Mountain #1 and Malin - Round Mountain #2 500kV lines. The installation of the PMUs will provide CAISO with improved data that will support system frequency response assessments and their compliance with BAL-003-1.1. In addition, PG&E has objectives to achieve through the implementation of these PMUs. PG&E’s objectives include an improved model validation process as well as enhanced situational awareness data and tools for use in Transmission Operations. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | System Operations | NERC BAL Compliance | NA | 2026-03-09 | 11 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5800680 | T.0008264 | PMU_CAISO_ROUND MOUNTAIN | 1 | 63 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2022 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-02-02 | 2020-12-01 | 2026-08-31 | Prioritization | NA | TRUE | 1100 | NA ¦ NA | 1629.3258 | 2316.8383 | 0 | 19.1905 | 51.2844 | 528.6512 | 992.267 | 725.4452 | 0 | 0 | 0 | 0 | 1591.3931 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC BAL-003 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1098 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | Lifecycle Replacement Analysis | Non-Wires | $100 Mil – $125 Mil | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5807118 | T.0009554 | Electric Transmission Operations Upgrade | 6 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-01 | 2028-12-01 | 2026-01-14 | NA | NA | TRUE | 48900 | NA ¦ NA | 14570.16 | 14570.16 | 0 | 0 | 27.4469 | 4965.6713 | 9394.3214 | 182.7205 | 0 | 5000 | 0 | 0 | 14387.4395 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1099 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | Lifecycle Replacement Analysis | Non-Wires | $100 Mil – $125 Mil | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5808113 | T.0009554 | Electric Transmission Operations Upgrade | 6 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-01 | 2028-12-01 | 2026-01-14 | NA | NA | TRUE | 48900 | NA ¦ NA | 2641.6786 | 2641.6786 | 0 | 0 | 0 | 1671.6924 | 893.8447 | 76.1415 | 0 | 0 | 0 | 0 | 2565.5371 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 2641.6786 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1100 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Non-Wires | $100 Mil – $125 Mil | NA | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5808395 | T.0009554 | Electric Transmission Operations Upgrade | 6 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-01 | 2028-12-01 | 2026-01-14 | NA | NA | FALSE | 48900 | NA ¦ NA | 2432.3063 | 2432.3063 | 0 | 0 | 0 | 0 | 1581.5017 | 850.8046 | 0 | 0 | 0 | 0 | 1581.5017 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1101 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Non-Wires | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5808745 | T.0009554 | Electric Transmission Operations Upgrade | 6 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-01 | 2028-12-01 | 2026-01-14 | NA | NA | TRUE | 48900 | NA ¦ NA | 862.5136 | 862.5136 | 0 | 0 | 0 | 780.9473 | 77.4528 | 4.1136 | 0 | 0 | 0 | 0 | 858.4 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 862.5136 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1102 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Non-Wires | $100 Mil – $125 Mil | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5811717 | T.0009554 | Electric Transmission Operations Upgrade | 6 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-01 | 2028-12-01 | 2026-01-14 | NA | NA | TRUE | 48900 | NA ¦ NA | 1307.0952 | 1307.0952 | 0 | 0 | 0 | 474.0929 | 762.4064 | 70.5958 | 0 | 0 | 0 | 0 | 1236.4994 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 1307.0952 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1103 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | 6 | NA | Non-Wires | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5811718 | T.0009554 | Electric Transmission Operations Upgrade | 6 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2028-12-01 | 2026-01-14 | NA | NA | FALSE | 48900 | NA ¦ NA | 338.8607 | 338.8607 | 0 | 0 | 0 | 0 | 329.2927 | 9.568 | 0 | 0 | 0 | 0 | 329.2927 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1104 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | T.0006190 | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 213 | 5a.Mitigates System Wide Failure Risk | NA | 5.21 | Non-IGP | 5782618 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2023-12-31 | NA | 2027-12-31 | NA | NA | FALSE | NA | NA ¦ NA | 1900.7272 | 1900.7272 | 398.1719 | -855.9931 | 20.8305 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 1900.7272 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2027 | 139.6862 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1105 | 2023-2033 Equipment for RAS |  |  | NA | Forecast placeholder for 2023-2033 Equipment for RAS | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.21 | Non-IGP | Ex112750 | NA | NA | NA | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 200 | 200 | 200 | 200 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1106 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | T.0006261 | Other [See Notes] | System Operations | NA | NA | 2026-02-12 | 16 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.3205 | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5801822 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2024-11-01 | 2025-12-31 | 2026-12-18 | Prioritization | NA | TRUE | 182000 | NA ¦ NA | 15232.1415 | 26954.976 | 0 | 11.3639 | 557.5518 | 5128.4247 | 8020.9511 | 10036.6846 | 3156.7236 | 0 | 0 | 0 | 13718.2915 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1107 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | T.0006261 | Other [See Notes] | System Operations | NA | NA | NA | 16 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5798442 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-01-02 | 2025-12-31 | 2026-06-30 | Prioritization | NA | TRUE | 182000 | NA ¦ NA | 3238.6838 | 4306.5335 | 5.4438 | 190.7815 | 79.529 | 742.013 | 1948.6245 | 832.8556 | 507.2861 | 0 | 0 | 0 | 2966.3919 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1108 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | T.0006261 | Other [See Notes] | System Operations | NA | NA | 2026-02-10 | 16 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.96252 | NA | 115 ¦ 60 kV | NA | NA | NA | 5.3 | Non-IGP | 5795040 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-05-01 | 2025-12-31 | 2026-06-30 | Workforce | Clearances | TRUE | 182000 | NA ¦ NA | 1333.7849 | 1663.7594 | 79.9481 | 246.3805 | 121.0231 | 141.8019 | 442.3746 | 632.2311 | 0 | 0 | 0 | 0 | 1031.5283 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1109 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Removal | NA | T.0006261 | Other [See Notes] | System Operations | NA | NA | NA | 14 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2173 | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5795881 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-02-01 | 2025-12-31 | 2024-05-24 | NA | NA | FALSE | 182000 | NA ¦ NA | 1097.6417 | 1097.6417 | 0 | 44.7383 | 722.4976 | 206.1251 | 124.2807 | 0 | 0 | 0 | 0 | 0 | 1097.6417 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 973.3611 | -891.7466 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1110 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | T.0006261 | Other [See Notes] | System Operations | NA | NA | NA | 14 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5792159 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-04-14 | 2025-12-31 | 2024-11-01 | NA | NA | TRUE | 182000 | NA ¦ NA | 23292.209 | 23434.9684 | 1448.0441 | 4526.0009 | 10215.1634 | 6583.4792 | 357.9888 | 69.9186 | 0 | 0 | 0 | 0 | 23271.027 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 22913.0382 | 357.9888 | 21.182 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1111 | Rocklin PACI RAS Ph 3 |  |  | Rocklin, Placer | This project is part of the SFGO RAS Lifecycle and Relocation Project - Phase 1 and is for the associated commissioning/testing at various remote sites. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0006261 | Other [See Notes] | System Operations | NA | NA | 2026-02-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.45068 | NA | NA | NA | NA | NA | 5.3 | Non-IGP | 5818738 | T.0006190 | SFGO RAS LifeCycle and Relocation | 8 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2026-12-18 | 2025-12-31 | NA | NA | FALSE | 33400 | NA ¦ NA | 35.4071 | 35.4071 | 0 | 0 | 0 | 0 | 0 | 35.4071 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1112 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-21 | 28 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.55624 | NA | NA | NA | NA | NA | 5.21 | Non-IGP | 5797502 | T.0007421 | Electric Transmission Operations Upgrade | 3 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2021-09-01 | 2021-12-31 | 2026-10-30 | Project Design | NA | TRUE | 900 | NA ¦ NA | 2382.4946 | 3146.9725 | 377.7657 | 1414.029 | 494.8391 | 67.6485 | 28.2122 | 735.0882 | 29.3898 | 0 | 0 | 0 | 2382.4946 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1113 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Other [See Notes] | System Operations | NA | NA | 2026-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 18.2105 | NA | NA | NA | NA | NA | NA | NA | 5799871 | T.0007421 | Electric Transmission Operations Upgrade | 3 | 63 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-03-25 | 2021-12-31 | 2022-03-30 | NA | NA | FALSE | 900 | NA ¦ NA | 20.7487 | 20.7487 | 0 | 7.748 | 13.0007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.7487 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 7.748 | 13.0007 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1114 | Transmission Circuit Breaker Online Monitoring |  |  | NA | Forecast placeholder for Transmission Circuit Breaker Online Monitoring. Install 8 transmission circuit breaker online monitors in 2025, 10 in 2026, 12 in 2027-2035 (unit cost $60k) | Substation - Circuit Breaker | New | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | EX113190 | NA | NA | NA | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | 2029-05-31 | OAI | NA | NA | FALSE | 2640 | NA ¦ NA | 0 | 2160 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 720 | 720 | 720 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1115 | Oakland K: Replace CB172 |  |  | Oakland, Alameda | Replacement of the existing 12kV Switchgear at Oakland K (Claremont) Substation | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace Breakers | NA | NA | 2026-03-05 | 59 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 3.9974 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5791478 | T.0000513 | OAKLAND "K" (CLAREMONT): REPLACE 12KV SW | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-03-29 | 2022-05-04 | 2025-10-29 | Project Design | NA | TRUE | 43200 | NA ¦ NA | 3062.8839 | 3276.5736 | 206.1127 | 1143.1134 | 86.4706 | 1068.1083 | 513.8301 | 215.6345 | 2.0033 | 0 | 0 | 0 | 3058.9357 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 2519.8342 | 3.1488 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1116 | GATES: Repl BK 3 Trans BRKR & SW |  |  | Fresno | Replace Gates Bank 3 (three single-phase, 1941 General Electric, 115/12kV, 6.25 MVA transformers), as well as Gates Bk 1 (three single-phase, 1951 Westinghouse, 230/115kV, 40 MVA transformers) with one new 230/12kV 45 MVA transformer with LTC. Replace 230kV CB 292 and switches 291 & 293 including the bypass switch 295. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace Breakers | NA | NA | 2026-03-12 | 70 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 230 kV | 240 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5782222 | T.0000810 | GATES: REPLACE BK3 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-09-10 | 2020-06-30 | 2020-05-26 | NA | NA | FALSE | 7400 | NA ¦ NA | 2455.6928 | 2455.6928 | -77.6281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2455.6928 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -70.7531 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1117 | Non-SF6 GIS Pilot Project |  |  | Livermore, Alameda | Installation of a single-bay, non-SF6-gas insulated switchgear (GIS) at PG&E’s Livermore Training Facility as a pilot that evaluates the GE-supplied alternative insulation gas, g3. The g3 gas has a much lower Global Warming Potential (GWP) than SF6. This pilot is part of PG&E’s sustainability initiative to reduce its CO2 footprint by 2050 in support of California’s goal of 80% reduction in greenhouse gas emissions. | Substation - Circuit Breaker | New | NA | NA | Asset Condition | Age/Condition - Replace Breakers | NA | NA | 2026-04-01 | NA | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.60395 | NA | 115 kV | NA | 9. Reliability (Low Safety Risk) | NA | 3.0011 | Non-IGP | 5777410 | T.0003481 | Non-SF6 GIS Pilot Project | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-09-17 | 2018-11-30 | 2026-12-21 | Prioritization | NA | TRUE | 800 | NA ¦ NA | 899.4329 | 1714.7075 | 8.1874 | 24.4345 | 772.6239 | 30.8352 | 0 | 726.8112 | 0 | 0 | 0 | 0 | 899.4329 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1118 | Purchase two 115kV 63kA mobile CBs |  |  | NA | This project will purchase two new mobile circuit breakers rated 115kV 63kA with interrupting capacity and 2000 amps continuous current (CC). The | Substation - Circuit Breaker | New | NA | NA | Asset Condition | Age/Condition - Replace Breakers | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5554019 | T.0009457 | Purchase 115kV 63kA mobile CBs | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-12-01 | 2025-09-01 | 2027-12-31 | Prioritization | NA | FALSE | 2000 | NA ¦ NA | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 3000 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 47.3783 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1119 | MOSS LANDING: Replace 500 KV Breakers |  |  | Monterey | This project will resolve current configuration issues and address reliability concerns. This project will rebuild Moss Landing 500kV Substation within the existing substation fence line. The project will replace the existing 500kV breakers and switches in a BAAH configuration, and upgrade the protection schemes. This will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 500 kV Breakers | NA | NA | 2026-03-10 | 32 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 41.3213 | NA | 500 kV | 321 | 9. Reliability (Low Safety Risk) | 10 | NA | NA | 5759485 | T.0000678 | MOSS LANDING 500KV Upgrade | 6 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-09-04 | 2020-03-31 | 2020-06-22 | NA | NA | FALSE | 46400 | NA ¦ NA | 36280.2913 | 36280.2913 | 2250.1301 | -66.8208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36280.2913 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 2127.8324 | -63.189 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1120 | CEM breakers - Purchase 6- 230kV and 4- 115kV CBs |  |  | NA | This project increases PG&E's Transmision Breakers CEM inventory in acticipation for higher number of failures in future years. The project proposes to purchase a total of six (6) 230kV and four (4) 115kV CEM breakers. | Substation - Circuit Breaker | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 115 kV | NA | NA | NA | 4.01 | IGP | Ex112782 | NA | NA | NA | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1800 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 900 | 900 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1121 | OAKLAND D: Replace 115 KV CB 112 132 152 |  |  | Oakland, Alameda | This project will replace the 115kV Circuit Breakers 122, 132, and 152 at Oakland D substation . PG&E’s Deteriorated Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. Breakers being replaced under this project are 1960s and 1970s vintage oil circuit breakers. These breakers are in deteriorated condition. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-16 | 53 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 0.54348 | NA | 115 kV | 80 | 9. Reliability (Low Safety Risk) | 1 | NA | NA | 5758808 | T.0000024 | Oakland D Replace Sub CB112, CB132 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-06-01 | 2019-03-21 | 2021-03-28 | Prioritization | NA | FALSE | 3626 | NA ¦ NA | 5014.007 | 5014.007 | 1415.3289 | 10.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5014.007 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 4585.9205 | 9.9127 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1122 | LODI: Replace CB 12 22 32 |  |  | Lodi, San Joaquin | This project will replace all 60kV circuit breakers, 60kV Main and Auxiliary bus structure and the associated equipment at Lodi Substation.The replacement criteria were developed based on technical assessments of the switches including design characteristics, system criticality, historical failure rates, onsite inspections, vintage, environmental factors, and operating conditions. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-16 | 63 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.93622 | NA | 60 kV | 48 | 9. Reliability (Low Safety Risk) | 20 | NA | NA | 5756866 | T.0000303 | LODI SUB: REPL CB 12, 22 AND 32 | 2 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-08-04 | 2019-10-17 | 2022-05-20 | Project Design | NA | FALSE | 7215 | NA ¦ NA | 14607.8906 | 14607.8906 | 4415.7357 | 3857.8096 | 1330.7626 | 107.6781 | 0 | 0 | 0 | 0 | 0 | 0 | 14607.8906 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 12454.5549 | 1252.4945 | 101.345 | -0.00013 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1123 | GOLD HILL: REPL 230KV CB 252, 212 |  |  | Folsom, Sacramento | This project will replace 230kV circuit breakers 212, 222, 242, 252, 712 and associated equipment at Gold Hill Substation. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 58 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 12.8702 | NA | 230 kV | 80 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5756856 | T.0000466 | GOLD HILL: REPL CBS 252,212,222,242,712 | 4 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-10-15 | 2020-12-18 | 2019-02-13 | NA | NA | FALSE | 10585 | NA ¦ NA | 7182.0536 | 7182.0536 | 27.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7182.0536 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 23.9724 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1124 | GOLD HILL: REPL 230kV CB 222 |  |  | Folsom, Sacramento | This project will replace 230kV circuit breakers 212, 222, 242, 252, 712 and associated equipment at Gold Hill Substation. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 58 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 12.8702 | NA | 230 kV | NA | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5784366 | T.0000466 | GOLD HILL: REPL CBS 252,212,222,242,712 | 4 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-06-05 | 2020-12-18 | 2019-07-09 | NA | NA | FALSE | 10585 | NA ¦ NA | 535.558 | 535.558 | 9.4815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535.558 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 9.4815 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1125 | GOLD HILL: REPL 230KV CB 242, 712 |  |  | Folsom, Sacramento | This project will replace 230kV circuit breakers 212, 222, 242, 252, 712 and associated equipment at Gold Hill Substation. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 60 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 12.8702 | NA | 230 kV | NA | NA | NA | NA | NA | 5784367 | T.0000466 | GOLD HILL: REPL CBS 252,212,222,242,712 | 4 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-10-15 | 2020-12-18 | 2022-03-23 | Prioritization | NA | FALSE | 10585 | NA ¦ NA | 2958.166 | 2958.166 | 469.8719 | 978.8802 | 31.2206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2958.166 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 2926.9454 | 31.2207 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1126 | CASCADE: Repl 60 KV Phase 2 CBS |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-16 | 63 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | NA | 60 kV | 95 | 9. Reliability (Low Safety Risk) | NA | 5.2 | IGP | 5777643 | T.0000651 | Cascade Substation Upgrade | 10 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2021-03-15 | 2022-01-31 | 2026-04-30 | Prioritization | NA | TRUE | 35800 | NA ¦ NA | 2961.9495 | 4576.2804 | 767.5361 | 292.6927 | 101.2361 | 142.9243 | 545.5153 | 1857.0307 | 0 | 0 | 0 | 0 | 2719.2497 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1127 | CASCADE: Replace 60 KV CB 42 52 62 72 |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-16 | 60 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | NA | 60 kV | 58 | 9. Reliability (Low Safety Risk) | NA | 5.2 | IGP | 5757727 | T.0000651 | Cascade Substation Upgrade | 10 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-03-10 | 2022-01-31 | 2025-01-23 | Prioritization | NA | TRUE | 35800 | NA ¦ NA | 7290.4529 | 7743.7483 | 834.2092 | 626.9971 | 466.0654 | 943.5371 | 805.7992 | 501.9719 | 0 | 0 | 0 | 0 | 7241.7764 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 7224.5764 | 48.5249 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1128 | MONTAGUE: Replace 115 KV CB 132 142 |  |  | San Jose, Santa Clara | The Montague Substation Bundle and Remote End projects will replace Circuit Breaker (CB) 132, CB 142, Circuit Switcher (CSW) 176, CSW 186, replace protection relays for Bank 1, Bank 2, Bank 3, line and bus protection relays, install Distribution SCADA on CB 2100, CB 2200 and CB 2300. In addition, the line and bus protection relays at the Remote End Substations Los Esteros and Trimble will be replaced. The Montague Substation Bundle and Remote Ends are comprised of multiple projects that contribute to the betterment of the PG&E Electric System. CB132 and CB142 are being replaced as part of the Deteriorated Breakers Replacement Program to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. The replacement of the old Protection relays at Montague Substation, as well as the Remote Ends will improve system reliability, whereas installing SCADA on all the distribution equipment in Montague Substation will provide system visibility for low side devices at Montague Substation. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-05 | 58 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.2309 | NA | 115 kV | 95 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5761188 | T.0000706 | MONTAGUE SUB 115 KV CB 132, 142 | 4 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-04 | 2023-02-01 | 2023-01-07 | NA | NA | FALSE | 9841 | NA ¦ NA | 4316.0243 | 4316.0243 | 817.4434 | 2069.7231 | 1182.3746 | 33.6108 | 0 | 0 | 0 | 0 | 0 | 0 | 4316.0243 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 3789.0813 | 29.5586 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1129 | WESTPARK: Replace 115KV CB 112 |  |  | Bakersfield, Kern | This project will replace one transmission class 115 kV breaker (CB 112). Westpark CB 112 is identified for replacement in 2019 as part of the deteriorated transmission breaker replacement program. The prioritization criteria were developed based upon technical assessments of the transmission breaker including: age, condition, high failure rate models, criticality, and overstress. In addition, factors such as recurring maintenance costs, availability of spare parts, and environmental issues are also considered. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-17 | 37 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7259 | NA | 115 kV | 42 | 9. Reliability (Low Safety Risk) | 12 | 3.0011 | IGP | 5757736 | T.0000740 | WESTPARK SUB 115KV CB 112 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-07-24 | 2019-04-30 | 2030-03-01 | Prioritization | NA | FALSE | 1310 | NA ¦ NA | 656.3624 | 2046.539 | 4.6302 | 0 | 0 | 0 | 12.0355 | 48.1417 | 0 | 0 | 250 | 800 | 648.3973 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1130 | KERN OIL: Repl 115 KV CB 162 |  |  | Oildale CDP, Kern | This project will replace one transmission class 115 kV breaker (CB 162). PG&E’s Deteriorated Transmission Breaker Replacement Program was developed to realize the savings associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency breaker replacements. Equipment replacements following a catastrophic failure can cost up to 30% more than planned replacements due to increased construction scope, premiums paid to expedite major materials, temporary construction to maintain service if the failure occurs during peak conditions, overtime labor charges, and clean-up of oil discharged as a result of the failure.Equipment identified for replacement is the following: • CB 162: 1951-vintage, Westinghouse, OCB, 115 kV, model number GM5. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-06 | 73 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.2122 | NA | 115 kV | 104 | NA | NA | NA | NA | 5761185 | T.0000760 | KERN OIL 115 KV CB 162 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-08-02 | 2018-11-07 | 2018-12-31 | NA | NA | FALSE | 2040 | NA ¦ NA | 1107.4337 | 1107.4337 | 0.9014 | 33.2874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107.4337 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 0.85611 | 31.6151 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1131 | MORGAN HILL: Replace 115 KV CB 172 |  |  | Morgan Hill, Santa Clara | Replace Morgan Hill 115 kV CB 172 as identified in the 2017-2018 Transmission Deteriorated Breaker Replacement Program. PG&E’s Deteriorated Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria include: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. The “year” a breaker is slated for replacement is based on the individual asset’s rank. The overall strategy dictates the replacement rate. The Circuit Breaker Strategy’s objective is to minimize failures and maximize useful life through an effective maintenance plan and by replacing breakers for which maintenance is either ineffective or uneconomical. The breakers were selected based upon 1-N ranking & the RIBA scores. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-04 | 38 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.8017 | NA | 115 kV | 42 | NA | NA | 5.11 | IGP | 5757733 | T.0000802 | MORGAN HILL SUB 115 KV CB 172 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2031-12-23 | NA | 2032-01-29 | NA | NA | FALSE | NA | NA ¦ NA | 0.6569 | 1761.7541 | 0.1554 | 0.04 | 0.044 | 0.0225 | 0 | 0.044 | 0 | 0 | 0 | 0 | 0.6569 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1132 | COTTONWOOD: Repl CB 152/192 |  |  | Cottonwood CDP, Shasta | Project scope is to replace both 230/115kV transmission transformers which will address the 115kV high voltage issue and improve reliability of the North Valley transmission system. Installing the 115kV bus tie breakers will address NERC category P2 breaker fault of Cottonwood CB 102 or, a NERC category P4 nearby fault plus a CB 102 fault. The CAISO approved shunt reactors/transformer replacement to mitigate the high voltage issue and additionally the 115kV bus tie breakers to mitigate the P2 and P4 contingencies. The MPAC and breakers replacement will replace the deteriorated asset and capture the efficiency of upgrading protection and controls, avoid rework and multiple clearances. The high-level scope includes the following: • Replace the existing Banks 1 and 4 with 230/115kV 420MVA, with LTC and associated bus selector switches. • Install new bay and new 230kV breaker to connect new Bank 1 to 230kV bus. • Replace Bank 1 low-side breaker CB 172 and the associated switches. • Replace Bank 4 low-side CB 192 and the associated switches. • Expand existing 115kV MPAC to accommodate protection and controls. • Expand SPCC to accommodate increased oil quantity of new banks. • Install new sectionalizing CB’s 912 and 922 w/switches to sectionalize 115kV bus to Sections D and E. • Install new CB 132 with switches and relocate Trinity-Cottonwood 115kV line to Bus Section E. • Install new bus paralleling breaker CB 102 with switches in Bus Section E. • Install new bus paralleling breaker CB 902 with switches in Bus Section D. • Replace the existing OCBs 142 and 152 with non-SF6 breakers and the associated switches. • Replace six of the existing 230kV OCBs (CBs 222, 232, 272, 292, 522, and 542) with new 230kV 2000A gas circuit breakers, and the associated breaker and bus selector switches. • Install new 230kV 2000A bus paralleling breaker (CB 502) and associated switches in place of the existing Transformer 1 CB 512 position. • Replace switches 213, 357, 359, 367, and 369. • Install new MPAC Building to house the protection, automation, and control equipment for the 230kV Bus Sections “E” and “F”. | Substation - Circuit Breaker | Replace | NA | T.0004659 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-19 | 38 | Lifecycle Replacement Analysis | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 26.1945 | NA | 115 kV | 80 | 9. Reliability (Low Safety Risk) | NA | 5.2 | IGP | 5781697 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-05-13 | 2028-04-30 | 2028-10-09 | NA | NA | FALSE | 51200 | NA ¦ NA | 700.6383 | 4545.7472 | 18.2521 | 27.5487 | 66.4447 | 52.2608 | 425.0646 | 1172.3537 | 295.0973 | 274.3424 | 8.18 | 0 | 657.2386 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1133 | COTTONWOOD: Replace Various CBs |  |  | Cottonwood CDP, Shasta | Project scope is to replace both 230/115kV transmission transformers which will address the 115kV high voltage issue and improve reliability of the North Valley transmission system. Installing the 115kV bus tie breakers will address NERC category P2 breaker fault of Cottonwood CB 102 or, a NERC category P4 nearby fault plus a CB 102 fault. The CAISO approved shunt reactors/transformer replacement to mitigate the high voltage issue and additionally the 115kV bus tie breakers to mitigate the P2 and P4 contingencies. The MPAC and breakers replacement will replace the deteriorated asset and capture the efficiency of upgrading protection and controls, avoid rework and multiple clearances. The high-level scope includes the following: • Replace the existing Banks 1 and 4 with 230/115kV 420MVA, with LTC and associated bus selector switches. • Install new bay and new 230kV breaker to connect new Bank 1 to 230kV bus. • Replace Bank 1 low-side breaker CB 172 and the associated switches. • Replace Bank 4 low-side CB 192 and the associated switches. • Expand existing 115kV MPAC to accommodate protection and controls. • Expand SPCC to accommodate increased oil quantity of new banks. • Install new sectionalizing CB’s 912 and 922 w/switches to sectionalize 115kV bus to Sections D and E. • Install new CB 132 with switches and relocate Trinity-Cottonwood 115kV line to Bus Section E. • Install new bus paralleling breaker CB 102 with switches in Bus Section E. • Install new bus paralleling breaker CB 902 with switches in Bus Section D. • Replace the existing OCBs 142 and 152 with non-SF6 breakers and the associated switches. • Replace six of the existing 230kV OCBs (CBs 222, 232, 272, 292, 522, and 542) with new 230kV 2000A gas circuit breakers, and the associated breaker and bus selector switches. • Install new 230kV 2000A bus paralleling breaker (CB 502) and associated switches in place of the existing Transformer 1 CB 512 position. • Replace switches 213, 357, 359, 367, and 369. • Install new MPAC Building to house the protection, automation, and control equipment for the 230kV Bus Sections “E” and “F”. | Substation - Circuit Breaker | Replace | NA | T.0004659 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-19 | 62 | Lifecycle Replacement Analysis | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 26.1945 | NA | 230 kV | 33 | 9. Reliability (Low Safety Risk) | NA | 5.2 | IGP | 5769042 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 64 | NA ¦ 5758737 ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-12-04 | 2028-04-30 | 2029-08-10 | Clearances | NA | FALSE | 51200 | NA ¦ NA | 746.5862 | 10337.4956 | 80.1742 | 35.1657 | 85.6031 | 89.8113 | 235.9508 | 1648.1444 | 2132 | 2311 | 1284 | 0 | 728.1433 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1134 | GOLD HILL: REPL 60KV CB 12 & UPGRADE 60K |  |  | Folsom, Sacramento | This project will replace 60kV and 115kV circuit breakers 12, 122, 142 and associated equipment at Gold Hill Substation as part of PG&E’s Deteriorated Breakers Replacement Program. | Substation - Circuit Breaker | Replace | NA | T.0004920 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 63 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 12.8702 | NA | 115 ¦ 60 kV | 130 | 9. Reliability (Low Safety Risk) | NA | 5.1 | IGP | 5761184 | T.0001157 | Gold Hill: Replace 60kV CB 12 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2033-02-28 | 2020-05-01 | 2033-06-01 | Prioritization | NA | FALSE | 4500 | NA ¦ NA | 518.9361 | 3773.5778 | 27.0157 | 62.3101 | 41.1742 | 34.3229 | 12.1461 | 33.3493 | 0 | 0 | 0 | 0 | 518.9361 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $5 Mil - $10 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1135 | PALO ALTO: Convert 115 KV Bus to BAAH |  |  | Palo Alto, Santa Clara | The Palo Alto switching station is already set-up for BAAH. However, it is operated as a nonstandard variant of Bus 1& 2 with six breakers installed for six lines. Presently it is required to trip the entire bus in order to protect SVP equipment. This project will replace the six breakers, install three additional breakers, and convert the bus to BAAH.Install modular protection, automation, and control (MPAC) panels in MPAC building for the 115 kV bus to replace the existing control building | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-06 | 52 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.0138 | NA | 115 kV | 472 | 9. Reliability (Low Safety Risk) | NA | 5.11 | IGP | 5769807 | T.0001493 | PALO ALTO SS: Convert 115kV Bus to BAAH | 2 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2029-05-21 | NA | 2031-12-31 | NA | NA | FALSE | NA | NA ¦ NA | 2230.9301 | 29097.4994 | 1112.3765 | 546.0706 | -261.1413 | 35.912 | 52.2165 | 537.696 | 0 | 0 | 0 | 0 | 2230.9301 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1136 | EL PATIO: Replace CB 122 142 |  |  | Campbell, Santa Clara | It is recommended by the project Team to proceed with the replacement of the transmissions breakers CB 122 and CB 142 at El Patio substation due to the RIBA ranking system which place these breakers at higher risk of failure due to the age and type. By planning, scoping, engineering and replacing these breakers at this time the company will have a higher cost savings and shortened clearance outages to perform the work compared to replacing the breakers after failure causing longer outages and higher replacement costs. Replacing these breakers will be in line with current company goals in providing efficient, reliable energy to our customers. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-05 | 64 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.392 | NA | 115 kV | 284 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5769808 | T.0001497 | El Patio CB 122 and 142 Planned Repl. | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-01-19 | 2021-02-17 | 2021-03-24 | NA | NA | FALSE | 2766 | NA ¦ NA | 3089.6624 | 3089.6624 | 2037.4385 | 396.6315 | -4.4125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.6624 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1957.0459 | 286.4223 | -3.1864 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1137 | RAVENSWOOD: Replace CB 152 162 312 322 |  |  | Menlo Park, San Mateo | Replace RAVENSWOOD CB 152, 162, 312, & 322 oil circuit breakers under the 2019 transmission breakers replacement program | Substation - Circuit Breaker | Replace | NA | T.0006761 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 56 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | NA | 115 kV | 120 | 9. Reliability (Low Safety Risk) | 11 | 3.0011 | IGP | 5761192 | T.0001608 | RAVENSWOOD SUB CB 152,162,312,322 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2032-07-08 | NA | 2033-01-24 | NA | NA | FALSE | NA | NA ¦ NA | 146.0451 | 5155.3194 | 31.3585 | 83.6734 | 10.934 | 5.0069 | 0 | 9.2743 | 0 | 0 | 500 | 1500 | 146.0451 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1138 | VACA DIXON - INST CB 402 |  |  | Solano | Replace overstressed 230kV CB 442, 452, 462 with 3000A CC, 63kA IC breakers and add new bus paralleling substitute breaker CB 402 as part of PG&E’s Deteriorated Breakers Replacement Program. | Substation - Circuit Breaker | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-25 | NA | Lifecycle Replacement Analysis | Other - Status Quo | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | 104 | 9. Reliability (Low Safety Risk) | 4 | 5.11 | IGP | 5761196 | T.0001609 | Vaca Dixon - REPL 442, 452, 462 INST 402 | 5 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-10-20 | 2027-03-01 | 2027-01-15 | NA | NA | TRUE | 14900 | NA ¦ NA | 4365.1587 | 5638.0464 | 157.4981 | 120.8488 | 170.4299 | 2169.7647 | 846.8817 | 1565.8503 | 526.4201 | 0 | 0 | 0 | 3545.776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1139 | Vaca Dixon: Repl OS CB 442 |  |  | Solano | Replace overstressed 230kV CB 442, 452, 462 with 3000A CC, 63kA IC breakers and add new bus paralleling substitute breaker CB 402 as part of PG&E’s Deteriorated Breakers Replacement Program. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-25 | 37 | Lifecycle Replacement Analysis | Other - Status Quo | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | NA | NA | NA | 5.11 | IGP | 5810426 | T.0001609 | Vaca Dixon - REPL 442, 452, 462 INST 402 | 5 | 64 | NA ¦ 5761196 ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-03-28 | 2027-03-01 | 2026-06-18 | NA | NA | TRUE | 14900 | NA ¦ NA | 1384.8791 | 3038.4671 | 0 | 0 | 0 | 3.065 | 1216.6875 | 1564.1607 | 254.5539 | 0 | 0 | 0 | 1219.7525 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1140 | Vaca Dixon: Repl OS CB 462 |  |  | Solano | Replace overstressed 230kV CB 442, 452, 462 with 3000A CC, 63kA IC breakers and add new bus paralleling substitute breaker CB 402 as part of PG&E’s Deteriorated Breakers Replacement Program. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-25 | 37 | Lifecycle Replacement Analysis | Other - Status Quo | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | NA | NA | NA | 5.11 | IGP | 5810428 | T.0001609 | Vaca Dixon - REPL 442, 452, 462 INST 402 | 5 | 64 | NA ¦ 5761196 ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-16 | 2027-03-01 | 2026-10-02 | NA | NA | TRUE | 14900 | NA ¦ NA | 1442.2341 | 2365.7685 | 0 | 0 | 0 | 1.0061 | 1265.7589 | 1099.0035 | 0 | 0 | 0 | 0 | 1266.765 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1141 | Vaca Dixon: Repl OS CB 452 |  |  | Solano | Replace overstressed 230kV CB 442, 452, 462 with 3000A CC, 63kA IC breakers and add new bus paralleling substitute breaker CB 402 as part of PG&E’s Deteriorated Breakers Replacement Program. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-25 | 27 | Lifecycle Replacement Analysis | Other - Status Quo | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | NA | NA | NA | 5.11 | IGP | 5810427 | T.0001609 | Vaca Dixon - REPL 442, 452, 462 INST 402 | 5 | 64 | NA ¦ 5761196 ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-10-13 | 2027-03-01 | 2027-01-08 | NA | NA | TRUE | 14900 | NA ¦ NA | 1366.0862 | 3238.1309 | 0 | 0 | 0 | 3.3223 | 1198.7333 | 1750.0464 | 286.0289 | 0 | 0 | 0 | 1202.0556 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1142 | SANTA ROSA A: Replace CB 132 |  |  | Santa Rosa, Sonoma | This project will replace deteriorating oil filled circuit breakers 132, 142 and 162 with non-SF6 breakers at Santa Rosa A Substation. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-02 | 53 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.91804 | NA | 115 kV | 30 | 9. Reliability (Low Safety Risk) | 12 | 3.0011 | IGP | 5772481 | T.0002317 | Santa Rosa A: Replace CB 132,142,162 | 3 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2031-01-16 | 2023-05-31 | 2031-03-11 | Prioritization | NA | FALSE | 7690 | NA ¦ NA | -45.6546 | 1272.9402 | 676.9747 | 216.6911 | 317.1441 | -46.9274 | -1414.9334 | 90.1044 | 0 | 0 | 0 | 0 | -45.6546 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1143 | SANTA ROSA: Repl CB 162 |  |  | Santa Rosa, Sonoma | This project will replace deteriorating oil filled circuit breakers 132, 142 and 162 with non-SF6 breakers at Santa Rosa A Substation. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-02 | 51 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.91804 | NA | 115 kV | NA | NA | NA | 3.0011 | IGP | 5793839 | T.0002317 | Santa Rosa A: Replace CB 132,142,162 | 3 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2031-01-02 | 2023-05-31 | 2031-03-26 | Prioritization | NA | FALSE | 7690 | NA ¦ NA | 8.0526 | 1558.9972 | 309.6608 | 49.6461 | 254.4931 | -126.3064 | -588.0046 | 39.2138 | 0 | 0 | 0 | 0 | 8.0526 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1144 | SANTA ROSA: Repl CB 142 |  |  | Santa Rosa, Sonoma | This project will replace deteriorating oil filled circuit breakers 132, 142 and 162 with non-SF6 breakers at Santa Rosa A Substation. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-02 | 51 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.91804 | NA | 115 kV | NA | NA | NA | 3.0011 | IGP | 5793879 | T.0002317 | Santa Rosa A: Replace CB 132,142,162 | 3 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2031-01-02 | 2023-05-31 | 2031-03-26 | Prioritization | NA | FALSE | 7690 | NA ¦ NA | -62.1189 | 1889.5915 | 344.8882 | 102.911 | 215.2111 | -131.577 | -700.5868 | 42.004 | 0 | 0 | 0 | 200 | -62.1189 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1145 | SAN LEANDRO U: Repl CB 182- 372- 382 |  |  | San Leandro, Alameda | Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. 1. Replace OCBs 182, 372, and 382 with new 115kV, 2000A circuit breakers. 2. Replace OCBs 182, 372, and 382 foundations. 3. Relocate and enlarge switchman platforms. 4. Evaluate and replace conductors as required. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 59 | Lifecycle Replacement Analysis | Wires - Bus Upgrade Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 10.2372 | NA | 115 kV | 242 | NA | NA | NA | NA | 5772691 | T.0002360 | San Leandro U: Replace CB 182, 372, 382 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-12-06 | 2019-06-30 | 2019-03-15 | NA | NA | FALSE | 2523 | NA ¦ NA | 5460.3662 | 5460.3662 | 122.0217 | 324.0097 | 68.9456 | 4.9874 | 0 | 0 | 0 | 0 | 0 | 0 | 5460.3662 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 234.51 | 309.6686 | 65.894 | 4.7666 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1146 | NEWARK: Repl CB 180 |  |  | Fremont, Alameda | Replace Circuit Breaker 180 at Newark substation. PG&E’s Deteriorated Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. The deteriorated breaker replacement program criteria are primarily based on the technical health and risk based assessments of the breakers. The health assessment includes dissolved gas analysis, oil quality data, on-site inspections, vintage, and maintenance costs. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-03 | 56 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 27.7611 | NA | 115 kV | 168 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5772747 | T.0002361 | Newark Sub Replace CB 180 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-11-02 | 2022-12-23 | 2022-12-23 | NA | NA | FALSE | 2180 | NA ¦ NA | 2495.2396 | 2495.2396 | 563.5983 | 1425.0019 | 478.536 | 1.5033 | 0 | 0 | 0 | 0 | 0 | 0 | 2495.2396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 2328.0073 | 1.3995 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $2 Mil - $3 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1147 | BALCH PH #2: Replace CB 232 |  |  | Fresno | Replace BALCH PH #2 CB 232 oil circuit breakers under the 2021 transmission breakers replacement program | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-12 | 68 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.54903 | NA | 230 kV | 168 | 9. Reliability (Low Safety Risk) | NA | 3.0011 | IGP | 5773862 | T.0002634 | Balch PH #2: Replace CB 322 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2032-09-03 | 2025-02-01 | 2032-11-02 | Prioritization | NA | FALSE | 3762 | NA ¦ NA | 790.3626 | 3636.4553 | 87.1833 | 546.3949 | 88.6394 | 57.9134 | 10.2316 | 49.5873 | 0 | 0 | 0 | 1398.2527 | 790.3626 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $3 Mil -$5 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1148 | EL PATIO: Replace CB 312 332 |  |  | Campbell, Santa Clara | It is recommended by the project Team to proceed with the replacement of the transmissions breakers CB 312 and CB 332 at El Patio substation due to the RIBA ranking system which place these breakers at higher risk of failure due to the age and type. By planning, scoping, engineering and replacing these breakers at this time the company will have a higher cost savings and shortened clearance outages to perform the work compared to replacing the breakers after failure causing longer outages and higher replacement costs. Replacing these breakers will be in line with current company goals in providing efficient, reliable energy to our customers. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-05 | 59 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.392 | NA | 115 kV | 155 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5777172 | T.0003435 | EL PATIO CB312 and CB332 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-09-08 | 2020-12-31 | 2020-12-17 | NA | NA | FALSE | 1797 | NA ¦ NA | 1395.6222 | 1395.6222 | 84.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1395.6222 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 74.7957 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1149 | Salinas Sub: Repl 60kV CB 2, 32 |  |  | Salinas, Monterey | Replace SALINAS 60KV CB 2 & 32 oil circuit breakers under the 2023 transmission breakers replacement program | Substation - Circuit Breaker | Replace | NA | T.0005977 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 58 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.4966 | NA | 60 kV | NA | 9. Reliability (Low Safety Risk) | 10 | 5.11 | IGP | 5777323 | T.0003464 | Salinas Sub: Repl 60kV CB 2, 32 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-01-09 | NA | 2029-05-30 | NA | NA | TRUE | NA | NA ¦ NA | 721.5144 | 3454.1729 | 160.7486 | 503.3578 | 4.2436 | 3.8867 | 49.2777 | 44.7661 | 0 | 0 | 2000 | 400 | 721.5144 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1150 | OAKLAND K: CB 162, 132, 152 |  |  | Oakland, Alameda | Replace OAKLAND K CB 162, 132, & 152 oil circuit breakers under the 2023 transmission breakers replacement program | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 60 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 3.9974 | NA | 230 kV | NA | 9. Reliability (Low Safety Risk) | 5 | 3.0011 | IGP | 5777325 | T.0003466 | Oakland K: CB 162,132,152 | 3 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-11-01 | 2027-01-08 | 2028-03-29 | Clearances | NA | FALSE | 6900 | NA ¦ NA | 1630.2055 | 3758.8113 | 75.3195 | 468.2768 | 6.8731 | 343.7305 | 627.4171 | 711.5657 | 0 | 0 | 0 | 0 | 1521.617 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1151 | OAKLAND L: Replace CB 312 and 412 |  |  | Oakland, Alameda | Replace OAKLAND L CB 312 and 412 oil circuit breakers under the 2023 transmission breakers replacement program | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 51 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 1.197 | NA | 230 kV | NA | 9. Reliability (Low Safety Risk) | 16 | 3.0011 | IGP | 5777326 | T.0003467 | Oakland L Sub: Repl CB 322, 422,312,412 | 2 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2031-05-19 | NA | 2032-01-16 | NA | NA | FALSE | NA | NA ¦ NA | 228.0866 | 3521.5393 | 0 | 205.1682 | 22.9184 | 0 | 0 | 0 | 0 | 0 | 0 | 919.3376 | 228.0866 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1152 | SWIFT SUB: REPLACE CB 412 |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Circuit Breaker | Replace | NA | T.0009169 ¦ T.0009536 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-06 | 53 | Lifecycle Replacement Analysis | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.1012 | NA | 115 kV | NA | NA | NA | 3.0011 | IGP | 5772488 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2029-07-23 | 2023-03-31 | 2029-09-19 | Bundling Dependencies | NA | FALSE | 65600 | NA ¦ NA | 288.979 | 1856.5674 | 73.2292 | 182.9051 | 16.9169 | 15.9279 | 0 | 17.5884 | 0 | 250 | 300 | 750 | 288.979 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1153 | Mountain View CB 112 & 122 Planned Repl |  |  | Mountain View, Santa Clara | This project proposes to replace existing substation transformer Bank 1 in order to eliminate a growing deficiency on both Mountain View Bank 1 and Mountain View Bank 3. Replace two existing 115 kV motor-operated switches (157 and 159) with circuit breakers. Presently any bus or bank fault will trip both existing 115 kV breakers CB 112 & CB 122. By adding two additional 115 kV circuit breakers, only the faulted bus or bank would experience an outage. This additional scope will improve the looped bus, provide a logical path to an ultimate five-element 115 kV ring bus, improve bank clearances and increase reliability by reducing momentary outages to the 39,141 existing customers on Mountain View Substation. Transmission Substation Work (MWC 61): • Replace 115 kV circuit switchers 159 and 157 with 115 kV circuit breakers. • Extend existing control building will to accommodate the new relays for the breakers. with 115 kV circuit breakers. • Replace existing CB 112 with new circuit breaker/disconnect switches. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-04 | 67 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8224 | NA | 115 kV | 290 | 9. Reliability (Low Safety Risk) | NA | 3.0011 | IGP | 5769810 | T.0005971 | Mountain View - Replace Bank 1 | 3 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-01-02 | 2028-12-06 | 2027-12-14 | NA | NA | TRUE | 22100 | NA ¦ NA | 5736.6752 | 12515.5573 | 6.7853 | 145.7536 | 36.8407 | 441.567 | 3646.0237 | 4544.2481 | 3581.2805 | 110 | 0 | 0 | 4276.9703 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1154 | Gold Hill: Repl 115kV CB 142 |  |  | Folsom, Sacramento | Replace 115 kV Circuit Breakers 142 and 172 and associated equipment as required. PG&E’s Deteriorated Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria include: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. The “year” a breaker is slated for replacement is based on the individual asset’s rank. The overall strategy dictates the replacement rate. The Circuit Breaker Strategy’s objective is to minimize failures and maximize useful life through an effective maintenance plan and by replacing breakers for which maintenance is either ineffective or uneconomical. The breakers were selected based upon the vintage, unreliable performance for breaker model types, Percentage of F6 gas leakage, high fault duty, and the critical nature of Gold Hill substation. Gold Hill Substation is located at HFTD zone 1. | Substation - Circuit Breaker | Replace | NA | T.0004920 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 62 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 12.8702 | NA | 115 kV | NA | NA | NA | 5.11 | IGP | 5801228 | T.0006348 | Gold Hill: Repl 115kV CB 142, 172 | 2 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-05-13 | 2025-05-30 | 2025-12-06 | Clearances | NA | TRUE | 6400 | NA ¦ NA | 2853.3962 | 2940.6785 | 0 | 65.8871 | 269.5487 | 1946.1443 | 559.9411 | 99.1573 | 0 | 0 | 0 | 0 | 2841.5212 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 2594.0859 | 10.732 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1155 | CEM breakers - purchase four 115kV CBs + |  |  | NA | This project will procure four (4) 115kV and two (2) 230kV circuit breakers (CBs) to increase Capitalized Emergency Material (CEM) inventory. PG&E maintains a stock of CEMs, which is equipment of long lead time and is kept on hand for emergency replacements. PG&E's Emergency Transmission Substation Replacement Program replaces transmission substation equipment which has failed while in service or is expected to fail in service due to rapidly deteriorating condition. Transmission breakers are among such equipment. The breakers would be taken out of service and replaced under emergency (MWC 65), using breakers from CEM stock. In 2019, an evaluation of the CEM breaker inventory showed a rapid depletion of CEM breakers due to increased number of emergency and just-in-time breaker replacements in recent years-a trend that is anticipated to continue for several years, which would exhaust the CEM breaker inventory. In order to provide emergency support and to improve emergency response time, it is recommended to purchase four 115kV and two 230kV circuit breakers for CEM stock. | Substation - Circuit Breaker | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | 115 kV | NA | NA | NA | 3.0011 | IGP | 5541690 | T.0006374 | CEM breakers - purchase four 115kV CBs + | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2025-09-02 | 2025-08-15 | NA | NA | TRUE | 842 | NA ¦ NA | 1218.2895 | 1218.2895 | 0 | 0 | 4.5947 | 0 | 1156.6984 | 56.9964 | 0 | 0 | 0 | 0 | 1161.2931 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1161.2931 | 56.9964 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1156 | Metcalf: Repl CBs 654,664,674,684 |  |  | Santa Clara | Replace overstressed CB 492, CB 502, & CB 632 at Metcalf 115 kV substation. | Substation - Circuit Breaker | Replace | NA | T.0007467 ¦ T.0007032 ¦ T.0007981 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 28 | Lifecycle Replacement Analysis | Other - Deferral | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 230 kV | NA | NA | NA | 5.2 | IGP | 5796971 | T.0007291 | Metcalf: Replace Overstressed CBs | 3 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-10-01 | 2028-01-28 | 2026-12-21 | NA | NA | TRUE | 24950 | NA ¦ NA | 3282.5907 | 8762.3422 | 31.3983 | 211.1708 | 259.6756 | 121.7546 | 2605.6348 | 3660.9094 | 451.9603 | 527.2097 | 312.244 | 0 | 3229.6341 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1157 | METCALF REPL (interim) |  |  | Santa Clara | Replace overstressed CB 492, CB 502, & CB 632 at Metcalf 115 kV substation. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-05 | 26 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 230 kV | NA | NA | NA | NA | NA | 5798882 | T.0007291 | Metcalf: Replace Overstressed CBs | 3 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-13 | 2028-01-28 | 2022-11-01 | NA | NA | FALSE | 24950 | NA ¦ NA | 425.7844 | 425.7844 | 12.1352 | 407.725 | 5.9242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425.7844 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 419.8602 | -8.431 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1158 | TRINITY: Repl 70 kV CBs 12,22,32 |  |  | Weaverville CDP, Trinity | 2022 Program AA Transmission Circuit Breaker Replacements: This 2022 program proposes to replace transmission circuit breakers at various voltage levels at Cooley, East Nicolaus, Evergreen, Fulton, Melones SW STA, Santa Maria, Smyrna, Trinity, Westwood SW STA, Caribou PH#1, and Herdlyn Substations, to address elevated risk of failure due to age and condition. PG&E’s Transmission Substation Circuit Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria includes: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-05 | 34 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.3227 | NA | 70 kV | NA | NA | NA | 5.11 | IGP | 5799685 | T.0007884 | Trinity - Repl 70kv CB 12, 22, 32 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2032-07-30 | NA | 2032-12-15 | NA | NA | FALSE | NA | NA ¦ NA | 58.6702 | 2884.4239 | 0 | 49.9689 | 6.6899 | 2.0114 | 0 | 3.7041 | 0 | 0 | 0 | 0 | 58.6702 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1159 | WESTWOOD SW STA: Replace CBs 22, 52 |  |  | Westwood CDP, Lassen | 2022 Program AA Transmission Circuit Breaker Replacements: This 2022 program proposes to replace transmission circuit breakers at various voltage levels at Cooley, East Nicolaus, Evergreen, Fulton, Melones SW STA, Santa Maria, Smyrna, Trinity, Westwood SW STA, Caribou PH#1, and Herdlyn Substations, to address elevated risk of failure due to age and condition. PG&E’s Transmission Substation Circuit Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria includes: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-09 | 42 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 0.47411 | NA | 60 kV | NA | NA | NA | 5.11 | IGP | 5799687 | T.0007886 | Westwood - Replace CB 22 & 52 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2032-07-30 | NA | 2032-12-15 | NA | NA | FALSE | NA | NA ¦ NA | 43.2524 | 2203.4682 | 0 | 35.9962 | 5.4372 | 1.819 | 0 | 2.7307 | 0 | 0 | 0 | 0 | 43.2524 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1160 | CARIBOU PH #1: Repl CB 22,42, 62,92,122 |  |  | Plumas | 2022 Program AA Transmission Circuit Breaker Replacements: This 2022 program proposes to replace transmission circuit breakers at various voltage levels at Cooley, East Nicolaus, Evergreen, Fulton, Melones SW STA, Santa Maria, Smyrna, Trinity, Westwood SW STA, Caribou PH#1, and Herdlyn Substations, to address elevated risk of failure due to age and condition. PG&E’s Transmission Substation Circuit Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria includes: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. | Substation - Circuit Breaker | Replace | NA | T.0010888 ¦ EX112246 ¦ T.0003628 ¦ T.0007507 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-02-10 | 37 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 0.96252 | NA | 115 ¦ 60 kV | NA | NA | NA | 5.11 | IGP | 5799688 | T.0007887 | Caribou - Repl CB 22, 42, 62, 92, 122 | 1 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2032-07-30 | NA | 2032-12-15 | NA | NA | FALSE | NA | NA ¦ NA | 51.1851 | 4836.4165 | 0 | 41.5276 | 7.5215 | 2.136 | 0 | 3.2315 | 0 | 0 | 0 | 0 | 51.1851 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1161 | Los Banos: Replace 70 kV_ 5 CBs |  |  | Merced | This planned project will replace Los Banos CBs 12, 22, 32, 52, and 92 with new 70 kV CBs. This project is needed to support the Gonzaga Wind Farm Generation Interconnection project (Q1378). The Gonzaga Wind project will add a new bay with (2) Breakers and a new control enclosure to Los Banos substation. This project will also convert the 70 kV Main & Aux to Double Bus Single Breaker (DBSB). This breaker replacement funded under MWC 64 will replace the five additional 70kV CBs at Los Banos. | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-06 | 58 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 70 kV | NA | NA | NA | 5.11 | IGP | 5799749 | T.0007906 | Los Banos_Replace 70 kV_ 5 CBs | 2 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-07-03 | 2025-02-01 | 2025-01-17 | NA | NA | TRUE | 3750.908 | NA ¦ NA | 2483.3391 | 2983.3391 | 0 | 156.2183 | 175.4163 | 1037.2837 | 1071.8442 | 42.5766 | 500 | 0 | 0 | 0 | 2440.7625 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 2028.0482 | 170.0539 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1162 | LOS BANOS: REPLACE 70 KV_ 5 CBS PH2 |  |  | Merced | This planned project will replace Los Banos CBs 12, 22, 32, 52, and 92 with new 70 kV CBs. This project is needed to support the Gonzaga Wind Farm Generation Interconnection project (Q1378). The Gonzaga Wind project will add a new bay with (2) Breakers and a new control enclosure to Los Banos substation. This project will also convert the 70 kV Main & Aux to Double Bus Single Breaker (DBSB). This breaker replacement funded under MWC 64 will replace the five additional 70kV CBs at Los Banos. | Substation - Circuit Breaker | Replace | NA | T.0003548 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-06 | 59 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 53.2803 | NA | 70 kV | NA | NA | NA | 3.0011 | IGP | 5815938 | T.0007906 | Los Banos_Replace 70 kV_ 5 CBs | 2 | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-07-01 | 2025-02-01 | 2025-11-24 | Project Design | NA | TRUE | 3750.908 | NA ¦ NA | 978.3299 | 978.3299 | 0 | 0 | 0 | 0 | 420.2325 | 558.0975 | 0 | 0 | 0 | 0 | 420.2324 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 420.2325 | 420.7928 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1163 | Tesla: Replace CB 612 |  |  | Alameda | Overstressed Breaker replacement. Tesla Replace 500 kV breakers | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-19 | 37 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 500 kV | NA | NA | NA | 3.0011 | IGP | EX139133 | TBD | TBD | TBD | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-12-01 | NA | 2028-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1150 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 450 | 700 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1164 | Oakland D: Replace CB 162, 172 |  |  | Oakland, Alameda | Replace aging/deteriorated Oakland D C B162/172 | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-16 | 63 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.54348 | NA | 115 kV | NA | NA | NA | 3.0011 | IGP | EX139158 | TBD | TBD | TBD | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-02-01 | NA | 2028-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 500 | 1000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1165 | Tesla: Uprate CB 622, 632 |  |  | Alameda | Overstressed T-Breakers, Uprating OS breakers at Tesla substation | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-19 | 33 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 500 kV | NA | NA | NA | 3.0011 | IGP | EX139155 | TBD | TBD | TBD | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-02-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 500 | 500 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1166 | Tesla: Rep CB 112 |  |  | Alameda | Replace aging/deteriorated Tesla CB 112 | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-19 | 38 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 115 kV | NA | NA | NA | 3.0011 | IGP | EX139154 | TBD | TBD | TBD | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-03-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 500 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1167 | Pittsburg: Replace 15-230 kV OS breakers |  |  | Pittsburg, Contra Costa | Overstressed T-Breakers Replacement, Pittsburg 230 kV breakers | Substation - Circuit Breaker | Replace | NA | T.0010880 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-06 | 34 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.72358 | NA | 230 kV | NA | NA | NA | 3.0011 | IGP | EX139157 | TBD | TBD | TBD | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 22799.999 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 500 | 0 | 7433.333 | 7433.333 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1168 | Mesa 132, 142 115 kV |  |  | Nipomo CDP, San Luis Obispo | Replace aging/deteriorated Mesa CB 132/142 | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-09 | 60 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.5414 | NA | 115 kV | NA | NA | NA | 3.0011 | IGP | EX113759 | TBD | TBD | TBD | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1600 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 250 | 300 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1169 | Brighton 112, 132, 152 |  |  | Sacramento, Sacramento | Replace aging/deteriorated Brighton CB 112/132/152 | Substation - Circuit Breaker | Replace | NA | T.0010289 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-03 | 58 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.4413 | NA | 115 kV | NA | NA | NA | 3.0011 | IGP | EX113764 | TBD | TBD | TBD | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1800 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 900 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1170 | Manteca 114, 124,174, 134, 144, 154, 164, 194 115 kV breakers |  |  | Manteca, San Joaquin | Replace aging/deteriorated Manteca CB 114, 124,174, 134, 144, 154, 164, 194 | Substation - Circuit Breaker | Replace | NA | T.0010898 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | 2026-03-14 | 64 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.8539 | NA | 115 kV | NA | NA | NA | 5.1001 | IGP | EX113762 | TBD | TBD | TBD | 64 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | NA | 2034-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2600 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 600 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1171 | CEM Forecast failure 2025, 3 Phase, 500/230kV, 374 MVA, 2 tanks |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113709 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 7000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1172 | CEM Forecast failure 2025, 3 Phase, 230/115kV, 420 MVA |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113710 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 7000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1173 | CEM Forecast failure 2025, 3 Phase, 230/(60x70)kV, 200 MVA |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 70 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113711 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 7000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1174 | CEM Forecast failure 2027, 3 Phase, 500/230kV, 374 MVA, 2 tanks |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113713 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 7000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1175 | CEM Forecast failure 2027, 3 Phase, 230/115kV, 420 MVA |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113714 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 7000 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1176 | CEM Forecast failure 2027, 3 Phase, 230/(60x70)kV, 200 MVA |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 70 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113715 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 7000 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1177 | CEM Forecast failure 2027, 3 Phase, 115/(60x70)kV, 200 MVA |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 115 ¦ 70 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113716 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 7000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1178 | CEM Forecast failure 2026, 3 Phase, 500/230kV, 374 MVA, 2 tanks |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113768 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 7000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1179 | CEM Forecast failure 2026, 3 Phase, 230/115kV, 420 MVA |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113769 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 7000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1180 | CEM Forecast failure 2026, 3 Phase, 115/(60x70)kV, 200 MVA |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 115 ¦ 70 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113770 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 7000 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1181 | CEM Forecast failure 2026, 3 Phase, 230/(60x70)kV, 200 MVA |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 70 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | EX113774 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 7000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1182 | CEM Forecast failure 2029 3 Phase, 500/230kV, 374 MVA, 2 tanks |  |  | NA | Forecast placeholder for 2029 CEM 500/230 kV 3 phase transformers | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX114013 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 7000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1183 | Emergency Transmission Xfmr non-500kV Banks Replacement |  |  | NA | Forecast placeholder for emergnecy tranmission non-500 kV transformer replacements | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 ¦ 70 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | EX139130 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 177840.7148 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 25855.5439 | 37561.9092 | 34927.5006 | 39777.6928 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1184 | CEM 500/230kV, 374 MVA, 1PH T-500-230-01 |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX139159 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 7000 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1185 | CEM 500/230kV, 374 MVA, 1PH T-500-230-03 |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX139160 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 7000 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1186 | CEM 500/230kV, 374 MVA, 1PH T-500-230-02 |  |  | NA | Transmission Transformer CEM inventory will meet compliance requirements and will maintain system reliability, with limited impact to major emergency replacement projects. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX139161 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 7000 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1187 | Emergency Transmission Xfmr 500kV Banks Replacement |  |  | NA | Forecast placeholder for emergnecy tranmission 500 kV transformer replacements | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | EX139162 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 76200 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 15600 | 14700 | 15600 | 15600 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1188 | KASSON: EM Replace BK 1 |  |  | San Joaquin | Due to the aThis project proposes to replace the deteriorated 115/60kV Transformer Bank 1, 60kV three-phase regulator, and associated equipment at Kasson Substation. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-31 | 58 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.1988 | NA | 115 ¦ 60 kV | 638 | 3. Emergency Preparedness | NA | NA | Non-IGP | 5773301 | T.0002471 | Kasson: EM Replace Bank 1 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-05-01 | 2019-08-05 | 2019-05-17 | NA | NA | FALSE | 6944 | NA ¦ NA | 9735.4988 | 9735.4988 | 72.4066 | 5.6129 | 11.2134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9735.4988 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 69.7361 | 5.4059 | 10.5926 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1189 | HENRIETTA: EM Replace BK 2 |  |  | Kings | Emergency replacement of Henrietta Bank 2 with one three-phase, 230/70 kV 200 MVA transformer. This emergency project is needed to maintain safe and reliable power to electric customers served on the Henrietta local 70kV transmission system and provide the following benefits: • Revenue lost during unplanned outages was not included in the economic evaluation. • Decrease in annual recurring maintenance costs by replacing a deteriorating transformer with newer equipment. • Reduction is the number of aging transformer banks and regulators that have reached the end of their life cycle. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-06 | 62 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 7.0079 | NA | 230 ¦ 70 kV | 638 | NA | NA | NA | Non-IGP | 5778968 | T.0003731 | HENRIETTA TXFR BK2 RPLC EMER | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-01-18 | 2018-06-01 | 2018-06-01 | NA | NA | FALSE | 6726 | NA ¦ NA | 7999.7299 | 7999.7299 | 3554.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7999.7299 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 4894.3934 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1190 | IGNACIO: EM REP BK 1 |  |  | Novato, Marin | This project will replace the Ignacio Substation Bank 1 with a 200MVA, 115/60kV LTC transformer.. This bank is expected to fail while in service, therefore, it is being replaced as an emergency project. The costs are based on an AACE Class 4 estimate. The funding authorization will support design, procurement and construction. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-05 | 14 | NA | Wires - Minimum Required Scope (spot repair) Alternative | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 11.9486 | NA | 115 ¦ 60 kV | NA | 3. Emergency Preparedness | 5 | NA | Non-IGP | 5786429 | T.0004883 | IGNACIO: EM REP BK 1 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-01-21 | 2020-01-28 | 2020-04-20 | NA | NA | FALSE | 6800 | NA ¦ NA | 5867.1233 | 5867.1233 | 1854.8941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5867.1233 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 1562.3149 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1191 | Vaca Dixon: Replace Bank 2 and 2A |  |  | Solano | Replace transmission bank 2/2A to one three-phase, 230/115 kV, 420 MVA, transformer bank with LTC at Vaca Dixon Substation. Due to concerns with the deteriorated transformer Westinghouse type, history of oil leaks, SAM recommends expediting the replacement of Vaca Dixon Bank 2/2A on emergency. The recommendation to expedite the bank under emergency had the review and concurrence of Substation Maintenance, Equipment Specialist, and Asset Strategy. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-25 | 71 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 ¦ 115 kV | NA | 3. Emergency Preparedness | 4 | 5.1001 | Non-IGP | 5788181 | T.0005466 | Vaca Dixon - Replace Bank 2 & 2A | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-06-16 | 2021-06-03 | 2021-12-17 | Clearances | NA | FALSE | 11850 | NA ¦ NA | 12352.9635 | 12352.9635 | 8621.3037 | 174.5732 | 0.9319 | 25.6128 | 239.7596 | 15.9059 | 0 | 0 | 0 | 0 | 12337.0576 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 11502.5788 | 168.5381 | 0.89968 | 24.7274 | -542.3409 | 14.3153 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1192 | Kerman: SW41 Tline work |  |  | Fresno | Install 1200AMPS center side break (V Type) switches for 41, 43 and 45 on existing northern structure at Kerman sub | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-17 | 77 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.2852 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5555920 | T.0005924 | KERMAN:REP EM SW 41 | 2 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-02-18 | NA | 2025-02-28 | NA | NA | TRUE | NA | NA ¦ NA | 348.6965 | 348.8775 | 0 | 0 | 0 | 221.6763 | 126.0218 | 1.1793 | 0 | 0 | 0 | 0 | 347.6981 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 312.9283 | 0.89859 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1193 | Rio Oso: Replace Bank 1 Project |  |  | Sutter | In late December 2020, Rio Oso 230/115 kV Bank 1 A Phase saw an internal fault and failed. Install 3 single phase mobile transformers rated at 40MVA each to replace Transformer Bank 1 at Rio Oso until the new 3 phase 420mva transformer is installed. Current plan is 12/23. The Mobiles do not have an emergency rating (same as normal rating). In addition during this period, Bank 2 will be limited to normal rating of 134.4 MVA three phase. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-04 | 70 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 9.3219 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5794995 | T.0006954 | Rio Oso: EM Repl Bank 1 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-07-05 | NA | 2024-12-06 | NA | NA | TRUE | 2000 | NA ¦ NA | 38112.1622 | 38311.9979 | 19855.5313 | 8717.3048 | 3798.7523 | 4312.2664 | 985.4242 | 634.1617 | 0 | 0 | 0 | 0 | 37677.8362 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 36692.412 | 985.4242 | 434.326 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1194 | PALERMO: JIT REPL BK 1 w/ 2 BANKS |  |  | Palermo CDP, Butte | 230/115x60kV Bank 1 has developed a leak and will be replaced on JIT Emergency project. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-13 | 58 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 8.0464 | NA | 230 ¦ 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5796018 | T.0007127 | Palermo: Em Repl Bk 1 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-07-15 | 2023-05-25 | 2023-05-25 | NA | NA | TRUE | 28100 | NA ¦ NA | 27573.9675 | 27579.9364 | 3954.5664 | 14472.4221 | 9112.2772 | 24.6995 | 9.8908 | 6.0804 | 0 | 0 | 0 | 0 | 27573.856 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 27539.2657 | 24.6995 | -2608.3745 | 0.10039 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1195 | Metcalf: Repl Bk 11B & 11C |  |  | Santa Clara | Emergency replacement of failed Bk 11B & 11C at Metcalf substation; | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-05 | 58 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5806639 | T.0009586 | Metcalf: EM Repl Bk 11B & 11C 74056286 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-02-15 | NA | 2028-05-01 | NA | NA | FALSE | 25000 | NA ¦ NA | 1642.765 | 21447.3384 | 0 | 0 | 122.343 | 1297.5855 | 165.5075 | 574.9989 | 0 | 0 | 0 | 0 | 1585.436 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1196 | Midway: Replace Bk 13 Spare Phase |  |  | Buttonwillow CDP, Kern | Emergency replacement of Miday Bank 13 spare transformer. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-03 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5807277 | T.0009605 | Midway: Replace Bk 13 Spare Phase | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-11-13 | NA | 2024-03-12 | NA | NA | TRUE | 9468 | NA ¦ NA | 2874.397 | 2943.3954 | 0 | 0 | 681.2392 | 2002.7232 | 174.3274 | 85.1055 | 0 | 0 | 0 | 0 | 2858.2899 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 2683.9625 | 174.3274 | 16.1071 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1197 | Helm:Replace Bank 1 |  |  | Fresno | Emergency replacement of failed Helm 230/70 kV Bank 1 | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-10 | 59 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 6.7555 | NA | 230 ¦ 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5808685 | T.0009930 | HELM: TXFR BK1 REP ETS51 | 1 | 65 | NA ¦ 5769943 ¦ T.0001589 ¦ 68 | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-22 | NA | 2024-04-12 | NA | NA | TRUE | 3676 | NA ¦ NA | 7685.4974 | 11832.1479 | 0 | 0 | 0 | 3717.4562 | 3962.2798 | 4152.4119 | 0 | 0 | 0 | 0 | 7679.736 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 3717.4562 | 3962.2798 | 5.7614 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1198 | Cottonwood EM Replace BK1 230/115KV |  |  | Cottonwood CDP, Shasta | Replace exisitng failed Cottonwood Transformer Bank 1 with one new 3 PH, 420MVA, 230/120/13.2kV transformer with LTC. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-19 | 66 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 26.1945 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5809680 | T.0010126 | Cottonwood: EM Replace BK1 230/115KV | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-04-22 | NA | 2024-08-03 | NA | NA | TRUE | NA | NA ¦ NA | 10667.101 | 14235.4379 | 0 | 0 | 0 | 3762.6055 | 5175.6911 | 5297.1414 | 0 | 0 | 0 | 0 | 8938.2965 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 3762.6055 | 5175.6911 | 1728.8045 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1199 | Gold Hill: EM Repl BK 5 |  |  | Folsom, Sacramento | This project proposes to replace the deteriorated Gold Hill Transformer # 5 (three (3) single phase, 115/60 kV, 26.6 MVA, General Electric vintage 1951 autotransformers) with four (4), single-phase, 30 MVA, 115/60 kV transformers to make this a firm autotransformer installation | Substation - Transformer | Replace | NA | T.0004950 | Emergency Event | Replace Transformer | NA | NA | 2026-03-05 | 75 | NA | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 12.8702 | NA | 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811847 | T.0010612 | GOLD HILL: EM REPLACE BANK 5 | 2 | 65 | NA ¦ 5786799 ¦ T.0000952 ¦ 68 | TRUE | 2021 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-01-28 | 2023-12-01 | 2026-04-10 | Bundling Dependencies | NA | TRUE | 15000 | NA ¦ NA | 16253.8606 | 17524.6477 | 0 | 0 | 0 | 9491.5663 | 5814.7356 | 2218.3459 | 0 | 0 | 0 | 0 | 15306.3018 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1200 | HOPLAND: EM REPLACE BANK 2 |  |  | Mendocino | This project will replace the 115/60kV Bank 2 at Hopland Substation with a new three-phase, 100MVA, 115/60kV transformer bank with load tap-changer (LTC) | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-02-13 | 74 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.63377 | NA | 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813825 | T.0010865 | HOPLAND: EM REPLACE BANK 2 | 1 | 65 | NA ¦ 5748000 ¦ T.0000830 ¦ 68 | TRUE | 2016 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-08-05 | 2018-08-14 | 2027-03-08 | Clearances | Prioritization | TRUE | 4575 | NA ¦ NA | 874.8982 | 2471.3432 | 0 | 0 | 0 | 0 | 716.5437 | 1409.1729 | 239.7394 | 0 | 0 | 0 | 716.5437 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1201 | Caribou PH#2 EM Replace Bk 11 |  |  | Plumas | Emergency Replacement of the Caribou PH 2 230/115/60kV Bank 11. | Substation - Transformer | Replace | NA | T.0007887 ¦ EX112246 ¦ T.0003628 ¦ T.0007507 | Emergency Event | Replace Transformer | NA | NA | 2026-03-02 | 51 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 2.2068 | NA | 230 ¦ 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813830 | T.0010888 | Caribou PH: Em Repl BK 11 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2030-11-18 | NA | 2031-08-11 | NA | NA | FALSE | NA | NA ¦ NA | 282.3486 | 28898.4005 | 0 | 0 | 0 | 0 | 230.0857 | 371.1064 | 0 | 0 | 0 | 0 | 230.0857 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1202 | Taft: Replace Bank 2 |  |  | Taft, Kern | Replacement of the failed 115/70kV Transformer Bank #2 at Taft Substation. Taft Substation is located in the vicinity of the City of Taft, within Kern County, California. Bank #2 is comprised of three single-phase 1955-vintage 20 MVA 115/70 kV Westinghouse transformers. | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-02 | 71 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 5.2046 | NA | 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815000 | T.0011207 | TAFT: Replace Bank 2 | 1 | 65 | NA ¦ 5777284 ¦ T.0003469 ¦ 68 | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-10-11 | NA | 2028-02-22 | NA | NA | TRUE | NA | NA ¦ NA | 122.1985 | 6574.4948 | 0 | 0 | 0 | 0 | 96.0493 | 4321.5991 | 0 | 0 | 0 | 0 | 96.0493 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1203 | Moss Landing: Repl Bk 9 |  |  | Monterey | Emergency Replacement of Moss Landing substation Transformer Bank #9 | Substation - Transformer | Replace | NA | NA | Emergency Event | Replace Transformer | NA | NA | 2026-03-10 | 48 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 41.3213 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815753 | T.0011404 | MOSS LANDING PP :EM RPL BK9 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-09-22 | NA | 2028-02-09 | NA | NA | FALSE | NA | NA ¦ NA | 168.3775 | 7116.5356 | 0 | 0 | 0 | 0 | 63.3513 | 2572.7251 | 0 | 0 | 0 | 0 | 63.3514 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | NA
1204 | EL DORADO PH: EM Replace CB 320 |  |  | El Dorado | This is a Just-in-time emergency replacement of 115kV CB 320. The breaker has had several issues and repairs over the years and the unit has been deemed too expensive to maintain. Substation Asset Management has concurred with the emergency replacement of the breaker, which remains in service and is being monitored by Maintenance. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-04 | 31 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.43336 | NA | 115 kV | NA | 3. Emergency Preparedness | NA | NA | Non-IGP | 5528580 | T.0003614 | El Dorado PH: Em Replace CB 320 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-11-04 | 2019-12-20 | 2019-12-20 | NA | NA | FALSE | 1654 | NA ¦ NA | 1682.5038 | 1682.5038 | 74.5299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1682.5038 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 69.5302 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1205 | Moraga Sub-EM Replace Reg 3 |  |  | Orinda, Contra Costa | Emergency Replacement of 115kV Bank #3 Regulator at Moraga sub | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | 19 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 15.8714 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5796162 | T.0007197 | Moraga Bank #3 Regulator | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-09-19 | 2024-01-12 | 2024-01-12 | NA | NA | FALSE | 5830.71 | NA ¦ NA | 5817.5844 | 5817.5844 | 71.5321 | 871.6504 | 4791.0436 | 72.3157 | 11.0427 | 0 | 0 | 0 | 0 | 0 | 5817.5844 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 5254.7731 | 9.9383 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1206 | MIDWAY: EM REG 11A-C/B-C PCB |  |  | Buttonwillow CDP, Kern | Emergency replacement of Midway Bank 11 regulator | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | 23 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5545527 | T.0007263 | MIDWAY: EM REG 11A-C/B-C PCB | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-12 | NA | 2026-06-24 | NA | NA | TRUE | NA | NA ¦ NA | 1039.8026 | 1041.2259 | 28.9273 | 171.2415 | 276.4914 | -47.4962 | 605.9751 | 6.0868 | 0 | 0 | 0 | 0 | 1035.1392 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 28.5082 | 168.7602 | 272.485 | -46.808 | 597.1944 | 4.5959 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1207 | Purchase CEM breakers for anticipated failures |  |  | NA | Increase CEM inventory for anticipated failures, 56 breakers in 70 - 500kV, each year in 2027 - 2029 | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | EX113779 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 25000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 8600 | 9500 | 6900 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1208 | Emergency Transmission Circuit Breaker Replacement of Failed and JIT |  |  | NA | Forecast plavceholder for Emergency Transmission Circuit Breaker Replacement of Failed and JIT | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | EX139131 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 89520 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 18960 | 17760 | 18240 | 17280 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1209 | LAKEVILLE: EM Rep CB 232 and SWes |  |  | Sonoma | Replace HVCB 232 and associated SW's. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-13 | 40 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 14.7021 | NA | 230 kV | 638 | 3. Emergency Preparedness | NA | NA | Non-IGP | 5526881 | T.0003355 | LAKEVILLE: EM Replace CB 232 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-04 | 2022-01-13 | 2022-01-13 | NA | NA | FALSE | 2370 | NA ¦ NA | 2347.9913 | 2347.9913 | 1149.9823 | 505.0385 | 35.8353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2347.9913 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1034.9841 | 367.3514 | 30.9005 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1210 | FAMOSO: EM Repl CB 132- 152 |  |  | Kern | Famoso Substation is located in the vicinity of the City of McFarland, within Kern County, California. Circuit breakers 132 and 152 were installed in 1963. These need to be replaced for improved quality and efficiency. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-05 | 61 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.8913 | NA | 115 kV | 638 | 3. Emergency Preparedness | NA | 5.1001 | Non-IGP | 5781324 | T.0004147 | Famoso: Rep EM CB 132_152 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-02-10 | NA | 2024-12-19 | NA | NA | TRUE | 736 | NA ¦ NA | 6323.775 | 6376.9038 | 443.8714 | 616.7108 | 413.9792 | 536.0556 | 641.4473 | 56.4526 | 0 | 0 | 0 | 0 | 6320.4512 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 5796.207 | 2.9625 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1211 | MORRO BAY: EM Repl CB 622 |  |  | Morro Bay, San Luis Obispo | Replacement of 230KV HVCB 622. Existing 50+ year old 230KV OCB 622 to be replaced along with 230kV SW 621. relocated on new foundations. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | 59 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion ¦ Flooding |  | NA | 12.614 | NA | 230 kV | 638 | 3. Emergency Preparedness | NA | NA | Non-IGP | 5532305 | T.0004257 | MORRO BAY EM REP CB 622 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-03-10 | NA | 2020-08-06 | NA | NA | FALSE | NA | NA ¦ NA | 2006.1188 | 2006.1188 | 12.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2006.1188 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 ¦ 2026 | 12.5507 | 0 | 0 | -200.6117 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1212 | WOODWARD: EM Repl CB 122 |  |  | Fresno, Fresno | Emergency replacement of 115 KV HVCB 122 Woodward. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-13 | 32 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.9838 | NA | 115 kV | NA | 3. Emergency Preparedness | NA | NA | Non-IGP | 5531795 | T.0004262 | WOODWARD: REPL CB 122 (JIT) | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-11-04 | 2020-12-17 | 2020-12-17 | NA | NA | FALSE | 1253 | NA ¦ NA | 1263.2091 | 1263.2091 | 329.9357 | 3.975 | 0 | 10.4627 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.2091 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 ¦ 2026 | 281.6908 | 11.6348 | 0 | 59.0839 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1213 | SARATOGA: EM REP: CB232 230KV 74020947 |  |  | Saratoga, Santa Clara | This project proposes to replace CB 232, Air Switch 233, and supporting equipment. Saratoga Bank 1 failed in May of 2018 due to corrosive sulfur corrosion. The transformer is being replaced under emergency order 74019563. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-04 | 34 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.4212 | NA | 230 kV | 638 | 3. Emergency Preparedness | NA | NA | Non-IGP | 5783358 | T.0004264 | SARATOGA: EM REP: CB232 230KV | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-01-27 | 2020-08-31 | 2020-06-24 | NA | NA | FALSE | 4900 | NA ¦ NA | 2349.4057 | 2349.4057 | -12.5088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2349.4057 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -11.4848 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1214 | EM CLAYTON SUB - REPL. CB 112 |  |  | Concord, Contra Costa | Emergency replacement of circuit breakers at EM Clayton Sub. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-05 | 48 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.9731 | NA | 115 kV | NA | 3. Emergency Preparedness | NA | NA | Non-IGP | 5532804 | T.0004363 | Clayton Sub CB 112 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-10-30 | 2020-12-07 | 2020-12-07 | NA | NA | FALSE | 2150 | NA ¦ NA | 2134.1988 | 2134.1988 | 158.9284 | 43.9252 | 4.4658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2134.1988 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 6.7085 | 40.7196 | -175.1107 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1215 | ROSSMOOR INSTALL 230KV BUS TIE BREAKER |  |  | Walnut Creek, Contra Costa | Phase 1 of the project was to replace Rossmoor failed transformer 2 under emergency conditions to have in service by 9/11/2019. Phase 2 of this project is to remove the temp transformer protection and replace with the final SMP design. The project will also add a 230kV Bus Sectionalizing Circuit Breaker for increased reliability and operational flexibility that is much needed in the sensitive Rossmoor/Lafayette area | Substation - Circuit Breaker | New | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.0542 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804086 | T.0004810 | Rossmoor: EM Replace Bank 2 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-03 | NA | 2026-10-26 | NA | NA | TRUE | 2152 | NA ¦ NA | 868.7792 | 2718.3938 | 0 | 0 | 24.2681 | 218.4997 | 601.875 | 1792.1435 | 81.6074 | 0 | 0 | 0 | 844.6428 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1216 | BRIDGEVILLE INSTALL SYNC PANEL |  |  | Humboldt | Replace 115kV Oil Circuit Breakers with new SF6 Circuit Breakers for breaker 172, 182, and 112, relocate circuit breaker 102, replace switches 111, 113, 115, 181, 183, 185, add new switches 175 & 101, add new 115kV line CCVTs, add new 115kV wave trap and CCVT with carrier accessories. 112, relocate circuit breaker 102, replace switches 111, 113, 115, 181, 183, 185, add new switches 175 & 101, add new 115kV line CCVTs, add new 115kV wave trap and CCVT with carrier accessories. Humboldt Substation. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-02 | 62 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.569 | NA | 115 kV | NA | 3. Emergency Preparedness | NA | NA | Non-IGP | 5539731 | T.0005831 | Humboldt - EM Replace CB 102,112,172,182 | 4 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-06-15 | 2023-07-10 | 2020-06-29 | NA | NA | FALSE | 6791 | NA ¦ NA | 134.3635 | 134.3635 | 5.0965 | 0.891 | 0 | -2.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 134.3635 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 ¦ 2026 | -14.8172 | 0.76008 | 0 | 4.508 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1217 | HUMBOLDT - EM REPL CB 112, 172, 182, 201 |  |  | Humboldt | Replace 115kV Oil Circuit Breakers with new SF6 Circuit Breakers for breaker 172, 182, and 112, relocate circuit breaker 102, replace switches 111, 113, 115, 181, 183, 185, add new switches 175 & 101, add new 115kV line CCVTs, add new 115kV wave trap and CCVT with carrier accessories. 112, relocate circuit breaker 102, replace switches 111, 113, 115, 181, 183, 185, add new switches 175 & 101, add new 115kV line CCVTs, add new 115kV wave trap and CCVT with carrier accessories. Humboldt Substation. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-02 | 62 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.569 | NA | 115 kV | NA | 3. Emergency Preparedness | NA | NA | Non-IGP | 5791020 | T.0005831 | Humboldt - EM Replace CB 102,112,172,182 | 4 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-04 | 2023-07-10 | 2023-07-10 | NA | NA | FALSE | 6791 | NA ¦ NA | 5044.4879 | 5044.4879 | 1237.0789 | 2504.3902 | 744.2222 | -22.56 | 0 | 0 | 0 | 0 | 0 | 0 | 5044.4879 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 5067.0478 | -477.0454 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1218 | Kerman: REP EM SW 41 |  |  | Fresno | Install 1200AMPS center side break (V Type) switches for 41, 43 and 45 on existing northern structure at Kerman sub | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-17 | 77 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.2852 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5540141 | T.0005924 | KERMAN:REP EM SW 41 | 2 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-03-03 | NA | 2025-03-12 | NA | NA | TRUE | NA | NA ¦ NA | 1122.2142 | 1122.2142 | 7.0544 | 116.0787 | 4.8268 | 426.9051 | 535.9662 | 0.0224 | 0 | 0 | 0 | 0 | 1122.1918 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 38.4149 | 116.0787 | 4.8268 | 426.9051 | 423.7471 | 0.02013 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1219 | METCALF: EM REPLACE CB 694 |  |  | Santa Clara | Replace 230kV Cap Bank Step 5 High Voltage Circuit Breaker 694. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-05 | 24 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 230 kV | NA | NA | NA | NA | Non-IGP | 5540301 | T.0005958 | METCALF: EM Replace CB 694 74033781 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-01-04 | 2021-10-01 | 2021-10-15 | NA | NA | FALSE | 1490 | NA ¦ NA | 1447.2547 | 1447.2547 | 1194.8846 | 5.8654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1447.2547 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1075.3965 | -65.7141 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1220 | Newark: Replace CB 994 |  |  | Fremont, Alameda | Emergency replacement of 230kV CB 974 & 994 at Newark Sub | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 27.7611 | NA | 230 kV | NA | NA | NA | NA | Non-IGP | 5540555 | T.0006049 | NEWARK: REPL CAP BREAKER 994 EMER | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-04 | NA | 2021-07-20 | NA | NA | FALSE | NA | NA ¦ NA | 1362.5843 | 1362.5843 | 1026.7653 | 57.9305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1362.5843 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1304.6537 | -17.6425 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1221 | MILPITAS: EM Replace CB 342 115KV |  |  | Milpitas, Santa Clara | Replace existing failed CB342 with new breaker from CEM Stock, If breaker is equipped with dual trip coils, Jumper Trip Coils 1 and 2 at the breaker cabinet. The cap bank breaker 694 tripped due to internal fault on C phase. Since step 2 cap bank breaker 664 already failed, it is important to replace 694 immediately as two of the five steps are currently out of service. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-02 | 30 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.3452 | NA | 115 kV | NA | NA | NA | NA | Non-IGP | 5792842 | T.0006430 | MILPITAS EM Replace CB 342 74035988 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-11-09 | 2021-10-22 | 2022-01-13 | NA | NA | FALSE | 1321 | NA ¦ NA | 1306.6932 | 1306.6932 | 279.0253 | 30.781 | 3.0005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1306.6932 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 1135.9014 | 2.5877 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1222 | Gold Hill: Replace CB 202 Project |  |  | Folsom, Sacramento | On 12/10/2020, during switching for new Gold Hill CB 242 Test Program, the Gold Hill 230kV Bus-Tie CB 202 failed and was determined irrepairable after an immediate investigation. Substation Asset Implementation concurred to the emergency replacement of the failed circuit breaker on 12/14/2020. After performing the walkdown meeting, it was determined that the breaker foundation should be replaced due to age and that 2 sets of CCVT's would need to be installed for 230kV Bus 1 & 2 since the existing bus PT's were internal to the failed CB 202. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-05 | 56 | NA | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 12.8702 | NA | 230 kV | NA | NA | NA | NA | Non-IGP | 5794387 | T.0006912 | Gold Hill: Em Replace CB 202 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-01-06 | 2021-03-31 | 2021-03-31 | NA | NA | FALSE | 1380 | NA ¦ NA | 1398.5308 | 1398.5308 | 1278.4557 | 0.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1398.5308 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1322.4145 | 0.07114 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1223 | Kern PP: Emerg Repl CB 112 |  |  | Bakersfield, Kern | Emergency replacement of failed Kern PP 115 kV CB 112 | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-04 | 59 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 37.7504 | NA | 115 kV | NA | NA | NA | NA | Non-IGP | 5543274 | T.0006913 | KERN PP: EM CB 112 FAIL | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-08 | 2021-04-30 | 2021-05-10 | NA | NA | FALSE | 912 | NA ¦ NA | 1070.2221 | 1070.2221 | 1016.3154 | 46.0845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070.2221 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 ¦ 2026 | 950.6198 | -46.0403 | 58.6204 | 0 | -7e-05 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1224 | Morro Bay: Emerg Repl CB 532 |  |  | Morro Bay, San Luis Obispo | Emergency replacement of Morro Bay 230 kV CB 532 (Diablo 230 kV line) due to a SF6 leak. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | 61 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion ¦ Flooding |  | NA | 12.614 | NA | 230 kV | NA | NA | NA | NA | Non-IGP | 5543273 | T.0006917 | MORRO BAY: EM REP CB 532 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-01 | 2021-12-07 | 2021-12-06 | NA | NA | FALSE | 1280.6957 | NA ¦ NA | 1280.6957 | 1280.6957 | 1175.7949 | 103.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1280.6957 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1058.2155 | 93.1936 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1225 | Lakeville: EM REPL CB262 |  |  | Sonoma | Emergency replacement of CB 222 and 262 at Lakeville substation. Both circuit breaker failed service testing and deemed unable to place back into service due to the possibility of catastrophic failure. CB 222 needed to be put into service first, followed by CB 262. CB 222 foundation was reused but new beam was used to support the new breaker, 2 CCVT foundations were placed on the high side for 3 phase line potential and a new bus transfer switch was installed inside the 230kv MPAC building. For CB 262, new foundation was installed for the new breaker, 2 new CCVT foundation on the line side and a bus potential was installed inside the 230kv MPAC building. Existing wires were used for both breakers. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-13 | 39 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 14.7021 | NA | 230 kV | NA | NA | NA | NA | Non-IGP | 5545284 | T.0007237 | Lakeville: Repl CB 222 and 262 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-05-03 | 2021-07-12 | 2021-05-17 | NA | NA | FALSE | 1403 | NA ¦ NA | 1381.2497 | 1381.2497 | 1351.9651 | 29.2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1381.2497 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1216.7684 | -6.5025 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $1 Mil - $2 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1226 | Oakland L: Replace CB322 & CB422 |  |  | Oakland, Alameda | Emergency replacement failed 115 kV oil HVCB 322 and 422 at Oakland L sub. Install 3 CCVTs and pull all new control cables. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-05 | 82 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 1.197 | NA | 115 kV | NA | NA | NA | NA | Non-IGP | 5796720 | T.0007256 | Oak L: EM Repl CB322 & CB422 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-28 | 2021-06-15 | 2021-06-24 | NA | NA | FALSE | 1827 | NA ¦ NA | 1791.0014 | 1791.0014 | 1762.7601 | 28.2413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1791.0014 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1762.76 | -92.2891 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1227 | Famoso: Emerg Repl CB 22 |  |  | Kern | Based on the ageing factor, non-standard wooden pole installations & maintenance challenges, replace existing CB 22 and associated switches, structures and PT's with a new CB 22, switches & PT's to match standards. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-05 | 63 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.8913 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5545884 | T.0007371 | FAMOSO: EM REPL CB 22 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-12-01 | NA | 2023-02-06 | NA | NA | TRUE | NA | NA ¦ NA | 1792.5694 | 1825.569 | 74.7791 | 1117.2302 | 367.3786 | 33.1311 | 200.0504 | 32.9996 | 0 | 0 | 0 | 0 | 1792.5694 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 37.3896 | 558.6142 | 183.6892 | 16.5652 | 100.0248 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1228 | JEFFERSON SUB: EM REPL CB2612 & CB2712 |  |  | San Mateo | Emergency replacement of Jefferson 230 kV CB 2712 and 2612, along with the Protection relays for the CBs and shunt reactors. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | 18 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.7091 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5798806 | T.0007616 | JEFFERSON SUB: EM REPL CB2712 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-10-09 | 2024-02-12 | 2024-02-12 | NA | NA | FALSE | 894 | NA ¦ NA | 4546.8603 | 4546.8603 | 49.2371 | 893.3985 | 2704.1866 | 899.6481 | 0.39 | 0 | 0 | 0 | 0 | 0 | 4546.8603 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 4110.3256 | 0.351 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1229 | El Cerrito G: Replace 115KV CB112 |  |  | El Cerrito, Contra Costa | The oil filled 115 kV CB 112 at El Cerrito G substation on the 115 kV Sobrante No 1 line will be replaced with a MEPPI, 40 kA, 2000 AMP HVCB. The oil filled breaker was found with bad CTs and had to be taken out of service during the prechecks leading up to the Test Program and release to operations of BAAH Bay 5 & 6 and Bank 2. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-11 | 70 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 8.2538 | NA | 115 kV | NA | NA | NA | NA | Non-IGP | 5799318 | T.0007744 | El Cerrito G: EM Repl 115kV CB 112 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-02-03 | 2022-03-31 | 2022-03-31 | NA | NA | FALSE | 912 | NA ¦ NA | 1088.5335 | 1088.5335 | 360.9026 | 726.1845 | 1.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.5335 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 911.1466 | 1.2095 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1230 | HARDING: EM INST 60KV CBS 12, 22 |  |  | Stockton, San Joaquin | This project proposes to replace Bank 1 with a 16 MVA 60/12x4 kV dual winding transformer, enhance the ground grid, implement a Shakespeare Wall, install neutral reactors, deploy a 12 kV Shelter Aisle Switchgear, and complete necessary civil construction for the project. | Substation - Circuit Breaker | New | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | NA | NA | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.14046 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811721 | T.0007980 | HARDING: REBUILD SUBSTATION | 3 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-03-29 | 2028-02-29 | 2028-03-31 | NA | NA | FALSE | 35600 | NA ¦ NA | 1139.1946 | 3969.0479 | 0 | 0 | 0 | 79.2886 | 933.9761 | 338.0223 | 0 | 0 | 0 | 0 | 1013.2647 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1231 | Evergreen EM Repl CB 152 |  |  | San Jose, Santa Clara | The existing 115KV Breaker CB 152 at Evergreen Substation is leaking gas out and recommended for replaceemnt. This project will replace the existing breaker CB 152 with a new 115kV breaker with associated switches & Structure | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-05 | 38 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.3776 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5800379 | T.0008197 | Evergreen EM Repl CB 152 74046522 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-06-14 | 2023-09-01 | 2023-09-01 | NA | NA | TRUE | 900 | NA ¦ NA | 2329.8156 | 2330.8197 | 0 | 324.5107 | 2073.3494 | -89.5016 | 21.4571 | 1.0041 | 0 | 0 | 0 | 0 | 2329.8156 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 2162.203 | -80.4199 | 19.3127 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1232 | COCO PP: EM REPL CB 410 |  |  | Antioch, Contra Costa | During the CB410 test at Contra Costa PP, It was found that it had expelled oil from the breather. Further testing of the oil indicated flammability levels of +400%. In addition to the internal inspection, pre- insertion resistor values were tested and found to be out of spec per the manufacturers' guidance @ 13.8 ohms (Req. 1.4 ohms +/- 20%). Therefore, SAI concurred to the emergency replacement of CB410. In addition, the project entails installing 3 new CCVTs on A/B/C phase line side and 1 new CCVT on C phase bus side. Also, due to the foundation's existing condition, Civil recommended replacing the breaker foundation. Civil scope also includes installation of new operating platform for the circuit breaker, foundations for the CCVT support structures, and verhicle guard posts. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | 37 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence ¦ Corrosion |  | NA | 19.1042 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5550544 | T.0008580 | CoCo PP: EM Repl CB 410 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-16 | 2022-12-12 | 2022-12-12 | NA | NA | FALSE | 1317 | NA ¦ NA | 1215.3385 | 1215.3385 | 0 | 849.1281 | 120.1629 | 214.5033 | 31.5442 | 0 | 0 | 0 | 0 | 0 | 1215.3385 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 764.2155 | 108.1466 | 193.053 | 28.3895 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1233 | OAKLAND K REPLACE 115KV CB162 |  |  | Oakland, Alameda | During the inspection of CB162 at Oakland K (Claremont), it was found that the compressor would not hold air. Therefore, the existing oil circuit breaker must be replaced under an emergency replacement project. Additionally, a new CCVT on the line side (C-phase) needs to be installed to provide potentials to protection relays. CB162 was scheduled to be replaced under a planned project in 2023. Due to this emergency, CB162 will be replaced under this emergency project, and the breaker switches, structures, and the by-pass switches will be replaced on the planned project. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-05 | 51 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 3.9974 | NA | 115 kV | NA | NA | NA | NA | Non-IGP | 5802458 | T.0008628 | Oak K: EM Repl CB 162 115kV | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-06 | NA | 2022-11-07 | NA | NA | TRUE | 750 | NA ¦ NA | 1018.3809 | 1019.3115 | 0 | 788.9766 | 214.5834 | 14.8209 | 0 | 0.9306 | 0 | 0 | 0 | 0 | 1018.3809 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 710.7725 | 193.1249 | 13.3387 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1234 | Newark: Repl CB 470 |  |  | Fremont, Alameda | The emergency replacement of circuit breaker 470 at Newark substation | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 27.7611 | NA | 115 kV | NA | NA | NA | NA | Non-IGP | 5802984 | T.0008739 | NEWARK: EM Replace CB 470 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-03-03 | 2023-04-07 | 2023-04-06 | NA | NA | FALSE | 1221.117 | NA ¦ NA | 1216.1166 | 1216.1166 | 0 | 82.8052 | 1126.4502 | 6.8612 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.1166 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 1089.2671 | 6.1751 | -1e-05 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1235 | Sisquoc: Repl CB 112 (EM) |  |  | Santa Barbara | Emergency replacement of Sisquoc CB 112 | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-03 | 35 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 3.9084 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5551683 | T.0008971 | SISQUOC: EM REP CB 112 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-02-27 | NA | 2023-06-27 | NA | NA | TRUE | NA | NA ¦ NA | 1094.8476 | 1094.8476 | 0 | 0 | 836.6053 | 91.0696 | 167.1728 | 0 | 0 | 0 | 0 | 0 | 1094.8476 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 752.9449 | 81.9627 | 150.4555 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1236 | Moraga: Repl OCBs 612 & 622 |  |  | Orinda, Contra Costa | The emergency replacement of oil circuit breakers 612 and 622 at Moraga substation | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | 61 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 15.8714 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804045 | T.0009053 | Moraga: Repl OCBs 612 & 622 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-10-10 | 2024-02-18 | 2024-02-18 | NA | NA | TRUE | 3957.3 | NA ¦ NA | 3900.5679 | 3900.5679 | 0 | 0 | 2139.8883 | 1363.6008 | 396.6382 | 0.4405 | 0 | 0 | 0 | 0 | 3900.1274 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 3503.4891 | 396.6382 | -380.8687 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1237 | PLACER - EMER REPL CB 142 |  |  | Placer | Emergency Replacement of Placer substation Circuit Breaker 142 | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-04 | 63 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 kV | NA | NA | NA | NA | NA | 5552659 | T.0009175 | PLACER: EM REPLACE CB 142 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-04-24 | NA | 2023-06-12 | NA | NA | TRUE | NA | NA ¦ NA | 1003.3351 | 1009.7501 | 0 | 0 | 722.1316 | 20.4453 | 260.7583 | 6.415 | 0 | 0 | 0 | 0 | 1003.3351 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 649.9184 | 18.4007 | 234.6824 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1238 | Brighton: EM Repl OCB 112 |  |  | Sacramento, Sacramento | Emergency replacement of Brighton OCB 112 | Substation - Circuit Breaker | Replace | NA | EX113764 | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | 58 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 6.4413 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5557635 | T.0010289 | BRIGHTON - EM REPLACE OCB 112 - 74060801 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-02-02 | NA | 2026-07-08 | NA | NA | TRUE | NA | NA ¦ NA | 425.5232 | 1070.4365 | 0 | 0 | 0 | 5.9592 | 387.9354 | 676.5421 | 0 | 0 | 0 | 0 | 393.8945 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 5.3632 | 349.1421 | 28.4658 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1239 | Contra Costa PP: Repl CB 600 |  |  | Antioch, Contra Costa | CB 600 at CoCo PP failed and will be replaced on an emergency basis. A new breaker will be released from CEM stock (230kV, 3000A, 63kA S/N: SG000129760001; Model #: 200SFMT-63F1 MEPPI). Substation Engineering to order the replacement breaker. The existing foundation will also be replaced. Breaker failure/reclosing relay and set B relay will be replaced. The CT wires were megger and did not pass the megger test; therefore, this project will be installing new wiring. Additionally, the scope will also include de-terminating all the wires and drops from the currently abandoned CB 670. If construction resources are available in 2024, CB 670 will also be demolished and removed from the station | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | 37 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 19.1042 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5558568 | T.0010535 | CoCo PP: EM Repl CB 600 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-18 | NA | 2025-03-22 | NA | NA | TRUE | NA | NA ¦ NA | 1146.7102 | 1413.0745 | 0 | 0 | 0 | 304.2455 | 657.759 | 212.5079 | 0 | 0 | 0 | 0 | 962.0046 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 273.8212 | 591.9834 | 166.2351 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1240 | Gold Hill: EM Repl CB 172 |  |  | Folsom, Sacramento | This project proposes to replace the deteriorated Gold Hill Transformer # 5 (three (3) single phase, 115/60 kV, 26.6 MVA, General Electric vintage 1951 autotransformers) with four (4), single-phase, 30 MVA, 115/60 kV transformers to make this a firm autotransformer installation | Substation - Circuit Breaker | Replace | NA | T.0004920 | Emergency Event | Replace Breakers | NA | NA | 2026-03-05 | 63 | NA | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 12.8702 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811848 | T.0010612 | GOLD HILL: EM REPLACE BANK 5 | 2 | 65 | NA ¦ 5786799 ¦ T.0000952 ¦ 68 | TRUE | 2021 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-11-04 | 2023-12-01 | 2026-04-10 | Bundling Dependencies | NA | TRUE | 15000 | NA ¦ NA | 1977.0521 | 2513.5847 | 0 | 0 | 0 | 1276.5432 | 334.9411 | 905.6808 | -3.5804 | 0 | 0 | 0 | 1611.4843 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1241 | MORAGA: EM REPL CB 642 & 712 |  |  | Orinda, Contra Costa | The emergency replacement of oil circuit breakers 712 and 642 at Moraga substation | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-03 | 62 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 15.8714 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813599 | T.0010949 | Moraga: EM Repl CB 642 & 712 | 2 | 65 | NA ¦ 5770156 ¦ T.0001635 ¦ 64 | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-11-03 | NA | 2026-05-29 | NA | NA | TRUE | NA | NA ¦ NA | 3324.0745 | 4907.6521 | 0 | 0 | 0 | 0 | 2496.5647 | 2411.0874 | 0 | 0 | 0 | 0 | 2496.5647 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1242 | McKee: Repl CB 152 |  |  | San Jose, Santa Clara | Emergency Replacement of McKee substation Circuit Breaker 152 | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-03 | 60 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7628 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5814522 | T.0011049 | Mc KEE SUB: EM RPL CB 152 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2026-05-28 | NA | 2026-11-30 | NA | NA | TRUE | NA | NA ¦ NA | 406.0735 | 1098.3566 | 0 | 0 | 0 | 0 | 63.6657 | 1033.6868 | 1.0042 | 0 | 0 | 0 | 63.6656 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1243 | Lawrence: Repl CB 142 |  |  | Sunnyvale, Santa Clara | Emergency Replacement of Lawrence substation Circuit Breaker 142 | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-05 | 65 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.8829 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561159 | T.0011124 | LAWRENCE SUB:EM RPL CB 142 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-05-16 | NA | 2030-04-18 | NA | NA | FALSE | NA | NA ¦ NA | 36.0622 | 3105.6697 | 0 | 0 | 0 | 0 | 31.4768 | 1055.6239 | 967.1137 | 0 | 0 | 0 | 31.4768 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1244 | Lawrence: Repl CB 132 |  |  | Sunnyvale, Santa Clara | Emergency Replacement of Lawrence substation Circuit Breaker 132 | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-05 | 65 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.8829 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561121 | T.0011126 | LAWRENCE SUB:EM RPL CB 132 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-06-06 | NA | 2030-04-19 | NA | NA | FALSE | NA | NA ¦ NA | 29.0176 | 3008.5608 | 0 | 0 | 0 | 0 | 25.528 | 1037.0256 | 968.0857 | 0 | 0 | 0 | 25.5279 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1245 | Santa Rosa A: EM REPL CB 132 |  |  | Santa Rosa, Sonoma | This project will replace failed oil filled circuit breakers 132 with non-SF6 breakers at Santa Rosa A Substation. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-02 | 53 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 0.91804 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815439 | T.0011269 | Santa Rosa A: Replace CB 132 | 1 | 65 | NA ¦ 5772481 ¦ T.0002317 ¦ 64 | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-11-02 | NA | 2027-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 1577.2951 | 2575.6527 | 0 | 0 | 0 | 0 | 1556.5761 | 116.7195 | 880.5944 | 0 | 0 | 0 | 1556.5761 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1246 | Santa Rosa A: EM REPL CB 142 |  |  | Santa Rosa, Sonoma | This project will replace failed oil filled circuit breakers 132 with non-SF6 breakers at Santa Rosa A Substation. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-02 | 51 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.91804 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815440 | T.0011270 | Santa Rosa A: Replace CB 142 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 2 | 2026-03-02 | NA | 2027-03-15 | NA | NA | TRUE | NA | NA ¦ NA | 778.7284 | 2160.1732 | 0 | 0 | 0 | 0 | 769.4621 | 740.7365 | 649.9746 | 0 | 0 | 0 | 769.4621 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1247 | Santa Rosa A: EM REPL CB 162 |  |  | Santa Rosa, Sonoma | This project will replace failed oil filled circuit breakers 132 with non-SF6 breakers at Santa Rosa A Substation. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-03-02 | 53 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.91804 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815441 | T.0011271 | Santa Rosa A: Replace CB 162 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-11-02 | NA | 2027-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 637.2448 | 1496.695 | 0 | 0 | 0 | 0 | 629.8483 | 46.0935 | 801.4326 | 0 | 0 | 0 | 629.8483 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1248 | Emergency Replacement , Overall Budget |  |  | NA | Bucket for Substation Emergency replacement | Substation - Multiple | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | NA | 638 | 3. Emergency Preparedness | NA | 5.1001 | Non-IGP | 5506263 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 1338.2663 | 11488.2663 | 0 | 0 | 0 | 0 | 0 | 10150 | 0 | 0 | 0 | 0 | 1338.2663 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1249 | MWC 65 Emergency Preparedness, mobile T-Sub |  |  | NA | Forecast placeholder for substation emergency mobile equipment | Substation - Multiple | Replace | NA | NA | Emergency Event | Substation Reliability | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | EX130199 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 15000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 5000 | 5000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1250 | Emergency Transmission Other/Minor Equipment Replacement |  |  | NA | Forecast placeholder for Emergency Transmission Other/Minor Equipment Replacement | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | EX139129 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 135000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 27000 | 27000 | 27000 | 27000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1251 | High Risk Targeted Minor Critical Electrical Equipment Replacements |  |  | NA | Replace minor critical electrical equipment in protection zone; high risk being addressed under 65F as JIT initiated | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | EX139166 | NA | NA | NA | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 6000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 6000 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1252 | METCALF: EM Replace AC Panel BK 11 |  |  | Santa Clara | Emergency replacement of Metcalf AC Panel BK 11 | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-05 | 55 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 37.8815 | NA | 500 ¦ 230 kV | 638 | 3. Emergency Preparedness | NA | NA | Non-IGP | 5522282 | T.0001870 | METCALF BK11 AC PANEL 74005700 EM | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-01 | 2022-09-07 | 2022-09-07 | NA | NA | FALSE | 1265 | NA ¦ NA | 1219.896 | 1219.896 | 582.6065 | 123.5888 | 6.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219.896 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 524.3459 | 111.2299 | -27.8079 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1253 | TESLA: EM Replace Station Service BK 4 |  |  | Alameda | Replace the existing station service transformer #4, #5 and #6. Install a new station service transformer by CB 522. Replace the outdoor AC panels for station service transformer #4 and #5. | Substation - Voltage Support Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-19 | 19 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 69.382 | NA | 500 ¦ 230 ¦ 115 kV | 638 | 3. Emergency Preparedness | NA | 5.1001 | Non-IGP | 5522385 | T.0001996 | TESLA: EM REPL STATION SERVICE BANK #4 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-10-21 | NA | 2024-01-24 | NA | NA | FALSE | NA | NA ¦ NA | 4837.1572 | 4837.1572 | 37.0763 | 958.6231 | 2469.4271 | -88.0874 | 4.4722 | 0 | 0 | 0 | 0 | 0 | 4837.1572 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 33.3687 | 862.7607 | 2222.4842 | -79.2788 | 4.025 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1254 | VACA DIXON: EM Install Station Lighting |  |  | Solano | Substation Maintenance brought up a safety issue at Vaca Dixon Substation that existed due to insufficient lighting within the station that made the station difficult and dangerous to navigate for any personnel driving in the station at night. This project will install standard lighting, including new conduit runs and lighting panels, in all required areas of the 60kV, 230kV and 500kV yards at Vaca Dixon Substation. While Project Engineering support is being provided by internal Substation Engineering, design has been contracted to HDR since they are also designing several other projects at the station and the construction will be performed by Station Construction. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-25 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 ¦ 115 kV | 638 | 3. Emergency Preparedness | NA | NA | Non-IGP | 5774677 | T.0002896 | Vaca Dixon: JIT Install Station Lighting | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-11-28 | 2018-01-16 | 2019-06-05 | Project Design | NA | FALSE | 3200 | NA ¦ NA | 3636.0062 | 3636.0062 | 12.8089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3636.0062 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -8.3285 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1255 | KERCKHOFF: EM Replace SW 113 and CB 112 |  |  | Fresno | The project objective is to replace existing 115kV breaker 112 with a new breaker; Replace existing switch 111 and 113 with new switches and replace existing CB 112 dead end structure with a new structure | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-03 | 36 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.0825 | NA | 115 kV | 638 | 3. Emergency Preparedness | NA | 5.1001 | Non-IGP | 5776919 | T.0003366 | EM KERCKHOFF REP SW 113 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-01-23 | NA | 2024-07-29 | NA | NA | TRUE | 1022 | NA ¦ NA | 1030.3136 | 1030.3136 | 154.9724 | 86.7045 | 37.4342 | 49.5303 | 0 | 0 | 0 | 0 | 0 | 0 | 1030.3136 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1030.3136 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1256 | ROUND MOUNTAIN: Repl Backup Generator |  |  | Round Mountain CDP, Shasta | Replace under sized backup generator with larger backup generator with minimum size of 450VA. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-09 | 26 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | 29.1389 | NA | 500 ¦ 230 kV | 638 | 3. Emergency Preparedness | NA | 5.1001 | Non-IGP | 5531647 | T.0004226 | ROUND MTN: EM REPL BACKUP GEN | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 2 | 2026-03-02 | NA | 2026-09-03 | NA | NA | FALSE | NA | NA ¦ NA | 1181.1605 | 1195.2455 | 381.3576 | 247.2962 | 161.7761 | 21.2828 | 6.2713 | 0 | 0 | 0 | 0 | 0 | 1181.1605 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 343.2219 | 222.5667 | 145.5986 | 19.1545 | 5.6442 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1257 | ROUND MOUNT: EM Repl MOAS 821- 823- 825 |  |  | Round Mountain CDP, Shasta | Install approximately 300ft of 30" trench North of MOAS's 821, 825, 831, and 835 to route MOAS's 821, 825, 831, and 835 control, power, alarm and fiber conductors. | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-09 | 23 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | 29.1389 | NA | 500 kV | 638 | 3. Emergency Preparedness | NA | NA | Non-IGP | 5782104 | T.0004266 | ROUND MOUNTAIN: EM Rep MOAS 821,823,825, | 2 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-07-01 | 2019-12-09 | 2020-02-25 | NA | NA | FALSE | 7129 | NA ¦ NA | 6755.0939 | 6755.0939 | -30.4008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6755.0939 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -28.5588 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1258 | Round Mountain Install Interlock at 500k |  |  | Round Mountain CDP, Shasta | Install approximately 300ft of 30" trench North of MOAS's 821, 825, 831, and 835 to route MOAS's 821, 825, 831, and 835 control, power, alarm and fiber conductors. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-09 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | 29.1389 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5545806 | T.0004266 | ROUND MOUNTAIN: EM Rep MOAS 821,823,825, | 2 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-03-04 | 2024-03-18 | 2024-03-18 | NA | NA | FALSE | 294 | NA ¦ NA | 273.1588 | 273.1588 | 24.3506 | 44.9908 | 26.4791 | 176.7122 | 0.6261 | 0 | 0 | 0 | 0 | 0 | 273.1588 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 24.3506 | 44.9908 | 26.4791 | 149.4589 | 0.5635 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1259 | Bellota: Replace Switch 433 & 43530KV |  |  | San Joaquin | This project proposal is for Bellota Substation, located in San Joaquin County. Due to 230 kV switch failure of breaker disconnecting switch SW433 and probable failure of SW435, SW423 & SW425 in the future, these switches shall be replaced. | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-14 | 13 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | 638 | 3. Emergency Preparedness | NA | 5.1001 | Non-IGP | 5533824 | T.0004480 | BELLOTA: EM Replace Switch 433 & 435 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-10-01 | NA | 2020-06-04 | NA | NA | FALSE | NA | NA ¦ NA | 1780.6652 | 1780.6652 | 2.9755 | 1.3976 | 2.3006 | 10.7782 | 0.4015 | 0 | 0 | 0 | 0 | 0 | 1780.6652 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 2.6779 | 1.2579 | 2.0705 | 9.7004 | 0.36136 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1260 | Drum PH: EM Repl 115 kV Structures |  |  | Placer | Replace 115kV SW 363’s (2), 357, 353’s (2), 347, 343’s (2) and related structures. | Substation - Structure | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-12 | 116 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.2491 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811342 | T.0004814 | Drum PH 1: Replace SW 333 Structure-WSIP | 2 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-10-01 | NA | 2026-12-02 | NA | NA | TRUE | NA | NA ¦ NA | 173.9906 | 2686.1205 | 0 | 0 | 0 | 5.1646 | 144.0582 | 2523.7661 | 13.1316 | 0 | 0 | 0 | 149.2228 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1261 | Drum PH 1:Replace SW363 Structure-WSIP |  |  | Placer | Replace 115kV SW 363’s (2), 357, 353’s (2), 347, 343’s (2) and related structures. | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-12 | 114 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ TRUE | FALSE | Heat Wave ¦ Weather |  | NA | 2.2491 | NA | 115 kV | NA | 3. Emergency Preparedness | NA | 5.1001 | Non-IGP | 5785879 | T.0004814 | Drum PH 1: Replace SW 333 Structure-WSIP | 2 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-04-14 | NA | 2024-06-28 | NA | NA | TRUE | 200 | NA ¦ NA | 6080.6506 | 6117.6803 | 454.0676 | 389.4896 | 131.2555 | 208.9156 | 22.1304 | 11.6424 | 0 | 0 | 0 | 0 | 6080.6506 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 5562.691 | 19.9174 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Wildfire Related] WSIP [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1262 | MORRO BAY SWSTA: EM FLOOD MITIGATION TRN |  |  | Morro Bay, San Luis Obispo | Minimize or reduce impact of flooding on the Transmission Switching Station. | Substation - Structure | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 12.614 | NA | 230 ¦ 115 kV | NA | 3. Emergency Preparedness | NA | NA | Non-IGP | 5536006 | T.0004816 | MORRO BAY SWSTA: EM FLOOD MITIGATION TRN | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-01 | NA | 2021-10-05 | NA | NA | FALSE | NA | NA ¦ NA | 2623.2058 | 2623.2058 | 1445.8825 | 28.9268 | 0.4492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2623.2058 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1445.8825 | 28.9268 | 0.44917 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1263 | Placer: Repair/Refurbish Bank 1_WSIP |  |  | Placer | Refurbish bank #1 bushings at Placer sub | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-04 | 69 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | Weather |  | NA | 2.9734 | NA | 115 ¦ 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5539564 | T.0005806 | Placer: Replace BK1 Bushings - WSIP | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-23 | 2021-05-14 | 2021-05-14 | NA | NA | TRUE | 1149.7705 | NA ¦ NA | 1160.2543 | 1160.8066 | 964.6152 | 20.8092 | 53.7582 | 61.4102 | 7.7431 | 0.5523 | 0 | 0 | 0 | 0 | 1160.2543 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 868.1535 | 18.7283 | 48.3825 | 55.2692 | 6.9688 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Wildfire Related] WSIP [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1264 | Round Mountain: Em Repl Rear Gate-WSIP |  |  | Round Mountain CDP, Shasta | Back in 2016, as part of substation security upgrade program (Tier 2/3), the old substation fence was replaced with 10’ high pre-cast walls on the west side only, and with 10’ high non-visibility fence (with vertical vinyl slats) along all other sides. Later, during WSIP (wildfire) inspections, it was determined that on the north side of the substation, the fencing with vinyl slats is too close to energized equipment, and approximately for 1400 linear feet of fencing, the non-visibility vinyl slats were removed. This included one double swing gate as well. Corporate security has determined that the visibility into the substation for the sections with removed vinyl slats is unacceptable, and measures should be taken to install new fencing per Corporate Security Standard SEC-2010S Rev 0, to prevent visibility into the substation. This area is Highlighted in the attached drawing 3015615_R2. For this replacement of 1400 feet, Corporate Security has determined that Shakespeare fence (manufactured by Safefence) is an acceptable replacement. After consulting with Shakespeare manufacturing, we have determined that we can salvage, and re-use the existing 6” diameter fence posts, and pier foundations (at a very large saving, especially since the existing fencing is less than 6 years old). Shakespeare will provide clips, that can be bolted into the existing fence posts, and Shakespeare fence panels can be secured into these clips. Therefore, there will not be any foundation work, or fence post installation. | Substation - Structure | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-09 | 6 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ TRUE | FALSE | Weather ¦ Extreme Heat |  | NA | 29.1389 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5540303 | T.0005956 | ROUND MOUNTAIN: EM REPL FENCE | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-22 | 2024-05-15 | 2024-05-15 | NA | NA | FALSE | 1128 | NA ¦ NA | 1108.9534 | 1108.9534 | 27.5553 | 43.7046 | 65.4257 | 964.8006 | 1.3584 | 0 | 0 | 0 | 0 | 0 | 1108.9534 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 31.9809 | 41.5192 | 62.1543 | 916.5605 | 56.7386 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Wildfire Related] WSIP [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1265 | Trinity Sub: Em Repl Fence-WSIP |  |  | Weaverville CDP, Trinity | PG&E proposes to replace the entire existing fence with both chain link and non-conductive fencing at the Trinity Substation | Substation - Structure | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ TRUE | FALSE | Corrosion |  | NA | 1.3227 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5541291 | T.0006200 | Trinity Sub: Em Repl Fence-WSIP | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-10-16 | 2024-01-19 | 2024-01-19 | NA | NA | TRUE | 1673 | NA ¦ NA | 1739.1577 | 1739.1577 | 37.8933 | 85.8829 | 1425.9464 | 66.2506 | 117.3697 | 0 | 0 | 0 | 0 | 0 | 1739.1577 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 39.3373 | 77.2943 | 1283.3516 | 59.6255 | 279.549 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Wildfire Related] WSIP [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1266 | Colusa: Rebuild 60 kV |  |  | Colusa, Colusa | Due to the recent catastrophic failure of Bank 2 A-phase transformer, Substation Asset Management has concurred to emergency replace Bank 2 with a 3-phase transformer (JO# 74031330). This project will be performed in conjunction with the Colusa Emergency Replace Distribution Equipment (JO# 74017764) to allow extensive remediation to be performed. A third JO was issued to replace Bank 1 on a just-in-time emergency basis (JO# 74032102). In addition, a fourth JO has been issued to replace the 60kV equipment under emergency (JO# 74035560). When all work is completed, the station will be fully rebuilt and remediated. | Substation - Structure | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-11 | 19 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 0.25267 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5792278 | T.0006254 | Colusa: Replace 60kV Equipment | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-06-28 | 2024-03-29 | 2024-03-29 | NA | NA | FALSE | 208 | NA ¦ NA | 2264.198 | 2264.198 | 1129.7171 | 556.906 | 236.8871 | 318.1477 | -19.8015 | 0 | 0 | 0 | 0 | 0 | 2264.198 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 2086.9447 | -17.8213 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1267 | Vaca Dixon: Replace 230 kV Shunt Caps |  |  | Solano | Emergency replacement of 230 kV Shunt Caps at Vaca-Dixon substation | Substation - Reactive Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-25 | 39 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5792199 | T.0006308 | Vaca Dixon: Em Repl 230kV Shunt Caps | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-05-10 | 2023-11-01 | 2023-11-01 | NA | NA | FALSE | 250 | NA ¦ NA | 10009.8591 | 10009.8591 | 3212.9739 | 1469.5746 | 4838.5301 | 88.165 | 1.0124 | 0 | 0 | 0 | 0 | 0 | 10009.8591 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 9010.2817 | -168.8353 | 0.88381 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1268 | PITTSBURG PP: EM REPL 230KV SW 419 |  |  | Pittsburg, Contra Costa | Emergency replacement of Pittsburg PP 230 kV SW 419. Switch 419 failed during normal maintenance interval. This 230kV switch is a part of two bus selector switches located at bus section D. Civil engineering determined that the existing switch support structure does not meet current seismic standard. Complete replacement of the switch support structure, its foundations, and two bus selector switches is recommended. | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-04 | 24 | NA | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 28.8512 | NA | 230 kV | NA | NA | NA | NA | Non-IGP | 5543039 | T.0006821 | Pittsburg PP - Switch 419 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-12 | 2022-06-02 | 2022-06-02 | NA | NA | FALSE | 1480 | NA ¦ NA | 1461.605 | 1461.605 | 622.9428 | 823.1462 | -7.6296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1461.605 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 1322.3114 | -153.0274 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1269 | Carbona: EM T L Shoofly |  |  | San Joaquin | Replace Carbona Transformer Bank 2 with a larger transformer, upgrade 60kV equipment, replace the Carbona Bank 1 foundation, replace the entire 12kV bus with switchgear, and establish a new distribution circuit outside of the substation. The capacity increase is needed to eliminate a 30 percent normal overload of Carbona Bank 1, a 33 percent normal overload of the Carbona 1104 distribution feeder, and a 38 percent normal overload of the Tracy 1102 distribution feeder. These overloads are forecasted to occur by summer 2022 and are the result of several large new business applications including Amazon and Home Depot warehouse-distribution centers. Transmission Substation Work (MWC 61) under this Project – Planning Order 5797580: • Install 60 kV main bus comprised of 2300Al bare conductor. • Install two 60 kV, 1200 A circuit breakers and associated disconnect switches. • Install one 60 kV, 1200 motor-operated air switch (MOAS) to sectionalize the 60 kV bus. • Install current and potential transformers and surge arresters as required for system protection. • Install 60kV control and protection racks inside the new switchgear building. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-05 | NA | NA | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.27151 | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5558846 | T.0007057 | CARBONA: EM REPL BANK 2A AND 2B | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-11-17 | 2023-09-30 | 2022-11-17 | NA | NA | FALSE | 32000 | NA ¦ NA | 269.3511 | 269.3511 | 0 | 0 | 0 | 269.3511 | 0 | 0 | 0 | 0 | 0 | 0 | 269.3511 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 215.4809 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1270 | Midway: Repl 500kV Bk Tert Insul |  |  | Buttonwillow CDP, Kern | Emergency replacement of Midway 500 kV Bank 11 Tertiary Reactor | Substation - Reactive Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 500 kV | NA | NA | NA | 5.1001 | Non-IGP | 5544579 | T.0007084 | MIDWAY: EM BK 11 TERT REACTOR FDN-INSUL | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2023-09-07 | NA | 2027-03-22 | NA | NA | TRUE | NA | NA ¦ NA | 3876.2483 | 3876.2483 | 42.982 | 415.5387 | 2400.2051 | 777.7806 | 239.742 | 0 | 0 | 0 | 0 | 0 | 3876.2483 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2027 | 39.9927 | 386.639 | 2233.2768 | 723.6879 | 223.0685 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1271 | GARBERVILLE: EM Repl 33,35,43,45 |  |  | Garberville CDP, Humboldt | Emergency replacement of 60kV SW 33, 35, 43, & 45 at Garberville Sub | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-02 | 76 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.3065 | NA | 60 kV | NA | NA | NA | NA | Non-IGP | 5544620 | T.0007086 | GARBERVILE:EMRPL SW33,35,43,45, 74038748 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-05-02 | 2022-05-14 | 2022-05-14 | NA | NA | FALSE | 2950 | NA ¦ NA | 2935.3454 | 2935.3454 | 146.3048 | 2788.8737 | 0.1669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2935.3454 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 129.3263 | 2551.058 | 0.15244 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1272 | Vaca Dixon: Replace 1301 Shunt Reactors |  |  | Solano | On 2/12/2021, one of the Vaca Dixon CB 1301 tertiary reactors became over-heated and caught fire, causing the 500/230kV Bank 11 and associated 1301/1302/1303/1304 tertiary reactors to be cleared until the fire burned out. On 2/22/2021, Substation Asset Implementation concurred to the emergency replacement of all three 1301 tertiary reactors using new equipment recently ordered for a similar job at Table Mountain Substation that was cancelled. Upon performing the walkdown meeting on 4/14/2021, it was determined that the new reactors would not match the existing, non-standard footings and that the foundations and support insulators would need to be replaced as well. This project will replace the TB 11 Tertiary reactors 1301 ABC phases, including the foundations and support insulators | Substation - Reactive Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-25 | 32 | NA | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 ¦ 230 kV | NA | NA | NA | NA | Non-IGP | 5544723 | T.0007114 | Vaca Dixon: Em Repl 1301 Reactors | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-18 | 2022-01-28 | 2022-01-28 | NA | NA | FALSE | 1430 | NA ¦ NA | 1408.4625 | 1408.4625 | 945.7677 | 445.9902 | 16.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1408.4625 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 851.191 | 401.391 | 83.986 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1273 | IGNACIO: EM Repl SW 183 & 185 |  |  | Novato, Marin | Emergency replacement of deteriorating 115 kV SW 183,185 at Ignacio substation | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-05 | 62 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.9486 | NA | 115 kV | NA | NA | NA | NA | Non-IGP | 5796093 | T.0007170 | Ignacio: Repl Sw 183 & 185 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-26 | 2021-04-30 | 2021-04-30 | NA | NA | FALSE | 1538 | NA ¦ NA | 1449.3761 | 1449.3761 | 1449.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1449.3761 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 1414.6534 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $2 Mil - $3 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1274 | Monta Vista-Replace 230kV SW Stru/Slope |  |  | Cupertino, Santa Clara | To better serve nearby Santa Clara County residents and businesses, PG&E proposes to upgrade substation equipment foundations and stabilize the northern substation slope. Located in Santa Clara County, the Monta Vista Substation is bounded by grassland to the north, a wooded area to the east, a railroad to the south and southeast, and maintenance roads to the west and is located within the community of Cupertino. Specifically, PG&E will stabilize the slope outside of the PG&E fence to the north of the substation. The work will extend from the substation fence for approximately 150 feet adjacent to the existing fence line and 12 feet down the embankment. All vegetation will be cleared off the slope. The slope vegetation consists of ruderal plants such as thistles and common weeds. The slope will be compacted, and galvanized metal spikes that are 10 to 20 feet in length will be driven into the ground which will hold the metal mesh on the slope. Anchors will also be placed 10-15 feet below grade level to secure the mesh. Jute netting will be placed under the metal mesh as a first layer of soil stabilization. DrillTech will broadcast seed the area after the jute netting is placed. Work will occur outside of the fence with a small excavator on the flat area adjacent to the fence. The bottom of the embankment has an open metal culvert which extends the entire 150-foot length, with a small portion enclosed (approximately 10 feet). No work or equipment will occur within or beyond the culvert. Additionally, PG&E will install new foundations for a new bus structure, circuit breaker, and current transformer inside of the substation fence | Substation - Structure | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | 66 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8314 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5796394 | T.0007213 | MONTA VISTA Rep 230kV Structure 74039803 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-09-22 | NA | 2026-06-15 | NA | NA | TRUE | 1000 | NA ¦ NA | 4218.5919 | 5033.6598 | 473.9633 | 1499.7621 | 183.6898 | 752.1187 | 451.4443 | 1672.6817 | 0 | 0 | 0 | 0 | 3360.978 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1275 | Humboldt: EM Relocate Card Reader |  |  | Humboldt | Remove and replace 20ft main sliding gate. Replace approximiately 50ft of chain-link fence with 8ft non-conductive fence with “V” shaped non-conductive panels to the north of sliding gate and approximiately 10ft of chain-link fence to the south. Relocate entrance and exit card reader. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-02 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.569 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5797998 | T.0007484 | HUMBOLDT: EM REPL CARD READER, 74042403 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-06-01 | NA | 2024-11-07 | NA | NA | TRUE | NA | NA ¦ NA | 1213.5071 | 1219.2403 | 48.5705 | 120.5186 | 514.953 | 294.4436 | 253.652 | -12.8972 | 0 | 0 | 0 | 0 | 1232.1376 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 888.4087 | 228.2866 | -16.7675 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1276 | Bellota: Replace SW 243 |  |  | San Joaquin | Replace Rancho Seco-Bellota 230kV line 2 SW 243. Substation maintenance has not had success in making repairs to gear box or adjustments to fully open switch resulting in its replacement. Existing switch is underhung 6 pole gang operated and will be replaced with SW 241 and SW 243 for CB 240. | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-14 | 60 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | NA | Non-IGP | 5547159 | T.0007630 | BELLOTA REPLACE SWITCH 243 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-04-04 | 2023-07-19 | 2023-07-19 | NA | NA | FALSE | 1203.907 | NA ¦ NA | 1199.7632 | 1199.7632 | 25.2959 | 473.8872 | 687.1174 | 13.4626 | 0 | 0 | 0 | 0 | 0 | 0 | 1199.7632 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 22.7663 | 426.4987 | 618.4057 | -107.86 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1277 | PITTSBURG PP: EM REPL CB822 & SWITCH 823 |  |  | Pittsburg, Contra Costa | During a regular maintenance inspection of the 230KV double bus single breaker section of the Pittsburg Power Plant Substation found that the Switch 823 mechanical arms failed and deemed to be unrepairable. This Switch 823 is a part of the section tie breaker that connects Bus Section E and Bus Section D Main Bus 2. Civil Engineering determined that re-using the current latctice structure would fail under peak wind loads and the existing pile/pilecap connection is not sufficient for seismic load transfter. Due to this analysis, The Switches on the current lattice structure would be removed and a new switch structures and will be installed for the new switches. In addition during the walkdown, it was found that the current CB 822 and its structure is deteriorating and in need of replacement. This project will also include replacing the deteriorating CB 822 with a 230KV 3000A 63KA High voltage breaker. | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-04 | 31 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 28.8512 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5547227 | T.0007657 | Pittsburg PP SWitch 823 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-09-25 | 2024-01-31 | 2024-01-31 | NA | NA | FALSE | 2932 | NA ¦ NA | 2853.7209 | 2853.7209 | 29.8556 | 289.3786 | 2008.7564 | 502.7477 | 22.9827 | 0 | 0 | 0 | 0 | 0 | 2853.7209 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 319.2341 | 1797.1206 | 457.0434 | -5.0494 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1278 | MORAGA: EM REPL SINKHOLE & DRAIN PIPE |  |  | Orinda, Contra Costa | There are three areas of repair needed which are related to drainage and erosion for the substation. 1. Failed culvert from SPCC pond #2 to water outlet has caused a massive sinkhole just outside the West corner of the sub. Phase 1 of this item is to replace the portion of the failed culvert and fill up the sinkhole. Phase II is to replace the rest of the culvert which has showed signs of damage, but will require a lengthy permitting process and environmental reviews. 2. Repair erosion damages caused by clogged Grizzly(the inlet of the 48" culvert pass under the Sub) near the precast security walls. 3. Repair the V-ditch near bank 3 and replace the crashed pipe between two catch basins. | Substation - Structure | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | 74 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 15.8714 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5549230 | T.0008251 | Moraga: Em Repl Sinkhole & Drain Pipe | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-26 | 2023-11-22 | 2023-11-22 | NA | NA | FALSE | 1334 | NA ¦ NA | 1233.7754 | 1233.7754 | 0 | 737.4873 | 469.3016 | 25.6533 | 1.3332 | 0 | 0 | 0 | 0 | 0 | 1233.7754 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 1206.7889 | 25.6533 | -122.0444 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1279 | BELL-EM REPL OPT MTR CT ADD 3 PH.CCVT |  |  | Placer | Replacing Bell Line Relays due to failed Optical CT | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-04 | 26 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 0.91963 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5549741 | T.0008373 | BELL EM REPL OPT MTR CT_PT | 2 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-14 | NA | 2025-04-11 | NA | NA | TRUE | NA | NA ¦ NA | 1433.7001 | 1440.463 | 0 | 15.8308 | 153.9422 | 383.623 | 879.0697 | 7.9974 | 0 | 0 | 0 | 0 | 1432.4657 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 14.2477 | 138.5481 | 345.2609 | 791.163 | 1.1109 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1280 | Clovis sub:EM Repl CS 387 |  |  | Clovis, Fresno | Emergency Replacement of Clovis substation SW 87 | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | 62 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.5415 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5801882 | T.0008473 | CLOVIS: EM Repl SW 387 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-29 | NA | 2025-03-17 | NA | NA | TRUE | NA | NA ¦ NA | 1076.0718 | 1076.0718 | 0 | 78.6753 | 129.1789 | 479.071 | 369.1525 | 19.9941 | 0 | 0 | 0 | 0 | 1056.0777 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1056.0777 | 19.9941 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1281 | COBURN: EM REP SW 11 & OB INS 60KV |  |  | Monterey | Emergency replacement of Coburn 60 kV SW 11 and OB insulators | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-04 | 66 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.435 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5550456 | T.0008562 | COBURN: EM REP SW 11 & OB INS | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-03-01 | NA | 2027-03-26 | NA | NA | TRUE | NA | NA ¦ NA | 224.4225 | 2086.2741 | 0 | 54.3684 | 83.3817 | 45.3623 | 23.9154 | 162.9816 | 1716.2646 | 0 | 0 | 0 | 207.0279 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 48.9316 | 75.0436 | 40.8262 | 21.524 | 15.6551 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1282 | VACA DIXON: EM REPLACE 1306 ABC REACTORS |  |  | Solano | Emergency replacement of Shunt Reactor 1306 reactor at Vaca-Dixon substation due to failure | Substation - Reactive Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-25 | 16 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | NA | NA | NA | NA | Non-IGP | 5550552 | T.0008591 | Vaca Dixon: Em Repl 1306 Reactors | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-06-13 | 2023-10-12 | 2023-10-12 | NA | NA | TRUE | 1400.9411 | NA ¦ NA | 1400.8424 | 1401.0935 | 0 | 52.2795 | 1341.8107 | 6.7523 | 0 | 0.251 | 0 | 0 | 0 | 0 | 1400.8424 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 47.0516 | 1207.6296 | 6.077 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1283 | Bellota: EM Replace SW 233 |  |  | San Joaquin | Emergency replacement of failed SW 233 at Bellota substation | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-14 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5551341 | T.0008848 | Bellota: EM Replace SW 233 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-05-06 | NA | 2024-07-01 | NA | NA | FALSE | NA | NA ¦ NA | 1153.1078 | 1153.1078 | 0 | 8.2782 | 219.0414 | 872.81 | 52.9782 | 0 | 0 | 0 | 0 | 0 | 1153.1078 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 7.4504 | 197.1372 | 785.5287 | 47.6804 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1284 | Oakland J: Replace 115kV PTs & Structure |  |  | Oakland, Alameda | Emergency project to replace failed 115kV bus PTs & associated structures. The failed PTs caused outages to 50,000 customers as well as failure of other equipment. | Substation - Structure | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-09 | 64 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 2.5059 | NA | 115 kV | NA | NA | NA | NA | Non-IGP | 5552205 | T.0009033 | Oak J: EM Repl 115kV Bus PTs & Structure | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-02-21 | 2023-04-19 | 2023-04-19 | NA | NA | FALSE | 2983.3664 | NA ¦ NA | 2983.3664 | 2983.3664 | 0 | 0 | 2927.8293 | 55.5371 | 0 | 0 | 0 | 0 | 0 | 0 | 2983.3664 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 2635.0461 | 49.9836 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1285 | Brighton: EM Replace Sub fence |  |  | Sacramento, Sacramento | Emergency replacement of fence at Brighton substation. | Substation - Structure | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 6.4413 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5804686 | T.0009142 | BRIGHTON: EM REPLACE FENCE | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-09-08 | NA | 2026-06-30 | NA | NA | TRUE | 1900 | NA ¦ NA | 4499.8408 | 7659.5914 | 0 | 0 | 292.098 | 344.6668 | 3019.7273 | 4003.0994 | 0 | 0 | 0 | 0 | 3656.4921 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1286 | CHESTER EM REPL WOOD POLE |  |  | Chester CDP, Plumas | Emergency replacement of Chester Bank 1 and wood poles | Substation - Structure | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-09 | 37 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 0.077356 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5558907 | T.0009421 | Chester: Em Repl Wood Pole | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-03-18 | NA | 2025-03-22 | NA | NA | TRUE | NA | NA ¦ NA | 1194.8503 | 1194.8503 | 0 | 0 | 0 | 19.6183 | 1143.0453 | 32.1867 | 0 | 0 | 0 | 0 | 1162.6636 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1162.6636 | 32.1867 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1287 | Midway: Replace Midway BK13 C Bushings |  |  | Buttonwillow CDP, Kern | Emergency replacement of Midway BK13 C Bushings | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | 50 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5554007 | T.0009469 | MIDWAY: EM BK 13 C PHASE BUSHING REPLC | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-08-20 | NA | 2026-02-02 | NA | NA | TRUE | NA | NA ¦ NA | 1290.8324 | 1290.8324 | 0 | 0 | 55.1823 | 937.3047 | 298.3455 | 0 | 0 | 0 | 0 | 0 | 1290.8324 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 992.4869 | 298.3455 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1288 | Midway: Replace Midway BK13 A Bushings |  |  | Buttonwillow CDP, Kern | Emergency replacement of failed BK13 A Bushings at Midway substation; | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5554008 | T.0009471 | MIDWAY: EM BK 13 A PHASE BUSHING REPLC | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-07-12 | NA | 2024-09-18 | NA | NA | FALSE | NA | NA ¦ NA | 1371.6153 | 1371.6153 | 0 | 0 | 7.7653 | 1355.4421 | 8.4079 | 0 | 0 | 0 | 0 | 0 | 1371.6153 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1363.2074 | 8.4079 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1289 | Vaca Dixon: EM Repl old Bank 5 bushings |  |  | Solano | This project replaced the old Vaca Dixon 230/115kV Bank 5 single-phase transformer bushings, including the spare transformer, relocated them to the emergency stock yard and removed the old foundations and grounds | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-25 | 50 | NA | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 42.1076 | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5552502 | T.0009711 | Vaca Dixon: Em Repl BK5 Bushings | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-07 | 2025-04-25 | 2025-04-25 | NA | NA | TRUE | 1130 | NA ¦ NA | 1100.0605 | 1100.0605 | 0 | 0 | 2.0168 | 352.5317 | 746.2276 | -0.7155 | 0 | 0 | 0 | 0 | 1100.776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 319.0935 | 552.7212 | -0.56671 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1290 | Placer: EM Replace Batteries |  |  | Placer | Emergency replacement of failed station batteries at Placer sub | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5555366 | T.0009798 | PLACER: EM REPLACE BATTERIES-74057153 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-07-09 | 2024-09-06 | 2024-09-06 | NA | NA | TRUE | 2400 | NA ¦ NA | 2322.4075 | 2322.4075 | 0 | 0 | 163.9331 | 2022.8952 | 135.5793 | 0 | 0 | 0 | 0 | 0 | 2322.4075 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1093.4135 | 996.7532 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1291 | SUISUN: JIT REPLACE CKT SW 177 |  |  | Fairfield, Solano | Emergency replacement of Circuit Switcher 177 at Suisun 115 kV substation. | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-04 | 51 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.1706 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5556445 | T.0010117 | Suisun: Em Replace MOAS 177 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-09-30 | NA | 2027-11-30 | NA | NA | TRUE | NA | NA ¦ NA | 304.8258 | 1449.2415 | 0 | 0 | 0 | 35.2265 | 261.0093 | 296.4347 | 847.8794 | 0 | 0 | 0 | 296.2359 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 31.7037 | 234.908 | 7.7309 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1292 | Taft-Cuyama #1 70kv |  |  | Cuyama CDP, Santa Barbara ¦ Kern ¦ San Luis Obispo ¦ Santa Barbara ¦ Taft, Kern | Failure of switches 35 and 45 outlined the need for an updated 70kV bus section at Cuyama substation. The goal of this project is to greenfield three new 70kV breakers in a “loop” configuration to allow much greater operational flexibility and fault clearing capabilities. This project will also install 3 breaker SMP packages for the new breakers, 2 line SMP packages for the Taft-Cuyama #1 and #2 70kV lines, and a GARD8000 DTT package to trip nearby Cuyama Solar. There will be transmission line work required to relocate the existing 70kV Taft-Cuyama #1 and #2 lines to their new locations. | Substation - Line Termination | Relocate | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2025-06-24 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815398 | T.0010146 | CUYAMA: EM SW 35 & 45 REPLACEMENT | 3 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-11-23 | NA | 2027-02-12 | NA | NA | TRUE | NA | NA ¦ NA | 15.8401 | 83.332 | 0 | 0 | 0 | 0 | 12.0436 | 70.5396 | 0 | 0 | 0 | 0 | 12.0436 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1293 | Taft-Cuyama #2 70kv |  |  | Cuyama CDP, Santa Barbara ¦ Kern ¦ San Luis Obispo ¦ Santa Barbara ¦ Taft, Kern | Failure of switches 35 and 45 outlined the need for an updated 70kV bus section at Cuyama substation. The goal of this project is to greenfield three new 70kV breakers in a “loop” configuration to allow much greater operational flexibility and fault clearing capabilities. This project will also install 3 breaker SMP packages for the new breakers, 2 line SMP packages for the Taft-Cuyama #1 and #2 70kV lines, and a GARD8000 DTT package to trip nearby Cuyama Solar. There will be transmission line work required to relocate the existing 70kV Taft-Cuyama #1 and #2 lines to their new locations. | Substation - Line Termination | Relocate | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2025-11-20 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5815399 | T.0010146 | CUYAMA: EM SW 35 & 45 REPLACEMENT | 3 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-11-23 | NA | 2027-02-12 | NA | NA | TRUE | NA | NA ¦ NA | 28.6077 | 96.9932 | 0 | 0 | 0 | 0 | 21.2769 | 74.851 | 0 | 0 | 0 | 0 | 21.2769 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1294 | Cuyama: Replace SW 35 & 45 |  |  | Cuyama CDP, Santa Barbara | Failure of switches 35 and 45 outlined the need for an updated 70kV bus section at Cuyama substation. The goal of this project is to greenfield three new 70kV breakers in a “loop” configuration to allow much greater operational flexibility and fault clearing capabilities. This project will also install 3 breaker SMP packages for the new breakers, 2 line SMP packages for the Taft-Cuyama #1 and #2 70kV lines, and a GARD8000 DTT package to trip nearby Cuyama Solar. There will be transmission line work required to relocate the existing 70kV Taft-Cuyama #1 and #2 lines to their new locations. | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-13 | 66 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 1.1317 | NA | 70 kV | NA | NA | NA | 5.1001 | Non-IGP | 5809860 | T.0010146 | CUYAMA: EM SW 35 & 45 REPLACEMENT | 3 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-09-03 | NA | 2027-06-11 | NA | NA | TRUE | NA | NA ¦ NA | 892.7639 | 4881.0656 | 0 | 0 | 0 | 84.1478 | 737.6663 | 3883.2449 | 176.0067 | 0 | 0 | 0 | 821.8141 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1295 | Midway: Replace Bank 12 C PH Bushings |  |  | Buttonwillow CDP, Kern | Emergency replacement of Midway BK12 C PH Bushings | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-03 | 50 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5557739 | T.0010339 | Midway: Replace Bank 12 C PH bushings | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-07-09 | NA | 2026-02-02 | NA | NA | FALSE | NA | NA ¦ NA | 1357.9795 | 1357.9795 | 0 | 0 | 0 | 1292.3439 | 65.6356 | 0 | 0 | 0 | 0 | 0 | 1357.9795 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1292.3439 | 65.6356 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1296 | Tesla: EM Repl BK2 A ph Bushings |  |  | Alameda | Emergency replacement of Tesla BK2 ABC & Spare Bushings | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-19 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5557785 | T.0010370 | TESLA: EM REPL BK2 A PH BUSHS | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-07-01 | NA | 2027-07-30 | NA | NA | TRUE | NA | NA ¦ NA | 54.2373 | 1765.6263 | 0 | 0 | 0 | 16.8789 | 29.5658 | 7.7925 | 1711.3891 | 0 | 0 | 0 | 46.4448 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 16.8228 | 29.4675 | 7.7666 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1297 | CAMP EVERS SUB:EM RPL MOAS 177 |  |  | Scotts Valley, Santa Cruz | Emergency Replacement of Camp Evers substation MOAS 177 | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-03 | 55 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.2126 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5558296 | T.0010472 | CAMP EVERS SUB:EM RPL MOAS 177 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-22 | NA | 2026-07-27 | NA | NA | TRUE | NA | NA ¦ NA | 401.3775 | 1332.1264 | 0 | 0 | 0 | 26.5429 | 335.4595 | 970.124 | 0 | 0 | 0 | 0 | 362.0023 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 26.5429 | 335.4595 | 39.3752 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1298 | Westpark: Replace CKSW 187 |  |  | Bakersfield, Kern | Emergency replacement of Westpark Circuit Switcher 187 | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-17 | 39 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7259 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5558340 | T.0010488 | WESTPARK: EM CKSW 187 REPLACEMENT | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-13 | NA | 2026-05-18 | NA | NA | TRUE | NA | NA ¦ NA | 1123.1821 | 1271.4291 | 0 | 0 | 0 | 96.9949 | 973.3093 | 164.4961 | 36.6288 | 0 | 0 | 0 | 1070.3042 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 96.9949 | 973.3094 | 52.8778 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1299 | MERCED: REPL SW 185 WITH CB |  |  | Merced | Emergency replacement of Merced SW 185 with CB | Substation - Switch | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2026-02-03 | 38 | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7481 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5812664 | T.0010671 | Merced: EM Replace SW 185 with CB 185 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-09-02 | 2019-07-09 | 2026-04-30 | Prioritization | NA | TRUE | 4981 | NA ¦ NA | 3030.235 | 3899.8076 | 0 | 0 | 0 | 1437.3137 | 871.0508 | 1591.4431 | 0 | 0 | 0 | 0 | 2308.3645 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1300 | Oakland D CB172 Replacement |  |  | Oakland, Alameda | Emergency Replacement of Oakland D substation Circuit Breaker 172 | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-16 | 56 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 0.54348 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813598 | T.0010813 | Oak D: EM Repl CB172 | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-01-29 | NA | 2025-09-08 | NA | NA | TRUE | NA | NA ¦ NA | 987.0074 | 1006.1801 | 0 | 0 | 0 | 0 | 975.0826 | 31.0975 | 0 | 0 | 0 | 0 | 975.0826 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 879.1795 | 10.7323 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1301 | Moraga: Replace CB 712 & 642 Transmissio |  |  | Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa ¦ Piedmont, Alameda | The emergency replacement of oil circuit breakers 712 and 642 at Moraga substation | Substation - Circuit Breaker | Replace | NA | NA | Emergency Event | Replace Breakers | NA | NA | 2025-08-21 | 63 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5815958 | T.0010949 | Moraga: EM Repl CB 642 & 712 | 2 | 65 | NA ¦ 5770156 ¦ T.0001635 ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-11-03 | NA | 2026-05-29 | NA | NA | TRUE | NA | NA ¦ NA | 112.9148 | 202.6029 | 0 | 0 | 0 | 0 | 75.8331 | 126.7698 | 0 | 0 | 0 | 0 | 75.8331 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1302 | Humboldt: Repl SVC Control |  |  | Humboldt | Emergency replacement of Humboldt SVC controller | Substation - Reactive Equipment | Replace | NA | T.0009741 | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-02 | 16 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 4.569 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813357 | T.0011162 | HUMBOLDT: EM REPL SVC CNTRLLR | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-07-23 | NA | 2027-10-29 | NA | NA | TRUE | NA | NA ¦ NA | 149.8544 | 7446.7379 | 0 | 0 | 0 | 0 | 85.6081 | 321.5399 | 6832.6488 | 0 | 0 | 0 | 85.6081 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1303 | Tesla: EM Repl BK 4 Bushing |  |  | Alameda | Emergency replacement of Tesla Transformer Bank 4 bushings | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-19 | 21 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561941 | T.0011377 | TESLA: EM REPL BK4 A-B-C BUSHINGS | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-03-01 | NA | 2027-04-23 | NA | NA | FALSE | NA | NA ¦ NA | 3.7572 | 2429.8258 | 0 | 0 | 0 | 0 | 2.6717 | 1.0854 | 2426.0687 | 0 | 0 | 0 | 2.6718 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 2.6691 | 1.0843 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1304 | Tesla: EM Repl BK 6 Bushing |  |  | Alameda | Emergency replacement of Tesla Transformer Bank 6 bushings | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-19 | 24 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5561940 | T.0011526 | TESLA EM RELP BK6 A-B-C BUSHS | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-03-01 | NA | 2027-04-23 | NA | NA | FALSE | NA | NA ¦ NA | 6.7613 | 2593.3299 | 0 | 0 | 0 | 0 | 5.6759 | 1.0854 | 2586.5687 | 0 | 0 | 0 | 5.6759 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 5.6683 | 1.084 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1305 | Vaca Dixon: EM Replace BK 11A Bushings |  |  | Solano | Emergency replacement of Vaca Dixon Bank 11A bushings | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-25 | 21 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 42.1076 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5563185 | T.0011636 | Vaca Dixon: Em Repl BK11 Bushings | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-12-03 | NA | 2028-03-02 | NA | NA | FALSE | NA | NA ¦ NA | 7.5225 | 3763.0126 | 0 | 0 | 0 | 0 | 7.214 | 23.4162 | 115.5325 | 0 | 0 | 0 | 7.2139 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 0 | 6.4926 | 0.27772 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1306 | Vaca Dixon: EM Repl BK 12 A,B,C Bushings |  |  | Solano | Emergency Replacement of Vaca-Dixon substation Transformer Bank #12 Bushings | Substation - Other Equipment | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-03-25 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 42.1076 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5563783 | T.0011773 | Vaca Dixon: Em Repl BK12 Bushings | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-01-04 | NA | 2028-03-29 | NA | NA | FALSE | NA | NA ¦ NA | 2.4071 | 2935.2519 | 0 | 0 | 0 | 0 | 1.4813 | 25.143 | 0 | 0 | 0 | 0 | 1.4814 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 0 | 1.3332 | 0.83316 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1307 | Evergreen: Repl Perimeter Fence |  |  | San Jose, Santa Clara | Emergency Replacement of Evergreen substation security fence | Other - Physical Security | Replace | NA | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | 2026-02-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.3776 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5817340 | T.0011892 | EVERGREEN SUB:EM RPL FENCE | 1 | 65 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-09 | NA | 2027-09-01 | NA | NA | TRUE | NA | NA ¦ NA | 59.7436 | 2411.0189 | 0 | 0 | 0 | 0 | 12.4619 | 539.9284 | 1650.3592 | 0 | 0 | 0 | 12.462 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | NA
1308 | Replace Minor Critical Electrical Equipment |  |  | NA | Forecast placeholder for replacement of minor critical electrical equipment in bus protection zone | Substation - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | EX113776 | NA | NA | NA | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 24000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 6000 | 6000 | 6000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1309 | Misc Replacements |  |  | NA | Replacement of deteriorating "minor" equipment, including but not limited to CT/PT, CCVT, Lightning Arresters, bushings. Failures of these minor equipment have significant impact to reliability. | Substation - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | 5506318 | NA | NA | NA | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 20000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 4000 | 4000 | 4000 | 4000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1310 | Transmission Mobile Transformer Purchase 2027 |  |  | NA | Forecast placeholder for Transmission Mobile Transformer Purchase 2027 to prepare for Emergency transformer failures | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | Ex112789 | NA | NA | NA | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8100.5494 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 8100.5494 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1311 | MAT 66A - ET Sub Repl Miscellaneous Civil Assets |  |  | NA | Placeholder for replacing miscellaneous civil assets, such as buildings, roofs, fence, and roadways | Substation - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | Ex112796 | NA | NA | NA | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 12000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 3000 | 0 | 3000 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1312 | new storage facility for CEM equipment and Mobiles |  |  | NA | Build a new storage facility for CEMs and mobiles for emergency response. Potential location is in Stockton/Modesto/Tracy areas | Substation - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | EX139262 | NA | NA | NA | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 12000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 12000 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1313 | Grand Island Sub Steel Pole Replacement |  |  | Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Substation - Other Equipment | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2026-03-02 | 98 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.9111 | NA | 115 kV | NA | NA | NA | NA | NA | 5800998 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2023-10-25 | 2021-10-31 | 2026-06-01 | Prioritization | NA | TRUE | 150900 | NA ¦ NA | 476.9573 | 912.7128 | 0 | 282.5264 | 216.6367 | -9.1176 | -20.1588 | 438.3261 | 0 | 0 | 0 | 0 | 469.8867 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1314 | TABLE MOUNTAIN: Repl 500 KV CAP BK 4 |  |  | Butte | Replace the existing 500kV No. 4 Series Capacitor at Table Mountain Substation. PG&E designed this project to minimize clearance requirements and impacts to the Pacific AC Intertie by installing the new capacitor unit at a new location, leaving the existing equipment in service during project construction. After the new capacitor is installed, a two-week clearance will put the new equipment in service. Then the vintage capacitor will be removed. In addition, this project will install a new modular protection and control (MPAC) building for SCADA control and communication. | Substation - Reactive Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-20 | 40 | Lifecycle Replacement Analysis | Wires - Location/Route Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | 500 kV | 581 | NA | NA | NA | NA | 5756399 | T.0000495 | Table Mountain Cap Bank No. 4 | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-02-08 | 2017-03-31 | 2018-12-29 | Clearances | NA | TRUE | 18054 | NA ¦ NA | 30519.6299 | 30891.923 | 41.0976 | 20.8197 | 0 | 15.3989 | 9.6951 | 372.2931 | 0 | 0 | 0 | 0 | 30519.6299 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 ¦ 2025 ¦ 2026 | 39.8255 | -1429.6597 | 0 | 14.1473 | 8.9071 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1315 | Potrero Sub. - Hunters Point 115 kV MPAC |  |  | San Francisco, San Francisco | This proposed project will rebuild the entire Hunters Point Substation about 2,000 feet from its current location but is still within the existing PG&E parcel. Rebuilding at a new site has many benefits based on lessons learned from other substation rebuild projects. Specific scope of work includes: • A new 115 kV bus using gas-insulated switchgear (GIS) in a breaker-and-a-half (BAAH) configuration, • 115 kV modular protection, automation, and control (MPAC) panels, • New 12 kV switchgear in a double-bus-double-breaker configuration, • Two new 115/12 kV substation transformers, • Spill prevention control and countermeasure (SPCC) facilities, and • Relocation and potentially undergrounding of the 115 kV transmission and 12 kV outlets. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-12 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5795306 | T.0000590 | Hunters Point Substation | 4 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2033-10-13 | 2017-12-15 | 2039-02-07 | Prioritization | NA | FALSE | 190398 | NA ¦ NA | 80.0174 | 2459.1761 | 12.5324 | 38.6462 | 13.1872 | 7.3101 | 7.338 | 34.1787 | 0 | 0 | 0 | 0 | 79.0139 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $200 Mil - $250 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1316 | Mission Sub. - Hunters Point 115 kV MPAC |  |  | San Francisco, San Francisco | This proposed project will rebuild the entire Hunters Point Substation about 2,000 feet from its current location but is still within the existing PG&E parcel. Rebuilding at a new site has many benefits based on lessons learned from other substation rebuild projects. Specific scope of work includes: • A new 115 kV bus using gas-insulated switchgear (GIS) in a breaker-and-a-half (BAAH) configuration, • 115 kV modular protection, automation, and control (MPAC) panels, • New 12 kV switchgear in a double-bus-double-breaker configuration, • Two new 115/12 kV substation transformers, • Spill prevention control and countermeasure (SPCC) facilities, and • Relocation and potentially undergrounding of the 115 kV transmission and 12 kV outlets. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-02-05 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.83366 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5795305 | T.0000590 | Hunters Point Substation | 4 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2037-08-12 | 2017-12-15 | 2039-03-28 | Prioritization | NA | FALSE | 190398 | NA ¦ NA | 86.8385 | 3751.9771 | 13.784 | 37.2303 | 18.4913 | 8.4292 | 7.8147 | 37.1754 | 0 | 0 | 0 | 0 | 85.7495 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $200 Mil - $250 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1317 | Martin Sub. - Hunters Point 115 kV MPAC |  |  | Brisbane, San Mateo | This proposed project will rebuild the entire Hunters Point Substation about 2,000 feet from its current location but is still within the existing PG&E parcel. Rebuilding at a new site has many benefits based on lessons learned from other substation rebuild projects. Specific scope of work includes: • A new 115 kV bus using gas-insulated switchgear (GIS) in a breaker-and-a-half (BAAH) configuration, • 115 kV modular protection, automation, and control (MPAC) panels, • New 12 kV switchgear in a double-bus-double-breaker configuration, • Two new 115/12 kV substation transformers, • Spill prevention control and countermeasure (SPCC) facilities, and • Relocation and potentially undergrounding of the 115 kV transmission and 12 kV outlets. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-12 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5795304 | T.0000590 | Hunters Point Substation | 4 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2038-06-29 | 2017-12-15 | 2039-05-16 | Prioritization | NA | FALSE | 190398 | NA ¦ NA | 85.6725 | 4829.9467 | 15.2999 | 43.2159 | 12.0606 | 6.2885 | 7.7331 | 33.4421 | 0 | 0 | 0 | 0 | 84.5981 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $200 Mil - $250 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1318 | TABLE MOUNTAIN: Repl 500 KV CAP on BK 3 |  |  | Butte | Replace the existing 500kV Series Capacitor Bank 3 (Table Mountain SC#3) at Table Mountain Substation and associated equipment to support the power transfer on three major transmission paths | Substation - Reactive Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-20 | 39 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | 500 kV | 1797 | 9. Reliability (Low Safety Risk) | 5 | NA | NA | 5767919 | T.0000677 | Table Mountain Cap Bank No. 3 | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-29 | 2022-12-14 | 2022-08-31 | NA | NA | TRUE | 28500 | NA ¦ NA | 35049.1428 | 35443.264 | 10669.387 | 18599.7415 | 24.0489 | 41.454 | 0.7721 | 395.4348 | 0 | 0 | 0 | 0 | 35047.8292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 31159.7609 | 21.2575 | 36.6426 | 0.68253 | 1.1612 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1319 | VACA DIXON: REP 500 KV Series CAP BK 1 |  |  | Solano | Replace the existing 500kV Series Capacitor Bank 1 and associated circuit breakers, and upgrade the associated protection and control systems at Vaca Dixon Substation to support the power transfer on three major transmission paths. | Substation - Reactive Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-25 | 35 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | 1797 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5768878 | T.0001165 | Vaca Dixon 500Kv Replace Bank 1 | 1 | 66 | NA ¦ 5763138 ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-04-08 | 2020-03-31 | 2019-12-13 | NA | NA | FALSE | 26231 | NA ¦ NA | 26677.8491 | 26677.8491 | 41.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26677.8491 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 38.0055 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1320 | TESLA: Replace 500 KV Series CAP BK 2 |  |  | Alameda | Replace the existing 500kV Series Capacitor Bank 2 (Tesla SC#2) at Tesla Substation and associated equipment to support the power transfer on three major transmission paths. | Substation - Reactive Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-19 | 50 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 69.382 | NA | 500 kV | 1797 | 9. Reliability (Low Safety Risk) | 9 | NA | NA | 5760991 | T.0001451 | TESLA REPLACE 500KV SERIES Cap BANK 2 | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-26 | 2020-05-21 | 2021-06-21 | Workforce | NA | FALSE | 36564 | NA ¦ NA | 40004.653 | 40004.653 | 19288.8361 | 82.9707 | 10.7113 | 297.7449 | 152.8776 | 0 | 0 | 0 | 0 | 0 | 40004.653 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 35417.077 | 74.1174 | 9.5683 | 265.9742 | 136.5649 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1321 | CORDELIA: Remove Control Building |  |  | Fairfield, Solano | Removal of the control building at Cordelia Substation. Cordelia Substation is located in the vicinity of the City of Fairfield, within Solano County, California. The old control building located at Cordelia Substation in PG&E’s property has experience many intrusions since the building was decommissioned. Although, the building was boarded up, and recently had the metal doors welded and shut to prevent break-ins, over the years the building has been vacant and has been vandalized several times. In 2015, an emergency project was approved to temporarily seal all entrances with concrete due to the vandalism and continuous break-ins. The concrete building was built in the early 1900s, and has many glass windows and Spanish roof tiles. Due to the building’s vintage it is no longer seismically safe, and it is not cost effective to continually make repairs. We believe the building may also be a historic item that may need to confirm prior to removing the building. | Substation - Modular Protection and Automation Control Building | Removal | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-02-19 | 73 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.9782 | NA | 115 ¦ 60 kV | 20 | 9. Reliability (Low Safety Risk) | 20 | 2.0001 | Non-IGP | 5769863 | T.0001516 | Cordelia: Remove Control Building | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2032-07-30 | NA | 2033-05-03 | NA | NA | FALSE | NA | NA ¦ NA | 614.6378 | 6784.6686 | 157.7779 | 378.599 | 3.3371 | 17.1494 | 40.1566 | 45.0067 | 0 | 0 | 0 | 0 | 606.9298 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1322 | VACA DIXON: REP 500 KV Series CAP BK 2 |  |  | Solano | Replace the existing 500kV Series Capacitor Bank 2 at Vaca Dixon Substation and associated circuit breakers, and upgrade the associated protection and control systems to support the power transfer on three major transmission paths | Substation - Reactive Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-25 | 35 | Lifecycle Replacement Analysis | Wires - Voltage Support/Reactive Support Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | 581 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5759161 | T.0001606 | Vaca Dixon 500kV Replace Bank 2 | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-11-06 | 2018-12-27 | 2019-05-31 | NA | NA | FALSE | 28306 | NA ¦ NA | 29046.7523 | 29046.7523 | 8.9379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29046.7523 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 8.3654 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1323 | POTRERO: Replace SVC Controller |  |  | San Francisco, San Francisco | The average lifespan of SVC systems is 30-35 years, and the PC based controls have a lifespan of 15-17 years. The strategy is to replace the SVC controls on a planned basis as opposed to emergency replacements. The SVC controller replacement project will replace both MACH 2 computers (System A & B), and OWS computer of the SVC controller at Potrero Substation. | Substation - Voltage Support Equipment | Replace | NA | T.0000557 | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-12 | 21 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 230 kV | 1797 | 9. Reliability (Low Safety Risk) | 5 | 5.101 | Non-IGP | 5773178 | T.0002438 | POTRERO SUB: REPLACE SVC CONTROLLER | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-09-02 | 2023-03-31 | 2026-10-26 | Prioritization | NA | TRUE | 5656 | NA ¦ NA | 5624.1251 | 8415.9397 | 171.2375 | 2658.0319 | 321.0718 | 730.9317 | 413.8724 | 2875.5054 | 0 | 0 | 0 | 0 | 5540.4344 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1324 | McCall: Repl Synch Condensers #2 |  |  | Fresno | This project proposes to replace the existing Synchronous Condener #2 at McCall Substation with similar size (40 MVAR) unit to improve the electric transmission system reliability, and safety, and help improve the transmission grid reliability, and efficiency to serve electric customers in Fresno and Madera Counties. | Substation - Reactive Equipment | Replace | NA | T.0001020 | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-06 | 31 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 16.2494 | NA | 230 kV | NA | 9. Reliability (Low Safety Risk) | NA | 4.0101 | Non-IGP | 5773867 | T.0002639 | McCall: Repl Synch Condensers #2 | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 5 | 2030-10-15 | NA | 2030-11-27 | NA | NA | FALSE | NA | NA ¦ NA | 131.59 | 2029.644 | 8.0676 | 105.0255 | 8.4898 | 4.3429 | 3.2635 | 10.1341 | 0 | 0 | 0 | 0 | 129.9398 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1325 | PAUL SWEET: Replace Statcom |  |  | Live Oak CDP, Santa Cruz | The project scope of work includes following: • Replace the existing 1998 vintage StatCom with a modern StatCom • Re-use existing 115 kV interconnection equipment and shunt capacitors • Replace StatCom transformers | Substation - Voltage Support Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-02-03 | 28 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.5678 | NA | 115 kV | 186 | 9. Reliability (Low Safety Risk) | 12 | 4.0101 | Non-IGP | 5777261 | T.0003455 | PAUL SWEET SUB: Replace STATCOM | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-11-02 | NA | 2030-09-16 | NA | NA | FALSE | NA | NA ¦ NA | 92.8294 | 11526.1208 | 11.1307 | 19.2184 | 6.0984 | 3.0735 | 1.6809 | 34.7884 | 400 | 5000 | 6000 | 0 | 91.3324 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1326 | Oak K: Replace CB 152 |  |  | Kensington CDP, Contra Costa | Replace OAKLAND K CB 162, 132, & 152 oil circuit breakers under the 2023 transmission breakers replacement program | Substation - Circuit Breaker | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-05 | 53 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.0084772 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5818865 | T.0003466 | Oakland K: CB 162,132,152 | 3 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-11-05 | 2027-01-08 | 2027-03-31 | NA | NA | TRUE | 6900 | NA ¦ NA | 0 | 1666.4755 | 0 | 0 | 0 | 0 | 0 | 1317.0223 | 349.4532 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1327 | Moraga: Repl Relay on Moraga-Claremont |  |  | Orinda, Contra Costa | Replace OAKLAND K CB 162, 132, & 152 oil circuit breakers under the 2023 transmission breakers replacement program | Substation - Protection Relay | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-03 | 20 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 15.8714 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5563581 | T.0003466 | Oakland K: CB 162,132,152 | 3 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-11-01 | 2027-01-08 | 2028-05-03 | Clearances | NA | FALSE | 6900 | NA ¦ NA | 9.9179 | 260.4097 | 0 | 0 | 0 | 0 | 9.4773 | 36.9634 | 0 | 0 | 0 | 0 | 9.4774 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1328 | STANISLAUS PWR HOUSE SUB UPGRADE |  |  | Tuolumne | The project will increase system performance and reduce fire ignition risk in Calaveras, San Joaquin, Stanislaus, and Tuolumne counties by the following: • Replacement of approximately 30.6 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Manteca No. 1 115 kV Line on the following sections: o Stanislaus Powerhouse (PH) to Tower No. 020/132 (21.2 miles) o Tower No. 021/136 to Tower No. 030/195 (9.4 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Manteca No. 2 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Riverbank Jct SS 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 410 existing structures with new steel structures • Upgrade terminal equipment at Stanislaus PH | Substation - Line Termination | Upgrade/Retrofit | NA | T.0004515 ¦ T.0007979 ¦T.0008743 | Asset Condition | Line Termination | NA | NA | 2026-02-03 | 90 | NA | Other - Deferral | $250 Mil – $300 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.932 | NA | 115 kV | NA | NA | NA | 5.4 | Non-IGP | 5784382 | T.0004301 | Stanislaus Manteca T-Line Rebuild-PH2 | 12 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6382-E | 2021-10-28 | Approved | 2021 | Construction (25%-50%) | 2 | 2025-09-27 | 2030-05-01 | 2027-04-06 | NA | NA | TRUE | 242000 | NA ¦ NA | 1493.29 | 7374.0437 | 148.2934 | 244.9999 | 40.0861 | 42.9278 | 480.3612 | 2503.1876 | 3184.9719 | 444.8095 | 310.6615 | 0 | 956.6684 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | NA
1329 | Melones Switching Station Upgrade |  |  | Tuolumne | The project scope of work includes following: • Rebuild 7.55 miles of 2/0 CU and 4/0 AAC conductors on the Stanislaus-Melones Sw Sta-Manteca No. 1 115 kV Line from Melones Substation to structure 018/115. • Rebuild 7.53 miles of 2/0 CU and 4/0 AAC conductors on the Stanislaus-Melones Sw Sta-Riverbank Jct 115 kV Line from Melones Substation to structure 007/043. The Stanislaus-Melones SS-Manteca No. 1 and Stanislaus-Melones SS-Riverbank Jct SS 115 kV lines are comprised of 2/0 7-strand hemp core copper (2/0 CU) and 4/0 AAC conductors mounted on lattice steel towers. The 2/0 CU conductor is no longer being used in the system and must be repaired using parts that are difficult to procure, which contribute to extended outages caused by conductor failures. Since 2007, a review of historical outage data shows that these T-Lines experienced 27 outages caused by conductor failure. The 2/0 CU has the second highest failure rate per mile of any conductor in the PG&E Transmission System. The poor conductor reliability is exacerbated by the fact that these T-Lines are in a Tier 2 HFTD and that wire down, or asset failure is a potential ignition source. Overall, these lines experienced a total of 186 outages in the past fifteen years. The primary causes of the outages included equipment failure (conductor, connector, insulator, structure, circuit breaker, and relay), animal contacts (bird contact and animal waste), vegetation encroachment, and external contacts (vandalism and safety clearances). In addition, weather events (fire, snow, lightning, rain, and wind) have a secondary role in these outages. These conditions could result in future electrical T-Line outages and fire ignition. Engineering analysis indicated that the Stanislaus-Melones SS-Manteca No. 1 line has approximately 56 twist splices and the Stanislaus-Melones SS-Riverbank Jct SS line has approximately 103 twist splices. A total of 159 twist splices were found in these two lines and the lines are in Tier 2 HFTD. A splice failure in a HFTD can result in a wildfire ignition and twist splices are known to have higher rates of failure when compared to other splices. One existing energy storage generation plant, totaling 99 MW, in the San Joaquin County is currently awaiting this project to allow full deliverability of their generation. Additionally, the Stanislaus-Melones SS-Manteca No. 1 and Stanislaus-Melones SS-Riverbank Jct SS 115 kV lines have been identified as a constraint for full deliverability for the planned generator, which have a signed interconnection agreement. The planned energy storage generation plant is planned to be online by 2027. If the Stanislaus-Melones SS-Manteca No. 1 and Stanislaus-Melones SS-Riverbank Jct SS 115 kV lines are not reconductored, the full deliverability of existing and planned generation will be impacted which will jeopardize achieving California’s Renewable Portfolio Standard goals and may lead to financial penalties. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0004301 ¦ T.0008743 ¦ T.0007979 | Reliability | Line Termination | NA | NA | 2026-02-05 | 90 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.85823 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5809024 | T.0004515 | Stan-Melones Tap Lines: Repl CU cond | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7445-E | 2024-12-03 | Approved | 2024 | Planning | 5 | 2026-04-02 | 2028-12-30 | 2027-02-26 | NA | NA | TRUE | 49600 | NA ¦ NA | 101.4729 | 1827.4982 | 0 | 0 | 0 | 0 | 99.8061 | 163.6921 | 502.3712 | 881 | 0 | 0 | 99.8061 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | NA
1330 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NA | NA | 2026-03-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 77.6619 | NA | 230 kV | NA | NA | NA | NA | NA | 5790590 | T.0006452 | Electric Transmission Substation Security Upgrade | 9 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-18 | 2023-08-15 | 2022-10-05 | NA | NA | FALSE | 20060 | NA ¦ NA | 1652.4367 | 1652.4367 | 15.1034 | 1612.5533 | 53.167 | -28.387 | 0 | 0 | 0 | 0 | 0 | 0 | 1652.4367 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 1574.8922 | 51.3979 | -27.4424 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1331 | Geysers 3 & 4: Decommission sub |  |  | Sonoma | This planned project will convert Eagle Rock 115 kV bus to DBSB, decommission Geysers 3 & 4, and build 1.5 miles between Eagle Rock and Cloverdale Substations | Substation - Multiple | Removal | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-02 | 54 | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.31702 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5799858 | T.0007732 | EAGLE ROCK: CONVERT 115kV BUS | 3 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-03-30 | NA | 2028-08-14 | NA | NA | FALSE | NA | NA ¦ NA | 5.0541 | 1592.4643 | 0 | 4.1993 | 0 | 0 | 0.3422 | 98.0871 | 200 | 500 | 0 | 0 | 4.5414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1332 | Vaca Dixon: Reloc Trai T Gas Pipeline |  |  | Solano | After reviewing the drivers for the Replacement, it was determined that eliminating the High Consequence Area, HCA, driver would be the less impactful & most cost-effective approach. The driver for the HCA is an identified site within the potential impact radius, PIR. This Identified-Site, ID-Site, is within Vacaville Substation, which is a PG&E facility. The ID-Site is a 3-wide mobile trailer office that the substation supervisor & his crew occupy. The existing trailer is rented from Pacific Mobile Structure, costing PG&E approximately $3266 monthly, roughly $40k annually. After consulting with stakeholders, including the HCA Team, we decided that the relocation/removal of the existing trailer outside of the PIR, is the best approach to eliminating risk while achieving the objective of this project. The project team has identified a new site for the trailer outside the PIR. The HCA Team has performed its preliminary review and confirmed that the new location will be outside the PIR. The removal of the existing trailer, purchase of a 4-wide trailer & site improvements are expected to cost approximately 2 million, which yields 1.8 million of savings from the original cost for the replacement/DE (3.8 million). | Other | Relocate | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | 2026-03-25 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 42.1076 | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | 5818055 | T.0010141 | Vaca Dixon Reloc Trai T Gas Pipeline | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-07-08 | 2026-04-13 | 2026-03-31 | NA | NA | TRUE | 4041 | NA ¦ NA | 3990.6757 | 4002.6478 | 0 | 0 | 0 | 0 | 2671.3467 | 1331.301 | 0 | 0 | 0 | 0 | 2671.3467 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1333 | Contra Costa: Remove Wave Trap |  |  | Antioch, Contra Costa | This planned project will replace Las Positas Substation’s failed CKT SW 286 and Motor Operated Air Switch (MOAS) 289 with four (4) 230 kV circuit breakers (CBs) that will be interconnected in a “Ring” bus configuration, install one (1) new control building to be installed near the 60 kV yard, install new relays on all new 230 kV CBs (Nos. 222, 232, 262, 272). This planned project is needed to maintain safe and reliable power to the East Bay area and will support PG&E top-level initiatives such as improved service reliability, improved operational flexibility, and reducing operating costs. | Substation - Switch | Replace | NA | NA | Asset Condition | Age/Condition - Replace Switches | NA | NA | 2026-03-03 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 15.1779 | NA | 230 kV | NA | NA | NA | NA | NA | 5548159 | T.0000185 | Las Positas:Convert 230kV Bus & Repl Rly | 5 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-05-01 | 2023-06-30 | 2023-06-21 | NA | NA | FALSE | 7851 | NA ¦ NA | 623.0288 | 623.0288 | 0 | 283.626 | 338.7136 | 0.6892 | 0 | 0 | 0 | 0 | 0 | 0 | 623.0288 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 265.8115 | 317.4389 | 0.64586 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1334 | LAS POSITAS: 230KV RING CONV & BLDG INST |  |  | Livermore, Alameda | This planned project will replace Las Positas Substation’s failed CKT SW 286 and Motor Operated Air Switch (MOAS) 289 with four (4) 230 kV circuit breakers (CBs) that will be interconnected in a “Ring” bus configuration, install one (1) new control building to be installed near the 60 kV yard, install new relays on all new 230 kV CBs (Nos. 222, 232, 262, 272). This planned project is needed to maintain safe and reliable power to the East Bay area and will support PG&E top-level initiatives such as improved service reliability, improved operational flexibility, and reducing operating costs. | Substation - Switch | Replace | NA | NA | Asset Condition | Age/Condition - Replace Switches | NA | NA | 2026-04-02 | 32 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.2184 | NA | 230 kV | NA | 9. Reliability (Low Safety Risk) | 6 | NA | NA | 5785643 | T.0000185 | Las Positas:Convert 230kV Bus & Repl Rly | 5 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-01 | 2023-06-30 | 2023-06-30 | NA | NA | FALSE | 7851 | NA ¦ NA | 7224.4324 | 7224.4324 | 2937.8898 | 3932.6052 | 2923.8638 | 106.4029 | -3492.0687 | 6.8493 | 0 | 0 | 0 | 0 | 7217.5831 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | -728.0504 | 0 | 9928.1768 | 99.1134 | -2871.8221 | 6.7858 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1335 | LAS POSITAS: 230KV RING CONV Phase 2 |  |  | Livermore, Alameda | This planned project will replace Las Positas Substation’s failed CKT SW 286 and Motor Operated Air Switch (MOAS) 289 with four (4) 230 kV circuit breakers (CBs) that will be interconnected in a “Ring” bus configuration, install one (1) new control building to be installed near the 60 kV yard, install new relays on all new 230 kV CBs (Nos. 222, 232, 262, 272). This planned project is needed to maintain safe and reliable power to the East Bay area and will support PG&E top-level initiatives such as improved service reliability, improved operational flexibility, and reducing operating costs. | Substation - Switch | Replace | NA | NA | Asset Condition | Age/Condition - Replace Switches | NA | NA | 2026-04-02 | 32 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.2184 | NA | 230 kV | NA | NA | NA | 3.0011 | Non-IGP | 5798813 | T.0000185 | Las Positas:Convert 230kV Bus & Repl Rly | 5 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-02 | 2023-06-30 | 2024-06-18 | Project Design | NA | TRUE | 7851 | NA ¦ NA | 7035.4293 | 7036.9486 | 0 | 6.01 | 26.2161 | 2619.5708 | 4373.8707 | 11.281 | 0 | 0 | 0 | 0 | 7025.6676 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 2390.3043 | 4584.882 | 9.6887 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1336 | Cottonwood Sub repl 115kV SW133,135,163 |  |  | Cottonwood CDP, Shasta | This project will replace 115kV switches 131, 133, 135, 161, 163, 165 and associated equipment as required at Cottonwood Substation. Maintenance has identified 115kV switches 131, 133, 135, 161, 163 and 165 to be ergonomically unsafe, old, and difficult to operate. The replacement of these switches will make their operation safe and reliable while the relocation of HVCB 132 will ensure the switches an extended life expectancy. The completion of this project is essential to maintain safe and reliable power to electric customers served from Cottonwood substation. | Substation - Switch | Replace | NA | NA | Asset Condition | Age/Condition - Replace Switches | NA | NA | 2026-03-19 | 19 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 26.1945 | NA | 115 kV | NA | NA | NA | NA | NA | 5792847 | T.0006463 | COTTONWOOD SUB REPL 115kV SW133,135,163 | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-31 | 2022-11-04 | 2022-12-22 | NA | NA | FALSE | 3800 | NA ¦ NA | 1753.3812 | 1753.3812 | 137.1829 | 1517.9465 | 95.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1753.3812 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 1496.7646 | -85.6982 | 171.9473 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1337 | EAST PORTAL SUB - REPL 115KV MOAS 117 |  |  | Orinda, Contra Costa | The project scope of work includes the following: • Replace the 115kV MOAS 117 on the Sobrante-Claremont line • Replace the 115kV MOAS 119 on the Sobrante-Claremont line • Upgrade associated equipment if required East Portal is a single customer distribution substation and it is in Contra Costa County in the Concord Division. The Motor Operated Air Switch (MOAS) 117 & 119 at East Portal are in service for the last 50 years and are at the end of their useful life. Both serve as 115kVline switching to Sobrante and Claremont. Based on the age and performance, it was recommended by Asset Strategy to replace the MOAS 117 & 119 at East Portal. The Sobrante-Grizzly-Claremont #1 115 kV line associated with the switches is rated less than 1200 Amps. CB 172 maximum load is only 125 A as it supplies only the Bart Bank rated 25 MVA. The new SWs 117 and 119 will be rated for 1200 A like the existing ones. | Substation - Switch | Replace | NA | NA | Asset Condition | Age/Condition - Replace Switches | NA | NA | 2026-03-06 | 54 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 0.37448 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5793673 | T.0006778 | East Portal Sub - Repl 115kV MOAS 117 | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2031-02-21 | NA | 2031-04-17 | NA | NA | FALSE | NA | NA ¦ NA | 115.2855 | 1196.9504 | 70.5678 | 31.7848 | 8.9806 | 3.9523 | 0 | 7.721 | 0 | 0 | 0 | 0 | 115.2855 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1338 | Bellota: Repl 230 kV SWs 417,419,477,479 |  |  | San Joaquin | Bellota (4) 230kV SWs have been targeted for replacement as part of the PG&E Transmission Proactive Disconnect Air Swithches Replacement Program. The prioritization criteria for this program is primarily based on maintenence condition assessment. The predominant factors include operating condition, age, safety, and impact of consequence of an in-service failure, availability of spare parts. | Substation - Switch | Replace | NA | NA | Asset Condition | Age/Condition - Replace Switches | NA | NA | 2026-03-14 | 78 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | 3.0011 | Non-IGP | 5799119 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-03-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 900 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1339 | Stagg sub - repl (14) 60 kV vintage SWs 11, 13, 15, 23, 25, 31, 33, 35, 41, 42, 45, 51, 52 and 55 |  |  | Stockton, San Joaquin | Stagg sub (14) 60kV SWs have been targeted for replacement as part of the PG&E Transmission Proactive Disconnect Air Swithches Replacement Program. The prioritization criteria for this program is primarily based on maintenence condition assessment. The predominant factors include operating condition, age, safety, and impact of consequence of an in-service failure, availability of spare parts. | Substation - Switch | Replace | NA | NA | Asset Condition | Age/Condition - Replace Switches | NA | NA | 2026-03-06 | 57 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 8.5909 | NA | 60 kV | NA | NA | NA | 3.0011 | Non-IGP | EX112115 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-03-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 500 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1340 | Metcalf - Switches identified by Maintenance personnel 500KV Switches |  |  | Santa Clara | Metcalf 500kV Switches (711,713,723,771,781,811,813,821,823,921,923,931) have been identified for replacement as part of the PG&E transmission equipment replacent | Substation - Switch | Replace | NA | NA | Asset Condition | Age/Condition - Replace Switches | NA | NA | 2026-03-05 | 61 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 500 kV | NA | NA | NA | 3.0011 | Non-IGP | Ex112771 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-03-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1341 | SYSPLN - 66E - Climate Change |  |  | NA | Forecast placeholder for to address climate issues such as flooding mitigations. Mitigations may include walls, substation grading, etc. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | EX113778 | NA | NA | NA | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 12000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 3000 | 0 | 3000 | 3000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1342 | MARTIN: Retrofit 230 KV Bus |  |  | Brisbane, San Mateo | This project provides seismic upgrade of the Martin Substation 230kV System. The scope will include the following activities•Seismic retrofit of 230kV Bus components per IEEE 693•Replace switches and insulators with seismic qualified equipment•Provide flexible connections to allow for lateral movement during earthquakes Under this AA, the team will:•Finalize the scope of work•Perform preliminary engineering•Evaluate Construction bids•Develop construction sequence•Develop job estimate & schedule. | Substation - Structure | Replace | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | 2026-03-12 | 50 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 230 kV | 470 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5764038 | T.0000028 | Martin Sub: 230kV Bus Retrofit | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-11-26 | 2019-07-09 | 2019-05-18 | NA | NA | FALSE | 8393 | NA ¦ NA | 9047.7609 | 9047.7609 | 24.5981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9047.7609 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 23.0115 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1343 | Biola New Structures&Switches: CB12 & 22 |  |  | Fresno | This equipment is nominated for replacement based on an assessment study performed by PG&E’s Civil Engineering team on transmission class structures in substations. | Substation - Structure | Replace | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | 2026-02-20 | 27 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | 0.87974 | NA | 70 kV | 236 | 9. Reliability (Low Safety Risk) | NA | 3.0011 | Non-IGP | 5759178 | T.0000910 | BIOLA: INSTALL T-SCADA ON CB12 & 22 | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2031-01-23 | NA | 2031-03-25 | NA | NA | FALSE | NA | NA ¦ NA | 14.4527 | 62.1283 | 0.9953 | 0.8186 | 1.8847 | 0.4955 | 0 | 0.968 | 0 | 0 | 0 | 0 | 14.4527 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1344 | VACA DION: Mitigate ENV Comp |  |  | Solano | This project will upgrade the existing Spill Prevention Control and Containment (SPCC) plan in the 500kV yard at Vaca Dixon Substation to mitigate the environmental compliance issues identified by the Environment Management and Civil Engineering departments. There have been drainage issues at Vaca Dixon Substation for years that haven’t been resolved. The drainage issues raise compliance and safety risks, and other sensitive issues to adjacent wetland areas. | Substation - Structure | Replace | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | 2026-03-25 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 ¦ 230 ¦ 115 ¦ 60 kV | 776 | NA | NA | NA | NA | 5772490 | T.0002609 | VACA DIXON SUB:500KV ENV COMP MITIGAT | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-06-13 | 2017-10-31 | 2017-11-15 | NA | NA | FALSE | 7446.65 | NA ¦ NA | 7261.4178 | 7261.4178 | 51.2942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7261.4178 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 51.2211 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1345 | New Pad for CEM Banks |  |  | Alameda | Extend the existing CEM transformer foundation at the southwest corner of the sub | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | 2026-03-19 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | NA | NA | NA | NA | NA | NA | 5546164 | T.0007412 | New Pad for CEM Banks | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | NA | 2023-06-12 | NA | NA | FALSE | NA | NA ¦ NA | 1251.336 | 1251.336 | 0 | 67.6576 | 1153.9997 | 0.8935 | 27.1605 | 1.6247 | 0 | 0 | 0 | 0 | 1249.7113 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 60.8918 | 1038.5997 | 0.8041 | 24.4443 | 1.4623 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1346 | Herndon: Build New Transformer Pad |  |  | Fresno, Fresno | Increase CEM stock for 500/230kV 374MVA single-phase transformer and install a new storage pad at Herndon substation. | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | 2026-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 13.3414 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1 | Non-IGP | 5555299 | T.0009784 | 500/230kV 1-ph 374MVA New CEM Bank | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-03-02 | 2027-12-30 | 2026-05-29 | NA | NA | TRUE | 7540 | NA ¦ NA | 585.2588 | 953.3983 | 0 | 0 | 0 | 24.8999 | 392.916 | 535.5824 | 0 | 0 | 0 | 0 | 417.8159 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 24.8999 | 392.916 | 167.4429 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1347 | Laureles: repl 60kV lattice steel pole & foundation |  |  | Carmel Valley Village CDP, Monterey | This equipment is nominated for replacement based on an assessment study performed by PG&E’s Civil Engineering team on transmission class structures in substations. | Substation - Structure | Replace | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | 2026-02-09 | 126 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.1948 | NA | 60 kV | NA | NA | NA | 3.0011 | Non-IGP | EX111071 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1300 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 650 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1348 | Palermo: repl 60kV lattice steel pole & foundation |  |  | Palermo CDP, Butte | This equipment is nominated for replacement based on an assessment study performed by PG&E’s Civil Engineering team on transmission class structures in substations. | Substation - Structure | Replace | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | 2026-03-13 | 120 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 8.0464 | NA | 60 kV | NA | NA | NA | 3.0011 | Non-IGP | EX111072 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1300 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 650 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1349 | Rocklin: repl 2-70kV lattice steel pole & foundation |  |  | Rocklin, Placer | This equipment is nominated for replacement based on an assessment study performed by PG&E’s Civil Engineering team on transmission class structures in substations. | Substation - Structure | Replace | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | 2026-02-12 | 46 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.45068 | NA | 70 kV | NA | NA | NA | 3.0011 | Non-IGP | EX111074 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1350 | Oakland K: Replace 115kV Lattice Structure |  |  | Oakland, Alameda | In 2015, a temporary solution of adding cross bars to address buckling of the 115kV lattice structures was completed. This was only a temporary solution to a permanent fix. Replacement of 115 kV lattic structures is needed | Substation - Structure | Replace | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | 2026-03-05 | 106 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.9974 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | Ex112785 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1800 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 900 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1351 | EO-SYSPLN 66E - ET Sub Repl Other Equip |  |  | NA | Forecast placeholder for civil structure replacements | Substation - Structure | Replace | NA | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | 5533277 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 2000 | 2000 | 2000 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1352 | 66I placeholder-replace cement/glass insulators |  |  | NA | Insulators have been targeted for replacement as part of the PG&E Transmission Insulators Replacement Program. The prioritization criteria for this program is primarily based on maintenence condition assessment. The predominant factors include weathered, age, safety, and impact of consequence of an in-service failure, availability of spare parts. | Substation - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Insulators | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | Tx001554 | NA | NA | NA | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 500 | 500 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1353 | North Tower Sub: Replace OB Insulators |  |  | Vallejo, Solano | This project will replace the 115kV OB insulators at North Tower Substation. Improve safety and human performance. Improves employee safety by eliminating aging and deteriorated equipment that have high risk of catastrophic failure. | Substation - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Insulators | NA | NA | 2026-03-09 | 67 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 5.8111 | NA | 115 kV | 445 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5770522 | T.0001823 | North Tower Sub: Replace OB Insulators | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-16 | 2020-12-31 | 2022-11-10 | Prioritization | NA | FALSE | 1100 | NA ¦ NA | 1640.81 | 1640.81 | 690.2532 | 615.4883 | -6.1656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1640.81 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 1620.5193 | -6.055 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1354 | Brighton: Replace OB Insulators |  |  | Sacramento, Sacramento | This project is intended to replace the targeted 20” cap and pin insulators manufactured by Ohio Brass (Catalog # 35126) that were installed at Brighton Substation. Brighton substation was identified as having the targeted 115kV OB insulators and will be replaced under the program. By completing this project, the Company will be diligently addressing known reliability issues attributed to the existing equipment. | Substation - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Insulators | NA | NA | 2026-03-03 | 58 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 6.4413 | NA | 115 kV | 445 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5784147 | T.0004198 | Brighton: Replace OB insulators | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-01-14 | 2021-09-21 | 2022-02-23 | NA | NA | FALSE | 3706 | NA ¦ NA | 3512.7219 | 3512.7219 | 1074.7532 | 324.7567 | 3.9181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3512.7219 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 2855.0867 | 3.1274 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1355 | MWC 66 Fire Protection Upgrades |  |  | NA | Bucket for Fire Protection Upgrades. Fire protection projects are nominated considering life-safety issues, and business considerations (resource allocation, asset preservation and continuity of operations). Substation Asset Strategy then prioritizes the substations considering such factors as safety hazard to personnel, substation criticality, customer and system impact, facility condition and environmental issues. | Substation - Multiple | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | 5513328 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 500 | 500 | 500 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1356 | SF MARTIN: Repl Shunt Reactor HZ2 |  |  | Brisbane, San Mateo | Replace existing 230kV three (3) single phase reactors on HZ-2 line with three (3) new 230 kV reactors and make provisions for a spare in the future. | Substation - Reactive Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Reactors | NA | NA | 2026-03-12 | 48 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 230 kV | 18 | 9. Reliability (Low Safety Risk) | 4 | NA | NA | 5779901 | T.0000894 | SF H (MARTIN)-REPL SHUNT REACTOR BK HZ-2 | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-02-19 | 2020-11-13 | 2021-04-13 | NA | NA | FALSE | 11190 | NA ¦ NA | 8077.3588 | 8077.3588 | 3013.0043 | 11.9233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8077.3588 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 7143.5416 | 10.4875 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1357 | Los Banos: Replace Tertiary Reactors |  |  | Merced | The 500kV Air Core tertiary reactor insulators have been identified, by the Substation Standards group, as having a high rate of failure. The cause of the failure of the insulator is mechanical stress on the aging glass of the cap and pin insulator. There are 4 tertiary reactors at Los Banos 500kV bank1 and currently reactor 1302 is offline due to NG insulators. It has been determined that it is best to replace all four reactors (1301, 1302, 1303 & 1304). The fence will be replaced by nonconductive fence. Depending on the size of the new reactors, the fenced area may be increased to keep clearances and safe working distances. The existing animal abatement on the equipment will be reused. If the new reactor placement allows, the conductors and insulator support structures will be reused | Substation - Reactive Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Reactors | NA | NA | 2026-03-06 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 53.2803 | NA | 500 kV | NA | NA | NA | NA | NA | 5796645 | T.0007249 | Los Banos Replace Tertiary Reactors | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-06-20 | 2022-11-30 | 2022-11-04 | NA | NA | FALSE | 3910 | NA ¦ NA | 5217.6354 | 5217.6354 | 211.7312 | 4587.5226 | 406.7182 | 11.6634 | 0 | 0 | 0 | 0 | 0 | 0 | 5217.6354 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 4101.9532 | 345.9948 | 9.922 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1358 | Purchase 2 sets CEM Shunt Reactors |  |  | NA | Purchase 2 sets of 13.4kV 15 MVAR CEM Shunt Reactors. 500kV Tertiary Shunt Reactor Replacement Program addresses high risk of failure 15MVAR shunt reactors connected to the tertiary of 500kV banks to supply reactance and reduce overvoltage. Due to high failure and lack of proactive replacement CEM equipment needs to be procured. | Substation - Reactive Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Reactors | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 kV | NA | NA | NA | 3.002 | NA | 5547495 | T.0007699 | Purchase 2 sets CEM Shunt Reactors | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2022-12-31 | 2022-11-30 | NA | NA | FALSE | 500 | NA ¦ NA | 1205.0473 | 1205.0473 | 0 | 0 | 2.6628 | 1202.3845 | 0 | 0 | 0 | 0 | 0 | 0 | 1205.0473 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 1205.0473 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1359 | Round Mtn: Rep Ter Shnt Reac 1301&1303 |  |  | Round Mountain CDP, Shasta | This project proposes to replace Round Mountain tertiary shunt reactors 1301, and 1303 to address elevated risk of failure due to age and condition. PG&E has 40 in-service shunt reactors on 13.8kV tertiary buses of 500/230kV transformers. Since 2012 PG&E has four reactor failures causing fires and heavy smoke. Failures of reactors can remove 500kV/230kV transformers out of service from the electric transmission grid for an extended period. Procurement of Shunt Reactor can take more than 6 months. | Substation - Reactive Equipment | Replace | NA | EX112766 ¦ EX112765 | Asset Condition | Age/Condition - Replace Reactors | NA | NA | 2026-03-09 | 39 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | 29.1389 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5799660 | T.0007862 | Round Mtn: Rep Ter Shnt Reac 1301&1303 | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-08-24 | NA | 2027-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 15.2888 | 3323.6213 | 0 | 2.6366 | 0.4145 | 1.2092 | 0 | 928.8783 | 2390.1988 | 0 | 400 | 1500 | 4.2604 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1360 | Round Mountain: Repl 500kV SCB #1 |  |  | Round Mountain CDP, Shasta | Round Mountain 500kV SCB #1 have been targetted for replacement as part of the PG&E Reactive Equipment Replacement Program. Special reactive equipment gets replace on 30-year interval. | Substation - Reactive Equipment | Replace | NA | EX112766 ¦ T.0007862 | Asset Condition | Age/Condition - Replace Reactors | NA | NA | 2026-03-09 | 28 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | Ex112765 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 6000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 2000 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1361 | Round Mountain: Repl 500kV SCB #2 |  |  | Round Mountain CDP, Shasta | Round Mountain 500kV SCB #2 have been targetted for replacement as part of the PG&E Reactive Equipment Replacement Program. Special reactive equipment gets replace on 30-year interval. | Substation - Reactive Equipment | Replace | NA | EX112765 ¦ T.0007862 | Asset Condition | Age/Condition - Replace Reactors | NA | NA | 2026-03-09 | 28 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | Ex112766 | TBD | TBD | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 6000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 2000 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1362 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.2 | Non-IGP | EX113339 | NA | Electric Transmission Substation Security Upgrade | NA | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 11971.924 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 11971.924 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1363 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-19 | NA | NA | Wires - Replacement Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 26.1945 | NA | 230 ¦ 115 ¦ 60 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | 1 | NA | NA | 5773524 | T.0002572 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-09-16 | 2020-03-30 | 2020-08-31 | NA | NA | FALSE | 10388 | NA ¦ NA | 11511.6611 | 11511.6611 | 1128.7467 | 236.3895 | 1.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11511.6611 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1091.3126 | 228.5498 | 1.8331 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1364 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-03 | NA | NA | Wires - Replacement Alternative | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8314 | NA | 230 ¦ 115 ¦ 60 kV | 197 | 8. Compliance/Commitments With Low Safety Risk | 6 | NA | NA | 5773545 | T.0002574 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-08-30 | 2021-11-30 | 2022-03-15 | NA | NA | FALSE | 4989 | NA ¦ NA | 3371.1736 | 3371.1736 | 2401.8993 | 504.609 | 1.3711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3371.1736 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 3369.8025 | 1.371 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1365 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-13 | NA | NA | Wires - Replacement Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 14.7021 | NA | 230 ¦ 115 ¦ 60 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | 6 | NA | NA | 5773541 | T.0002579 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-03-02 | 2020-01-31 | 2020-03-05 | NA | NA | FALSE | 3555 | NA ¦ NA | 3268.1794 | 3268.1794 | -158.2948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3268.1794 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -149.8677 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1366 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 12.8702 | NA | 230 ¦ 115 ¦ 60 kV | 197 | 8. Compliance/Commitments With Low Safety Risk | 13 | NA | NA | 5773531 | T.0002580 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-02-22 | 2021-02-10 | 2021-08-06 | NA | NA | FALSE | 4990 | NA ¦ NA | 4766.0764 | 4766.0764 | 3852.9363 | 118.7668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4766.0764 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 4581.9377 | 117.0205 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1367 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.7615 | NA | 230 kV | 197 | 8. Compliance/Commitments With Low Safety Risk | 22 | NA | NA | 5773980 | T.0002584 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-01-04 | 2020-07-16 | 2021-03-08 | Workforce | NA | FALSE | 4313 | NA ¦ NA | 3196.0945 | 3196.0945 | 1247.7604 | 9.3775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3196.0945 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 3106.282 | 9.1314 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1368 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-09 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 10.5414 | NA | 230 ¦ 115 kV | 197 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5773543 | T.0002586 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-06-10 | 2018-06-29 | 2019-11-21 | Workforce | NA | FALSE | 2681 | NA ¦ NA | 2628.7186 | 2628.7186 | 31.8091 | 7.4502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2628.7186 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 29.9589 | 7.0169 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1369 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.9486 | NA | 230 ¦ 115 ¦ 60 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | 5 | NA | NA | 5773537 | T.0002589 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-08-07 | 2019-12-31 | 2020-11-16 | Prioritization | NA | FALSE | 4461 | NA ¦ NA | 5383.2247 | 5383.2247 | 45.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5383.2247 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 44.5375 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1370 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-11 | NA | NA | Wires - Replacement Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.4076 | NA | 230 ¦ 115 ¦ 60 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | 2 | NA | NA | 5773528 | T.0002590 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-03-31 | 2020-01-31 | 2020-06-30 | NA | NA | FALSE | 3597 | NA ¦ NA | 3351.3124 | 3351.3124 | -190.1749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3351.3124 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -181.9562 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1371 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-03 | NA | NA | Wires - Replacement Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.7091 | NA | 230 ¦ 60 kV | 197 | 8. Compliance/Commitments With Low Safety Risk | 4 | NA | NA | 5773539 | T.0002591 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-07-15 | 2018-08-06 | 2020-03-26 | Prioritization | NA | FALSE | 2478 | NA ¦ NA | 3050.3881 | 3050.3881 | 11.4187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3050.3881 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 11.0051 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1372 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-04 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 11.0767 | NA | 230 ¦ 115 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | 3 | NA | NA | 5773554 | T.0002592 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-08 | 2020-09-30 | 2022-06-13 | Prioritization | NA | FALSE | 3692 | NA ¦ NA | 3986.8661 | 3986.8661 | 1229.1681 | 175.3528 | 0.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3986.8661 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 3986.1174 | 0.7487 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1373 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.7504 | NA | 230 ¦ 115 ¦ 70 kV | 445 | 8. Compliance/Commitments With Low Safety Risk | 19 | 5.2 | Non-IGP | 5776721 | T.0003350 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-03 | 2021-12-31 | 2025-10-24 | Prioritization | NA | TRUE | 7500 | NA ¦ NA | 9312.4395 | 9329.1198 | 2095.3141 | 4582.9214 | 68.5882 | 854.155 | 1296.3518 | 5.6146 | 0 | 0 | 0 | 0 | 9323.5052 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 9323.5052 | -11.0657 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1374 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-02-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 kV | NA | NA | NA | 3.0011 | Non-IGP | 5801703 | T.0005697 | Electric Transmission Substation Security Upgrade | 10 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-11-03 | 2024-12-30 | 2028-01-18 | Prioritization | NA | FALSE | 17200 | NA ¦ NA | 580.3864 | 3245.3357 | 0 | 75.1135 | 334.5051 | 79.1428 | 79.8074 | 106.4832 | 0 | 0 | 0 | 0 | 568.5688 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1375 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-03 | NA | NA | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.1779 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5793671 | T.0006787 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-07-30 | 2024-05-21 | 2025-02-28 | Clearances | NA | TRUE | 2198 | NA ¦ NA | 3404.3904 | 3408.918 | 188.8318 | 112.4012 | 29.0939 | 2181.8247 | 859.57 | 37.1963 | 0 | 0 | 0 | 0 | 3371.7216 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 3275.6943 | 31.6989 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1376 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Replace | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-05 | NA | NA | Other - Deferral | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.851 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5793672 | T.0006889 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-01-19 | 2024-09-26 | 2027-03-16 | Prioritization | NA | TRUE | 960 | NA ¦ NA | 459.2595 | 2149.8816 | 149.4215 | 131.4721 | 29.366 | 130.3091 | 18.6908 | 81.9483 | 1608.6739 | 0 | 0 | 0 | 459.2595 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1377 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-20 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 47.516 | NA | 500 ¦ 230 ¦ 115 ¦ 60 kV | NA | NA | NA | 5.2 | Non-IGP | 5799099 | T.0007753 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-04-21 | 2025-08-07 | 2025-08-29 | NA | NA | TRUE | 3800 | NA ¦ NA | 2208.7841 | 2275.5286 | 0 | 4.8832 | 187.4474 | 203.7242 | 1587.3028 | 292.171 | 0 | 0 | 0 | 0 | 1983.3576 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1983.3576 | 225.4265 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1378 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-19 | NA | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 500 ¦ 230 ¦ 115 kV | NA | NA | NA | 5.2 | Non-IGP | 5799100 | T.0007754 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-09-15 | 2026-12-31 | 2026-10-14 | NA | NA | TRUE | 9900 | NA ¦ NA | 1055.6604 | 8134.7386 | 0 | 0 | 209.5013 | 104.6913 | 650.6361 | 7016.6431 | 153.2668 | 0 | 0 | 0 | 964.8288 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1379 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-06 | NA | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 53.2803 | NA | 500 ¦ 230 ¦ 70 kV | NA | NA | NA | 5.2 | Non-IGP | 5799101 | T.0007755 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-06-02 | 2026-05-31 | 2026-03-20 | NA | NA | TRUE | 8500 | NA ¦ NA | 2699.8265 | 3861.88 | 0 | 0 | 204.6607 | 246.2594 | 1487.4589 | 1913.6051 | 0 | 0 | 0 | 0 | 1938.3791 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1380 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-03 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 ¦ 230 ¦ 115 kV | NA | NA | NA | 5.2 | Non-IGP | 5799102 | T.0007756 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-18 | 2026-09-30 | 2026-07-08 | NA | NA | TRUE | 3400 | NA ¦ NA | 366.2617 | 1472.0602 | 0 | 0 | 66.633 | 179.5716 | 102.5546 | 1081.0357 | 42.2654 | 0 | 0 | 0 | 348.7592 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1381 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 77.6619 | NA | 500 ¦ 230 ¦ 70 kV | NA | NA | NA | 5.2 | Non-IGP | 5799103 | T.0007757 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-10 | 2026-10-30 | 2026-08-03 | NA | NA | TRUE | 3500 | NA ¦ NA | 401.036 | 1951.3928 | 0 | 0 | 61.2022 | 183.8734 | 138.8054 | 1531.218 | 36.2939 | 0 | 0 | 0 | 383.8809 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1382 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-17 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5811039 | T.0007758 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-14 | 2026-12-31 | 2026-12-03 | NA | NA | TRUE | 15800 | NA ¦ NA | 476.3168 | 8621.6328 | 0 | 0 | 0 | 94.1687 | 313.0814 | 7814.3827 | 400 | 0 | 0 | 0 | 407.2501 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1383 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-17 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | 230 ¦ 115 ¦ 60 kV | NA | NA | NA | 5.2 | Non-IGP | 5799104 | T.0007758 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-09-15 | 2026-12-31 | 2025-09-30 | NA | NA | TRUE | 15800 | NA ¦ NA | 723.9036 | 723.9036 | 0 | 0 | 174.0853 | 200.0262 | 342.7419 | 7.0501 | 0 | 0 | 0 | 0 | 716.8535 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 650.0851 | 6.3452 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1384 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 500 ¦ 230 ¦ 115 kV | NA | NA | NA | 5.2 | Non-IGP | 5799105 | T.0007759 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-02 | 2026-10-02 | 2026-10-02 | NA | NA | TRUE | 7000 | NA ¦ NA | 776.3716 | 5094.1454 | 0 | 0 | 166.61 | 199.8699 | 239.0234 | 4486.2351 | 0 | 0 | 0 | 0 | 605.5033 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1385 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-20 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 47.516 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5809935 | T.0009655 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-08-25 | 2026-08-07 | 2026-09-30 | NA | NA | TRUE | 4900 | NA ¦ NA | 328.6688 | 3365.0751 | 0 | 0 | 0 | 34.7931 | 276.385 | 2936.4367 | 117.4603 | 0 | 0 | 0 | 311.1781 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1386 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-20 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807540 | T.0009655 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-09-03 | 2026-08-07 | 2025-10-02 | NA | NA | TRUE | 4900 | NA ¦ NA | 2003.1069 | 2637.5106 | 0 | 0 | 0 | 630.6351 | 1089.4867 | 317.3888 | 0 | 0 | 0 | 0 | 1720.1218 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1720.1218 | 282.9851 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1387 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-02-05 | NA | NA | Other - Deferral | $2 Mil - $3 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 5.2961 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5810099 | T.0009656 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-18 | 2026-12-31 | 2026-11-13 | NA | NA | TRUE | 6000 | NA ¦ NA | 114.9933 | 2370.9063 | 0 | 0 | 0 | 5.1809 | 88.3314 | 2250.0963 | 27.2976 | 0 | 0 | 0 | 93.5124 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1388 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-19 | NA | NA | Other - Deferral | $2 Mil - $3 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807541 | T.0009656 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-07-18 | 2026-12-31 | 2025-08-01 | NA | NA | TRUE | 6000 | NA ¦ NA | 1228.3644 | 1237.2359 | 0 | 0 | 0 | 662.2672 | 545.8284 | 29.1404 | 0 | 0 | 0 | 0 | 1208.0955 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1208.0956 | 20.2688 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1389 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807542 | T.0009657 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-07-02 | 2026-12-31 | 2026-08-31 | NA | NA | TRUE | 7200 | NA ¦ NA | 776.4783 | 1982.7653 | 0 | 0 | 22.0059 | 494.1969 | 212.234 | 1254.3284 | 0 | 0 | 0 | 0 | 728.4368 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1390 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5810434 | T.0009657 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-01 | 2026-12-31 | 2026-10-13 | NA | NA | TRUE | 7200 | NA ¦ NA | 198.8388 | 2663.1788 | 0 | 0 | 0 | 43.7973 | 133.3421 | 2456.289 | 29.7504 | 0 | 0 | 0 | 177.1394 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1391 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-03 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5810484 | T.0009658 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-11-28 | 2026-12-31 | 2026-04-10 | NA | NA | TRUE | 7200 | NA ¦ NA | 2721.1897 | 3758.9331 | 0 | 0 | 0 | 20.3005 | 2427.0392 | 1311.5934 | 0 | 0 | 0 | 0 | 2447.3396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1392 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-03 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807543 | T.0009658 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-07-23 | 2026-12-31 | 2025-09-26 | NA | NA | TRUE | 7200 | NA ¦ NA | 1327.5677 | 1479.1049 | 0 | 0 | 19.8342 | 580.7493 | 682.1016 | 196.4198 | 0 | 0 | 0 | 0 | 1282.6851 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 672.094 | 22.4412 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1393 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5810483 | T.0009659 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-11 | 2025-12-31 | 2026-07-22 | Prioritization | NA | TRUE | 7300 | NA ¦ NA | 281.1514 | 4257.4047 | 0 | 0 | 0 | 21.7141 | 163.3864 | 3959.8729 | 112.4313 | 0 | 0 | 0 | 185.1005 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1394 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807544 | T.0009659 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-10-01 | 2025-12-31 | 2025-11-26 | NA | NA | TRUE | 7300 | NA ¦ NA | 1151.869 | 1279.5611 | 0 | 0 | 21.4622 | 457.5045 | 669.3521 | 131.2424 | 0 | 0 | 0 | 0 | 1148.3188 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1148.3188 | 3.5502 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1395 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-17 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 17.354 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5809985 | T.0009660 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-08-28 | 2027-02-26 | 2026-09-30 | NA | NA | TRUE | 6400 | NA ¦ NA | 153.1981 | 4430.2444 | 0 | 0 | 0 | 11.2629 | 71.4531 | 4097.5285 | 0 | 0 | 0 | 0 | 82.7159 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1396 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-17 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807545 | T.0009660 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-08-25 | 2027-02-26 | 2025-09-11 | NA | NA | TRUE | 6400 | NA ¦ NA | 864.1505 | 864.7627 | 0 | 0 | 24.1187 | 429.1321 | 389.527 | 21.9848 | 0 | 0 | 0 | 0 | 842.7779 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 762.9277 | 19.2353 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1397 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 37.8815 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5809983 | T.0009661 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-04 | 2026-08-31 | 2026-09-30 | NA | NA | TRUE | 6300 | NA ¦ NA | 127.8345 | 4103.8361 | 0 | 0 | 0 | 11.063 | 83.1857 | 3640.6205 | 356.5381 | 12.4289 | 0 | 0 | 94.2487 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1398 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807546 | T.0009661 | Electric Transmission Substation Security Upgrade | 2 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-09-30 | 2026-08-31 | 2025-10-24 | NA | NA | TRUE | 6300 | NA ¦ NA | 1616.0577 | 1616.3254 | 0 | 0 | 31.5908 | 846.1799 | 716.2492 | 22.3055 | 0 | 0 | 0 | 0 | 1594.0199 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1444.4921 | 19.834 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1399 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-20 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 47.516 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807547 | T.0009663 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-04-06 | NA | 2027-08-26 | NA | NA | TRUE | NA | NA ¦ NA | 97.8832 | 3910.7216 | 0 | 0 | 0 | 0 | 50.202 | 1332.998 | 2518.6472 | 600 | 0 | 0 | 50.202 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1400 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-19 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807548 | T.0009664 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-06-22 | NA | 2027-10-07 | NA | NA | TRUE | NA | NA ¦ NA | 182.9956 | 3201.2579 | 0 | 0 | 0 | 1.1367 | 164.4128 | 528.9901 | 2106.4584 | 694.6118 | 39.6096 | 0 | 165.5496 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1401 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807549 | T.0009665 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-06-04 | NA | 2028-02-02 | NA | NA | FALSE | NA | NA ¦ NA | 434.145 | 3181.3409 | 0 | 0 | 0 | 173.9225 | 229.0474 | 122.3176 | 1714.3669 | 941.6865 | 0 | 0 | 402.9699 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1402 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-03 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807550 | T.0009666 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-08-24 | NA | 2028-01-11 | NA | NA | FALSE | NA | NA ¦ NA | 37.1069 | 4640.3966 | 0 | 0 | 0 | 0 | 31.1044 | 1877.2921 | 1335 | 1387 | 10 | 0 | 31.1045 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1403 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-12 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807581 | T.0009667 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-06-15 | NA | 2027-06-29 | NA | NA | TRUE | NA | NA ¦ NA | 24.7226 | 4805.853 | 0 | 0 | 0 | 0 | 21.644 | 1981.196 | 2106.6034 | 463 | 0.013 | 0 | 21.644 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1404 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-17 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807582 | T.0009668 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-02-18 | NA | 2027-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 141.5762 | 13808.2476 | 0 | 0 | 1.9165 | 14.0027 | 104.7486 | 765.495 | 12422.0848 | 0 | 0 | 0 | 120.6678 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1405 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807583 | T.0009669 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-02-16 | NA | 2027-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 130.378 | 13880.9286 | 0 | 0 | 2.1645 | 15.3001 | 92.9653 | 825.7299 | 12444.7688 | 1280.9083 | 45.8644 | 0 | 110.4298 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1406 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-20 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 47.516 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807584 | T.0009670 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-10-01 | NA | 2027-10-28 | NA | NA | TRUE | NA | NA ¦ NA | 82.0692 | 4583.5431 | 0 | 0 | 0 | 0 | 77.6563 | 314.8677 | 3936.2134 | 2950 | 0 | 0 | 77.6562 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1407 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-19 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807585 | T.0009671 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-09-09 | NA | 2027-11-03 | NA | NA | TRUE | NA | NA ¦ NA | 91.5427 | 2925.026 | 0 | 0 | 0 | 0 | 83.6426 | 120.5942 | 2265.9893 | 925.8944 | 43.1996 | 0 | 83.6426 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1408 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807586 | T.0009672 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-08-17 | NA | 2027-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 383.8605 | 2876.3779 | 0 | 0 | 0 | 22.3438 | 347.2556 | 83.1433 | 602.0677 | 389.9478 | 0 | 0 | 369.5995 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1409 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-03 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807587 | T.0009673 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-10-01 | NA | 2028-02-18 | NA | NA | FALSE | NA | NA ¦ NA | 78.5451 | 3375.4859 | 0 | 0 | 0 | 0 | 74.7915 | 694.6381 | 1546 | 644 | 24 | 0 | 74.7915 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1410 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-12 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807589 | T.0009674 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-05-05 | NA | 2027-09-17 | NA | NA | TRUE | NA | NA ¦ NA | 75.6835 | 3756.7077 | 0 | 0 | 0 | 0 | 74.8687 | 1467.8129 | 1218.47 | 656 | 0.026 | 0 | 74.8687 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1411 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-17 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807590 | T.0009675 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-04-15 | NA | 2027-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 90.2647 | 10691.8664 | 0 | 0 | 1.7925 | 8.6052 | 77.5858 | 855.579 | 0 | 0 | 0 | 0 | 87.9836 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1412 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5807591 | T.0009676 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-05-21 | NA | 2027-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 82.8315 | 10895.3726 | 0 | 0 | 1.6685 | 8.2471 | 70.3819 | 861.5152 | 211.9523 | 1596.5417 | 574.4464 | 1.6689 | 80.2974 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1413 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.9377 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | EX139132 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-12-01 | NA | 2028-02-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 6100 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 3900 | 1872.775 | 327.225 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
1414 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-12 | NA | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.54903 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | EX139144 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-02-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 14076.4014 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 327.3188 | 654.6375 | 13094.4452 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
1415 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-14 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 14.7513 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | EX139145 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-02-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 14076.4014 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 327.3188 | 654.6375 | 13094.4452 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
1416 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-10 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 41.3213 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | EX139148 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-02-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 9290 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 260 | 520 | 8510 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
1417 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-09 | NA | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | NA | NA | NA | NA | 5.2 | Non-IGP | EX139149 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-02-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8100.5494 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 260 | 575.7475 | 7264.8019 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
1418 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-03 | NA | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 35.6227 | NA | 230 kV | NA | NA | NA | 5.2 | Non-IGP | EX139146 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-02-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 5266.858 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 260 | 518.466 | 0 | 4488.392 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
1419 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-03 | NA | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 35.6227 | NA | 500 kV | NA | NA | NA | 5.2 | Non-IGP | EX139147 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-02-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 6891.876 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 260 | 518.466 | 0 | 6113.41 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
1420 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-25 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 42.1076 | NA | 230 kV | NA | NA | NA | 5.2 | Non-IGP | EX139150 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-02-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 4629.1285 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 260 | 577.4725 | 0 | 3791.656 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
1421 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 2026-03-25 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 42.1076 | NA | 500 kV | NA | NA | NA | 5.2 | Non-IGP | EX139151 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-02-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8075.0332 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 260 | 577.4725 | 0 | 7237.5607 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
1422 | MPAC Buildings |  |  | NA | Bucket for Modular Protection and Automation Control Buildings | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 472 | 5a.Mitigates System Wide Failure Risk | NA | 5.2 | Non-IGP | 5507184 | NA | NA | NA | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 530.7775 | 12530.7776 | 0 | 0 | 0 | 0 | 0 | 0.0001 | 0 | 0 | 2000 | 5000 | 530.7775 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1423 | TEMPLETON: Replace 230/70 KV MPAC |  |  | San Luis Obispo | This project proposes to install one modular protection, automation and control (MPAC) equipment enclosure at 230 / 70 kV Templeton substation | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-02 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.6839 | NA | 230 ¦ 70 kV | 617 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5758359 | T.0000089 | Templeton 230kV and 70kV MPAC | 1 | 67 | NA ¦ 5759808 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-01-08 | 2019-12-01 | 2019-09-18 | NA | NA | FALSE | 9780 | NA ¦ NA | 9623.763 | 9623.763 | 665.6183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9623.763 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 634.5173 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1424 | KERN: Inst 230 KV MPAC Building |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.7504 | NA | 230 kV | 764 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5767884 | T.0000204 | Kern 230kV Bus Upgrade | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-05-02 | 2019-10-12 | 2019-03-07 | NA | NA | FALSE | 74400 | NA ¦ NA | 11502.4232 | 11502.4232 | 610.4325 | 17.2441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11502.4232 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 610.4325 | 17.2441 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1425 | ORO LOMA: Install 115 KV MPAC |  |  | Fresno | install protection, automation and control equipment at on the 115 kV bus at Oro Loma Substation. Installation of automation, protection and control equipment will increase the operational visibility and provide remote control capabilities that will help PG&E become the leading utility in the United States. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-10 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.8637 | NA | 115 kV | 235 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5744220 | T.0000563 | ORO LOMA: INSTALL 115 KV MPAC | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-09-04 | 2019-02-28 | 2019-11-06 | Workforce | NA | FALSE | 9038 | NA ¦ NA | 12433.7647 | 12433.7647 | 446.253 | 0 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12433.7647 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2023 ¦ 2026 | 446.253 | 0 | 0.04581 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1426 | MANTECA: Upgrade Vierra MPAC Remote End |  |  | Manteca, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-14 | 15 | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.8539 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 14 | 5.3 | Non-IGP | 5777418 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Construction (10%-25%) | 2 | 2026-02-20 | 2023-01-24 | 2026-05-08 | Prioritization | NA | TRUE | 41500 | NA ¦ NA | 1443.3952 | 1759.6129 | 27.7332 | 43.1306 | 207.7897 | 394.5622 | 260.2882 | 640.2479 | 2.7929 | 0 | 0 | 0 | 1116.5721 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1427 | TESLA: Upgrade Vierra MPAC Remote End |  |  | Alameda | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | 28 | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 9 | 5.3 | Non-IGP | 5777395 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2020-10-16 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Construction (10%-25%) | 2 | 2026-02-03 | 2023-01-24 | 2026-07-01 | Prioritization | NA | TRUE | 41500 | NA ¦ NA | 413.4888 | 590.2349 | 27.5627 | 38.3234 | 48.1345 | 46.7753 | 86.5661 | 204.6255 | 3.0171 | 0 | 0 | 0 | 382.5922 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1428 | TRACY: Upgrade Vierra MPAC Remote End |  |  | Tracy, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-31 | 15 | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.7469 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 13 | 5.3 | Non-IGP | 5777397 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Construction (25%-50%) | 2 | 2026-01-22 | 2023-01-24 | 2026-07-10 | Prioritization | NA | TRUE | 41500 | NA ¦ NA | 1888.343 | 2182.5656 | 41.8877 | 31.2087 | 150.8307 | 682.7102 | 492.2354 | 542.9236 | 3.3857 | 0 | 0 | 0 | 1636.2563 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1429 | KASSON: Upgrade Vierra MPAC Remote End |  |  | San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-31 | 15 | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.1988 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 10 | 5.3 | Non-IGP | 5777396 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 3 | 2026-05-15 | 2023-01-24 | 2026-07-21 | Prioritization | NA | TRUE | 41500 | NA ¦ NA | 1499.6671 | 1701.5164 | 34.7818 | 35.4488 | 165.5054 | 578.714 | 447.0827 | 234.0151 | 5.6103 | 0 | 0 | 0 | 1461.891 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1430 | RIPON: Upgrade Vierra MPAC Remote End |  |  | Ripon, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-11 | 10 | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.0603 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 16 | 5.3 | Non-IGP | 5777421 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2020-10-16 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 3 | 2026-04-13 | 2023-01-24 | 2026-07-30 | Prioritization | NA | TRUE | 41500 | NA ¦ NA | 290.3274 | 464.9341 | 11.3787 | 18.0991 | 24.7133 | 24.0779 | 116.5375 | 188.5938 | 13.5739 | 0 | 0 | 0 | 262.7663 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1431 | Vierra MPAC |  |  | Lathrop, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-06 | 27 | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.355 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 12 | 5.3 | Non-IGP | 5777394 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Operational | 1 | 2024-05-21 | 2023-01-24 | 2025-05-21 | Prioritization | NA | TRUE | 41500 | NA ¦ NA | 12085.2899 | 12646.8928 | 248.2162 | 106.2447 | 2217.2928 | 5041.5721 | 3463.9205 | 868.7494 | 40.4706 | 0 | 0 | 0 | 11737.6727 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 11679.1981 | 345.7225 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1432 | SANGER: Install 115 KV MPAC |  |  | Fresno | Install a new seven bay 115 kV BAAH bus, two MPAC buildings, and relocate all associated 115 kV lines at Sanger Substation. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-18 | NA | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.0513 | NA | 115 kV | 225 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5756775 | T.0000601 | Sanger Substation 115kV Bus Replacement | 4 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2017-07-13 | IS/MND | NA | CPUC | NA | PTC: A.15-09-012 | 2015-09-30 | Approved | 2017 | Operational | 1 | 2019-05-02 | 2019-12-31 | 2020-11-02 | Prioritization | NA | FALSE | 55300 | NA ¦ NA | 12147.1528 | 12147.1528 | 747.1901 | 101.3005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12147.1528 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 747.1901 | 101.3005 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1433 | MCCALL: Upgrades for Remote Ends |  |  | Fresno | Install a new seven bay 115 kV BAAH bus, two MPAC buildings, and relocate all associated 115 kV lines at Sanger Substation. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-18 | 20 | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.0513 | NA | 115 kV | 225 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5770340 | T.0000601 | Sanger Substation 115kV Bus Replacement | 4 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2017-07-13 | IS/MND | NA | CPUC | NA | PTC: A.15-09-012 | 2015-09-30 | Approved | 2017 | Operational | 1 | 2020-08-25 | 2019-12-31 | 2021-02-17 | Prioritization | NA | FALSE | 55300 | NA ¦ NA | 678.7618 | 678.7618 | 295.1673 | 4.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 678.7618 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 664.1148 | 4.3645 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1434 | DRUM PH 1: Inst Rio Oso 115KV Remote End |  |  | Placer | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Other - Operations Tech | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-12 | 21 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.2491 | NA | 115 kV | 462 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5770430 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-03-02 | 2019-12-02 | 2027-02-26 | Prioritization | NA | TRUE | 264900 | NA ¦ NA | 1785.1325 | 4637.1577 | 91.4002 | 337.4881 | 325.1157 | 341.8781 | 46.9956 | 1829.8646 | 1145.8069 | 0 | 0 | 0 | 1661.4861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1435 | BRIGHTON: Inst Rio Oso 230KV Remote End |  |  | Sacramento, Sacramento | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Other - Operations Tech | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | 17 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.4413 | NA | 230 kV | 462 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5770426 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2026-03-16 | 2019-12-02 | 2026-04-22 | Prioritization | NA | TRUE | 264900 | NA ¦ NA | 873.9104 | 1932.4288 | 64.9086 | 66.736 | 97.9379 | 114.3136 | 91.7042 | 874.5773 | 214.95 | 0 | 0 | 0 | 842.9015 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1436 | WOODLAND: Inst Rio Oso 115 KV Remote End |  |  | Woodland, Yolo | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Other - Operations Tech | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.8386 | NA | 115 kV | 462 | 5a.Mitigates System Wide Failure Risk | 12 | NA | NA | 5770427 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-01-06 | 2019-12-02 | 2023-03-08 | Prioritization | NA | FALSE | 264900 | NA ¦ NA | 3080.1998 | 3080.1998 | 658.1475 | 516.3038 | 599.7831 | 28.3182 | 0 | 0 | 0 | 0 | 0 | 0 | 3080.1998 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 3030.6131 | 28.0925 | -9e-05 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1437 | RIO OSO: Install 230 KV MPAC |  |  | Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | 16 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.3219 | NA | 230 kV | 462 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5732693 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-12-06 | 2019-12-02 | 2024-12-29 | Prioritization | NA | TRUE | 264900 | NA ¦ NA | 26676.5838 | 29921.0744 | 2761.3431 | 3455.5779 | 3583.9785 | 3859.2066 | 2099.5318 | 3248.8757 | 227.1725 | 0 | 0 | 0 | 26445.0262 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 23885.4974 | 2044.5356 | 225.4921 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1438 | RIO OSO: Install 115 KV MPAC |  |  | Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | 16 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.3219 | NA | 115 kV | 462 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5739019 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-03-20 | 2019-12-02 | 2024-12-29 | Prioritization | NA | TRUE | 264900 | NA ¦ NA | 23005.4377 | 25793.6756 | 2463.4675 | 3075.3223 | 2831.3786 | 3237.3192 | 2042.0285 | 1146.0663 | 1796.3927 | 0 | 0 | 0 | 22851.2166 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 20383.0526 | 1984.1535 | 149.8502 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1439 | TABLE MOUNTAIN: Inst Rio Oso Remote End |  |  | Butte | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Other - Operations Tech | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-20 | 8 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 47.516 | NA | 230 kV | 462 | 5a.Mitigates System Wide Failure Risk | 5 | 5.3 | Non-IGP | 5770422 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-02-24 | 2019-12-02 | 2025-04-29 | Prioritization | NA | TRUE | 264900 | NA ¦ NA | 1339.548 | 1423.5504 | 53.2716 | 78.5212 | 207.273 | 100.9862 | 375.9737 | 123.6206 | 0 | 0 | 0 | 0 | 1299.9299 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1257.6455 | 37.9781 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1440 | ATLANTIC: Inst Rio Oso 230KV Remote End |  |  | Roseville, Placer | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Other - Operations Tech | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | 15 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.6984 | NA | 230 kV | 462 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5770425 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-04-10 | 2019-12-02 | 2025-12-29 | Prioritization | NA | TRUE | 264900 | NA ¦ NA | 831.1839 | 1039.0593 | 47.2216 | 65.7425 | 120.8302 | 92.7271 | 111.6129 | 197.1916 | 21.1928 | 0 | 0 | 0 | 820.6749 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 805.9149 | 10.2347 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1441 | GREEN VALLEY: Install 115 KV MPAC |  |  | Interlaken CDP, Santa Cruz | This project will replace the existing 115 kV bus with five bays of breaker-and-a-half (BAAH) configuration. The new 115 kV BAAH bus will be located in the existing substation yard, which will require sequential construction of the new BAAH bays and removal of sections of the existing 115 kV bus. The protection and controls of the new equipment will be moved to the new Modular Protection Automation and Control (MPAC) building | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-02 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.6121 | NA | 115 kV | 428 | NA | NA | NA | NA | 5739635 | T.0000638 | Green Valley Substation Upgrade | 6 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-11-20 | 2019-12-31 | 2018-09-20 | NA | NA | FALSE | 47000 | NA ¦ NA | 7514.6871 | 7514.6871 | 69.6277 | 15.3162 | 0.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7514.6871 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 69.6277 | 15.3162 | 0.66912 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1442 | CASCADE: Install MPAC |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-16 | 15 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.021098 | NA | 115 kV | 58 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5766588 | T.0000651 | Cascade Substation Upgrade | 10 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-08-03 | 2022-01-31 | 2025-01-23 | Prioritization | NA | TRUE | 35800 | NA ¦ NA | 12307.1475 | 12533.8593 | 990.8437 | 853.1336 | 1004.5579 | 865.5172 | 437.9579 | 227.4326 | 0 | 0 | 0 | 0 | 12306.4268 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 12306.4268 | 0.72069 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1443 | CASCADE: Repl PACI RAS @ VGCC |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-16 | 15 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.021098 | NA | NA | 58 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5775779 | T.0000651 | Cascade Substation Upgrade | 10 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-02-04 | 2022-01-31 | 2025-04-30 | Prioritization | NA | TRUE | 35800 | NA ¦ NA | 394.0816 | 421.606 | 31.4181 | 21.7982 | 20.0527 | 59.8702 | 72.9696 | 29.8729 | 0 | 0 | 0 | 0 | 391.733 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 360.5932 | 2.11 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1444 | CASCADE: Repl PACI RAS @ SFCC |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Other - Remedial Action Scheme/Special Protection Scheme | Replace | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-16 | 15 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.021098 | NA | NA | 58 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5775778 | T.0000651 | Cascade Substation Upgrade | 10 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-02-04 | 2022-01-31 | 2025-06-04 | Prioritization | NA | TRUE | 35800 | NA ¦ NA | 369.3388 | 369.3388 | 35.3174 | 27.066 | 22.6596 | 10.2106 | 47.7437 | 0.6568 | 0 | 0 | 0 | 0 | 368.682 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 346.764 | 0.60343 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1445 | MONTA VISTA: Inst Jefferson Remote End |  |  | San Mateo | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Other - Operations Tech | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | 20 | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.7091 | NA | 230 kV | 472 | 3. Emergency Preparedness | 4 | 5.3 | Non-IGP | 5775342 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-10-06 | 2020-08-07 | 2026-07-07 | Prioritization | NA | TRUE | 39600 | NA ¦ NA | 2210.9253 | 3307.1504 | 230.5593 | 74.9192 | 60.9927 | 171.0322 | 672.975 | 1672.4756 | 18.0451 | 0 | 0 | 0 | 1616.6297 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1446 | MONTA VISTA: Repl Saratoga RE RLY |  |  | Saratoga, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-04 | NA | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.4212 | NA | 230 kV | 472 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5775339 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-07-21 | 2020-08-07 | 2022-12-12 | Prioritization | NA | FALSE | 39600 | NA ¦ NA | 2871.1256 | 2871.1256 | 681.8812 | 1594.7464 | 133.4626 | 35.3397 | 16.4306 | 0 | 0 | 0 | 0 | 0 | 2871.1256 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 2789.1269 | 38.3027 | 16.2624 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1447 | MONTA VISTA: Inst Metcalf Remote End |  |  | Cupertino, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Other - Operations Tech | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | NA | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.8314 | NA | 230 kV | 472 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5775340 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-05-28 | 2020-08-07 | 2024-07-14 | Prioritization | NA | FALSE | 39600 | NA ¦ NA | 719.158 | 719.158 | 64.2362 | 91.2292 | 94.9228 | 238.4018 | -2.0825 | 0 | 0 | 0 | 0 | 0 | 719.158 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 717.6868 | -2.0702 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1448 | MONTA VISTA: Install 230KV MPAC |  |  | Cupertino, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | 19 | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.8314 | NA | 230 kV | 472 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5774084 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-08-25 | 2020-08-07 | 2025-02-20 | Prioritization | NA | TRUE | 39600 | NA ¦ NA | 27579.2344 | 29583.4353 | 5269.3587 | 2536.1474 | 1712.9285 | 3248.1921 | 1508.6597 | 637.1176 | 668.1531 | 0 | 0 | 0 | 27646.1188 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 18198.6061 | -18198.6061 | 0 | 0 | 27137.649 | -65.2444 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1449 | MONTA VISTA: Repl Coyote RE RLY |  |  | San Jose, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-03 | 21 | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.5453 | NA | 230 kV | 472 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5775341 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-12-02 | 2020-08-07 | 2025-02-22 | Prioritization | NA | TRUE | 39600 | NA ¦ NA | 1882.5716 | 1882.5716 | 94.7651 | 82.8406 | 74.0654 | 491.8839 | 692.1749 | 2.7211 | 0 | 0 | 0 | 0 | 1879.8505 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1805.4282 | 2.5962 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1450 | MONTA VISTA: Upgd SLAC RE RLY |  |  | San Mateo | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | 19 | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.7091 | NA | 60 kV | 472 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5776918 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-10-28 | 2020-08-07 | 2026-01-20 | Prioritization | NA | TRUE | 39600 | NA ¦ NA | 2243.1821 | 2251.6197 | 125.0277 | 150.7264 | 130.5817 | 148.1877 | 211.4524 | 34.8714 | 0 | 0 | 0 | 0 | 2216.7483 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 2235.284 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1451 | WESTPARK: INSTALL MPAC BUILDING |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-17 | 24 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.7259 | NA | 115 kV | 705 | 5a.Mitigates System Wide Failure Risk | 12 | 5.3 | Non-IGP | 5773025 | T.0000980 | KERN PP 115kV BAAH & MPAC | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2023-08-21 | 2022-10-12 | 2028-04-28 | Prioritization | NA | FALSE | 77400 | NA ¦ NA | 10363.1826 | 22841.2654 | 241.2329 | 1879.2739 | 2926.0904 | 1824.3092 | 614.6177 | 3843.9832 | 2748.2742 | 0 | 0 | 0 | 10111.1269 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1452 | KERN OIL: Repl CB 132 RFL Gard |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.7504 | NA | 115 kV | 705 | 5a.Mitigates System Wide Failure Risk | 8 | 5.3 | Non-IGP | 5774637 | T.0000980 | KERN PP 115kV BAAH & MPAC | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-01-26 | 2022-10-12 | 2028-04-28 | Prioritization | NA | FALSE | 77400 | NA ¦ NA | 70.8545 | 291.936 | 4.0087 | 4.3295 | 0.3836 | 0 | 3.1189 | 4.3688 | 5.6861 | 193.7296 | 0 | 0 | 70.8545 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1453 | LIVE OAK: Repl CB 172 RFL Gard |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.7504 | NA | 115 kV | 705 | 5a.Mitigates System Wide Failure Risk | 17 | 5.3 | Non-IGP | 5774638 | T.0000980 | KERN PP 115kV BAAH & MPAC | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-01-31 | 2022-10-12 | 2028-04-28 | Prioritization | NA | FALSE | 77400 | NA ¦ NA | 140.8079 | 365.4386 | 7.3451 | 7.9357 | 0.7032 | 4.2876 | 11.6189 | 10.1569 | 10.7998 | 191.1751 | 0 | 0 | 139.1131 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1454 | KERN PP: INSTALL 115KV MPAC BLDG |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | 34 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.7504 | NA | 115 kV | 705 | 5a.Mitigates System Wide Failure Risk | 10 | 5.3 | Non-IGP | 5759901 | T.0000980 | KERN PP 115kV BAAH & MPAC | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-08-23 | 2022-10-12 | 2025-01-09 | Prioritization | NA | TRUE | 77400 | NA ¦ NA | 17020.7955 | 17020.7955 | 3603.2933 | 3065.5833 | 94.7055 | 2401.7284 | 305.7211 | 5.753 | 0 | 0 | 0 | 0 | 17015.0425 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 17015.0794 | 5.753 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1455 | Cottonwood MPAC_Remote End Round Mtn |  |  | Round Mountain CDP, Shasta | Project scope is to replace both 230/115kV transmission transformers which will address the 115kV high voltage issue and improve reliability of the North Valley transmission system. Installing the 115kV bus tie breakers will address NERC category P2 breaker fault of Cottonwood CB 102 or, a NERC category P4 nearby fault plus a CB 102 fault. The CAISO approved shunt reactors/transformer replacement to mitigate the high voltage issue and additionally the 115kV bus tie breakers to mitigate the P2 and P4 contingencies. The MPAC and breakers replacement will replace the deteriorated asset and capture the efficiency of upgrading protection and controls, avoid rework and multiple clearances. The high-level scope includes the following: • Replace the existing Banks 1 and 4 with 230/115kV 420MVA, with LTC and associated bus selector switches. • Install new bay and new 230kV breaker to connect new Bank 1 to 230kV bus. • Replace Bank 1 low-side breaker CB 172 and the associated switches. • Replace Bank 4 low-side CB 192 and the associated switches. • Expand existing 115kV MPAC to accommodate protection and controls. • Expand SPCC to accommodate increased oil quantity of new banks. • Install new sectionalizing CB’s 912 and 922 w/switches to sectionalize 115kV bus to Sections D and E. • Install new CB 132 with switches and relocate Trinity-Cottonwood 115kV line to Bus Section E. • Install new bus paralleling breaker CB 102 with switches in Bus Section E. • Install new bus paralleling breaker CB 902 with switches in Bus Section D. • Replace the existing OCBs 142 and 152 with non-SF6 breakers and the associated switches. • Replace six of the existing 230kV OCBs (CBs 222, 232, 272, 292, 522, and 542) with new 230kV 2000A gas circuit breakers, and the associated breaker and bus selector switches. • Install new 230kV 2000A bus paralleling breaker (CB 502) and associated switches in place of the existing Transformer 1 CB 512 position. • Replace switches 213, 357, 359, 367, and 369. • Install new MPAC Building to house the protection, automation, and control equipment for the 230kV Bus Sections “E” and “F”. | Other - Operations Tech | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-09 | 10 | NA | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 230 kV | NA | 5. Compliance/Commitments With Strong Safety Link | NA | 5.3 | Non-IGP | 5784659 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-12-04 | 2028-04-30 | 2029-03-20 | Clearances | NA | FALSE | 51200 | NA ¦ NA | 343.1987 | 1741.6482 | 7.1716 | 20.6934 | 36.6272 | 33.9349 | 225.8536 | 40.7518 | 72.9253 | 112.414 | 30.4934 | 0 | 337.0023 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1456 | Cottonwood MPAC_Remote End Delevan |  |  | Colusa | Project scope is to replace both 230/115kV transmission transformers which will address the 115kV high voltage issue and improve reliability of the North Valley transmission system. Installing the 115kV bus tie breakers will address NERC category P2 breaker fault of Cottonwood CB 102 or, a NERC category P4 nearby fault plus a CB 102 fault. The CAISO approved shunt reactors/transformer replacement to mitigate the high voltage issue and additionally the 115kV bus tie breakers to mitigate the P2 and P4 contingencies. The MPAC and breakers replacement will replace the deteriorated asset and capture the efficiency of upgrading protection and controls, avoid rework and multiple clearances. The high-level scope includes the following: • Replace the existing Banks 1 and 4 with 230/115kV 420MVA, with LTC and associated bus selector switches. • Install new bay and new 230kV breaker to connect new Bank 1 to 230kV bus. • Replace Bank 1 low-side breaker CB 172 and the associated switches. • Replace Bank 4 low-side CB 192 and the associated switches. • Expand existing 115kV MPAC to accommodate protection and controls. • Expand SPCC to accommodate increased oil quantity of new banks. • Install new sectionalizing CB’s 912 and 922 w/switches to sectionalize 115kV bus to Sections D and E. • Install new CB 132 with switches and relocate Trinity-Cottonwood 115kV line to Bus Section E. • Install new bus paralleling breaker CB 102 with switches in Bus Section E. • Install new bus paralleling breaker CB 902 with switches in Bus Section D. • Replace the existing OCBs 142 and 152 with non-SF6 breakers and the associated switches. • Replace six of the existing 230kV OCBs (CBs 222, 232, 272, 292, 522, and 542) with new 230kV 2000A gas circuit breakers, and the associated breaker and bus selector switches. • Install new 230kV 2000A bus paralleling breaker (CB 502) and associated switches in place of the existing Transformer 1 CB 512 position. • Replace switches 213, 357, 359, 367, and 369. • Install new MPAC Building to house the protection, automation, and control equipment for the 230kV Bus Sections “E” and “F”. | Other - Operations Tech | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | 16 | NA | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.7615 | NA | 230 kV | NA | 5. Compliance/Commitments With Strong Safety Link | NA | 5.3 | Non-IGP | 5784661 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-11-05 | 2028-04-30 | 2029-08-24 | Prioritization | NA | FALSE | 51200 | NA ¦ NA | 359.5565 | 1947.253 | 6.2519 | 11.8011 | 26.9912 | 32.128 | 258.3143 | 49.6524 | 248.2337 | 167.0009 | 138.4379 | 0 | 349.0045 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1457 | Cottonwood MPAC_Remote End Glenn |  |  | Glenn | Project scope is to replace both 230/115kV transmission transformers which will address the 115kV high voltage issue and improve reliability of the North Valley transmission system. Installing the 115kV bus tie breakers will address NERC category P2 breaker fault of Cottonwood CB 102 or, a NERC category P4 nearby fault plus a CB 102 fault. The CAISO approved shunt reactors/transformer replacement to mitigate the high voltage issue and additionally the 115kV bus tie breakers to mitigate the P2 and P4 contingencies. The MPAC and breakers replacement will replace the deteriorated asset and capture the efficiency of upgrading protection and controls, avoid rework and multiple clearances. The high-level scope includes the following: • Replace the existing Banks 1 and 4 with 230/115kV 420MVA, with LTC and associated bus selector switches. • Install new bay and new 230kV breaker to connect new Bank 1 to 230kV bus. • Replace Bank 1 low-side breaker CB 172 and the associated switches. • Replace Bank 4 low-side CB 192 and the associated switches. • Expand existing 115kV MPAC to accommodate protection and controls. • Expand SPCC to accommodate increased oil quantity of new banks. • Install new sectionalizing CB’s 912 and 922 w/switches to sectionalize 115kV bus to Sections D and E. • Install new CB 132 with switches and relocate Trinity-Cottonwood 115kV line to Bus Section E. • Install new bus paralleling breaker CB 102 with switches in Bus Section E. • Install new bus paralleling breaker CB 902 with switches in Bus Section D. • Replace the existing OCBs 142 and 152 with non-SF6 breakers and the associated switches. • Replace six of the existing 230kV OCBs (CBs 222, 232, 272, 292, 522, and 542) with new 230kV 2000A gas circuit breakers, and the associated breaker and bus selector switches. • Install new 230kV 2000A bus paralleling breaker (CB 502) and associated switches in place of the existing Transformer 1 CB 512 position. • Replace switches 213, 357, 359, 367, and 369. • Install new MPAC Building to house the protection, automation, and control equipment for the 230kV Bus Sections “E” and “F”. | Other - Operations Tech | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-16 | 10 | NA | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 5.7152 | NA | 230 kV | NA | 5. Compliance/Commitments With Strong Safety Link | NA | 5.3 | Non-IGP | 5784662 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-05-03 | 2028-04-30 | 2029-10-09 | Prioritization | NA | FALSE | 51200 | NA ¦ NA | 278.7377 | 1369.3737 | 3.4816 | 5.4325 | 25.553 | 33.4232 | 182.3316 | 53.9242 | 321.1414 | 212.9135 | 158.2757 | 0 | 262.4524 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1458 | Cottonwood Sub: Install 230kV MPAC |  |  | Cottonwood CDP, Shasta | Project scope is to replace both 230/115kV transmission transformers which will address the 115kV high voltage issue and improve reliability of the North Valley transmission system. Installing the 115kV bus tie breakers will address NERC category P2 breaker fault of Cottonwood CB 102 or, a NERC category P4 nearby fault plus a CB 102 fault. The CAISO approved shunt reactors/transformer replacement to mitigate the high voltage issue and additionally the 115kV bus tie breakers to mitigate the P2 and P4 contingencies. The MPAC and breakers replacement will replace the deteriorated asset and capture the efficiency of upgrading protection and controls, avoid rework and multiple clearances. The high-level scope includes the following: • Replace the existing Banks 1 and 4 with 230/115kV 420MVA, with LTC and associated bus selector switches. • Install new bay and new 230kV breaker to connect new Bank 1 to 230kV bus. • Replace Bank 1 low-side breaker CB 172 and the associated switches. • Replace Bank 4 low-side CB 192 and the associated switches. • Expand existing 115kV MPAC to accommodate protection and controls. • Expand SPCC to accommodate increased oil quantity of new banks. • Install new sectionalizing CB’s 912 and 922 w/switches to sectionalize 115kV bus to Sections D and E. • Install new CB 132 with switches and relocate Trinity-Cottonwood 115kV line to Bus Section E. • Install new bus paralleling breaker CB 102 with switches in Bus Section E. • Install new bus paralleling breaker CB 902 with switches in Bus Section D. • Replace the existing OCBs 142 and 152 with non-SF6 breakers and the associated switches. • Replace six of the existing 230kV OCBs (CBs 222, 232, 272, 292, 522, and 542) with new 230kV 2000A gas circuit breakers, and the associated breaker and bus selector switches. • Install new 230kV 2000A bus paralleling breaker (CB 502) and associated switches in place of the existing Transformer 1 CB 512 position. • Replace switches 213, 357, 359, 367, and 369. • Install new MPAC Building to house the protection, automation, and control equipment for the 230kV Bus Sections “E” and “F”. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | 31 | NA | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 26.1945 | NA | 230 kV | 1002 | 3. Emergency Preparedness | NA | 5.3 | Non-IGP | 5783341 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-03-11 | 2028-04-30 | 2029-12-19 | Prioritization | NA | FALSE | 51200 | NA ¦ NA | 8382.7236 | 22646.0869 | 63.4035 | 70.7023 | 137.3583 | 1927.34 | 5731.3314 | 3726.109 | 3108.124 | 2870.7899 | 2177.7209 | 15.7207 | 8093.3271 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1459 | MOSS LANDING: Inst 115 KV Auto-MPAC |  |  | Monterey | This project will replace the existing DBSB 115 kV bus with seven bays of BAAH configuration. The new 115kV BAAH bus will be located at the foot print of the old 230kV double bus single breaker site. The protection and controls of the new equipment will be moved to new MPAC buildings. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-10 | NA | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 41.3213 | NA | 115 kV | 764 | NA | NA | NA | NA | 5769267 | T.0001406 | Moss Landing 115kV BAAH | 2 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2017-05-02 | 2018-12-05 | 2018-07-27 | NA | NA | FALSE | 69500 | NA ¦ NA | 12857.5071 | 12857.5071 | 176.1947 | 110.1316 | 4.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12857.5071 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 176.1947 | 110.1317 | 4.1107 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1460 | PALO ALTO SS: Install MPAC |  |  | Palo Alto, Santa Clara | The Palo Alto switching station is already set-up for BAAH. However, it is operated as a nonstandard variant of Bus 1& 2 with six breakers installed for six lines. Presently it is required to trip the entire bus in order to protect SVP equipment. This project will replace the six breakers, install three additional breakers, and convert the bus to BAAH.Install modular protection, automation, and control (MPAC) panels in MPAC building for the 115 kV bus to replace the existing control building | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-06 | 53 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.0138 | NA | 115 kV | 472 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5774085 | T.0001493 | PALO ALTO SS: Convert 115kV Bus to BAAH | 2 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2029-01-11 | NA | 2029-07-25 | NA | NA | FALSE | NA | NA ¦ NA | 420.1924 | 16949.5395 | 51.9568 | 140.2299 | 0 | 12.9972 | 12.2221 | 1182.6231 | 5680.599 | 4541.674 | 3974.45 | 1150.001 | 420.1924 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1461 | HICKS: Install 230 KV MPAC |  |  | San Jose, Santa Clara | To reduce customer interruptions at Hicks Substation, it is recommended to re-connect existing T-Line and distribution bank connections and install four new 230kV circuit breakers to build a six-breaker ring bus in conjunction with a new MPAC building. This will reduce System Average Interruption Duration Index (SAIDI) impacts affecting these 44,000 customers. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-02 | NA | NA | Wires - Bus Upgrade Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.8635 | NA | 230 kV | 84 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5742960 | T.0001600 | HICKS SUB: 230 KV BUS REL IMPROV | 3 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2012 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-10-02 | 2017-08-29 | 2021-04-27 | Prioritization | NA | FALSE | 21300 | NA ¦ NA | 8658.858 | 8658.858 | 1784.7187 | 390.1742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8658.858 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 8269.8069 | 390.1742 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1462 | HICKS to METCLAF: Upgrade 230 KV Relay |  |  | San Jose, Santa Clara | To reduce customer interruptions at Hicks Substation, it is recommended to re-connect existing T-Line and distribution bank connections and install four new 230kV circuit breakers to build a six-breaker ring bus in conjunction with a new MPAC building. This will reduce System Average Interruption Duration Index (SAIDI) impacts affecting these 44,000 customers. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-02 | 46 | NA | Wires - Bus Upgrade Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.8635 | NA | 230 kV | 84 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5524128 | T.0001600 | HICKS SUB: 230 KV BUS REL IMPROV | 3 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2012 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-12-07 | 2017-08-29 | 2021-06-18 | Prioritization | NA | FALSE | 21300 | NA ¦ NA | 583.973 | 583.973 | 222.2734 | 4.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.973 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 217.6445 | 4.3789 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1463 | MIDWAY SUB: INSTALL 230kV MPAC |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | 56 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 230 kV | 705 | 5a.Mitigates System Wide Failure Risk | 9 | 5.3 | Non-IGP | 5782562 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-06-14 | 2022-04-01 | 2025-11-07 | Prioritization | NA | TRUE | 105100 | NA ¦ NA | 13479.9329 | 13479.9329 | 2693.0623 | 2509.8357 | 367.9386 | 336.7426 | 1765.9442 | 19.9102 | 0 | 0 | 0 | 0 | 13460.0227 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 13332.8124 | 19.6704 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1464 | ASHLAN: Install MPAC Building & OPGW |  |  | Fresno, Fresno | This project will upgrade the existing 230kV bus from looped design to a ring bus design as well as install an MPAC building and upgrade protection at Ashlan, Herndon, Gregg, and Figarden substations. These upgrades will improve reliability, safety, and maintenance at Ashlan substation and the 230kV protection in the local area. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.6505 | NA | 230 kV | 764 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5766581 | T.0002362 | Ashlan Ave 230kV Bus Reliability | 5 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5310-E | 2018-06-13 | Approved | 2018 | Operational | 1 | 2019-04-09 | 2020-02-11 | 2020-02-20 | NA | NA | FALSE | 40900 | NA ¦ NA | 8611.1701 | 8611.1701 | 570.3361 | -0.3453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8611.1701 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 547.9919 | -0.33183 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement
1465 | TESLA - INSTALL 230KV MPAC (SECTION C) |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | 40 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 288 | 5. Compliance/Commitments With Strong Safety Link | 9 | 5.3 | Non-IGP | 5776770 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 2 | 2025-12-10 | 2026-12-01 | 2027-05-03 | NA | NA | TRUE | 113900 | NA ¦ NA | 11164.9952 | 39823.6813 | 194.5451 | 181.5405 | 313.4306 | 4606.5054 | 5193.6159 | 9369.5935 | 4906.2196 | 8929.8234 | 121.3264 | 0 | 10627.7874 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1466 | Tesla - Tracy: 230kV Remote End |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | 21 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5793899 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-07-22 | 2026-12-01 | 2027-09-16 | Project Design | Scope Change | TRUE | 113900 | NA ¦ NA | 98.6194 | 850.566 | 20.8534 | 16.2067 | 0.8414 | 22.4193 | 33.8809 | 77.5383 | 583.1938 | 95.6322 | 0 | 0 | 94.2017 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1467 | Transformer Bank #6 Relay Replacement |  |  | San Joaquin | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-05 | 23 | Lifecycle Replacement Analysis | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 5.2961 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5817350 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-09-24 | 2026-12-01 | 2028-01-06 | Project Design | Scope Change | FALSE | 113900 | NA ¦ NA | 24.3641 | 4393.8713 | 0 | 0 | 0 | 0 | 7.4195 | 547.0986 | 0 | 0 | 0 | 0 | 7.4195 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1468 | Tesla - Newark: 230kV Remote End |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | 19 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5793938 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-02-22 | 2026-12-01 | 2028-03-20 | Project Design | Scope Change | TRUE | 113900 | NA ¦ NA | 311.5038 | 942.8513 | 40.6865 | 27.7173 | 1.0518 | 166.7453 | 61.4916 | 153.3577 | 19.0751 | 0 | 0 | 0 | 297.6925 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1469 | TESLA - INSTALL 230KV MPAC (SECT D & E) |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | 59 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 288 | NA | NA | 5.3 | Non-IGP | 5795886 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-26 | 2026-12-01 | 2028-07-13 | Project Design | Scope Change | FALSE | 113900 | NA ¦ NA | 9806.9223 | 72303.985 | 4.2051 | 20.7825 | 23.468 | 2060.2869 | 7281.5724 | 19243.0147 | 0 | 0 | 0 | 0 | 9390.3149 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1470 | Tesla - Kelso: 230kV Remote End |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | 33 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5793940 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-02-05 | 2026-12-01 | 2029-03-05 | Project Design | Scope Change | FALSE | 113900 | NA ¦ NA | 334.3758 | 5223.93 | 35.7249 | 23.4664 | 0.8414 | 205.3368 | 57.3606 | 153.242 | 195.9594 | 0 | 0 | 0 | 322.7302 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1471 | Tesla - Delta SW YD (CDWR): 230kV Rm End |  |  | Brentwood, Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | NA | 9 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5795708 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-01-25 | 2026-12-01 | 2029-03-22 | Prioritization | NA | FALSE | 113900 | NA ¦ NA | 77.8349 | 444.4662 | 12.2316 | 16.0067 | 1.0464 | 9.6479 | 34.345 | 52.3507 | 56.6318 | 262.2061 | 0 | 0 | 73.2776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1472 | Tesla - Kelso Ralph Greenridge WndPwr4 |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-31 | 33 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.4538 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5795709 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-03-26 | 2026-12-01 | 2029-05-18 | Prioritization | NA | FALSE | 113900 | NA ¦ NA | 51.8715 | 445.8094 | 1.4457 | 8.2826 | 0 | 14.9832 | 25.29 | 69.2284 | 55.2106 | 264.2319 | 7.1371 | 0 | 50.0014 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1473 | Transformer Bank #4 Relay Replacement |  |  | San Joaquin | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-05 | 20 | Lifecycle Replacement Analysis | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 5.2961 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5817349 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-05-01 | 2026-12-01 | 2029-07-12 | Project Design | Scope Change | FALSE | 113900 | NA ¦ NA | 29.5594 | 3860.0395 | 0 | 0 | 0 | 0 | 7.7407 | 440.3024 | 0 | 0 | 0 | 0 | 7.7407 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1474 | Tesla - Ravenswood: 230kV Remote End |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | 28 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5793900 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2030-01-18 | 2026-12-01 | 2030-02-15 | Project Design | Scope Change | FALSE | 113900 | NA ¦ NA | 532.0435 | 3342.5327 | 52.1957 | 22.9714 | 0.8923 | 355.4057 | 84.5948 | 226.1247 | 1157.7102 | 0 | 0 | 0 | 516.0598 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1475 | Tesla - Eight Mile Road: 230kV Remote En |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | 33 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5793901 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2030-02-19 | 2026-12-01 | 2030-04-15 | Prioritization | NA | FALSE | 113900 | NA ¦ NA | 715.4067 | 6105.685 | 41.1083 | 17.2395 | 0.8414 | 306.1964 | 312.4914 | 1528.335 | 1391.4398 | 0 | 0 | 0 | 677.877 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1476 | TESLA: 230kV MPAC - 500kV Building Telecom |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 500 ¦ 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5812669 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2030-05-14 | 2026-12-01 | 2030-09-06 | Project Design | Scope Change | FALSE | 113900 | NA ¦ NA | 476.6487 | 6844.8956 | 0 | 0 | 0 | 0.7346 | 428.8989 | 228.3154 | 0 | 0 | 0 | 0 | 429.6335 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1477 | Tesla - Stag: 230kV Remote End |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | 33 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5793902 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2030-09-09 | 2026-12-01 | 2030-10-04 | Prioritization | NA | FALSE | 113900 | NA ¦ NA | 685.3567 | 5636.0884 | 63.0865 | 34.9163 | 1.0518 | 299.7621 | 237.2068 | 1548.4658 | 1730.663 | 0 | 0 | 0 | 636.0234 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1478 | Tesla - Weber: 230kV Remote End |  |  | San Joaquin | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | 9 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.1366 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5795704 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2030-11-04 | 2026-12-01 | 2030-12-04 | Prioritization | NA | FALSE | 113900 | NA ¦ NA | 254.0144 | 1474.4804 | 30.1353 | 12.2746 | 0.1017 | 147.6232 | 72.3019 | 118.4497 | 337.6909 | 438.6308 | 0 | 0 | 262.4368 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1479 | VASONA SUB CB 212 RELAY UPGRADE |  |  | Los Gatos, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-04 | 27 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.5367 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5780954 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2026-01-20 | 2023-03-31 | 2027-03-16 | Bundling Dependencies | NA | TRUE | 65600 | NA ¦ NA | 3785.3423 | 12491.3213 | 113.9815 | 770.7405 | 136.7045 | 92.8991 | 291.1817 | 10247.382 | 731.684 | 203.1452 | 20.0349 | 0 | 1512.2552 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1480 | METCALF: INSTALL 115 KV MPAC |  |  | Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Modular Protection and Automation Control Building | New | NA | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | 29 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 115 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5776763 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2024-08-13 | 2023-03-31 | 2027-04-19 | Bundling Dependencies | NA | TRUE | 65600 | NA ¦ NA | 30896.9664 | 51436.5245 | 6306.0685 | 3929.447 | 6223.7657 | 5001.1888 | 5418.8546 | 8785.8797 | 1887.7945 | 2478.4405 | 2743.6851 | 2283.4301 | 27440.6006 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1481 | EDENVALE SUB CB 472 RELAY UPGRADE |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-03 | 9 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3853 | NA | 115 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5781018 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-03-26 | 2023-03-31 | 2027-04-26 | Bundling Dependencies | NA | TRUE | 78700 | NA ¦ NA | 291.1995 | 751.9372 | 126.9099 | 116.6297 | 19.8431 | -15.2418 | 0 | 131.7008 | 320.2663 | 8.0516 | 0 | 0 | 291.1995 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1482 | EL PATIO SUB: CB 452&462 RELAY UPGRADE |  |  | Campbell, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-05 | 13 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.392 | NA | 115 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5780956 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-05-06 | 2023-03-31 | 2027-07-06 | Bundling Dependencies | NA | TRUE | 65600 | NA ¦ NA | 290.2989 | 938.4282 | 22.2872 | 190.5947 | 18.6375 | 9.4676 | 0 | 61.6539 | 484.4185 | 2.675 | 0 | 0 | 290.2989 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1483 | PIERCY SUB CB 422 RELAY UPGRADE |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009169 ¦ T.0009536 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-03 | 26 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.3509 | NA | 115 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5781019 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-08-31 | 2023-03-31 | 2028-01-25 | Bundling Dependencies | NA | FALSE | 65600 | NA ¦ NA | 744.3924 | 4176.5568 | 101.286 | 262.0768 | 112.0357 | 20.3621 | 121.0945 | 380.7463 | 2886.4485 | 130.6849 | 55.0554 | 0 | 723.6217 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1484 | LOS ESTEROS SUB CB 362&462 RELAY UPGRADE |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-09 | 27 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.1703 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5780953 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-10-24 | 2023-03-31 | 2029-01-08 | Bundling Dependencies | NA | FALSE | 65600 | NA ¦ NA | 361.7085 | 1233.6547 | 17.8543 | 243.6211 | 23.4386 | 11.842 | 0 | 22.015 | 65.6959 | 784.2353 | 0 | 0 | 361.7085 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1485 | IBM-BAILEY SUB UPGRADE TAP |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-03 | 9 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3853 | NA | 115 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5781021 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-02-01 | 2023-03-31 | 2029-03-21 | Bundling Dependencies | NA | FALSE | 65600 | NA ¦ NA | 217.9682 | 808.9848 | 118.0253 | 35.2336 | 13.9675 | 6.9478 | 0 | 13.2664 | 189.4864 | 388.2638 | 0 | 0 | 217.9682 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1486 | SWIFT_INSTALL 115KV RELAY PACKAGE |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Other - Operations Tech | Upgrade/Retrofit | NA | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-06 | 29 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.1012 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5792225 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-09-07 | 2023-03-31 | 2029-09-24 | Bundling Dependencies | NA | FALSE | 65600 | NA ¦ NA | 606.128 | 2817.6907 | 18.4958 | 492.7942 | 72.672 | 22.1661 | 0 | 36.8914 | 94.3974 | 1013.7019 | 1019.9963 | 46.5757 | 606.128 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1487 | METCALF: INSTALL 230KV MPAC |  |  | Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | 28 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5776764 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-05-09 | 2023-03-31 | 2024-02-20 | Bundling Dependencies | NA | TRUE | 65600 | NA ¦ NA | 55896.6997 | 64649.0328 | 11177.8794 | 17581.8405 | 10416.3042 | 7736.7902 | 5132.1616 | 4242.8964 | 890.5982 | 1508.7216 | 1991.0337 | 16.385 | 54855.0619 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 43726.1418 | 4447.2355 | 902.6233 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1488 | MOSS LANDING: RELAY WORK - METCALF MPAC |  |  | Monterey | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-10 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 41.3213 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | 10 | 5.3 | Non-IGP | 5781029 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-07-15 | 2023-03-31 | 2024-10-12 | Bundling Dependencies | NA | TRUE | 65600 | NA ¦ NA | 2298.6878 | 2298.6878 | 103.8679 | 419.8455 | 45.4972 | 959.7698 | 729.5099 | 0.6681 | 0 | 0 | 0 | 0 | 2298.0197 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1486.4401 | 688.2806 | 0.63029 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1489 | COYOTE CB 382 RELAY UPGRADE |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-03 | 21 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.5453 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | NA | 5.3 | Non-IGP | 5780955 | T.0003803 | Metcalf 230kV & 115kV MPACs | 13 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-02-24 | 2023-03-31 | 2025-04-19 | Bundling Dependencies | NA | TRUE | 78700 | NA ¦ NA | 1359.959 | 1359.959 | 113.581 | 211.9408 | 32.1176 | 113.4908 | 833.4044 | 0 | 0 | 0 | 0 | 0 | 1359.959 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1275.6088 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1490 | WILSON: Install 115 KV MPAC |  |  | Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | 21 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 22.8151 | NA | 115 kV | 58 | 5a.Mitigates System Wide Failure Risk | 7 | 5.3 | Non-IGP | 5781261 | T.0004116 | WILSON: 115 kV ARP - BAAH | 7 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-11-13 | 2022-08-12 | 2029-10-29 | Prioritization | NA | FALSE | 66700 | NA ¦ NA | 118.6241 | 19452.9582 | 3.429 | 0 | 0 | 1.7049 | 19.2216 | 46.2247 | 8030.6828 | 2195.4908 | 4.6947 | 2.1214 | 114.205 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1491 | Wilson: Install 230KV MPAC |  |  | Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Modular Protection and Automation Control Building | New | NA | T.0001381 ¦ T.0002231 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 22.8151 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5816464 | T.0004116 | WILSON: 115 kV ARP - BAAH | 7 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-11-13 | 2022-08-12 | 2030-01-07 | Prioritization | NA | FALSE | 66700 | NA ¦ NA | 0 | 19558.8025 | 0 | 0 | 0 | 0 | 0 | 9.8585 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1492 | Pittsburg PP: Install 230kV Bus E MPAC |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | New | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | Lifecycle Replacement Analysis | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 28.8512 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5815203 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2025-07-09 | 2025-08-31 | 2027-04-13 | Bundling Dependencies | NA | TRUE | 64600 | NA ¦ NA | 12783.915 | 22425.3502 | 0 | 0 | 0 | 0 | 12225.2987 | 3596.0242 | 2331.6788 | 0 | 0 | 0 | 12225.2987 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1493 | SAN RAMON_UPGRADE PITTS MPAC REMOTE END |  |  | San Ramon, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | 10 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.3628 | NA | 230 ¦ 115 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.3 | Non-IGP | 5790830 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-06 | 2025-08-31 | 2026-04-28 | Bundling Dependencies | NA | TRUE | 64600 | NA ¦ NA | 731.1098 | 1227.4463 | 17.7646 | 25.0331 | 141.2079 | 91.956 | 407.1044 | 445.3719 | 47.2266 | 0 | 0 | 0 | 708.885 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1494 | TASSAJARA_UPGRADE PITTS MPAC REMOTE END |  |  | Blackhawk CDP, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-02 | 10 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.1384 | NA | 230 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.3 | Non-IGP | 5790831 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-27 | 2025-08-31 | 2026-06-26 | Bundling Dependencies | NA | TRUE | 64600 | NA ¦ NA | 564.5478 | 1573.0974 | 17.7314 | 13.0666 | 165.4465 | 193.6542 | 123.7927 | 949.587 | 55.6552 | 0 | 0 | 0 | 537.2553 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1495 | PITTSBURG TBC SFRAS_PITTSBURG MPAC UPGRA |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | 17 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 28.8512 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5791518 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-07-20 | 2025-08-31 | 2026-08-14 | Bundling Dependencies | NA | TRUE | 64600 | NA ¦ NA | 164.3897 | 862.2214 | 12.611 | 5.8231 | 7.4051 | 37.6805 | 82.3238 | 383.1931 | 74.486 | 40.208 | 0 | 0 | 156.5009 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1496 | TESORO_UPGRADE PITTS MPAC REMOTE END |  |  | Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-03 | 19 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.6359 | NA | 230 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | 23 | 5.3 | Non-IGP | 5790832 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-12-07 | 2025-08-31 | 2027-02-05 | Bundling Dependencies | NA | TRUE | 64600 | NA ¦ NA | 220.7482 | 1085.0028 | 18.8501 | 20.1029 | 14.1079 | 109.8175 | 29.5525 | 317.7 | 443.4364 | 36.31 | 28.997 | 150 | 213.7697 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1497 | PITTSBURG PP INSTALL 230KV BUS F MPAC |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 28.8512 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5801381 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-14 | 2025-08-31 | 2027-03-15 | Bundling Dependencies | NA | TRUE | 64600 | NA ¦ NA | 3230.3621 | 8041.277 | 0 | 5.6333 | 21.7628 | 40.3049 | 3092.4017 | 2256.6717 | 1333.8641 | 43.446 | 6.979 | 0 | 3160.1026 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1498 | TIDEWATER_UPGRADE PITTS MPAC REMOTE END |  |  | Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | 15 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.2848 | NA | 230 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | 9 | 5.3 | Non-IGP | 5790833 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-01-05 | 2025-08-31 | 2027-03-22 | Bundling Dependencies | NA | TRUE | 64600 | NA ¦ NA | 308.3078 | 1100.0021 | 16.3207 | 16.6836 | 42.9838 | 171.4505 | 32.1049 | 69.0314 | 617.4984 | 46.893 | 35.753 | 150 | 300.2129 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1499 | PITTSBURG PP: INSTALL 115KV BUS E MPAC |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | 24 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 28.8512 | NA | 115 kV | 137 | 5a.Mitigates System Wide Failure Risk | 14 | 5.3 | Non-IGP | 5784149 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-19 | 2025-08-31 | 2027-11-05 | Bundling Dependencies | NA | TRUE | 64600 | NA ¦ NA | 8879.9523 | 48720.659 | 148.5932 | 144.2491 | 410.3866 | 6879.2868 | 721.738 | 8407.1004 | 4032.5711 | 16300 | 21.638 | 0 | 8491.9206 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1500 | ELWORTHY_UPGRADE PITTS MPAC REMOTE END |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 28.8512 | NA | 230 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.3 | Non-IGP | 5791143 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-11-02 | 2025-08-31 | 2027-12-31 | Bundling Dependencies | NA | TRUE | 64600 | NA ¦ NA | 252.1211 | 1579.4556 | 22.474 | 16.3738 | 16.9591 | 46.773 | 128.0762 | 88.254 | 1009.5179 | 469.6274 | 0 | 0 | 245.8251 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1501 | TES_UPGRADE PITTS MPAC REMOTE END |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | 14 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 28.8512 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5791459 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-11-15 | 2025-08-31 | 2028-01-13 | Bundling Dependencies | NA | FALSE | 64600 | NA ¦ NA | 286.3694 | 883.0254 | 14.2995 | 10.9796 | 24.4263 | 172.6299 | 34.0947 | 74.9656 | 44.1493 | 217.2305 | 0 | 0 | 277.0486 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1502 | SAN MATEO_UPGRADE PITTS MPAC REMOTE END |  |  | San Mateo, San Mateo | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-17 | 14 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | 230 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | 7 | 5.3 | Non-IGP | 5790829 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-06-09 | 2025-08-31 | 2028-01-21 | Bundling Dependencies | NA | FALSE | 64600 | NA ¦ NA | 299.7861 | 1184.5857 | 22.4811 | 18.7651 | 11.7591 | 189.4227 | 28.2432 | 312.2759 | 172.3672 | 187.2595 | 0 | 0 | 295.195 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1503 | EASTSHORE_UPGRADE PITTS MPAC REMOTE END |  |  | Hayward, Alameda | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.9849 | NA | 230 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.3 | Non-IGP | 5790828 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-04-20 | 2025-08-31 | 2028-02-04 | Bundling Dependencies | NA | FALSE | 64600 | NA ¦ NA | 230.8108 | 938.1085 | 18.7618 | 17.6795 | 9.2877 | 63.1931 | 45.2612 | 118.4566 | 94.2701 | 217.6994 | 15.9468 | 0 | 178.2786 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1504 | LAKEWOOD_UPGRADE PITTS MPAC REMOTE END |  |  | Walnut Creek, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-02 | 25 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.1281 | NA | 230 ¦ 115 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | 8 | 5.3 | Non-IGP | 5790835 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-10-04 | 2025-08-31 | 2028-02-07 | Bundling Dependencies | NA | FALSE | 64600 | NA ¦ NA | 1436.4315 | 2957.5842 | 63.4473 | 652.1539 | 296.1396 | 248.2254 | 125.1009 | 159.5514 | 120.0787 | 679.8304 | 290.3544 | 27.3951 | 1413.968 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1505 | Pittsburg PP: Install 115kV Bus D MPAC |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | New | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | Lifecycle Replacement Analysis | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 28.8512 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5815204 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-09-16 | 2025-08-31 | 2028-03-28 | Bundling Dependencies | NA | FALSE | 64600 | NA ¦ NA | 7699.8183 | 25569.9768 | 0 | 0 | 0 | 0 | 7557.9751 | 4988.3888 | 0 | 0 | 0 | 0 | 7557.9751 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1506 | CLAYTON_UPGRADE PITTS MPAC REMOTE END |  |  | Concord, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | 24 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.9731 | NA | 230 ¦ 115 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | 11 | 5.3 | Non-IGP | 5790834 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-11-01 | 2025-08-31 | 2028-04-11 | Bundling Dependencies | NA | FALSE | 64600 | NA ¦ NA | 822.5798 | 7679.6023 | 27.5026 | 30.0953 | 13.9577 | 333.2145 | 371.528 | 101.2749 | 2476.77 | 3850.164 | 390.451 | 49.667 | 811.2754 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1507 | VGCC PACI RAS_PITTSBURG MPAC UPGRADE |  |  | Solano | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | NA | 16 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.3 | Non-IGP | 5790819 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-12-02 | 2025-08-31 | 2028-05-16 | Bundling Dependencies | NA | FALSE | 64600 | NA ¦ NA | 79.2723 | 1114.1094 | 7.2505 | 12.4129 | 5.0137 | 31.8657 | 14.1172 | 306.5457 | 55.8794 | 13.5026 | 92.113 | 22.9387 | 76.8684 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1508 | SFCC PACI RAS_PITTSBURG MPAC UPGRADE |  |  | San Francisco, San Francisco | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | NA | 16 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2173 | NA | 230 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.3 | Non-IGP | 5790863 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-12-02 | 2025-08-31 | 2028-05-16 | Bundling Dependencies | NA | FALSE | 64600 | NA ¦ NA | 59.135 | 1043.1622 | 7.2826 | 18.2766 | 5.8097 | 10.2701 | 8.5326 | 405.2156 | 0 | 0 | 0 | 0 | 57.5279 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1509 | CCCSD_IMHOFF_UPGRADE PITTS MPAC REMOTE E |  |  | Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-02 | 24 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.21496 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5791519 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-06-14 | 2025-08-31 | 2028-07-13 | Bundling Dependencies | NA | FALSE | 64600 | NA ¦ NA | 146.4681 | 1213.8846 | 16.1302 | 23.6973 | 20.9303 | 23.9817 | 22.5724 | 60.2888 | 104.7227 | 321.9618 | 6.0823 | 0 | 140.6376 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1510 | WILLOW PASS_UPGD_PITTSBURG_REMOTE E |  |  | Bay Point CDP, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.061 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5812294 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-02-07 | 2025-08-31 | 2031-01-30 | Prioritization | NA | FALSE | 64600 | NA ¦ NA | 25.7684 | 594.2641 | 0 | 0 | 0 | 0 | 24.1388 | 38.0627 | 0 | 0 | 0 | 0 | 24.1388 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1511 | PITTSBURG PP: INSTALL 230KV BUS D MPAC |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | 23 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 28.8512 | NA | 230 kV | 137 | 5a.Mitigates System Wide Failure Risk | 14 | 5.3 | Non-IGP | 5784148 | T.0004581 | Pittsburg PP MPAC Installation | 23 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-01-03 | 2025-08-31 | 2026-01-26 | NA | NA | TRUE | 64600 | NA ¦ NA | 21129.1597 | 32262.4282 | 705.4687 | 240.9185 | 1533.5323 | 11252.5204 | 5713.3207 | 2590.7208 | 1961.8151 | 4.866 | 23.4574 | 0 | 20078.417 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 19817.0184 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1512 | GOLD HILL 115_60kV - PACI RAS @ VGCC |  |  | Vacaville, Solano | Install protection, automation, and control equipment on the 230 kV, 115 kV and 60 kV system at Gold Hill Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | T.0004950 ¦ EX138973 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-02 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.725 | NA | 115 ¦ 60 kV | NA | NA | NA | 5.3 | Non-IGP | 5814670 | T.0004920 | Gold Hill: Install 115/60kV MPAC | 2 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-08 | 2023-11-30 | 2027-05-07 | Prioritization | NA | TRUE | 12200 | NA ¦ NA | 115.7598 | 1038.6234 | 0 | 0 | 0 | 0 | 82.9687 | 919.6086 | 36.0461 | 0 | 0 | 0 | 82.9687 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1513 | GOLD HILL: Install 115/60kV MPAC |  |  | Folsom, Sacramento | Install protection, automation, and control equipment on the 230 kV, 115 kV and 60 kV system at Gold Hill Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | NA | T.0004950 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | 36 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 12.8702 | NA | 115 kV | 472 | 5a.Mitigates System Wide Failure Risk | NA | 5.21 | Non-IGP | 5786799 | T.0004920 | Gold Hill: Install 115/60kV MPAC | 2 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-09-26 | 2023-11-30 | 2025-11-19 | Prioritization | NA | TRUE | 12200 | NA ¦ NA | 20693.4569 | 27850.1545 | 117.4837 | 213.6133 | 7510.7253 | 6429.6969 | 6137.5415 | 3243.3234 | 3247.2135 | 11.7391 | 0 | 0 | 20424.1352 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 20424.1352 | 269.3217 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1514 | GOLD HILL: Install 230kV MPAC |  |  | Folsom, Sacramento | Install protection, automation, and control equipment on the 230 kV, 115 kV and 60 kV system at Gold Hill Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | NA | T.0004950 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | 38 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 12.8702 | NA | 230 kV | 472 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.21 | Non-IGP | 5789535 | T.0004950 | Gold Hill: Installl 230/115 kV Txfmr | 5 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-10-04 | 2023-11-30 | 2030-01-07 | Prioritization | NA | FALSE | 12200 | NA ¦ NA | 647.4 | 29718.2363 | 15.5843 | 1.3312 | 1.464 | 165.8426 | 395.6843 | 1318.3017 | 868.1695 | 16584.4198 | 2500 | 0 | 582.6231 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1515 | RELAY REPL 230KV FULTON - LAKEVILLE LINE |  |  | Sonoma | Install protection, automation, and control equipment on the 230 kV system at Fulton Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 230 kV system and non-standard bus differential scheme that reduce the reliability of the station. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0007811 ¦ T.0007660 ¦ T.0005942 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-13 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 14.7021 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5797641 | T.0005940 | Fulton MPACs & Remote Ends | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-09-27 | NA | 2029-01-18 | NA | NA | FALSE | NA | NA ¦ NA | 76.2547 | 1661.8644 | 18.752 | 11.2536 | 10.7171 | 3.0626 | 26.3796 | 38.0746 | 0 | 0 | 0 | 0 | 70.1648 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1516 | 115KV RELAY REPL FULTON - EAGLE ROCK |  |  | Sonoma | Install protection, automation, and control equipment on the 230 kV system at Fulton Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 230 kV system and non-standard bus differential scheme that reduce the reliability of the station. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0007811 ¦ T.0007660 ¦ T.0005942 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | NA | NA | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.49 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5797642 | T.0005940 | Fulton MPACs & Remote Ends | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2029-09-14 | NA | 2030-01-24 | NA | NA | FALSE | NA | NA ¦ NA | 62.4895 | 3224.7841 | 7.0706 | 4.4778 | 9.2856 | 1.7107 | 23.6694 | 103.183 | 0 | 0 | 0 | 0 | 46.2141 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1517 | FULTON_INSTALL 230KV MPAC |  |  | Fulton CDP, Sonoma | Install protection, automation, and control equipment on the 230 kV system at Fulton Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 230 kV system and non-standard bus differential scheme that reduce the reliability of the station. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation. | Substation - Modular Protection and Automation Control Building | New | NA | T.0007811 ¦ T.0007660 ¦ T.0005942 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-11 | 68 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.4076 | NA | 230 kV | 672 | 5. Compliance/Commitments With Strong Safety Link | 2 | 5.3 | Non-IGP | 5790905 | T.0005940 | Fulton MPACs & Remote Ends | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-04-06 | NA | 2029-01-18 | NA | NA | FALSE | NA | NA ¦ NA | 1032.3381 | 53525.9776 | 200.5668 | 87.1648 | 29.4322 | 83.1357 | 589.71 | 3360.0468 | 13294.3272 | 68.0835 | 0 | 0 | 990.0095 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1518 | FULTON_INSTALL 115KV MPAC |  |  | Fulton CDP, Sonoma | Install protection, automation, and control equipment on the 115 kV system at Fulton Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 kV system and non-standard bus differential scheme that reduce the reliability of the station. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 20 years. The 115 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation. | Substation - Modular Protection and Automation Control Building | New | NA | T.0007811 ¦ T.0007660 ¦ T.0005940 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-11 | 28 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.4076 | NA | 115 kV | 166 | 5. Compliance/Commitments With Strong Safety Link | 2 | 5.3 | Non-IGP | 5790906 | T.0005940 | Fulton MPACs & Remote Ends | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-10-19 | NA | 2030-01-24 | NA | NA | FALSE | NA | NA ¦ NA | 377.7137 | 40177.1839 | 155.953 | 62.6707 | 24.1705 | 57.7228 | 67.4021 | 434.1755 | 14065.663 | 2285.2723 | 0 | 0 | 367.9189 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1519 | FULTON SUB - INSTALL 60KV MPAC |  |  | Fulton CDP, Sonoma | Install 60 kV MPAC at Fulton substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 60 kV system and non-standard bus differential scheme that reduce the reliability of the station. This project proposes to deploy a new 60 kV MPAC enclosure to support the concurrent, 230 kV and 115 kV MPAC Projects. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 60 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation, and the interconnected stations at the remote-end. | Substation - Modular Protection and Automation Control Building | New | NA | T.0007811 ¦ T.0005942 ¦ T.0005942 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-11 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.4076 | NA | 60 kV | NA | NA | NA | 5.3 | Non-IGP | 5798447 | T.0005940 | Fulton MPACs & Remote Ends | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-03-31 | NA | 2031-01-24 | NA | NA | FALSE | NA | NA ¦ NA | 218.3598 | 27583.3227 | 13.6996 | 83.0211 | 15.1094 | 41.6203 | 59.2156 | 339.5511 | 9102.5678 | 7808.1675 | 53.3428 | 0 | 212.6659 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1520 | RELAY REPL 230KV FULTON - IGNACIO LINE |  |  | Novato, Marin | Install protection, automation, and control equipment on the 230 kV system at Fulton Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 230 kV system and non-standard bus differential scheme that reduce the reliability of the station. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0007811 ¦ T.0007660 ¦ T.0005942 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.9486 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5797640 | T.0005940 | Fulton MPACs & Remote Ends | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-10-06 | NA | 2029-01-18 | NA | NA | FALSE | NA | NA ¦ NA | 57.0041 | 1787.2188 | 6.5457 | 11.8189 | 9.3051 | 2.1194 | 22.7028 | 35.3296 | 0 | 0 | 0 | 0 | 52.4919 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1521 | RELAY REPL 115KV FULTON - SANTA ROSA A |  |  | Santa Rosa, Sonoma | Install protection, automation, and control equipment on the 115 kV system at Fulton Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 kV system and non-standard bus differential scheme that reduce the reliability of the station. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 20 years. The 115 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0007811 ¦ T.0007660 ¦ T.0005940 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-02 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.91804 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5797644 | T.0005940 | Fulton MPACs & Remote Ends | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-09-26 | NA | 2030-01-24 | NA | NA | FALSE | NA | NA ¦ NA | 43.0974 | 1469.8508 | 12.9284 | 10.1582 | 9.6574 | 2.599 | 6.6923 | 27.4121 | 0 | 0 | 0 | 0 | 42.0352 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1522 | PLACER: Install 115/60kV MPAC |  |  | Placer | Deploy 115 kV MPAC and Upgrade 60 kV protective relaying equipment in the existing control building. The driver of the new MPAC building enclosure is to support the concurrent Placer 115 kV Bus Conversion Project in the same substation (MWC 61 & MWC 94) and various Placer substation Bus Protection Upgrade projects (MWC 3F), and Placer Transformer Addition Project (MWC 61). | Substation - Modular Protection and Automation Control Building | New | NA | T.0005697 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-04 | 66 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.9734 | NA | 115 kV | 439 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.11 | Non-IGP | 5733505 | T.0006004 | Placer: Install 115/60kV MPAC | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-06-18 | 2024-06-30 | 2028-01-07 | Prioritization | NA | FALSE | 12200 | NA ¦ NA | 3958.3299 | 28067.431 | 154.1883 | 180.1054 | 2973.3098 | 285.2683 | 278.8061 | 3423.8791 | 8020.33 | 6166.459 | 6000 | 500 | 3906.7629 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1523 | Lawrence: Install 115kV MPAC |  |  | Sunnyvale, Santa Clara | Install protection, automation, and control equipment on the 115 kV system at Lawrence Substation. The driver of the new MPAC building enclosure is to support the concurrent Lawrence 115 kV Ring Bus Conversion Project in the same substation (MWC 94). The Lawrence MPAC project will also address the “Fault Protection Scheme Deficiency” concerns at Lawrence substation. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-05 | 27 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.8829 | NA | 115 kV | 133 | NA | NA | 5.3 | Non-IGP | 5791858 | T.0006096 | Lawrence_Install 115kV MPAC | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2028-07-26 | NA | 2030-04-04 | NA | NA | FALSE | NA | NA ¦ NA | 152.5824 | 12411.4477 | 94.798 | 6.8959 | 7.5837 | 3.8794 | 30.8568 | 1517.434 | 7000 | 2500 | 1000 | 250 | 144.0138 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1524 | RAVENSWOOD SUB: INSTALL 115KV MPAC |  |  | Menlo Park, San Mateo | Install protection, automation, and control equipment on the 115 kV & 230 kV systems at Ravenswood Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 & 230 kV systems and non-standard bus differential scheme that reduce the reliability of the station.The 115 kV & 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Ravenswood Substation. | Substation - Modular Protection and Automation Control Building | New | NA | T.0007874 ¦ T.0001608 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.3472 | NA | 115 kV | NA | NA | NA | 5.21 | Non-IGP | 5797793 | T.0006509 | RAVENSWOOD SUB_INSTALL 230KV MPAC | 2 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-11-28 | NA | 2029-10-18 | NA | NA | FALSE | NA | NA ¦ NA | 204.1942 | 48403.4987 | 3.2776 | 136.8022 | -0.1875 | 2.748 | 46.9275 | 523.4709 | 2687.0986 | 3945.4281 | 319.7011 | 0 | 189.5678 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1525 | RAVENSWOOD SUB: INSTALL 230KV MPAC |  |  | Menlo Park, San Mateo | Install protection, automation, and control equipment on the 115 kV & 230 kV systems at Ravenswood Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 & 230 kV systems and non-standard bus differential scheme that reduce the reliability of the station.The 115 kV & 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Ravenswood Substation. | Substation - Modular Protection and Automation Control Building | New | NA | T.0007874 ¦ T.0001608 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | 28 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.3472 | NA | 230 kV | 184 | NA | NA | 5.21 | Non-IGP | 5792885 | T.0006509 | RAVENSWOOD SUB_INSTALL 230KV MPAC | 2 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-12-29 | NA | 2030-02-28 | NA | NA | FALSE | NA | NA ¦ NA | 469.4698 | 64841.8366 | 76.9524 | 310.7713 | -0.0301 | 7.6899 | 57.5892 | 482.7585 | 4881.2399 | 838.4503 | 178.0171 | 3.8088 | 452.9727 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1526 | SMARTVILLE SUB: INSTALL 60KV MPAC |  |  | Smartsville CDP, Yuba | Install protection, automation, and control equipment on the 60kV system at Smartville Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to execute concurrently with the bus conversion project from existing MaiNAux to DBSB in 94D. Smartville 60kV has lots of EM relays and makes sense to deploy MPAC solution and align with the bus work schedule. 60kV Bus Diff = KAB installed in Y1996. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.2017 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | 5792886 | T.0006510 | SMARTVILLE SUB_INSTALL 60KV MPAC | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-04-01 | NA | 2032-06-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 9500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 500 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1527 | Banta 115kV Conversion - MPAC Building |  |  | San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-04 | NA | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.54319 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5806221 | T.0006962 | Banta: Repl Bk 1 & Inst 115kV Ring Bus | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-08-11 | 2024-12-31 | 2027-12-10 | Prioritization | NA | TRUE | 17500 | NA ¦ NA | 3312.542 | 7151.8357 | 0 | 0 | 0 | 582.3639 | 2679.4442 | 1790.0276 | 1168.1795 | 600 | 0 | 0 | 3261.8081 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1528 | BANTA: UPGRADE TRACY REMOTE END |  |  | Tracy, San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-31 | 29 | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.7469 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5552803 | T.0006962 | Banta: Repl Bk 1 & Inst 115kV Ring Bus | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-10-08 | 2024-12-31 | 2027-12-16 | Prioritization | NA | TRUE | 17500 | NA ¦ NA | 157.6974 | 1102.3272 | 0 | 0 | 1.6975 | 40.5957 | 111.2425 | 198.7915 | 228.9021 | 250 | 0 | 0 | 153.5357 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 153.5357 | 4.1617 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1529 | BANTA: UPGRADE KASSON REMOTE END |  |  | San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-31 | 9 | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.1988 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5552802 | T.0006962 | Banta: Repl Bk 1 & Inst 115kV Ring Bus | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-10-06 | 2024-12-31 | 2028-01-27 | Prioritization | NA | TRUE | 17500 | NA ¦ NA | 280.8732 | 2274.108 | 0 | 0 | 5.833 | 62.7487 | 202.1329 | 753.3934 | 715.5231 | 250 | 0 | 0 | 270.7146 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 68.5817 | 202.1329 | 10.1586 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1530 | BANTA: UPGRADE VIERRA REMOTE END |  |  | Lathrop, San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-06 | 28 | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.355 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5552804 | T.0006962 | Banta: Repl Bk 1 & Inst 115kV Ring Bus | 8 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-08-18 | 2024-12-31 | 2028-03-09 | Prioritization | NA | TRUE | 17500 | NA ¦ NA | 201.9885 | 2434.686 | 0 | 0 | 3.1428 | 18.4429 | 168.0328 | 325.5322 | 1324.5934 | 370 | 0 | 0 | 189.6186 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 185.7562 | 12.118 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1531 | MT VIEW SUB - INSTALL 115KV MPAC |  |  | Mountain View, Santa Clara | Install 115 kV MPAC at Mountain View substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 kV system and non-standard bus differential scheme that reduce the reliability of the station. This project proposes to deploy a new 115 kV MPAC enclosure to support the concurrent, 115 kV Bus Conversion, Transformer #1 Replacement, and Feeder Circuit Breaker Replacement projects. Mountain View is one of the key substations in the Central Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 115 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Mountain View Substation, and the interconnected stations at the remote-end. | Substation - Modular Protection and Automation Control Building | New | NA | T.0005971 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.8224 | NA | 115 kV | NA | NA | NA | 5.21 | Non-IGP | 5799139 | T.0007709 | MT VIEW SUB - INSTALL 115KV MPAC | 2 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-08-25 | 2027-02-10 | 2027-06-18 | NA | NA | TRUE | 10540 | NA ¦ NA | 6998.4342 | 9356.2236 | 1.3816 | 411.8691 | 1417.6325 | 743.0281 | 4002.2567 | 1908.8782 | 864.4117 | 0 | 0 | 0 | 6576.1679 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1532 | Monta Vista: Upgrade Mt View MPAC Remote |  |  | Cupertino, Santa Clara | Install 115 kV MPAC at Mountain View substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 kV system and non-standard bus differential scheme that reduce the reliability of the station. This project proposes to deploy a new 115 kV MPAC enclosure to support the concurrent, 115 kV Bus Conversion, Transformer #1 Replacement, and Feeder Circuit Breaker Replacement projects. Mountain View is one of the key substations in the Central Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 115 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Mountain View Substation, and the interconnected stations at the remote-end. | Other - Operations Tech | Upgrade/Retrofit | NA | T.0005971 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8314 | NA | 115 kV | NA | NA | NA | 5.21 | Non-IGP | 5799751 | T.0007709 | MT VIEW SUB - INSTALL 115KV MPAC | 2 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-03-15 | 2027-02-10 | 2027-09-10 | Permitting | NA | TRUE | 10540 | NA ¦ NA | 554.6729 | 2299.9403 | 0 | 135.192 | 21.512 | 50.9588 | 339.7907 | 419.4748 | 1320.9632 | 27.6761 | 0 | 0 | 547.4535 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1533 | LOCKEFORD: INSTALL 115KV MPAC |  |  | Lockeford CDP, San Joaquin | This project proposes to reconfigure the Lockeford 115 kV bus into a Breaker-And-A-Half (BAAH) bus configuration starting in June 2022 and completing it by December 2027. This project will improve operational flexibility and electric service reliability for the customers in San Joaquin County. Upon completion of this project, the frequency and duration of electric service interruption will be significantly reduced, and the aging protection, automation, and control assets of the Lockeford 115 kV system will be replaced with Modular Protection Automation & Control enclosure (MPAC) under MWC 67. In addition, this project is also needed to support the installation of a new 115/21 kV distribution bank, which is aimed to go operational under MWC 46 in 2027. Completion of this project will facilitate the removal of the 75-year-old, deteriorated and idle 115/60 kV Lockeford bank1 that is currently being used for distribution bank 4 back up. The project scope of work includes the following: • Demolish existing 115 kV OCBs and associated switches • Convert Lockeford 115 kV Bus to Breaker-And-A-Half (BAAH) configuration • Install 8 Circuit Breakers; Three (3) BAAH bays • Install Breaker/Line disconnect Switches • Install CCVT as required • Install Bank Disconnect Switches, install necessary conduits and pull new wires as required | Substation - Modular Protection and Automation Control Building | New | NA | T.0002193 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2719 | NA | 115 kV | NA | NA | NA | 5.2 | Non-IGP | 5801426 | T.0008354 | Lockeford: Convert 115 kV Bus to BAAH | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-04-01 | NA | 2030-06-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 18000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 500 | 9000 | 6000 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1534 | Digital Sub Phase 2 French Camp |  |  | San Joaquin | This project proposes to develop DSS training infrastructure and related training materials and replace the current substation PAC scheme at French Camp with a PAC scheme deployed to the IEC 61850 standard in order to: • Improve PG&Es understanding and proficiency with IEC 61850 to help define PG&E specific standards, processes, and roles and responsibilities. • Provide a live substation where IEC 61850 based protection schemes and communication networks can be operated and maintained to prepare PG&E for large scale deployment of IEC 61850. • Document deployment cost and schedule benefits/challenges relative to PG&Es current SMP standard for PAC | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-04 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.85162 | NA | 60 kV | NA | NA | NA | 5.3 | Non-IGP | 5814821 | T.0011115 | Digital Sub Phase 2 French Camp | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-05-01 | NA | 2027-06-29 | NA | NA | TRUE | NA | NA ¦ NA | 642.1074 | 11901.2184 | 0 | 0 | 0 | 0 | 269.5425 | 6427.1848 | 5197.184 | 0 | 0 | 0 | 269.5426 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1535 | Digital Sub Phase 2 Jarvis |  |  | Union City, Alameda | This project proposes upgrading the current substation PAC scheme at Jarvis with a PAC scheme deployed to the IEC 61850 standard in order to: • Improve PG&Es understanding and proficiency with IEC 61850 to help define PG&E specific standards, processes, and roles and responsibilities. • Provide a live substation where IEC 61850 based protection schemes and communication networks can be operated and maintained to prepare PG&E for large scale deployment of IEC 61850. • Document deployment cost and schedule benefits/challenges relative to PG&Es current SMP standard for PAC PG&E hypothesizes that deploying Digital Substation (DSS) technology in accordance with the IEC 61850 standard will reduce overall asset management costs relative to the deployment of PG&E’s current Protection, Automation, and Control (PAC) scheme standards and processes. Transitioning to IEC 61850 will also reduce duration for the design, procure, construct, and commission of PAC schemes. DSS will support the upcoming demand for upgrades and capacity increases to the Electrical T&D system. DSS benefits customers with long term cost savings, future system flexibility, increased safety and increased deployment speed for new electrical capacity. To confirm this hypothesis, phase 2 of the DSS program will deploy new PAC schemes based upon the IEC 61850 standard at two Proof of Concept (PoC) sites. French Camp was the first of these two PoC substations. Jarvis will be the second. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.9822 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5814822 | T.0011116 | Digital Sub Phase 2 Jarvis | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-12-01 | NA | 2027-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 1.2222 | 9087.9132 | 0 | 0 | 0 | 0 | 0 | 2019.8222 | 6393.0693 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1536 | MONTA VISTA UPGRADE RELAYS |  |  | Los Gatos, Santa Clara | Install protection, automation, and control equipment on the 115kV system at Monta Vista Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0000675 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-05 | 17 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.7484 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5817359 | T.0011178 | Monta Vista: Install 115kV MPAC | 6 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-11-18 | NA | 2028-07-05 | NA | NA | FALSE | NA | NA ¦ NA | 39.5232 | 6460.6684 | 0 | 0 | 0 | 0 | 7.3261 | 869.2365 | 0 | 0 | 0 | 0 | 7.3261 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1537 | STELLING: Upgrade Monta Vista 115kV MPAC |  |  | Cupertino, Santa Clara | Install protection, automation, and control equipment on the 115kV system at Monta Vista Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | T.0000675 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-02 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.5481 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5816465 | T.0011178 | Monta Vista: Install 115kV MPAC | 6 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-06-13 | NA | 2028-08-14 | NA | NA | FALSE | NA | NA ¦ NA | 7.1369 | 2955.5429 | 0 | 0 | 0 | 0 | 6.9748 | 91.6628 | 0 | 0 | 0 | 0 | 6.9748 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1538 | LOS GATOS UPGRADE REM END |  |  | Cupertino, Santa Clara | Install protection, automation, and control equipment on the 115kV system at Monta Vista Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0000675 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | 12 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.8314 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5817358 | T.0011178 | Monta Vista: Install 115kV MPAC | 6 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-08-04 | NA | 2028-10-04 | NA | NA | FALSE | NA | NA ¦ NA | 1.3242 | 2537.6416 | 0 | 0 | 0 | 0 | 1.3076 | 88.5275 | 0 | 0 | 0 | 0 | 1.3076 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1539 | WHISMAN UPGRADE REMOTE END |  |  | Mountain View, Santa Clara | Install protection, automation, and control equipment on the 115kV system at Monta Vista Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0000675 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-05 | 7 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.1069 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5817378 | T.0011178 | Monta Vista: Install 115kV MPAC | 6 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-06-29 | NA | 2029-08-29 | NA | NA | FALSE | NA | NA ¦ NA | 1.9302 | 2707.3353 | 0 | 0 | 0 | 0 | 1.5984 | 183.7875 | 0 | 0 | 0 | 0 | 1.5984 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1540 | WOLFE: Upgrade Monta Vista 115kV MPAC Re |  |  | Cupertino, Santa Clara | Install protection, automation, and control equipment on the 115kV system at Monta Vista Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | T.0000675 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-05 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.7568 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5816461 | T.0011178 | Monta Vista: Install 115kV MPAC | 6 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-09-09 | NA | 2027-11-08 | NA | NA | TRUE | NA | NA ¦ NA | 8.6313 | 2558.6978 | 0 | 0 | 0 | 0 | 7.7285 | 414.2359 | 1994.2693 | 0 | 0 | 0 | 7.7285 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1541 | Monta Vista: Install 115kV MPAC |  |  | Cupertino, Santa Clara | Install protection, automation, and control equipment on the 115kV system at Monta Vista Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | T.0000675 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-03 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 15.8314 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | 5811104 | T.0011178 | Monta Vista: Install 115kV MPAC | 6 | 67 | NA ¦ Ex112742 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-01-04 | NA | 2029-03-30 | NA | NA | TRUE | NA | NA ¦ NA | 33.0133 | 8491.9198 | 0 | 0 | 0 | 0 | 23.931 | 467.9889 | 2000 | 3500 | 2000 | 500 | 23.9309 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1542 | Bahia: Install 230kV MPAC |  |  | Benicia, Solano | Install protection, automation, and control equipment on the 230kV system at Bahia Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. Bahia has one-of-a-kind BF SBF protection, oil refinary, odd bus configuration & MCGG bus protection and lots of old relays but with single relay upgraded historically, and Valero SPS-anti-island scheme. The 230kV side has four CB and two Dist-Transformers. The existing building has 12 panel spaces, which is insufficent for future substation upgrade. Using the latest standards, estimated* need 9 panels for bus diff for three bus sections, 4 breaker panels, 2 line panels, 2 circuit switcher panels, 2 bank panels, 1 SPS panel, 1 annunciator panel, and 1 comm panel. This makes 22 spaces. MPAC program recommend to proceed with MPAC deployment based on relay vintage, non-standard bus protection, and congested control building with no room for growth. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-02 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 3.2232 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5811109 | T.0011299 | Bahia: Install 230kV MPAC | 1 | 67 | NA ¦ EX113423 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-01-05 | NA | 2029-03-12 | NA | NA | FALSE | NA | NA ¦ NA | 128.9487 | 17420.4417 | 0 | 0 | 0 | 0 | 80.9856 | 839.456 | 8000 | 5000 | 3000 | 500 | 80.9856 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement
1543 | Vaca Dixon: Install 230kV MPAC |  |  | Solano | Install protection, automation, and control equipment on the 230kV system at Vaca Dixon Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-25 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5811108 | TBD | TBD | TBD | 67 | NA ¦ Ex112723 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-04-01 | NA | 2031-02-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 17750 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 750 | 1000 | 10000 | 4000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1544 | TESLA: Install 115 KV MPAC |  |  | Alameda | The scope associated with the Tesla 230kV MPAC Buildings and Remote Ends project includes installing two 230 kV MPAC buildings and two battery buildings at Tesla Substation and upgrading all identified remote end locations to match the new relays that will be installed at Tesla Substation: • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “C” elements. • Install a new 98’-0” X 15’-4” MPAC Enclosure for the 230 kV Bus Section “D” and “E” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “C” elements. • Install a new 34’-0” X 15’-4” Battery Enclosure for the 230 kV Bus Section “D” and “E” elements Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 115 kV | NA | NA | NA | 5.2 | Non-IGP | EX139402 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-02-01 | NA | 2031-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 16750 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 750 | 10500 | 3000 | 2000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1545 | VARIOUS: IEC-61850 DIGITAL MPAC PILOT |  |  | NA | Digital MPAC - IEC 61850 Pilot: MPAC has gone through multiple phases of design changes from MPAC-IPAC to MPAC-SMP. Implement the "Digital Substation" solution IEC-61850 will achieve financial benefits by converting copper-wiring to fiber-optics cables from the field equipment into control enclosures, digitalizing relaying equipments to achieve smaller enclosure size an and standardization will result in significant reduction in engineering, testing and project duration. PG&E will evaluate different IEC 61850 vendors at pilot locations before identifying the solution for the substation environment. Without the pilot project, implementing IEC-61850 will just be a table-top exercise. The pilot project will involve different functional groups: MPAC Core Team-Automation/Protection/Telecom, Test, Standard, Engineering, Sourcing, etc. Project scope include, engineering, procurement, construction, testing, and training. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.2 | Non-IGP | 5811105 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-06-01 | NA | 2027-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 10000 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [Primary Purpose] Infrastructure Enhancement
1546 | Kern Oil: Install 115kV MPAC |  |  | Oildale CDP, Kern | Install protection, automation, and control equipment on the 115kV system at Kern Oil Substation, where Kern Oil is with historical building. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to execute concurrently with the bus conversion project: PO 5777344 - Kern Oil 115kV convertt bus to BAAH (MAT 94D) - Y2030 FISD w/ 2027 KO. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-06 | 27 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.2122 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5791318 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-01-02 | NA | 2031-09-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 6000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 500 | 1000 | 4500 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1547 | Vaca Dixon: Install 60kV MPAC |  |  | Solano | MPAC projects address deficiencies in transmission relays and life-cycle replacement of legacy relays while integrating SCADA into the scheme. Telecom circuits and battery systems are typically also upgraded concurrently. A significant section of the substation, usually by bus or bus section and all remote terminals are upgraded. Vaca Dixon MPAC project is part of the overall Vaca Dixon bus upgrade project, and both jobs must be executed concurrently. | Substation - Modular Protection and Automation Control Building | New | NA | 5811108 ¦ T.0001609 ¦ T.0003461 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-25 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 42.1076 | NA | 60 kV | NA | NA | NA | 5.3 | Non-IGP | 5811106 | TBD | TBD | TBD | 67 | NA ¦ EX113422 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-04-01 | NA | 2031-10-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 16250 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 250 | 1000 | 8000 | 4000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1548 | Stagg: Install 230kV MPAC |  |  | Stockton, San Joaquin | Install protection, automation, and control equipment on the 230kV system at Stagg Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 8.5909 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112718 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2031-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 16750 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 750 | 1000 | 8000 | 3500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement
1549 | Reedley: Install 115kV MPAC |  |  | Fresno | Install protection, automation, and control equipment on the 115kV system at Reedley Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | T.0010649 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-10 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.5939 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112722 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-04-01 | NA | 2032-02-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 17500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 500 | 8000 | 5000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1550 | Palermo: Install 230kV MPAC |  |  | Palermo CDP, Butte | Install protection, automation, and control equipment on the 230kV system at Palermo Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-13 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 8.0464 | NA | 60 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112733 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-09-01 | NA | 2032-06-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 9250 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 250 | 0 | 6000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1551 | Lone Tree: Install 230kV MPAC |  |  | Antioch, Contra Costa | Install protection, automation, and control equipment on the 230kV system at Lone Tree Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-03 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3791 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112735 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-09-01 | NA | 2032-06-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 9250 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 250 | 0 | 6000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement
1552 | Salinas: Install 115kV MPAC |  |  | Salinas, Monterey | Install protection, automation, and control equipment on the 115kV system at Salinas Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.4966 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112736 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-09-01 | NA | 2032-06-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8750 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 250 | 0 | 6000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1553 | Birds Landing: Install 230kV MPAC |  |  | Solano | Install protection, automation, and control equipment on the 230kV system at Birds Landing Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | T.0008048 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-18 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.4512 | NA | 230 kV | NA | NA | NA | 5.2 | Non-IGP | Ex112725 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-06-01 | NA | 2032-10-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 18500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 500 | 8000 | 6000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement
1554 | Claremont: Install 115kV MPAC |  |  | Oakland, Alameda | Install protection, automation, and control equipment on the 115kV system at Claremont Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.9974 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | Ex112728 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-06-01 | NA | 2032-10-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 9750 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 750 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1555 | Salinas: Install 60kV MPAC |  |  | Salinas, Monterey | Install protection, automation, and control equipment on the 60kV system at Salinas Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.4966 | NA | 60 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112737 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-09-01 | NA | 2032-10-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8750 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 250 | 0 | 6000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1556 | Divide: Install 115kV MPAC |  |  | Santa Barbara | Install protection, automation, and control equipment on the 115kV system at Smartville Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to execute concurrently with the bus conversion project to convert the existing bus to DBSB. Y2030 FISD w/ 2027 KO. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.9377 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112743 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-06-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 10272.36 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 500 | 0 | 6000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1557 | Ignacio: Install 115kV MPAC |  |  | Novato, Marin | Install protection, automation, and control equipment on the 115kV system at Ignacio Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. The Ignacio 115kV MPAC project is planned to be executed concurrently with the Ignacio 60kV MPAC project. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.9486 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112726 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-03-01 | NA | 2033-02-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 12131.406 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 500 | 0 | 7631.406 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1558 | Ignacio: Install 60kV MPAC |  |  | Novato, Marin | Install protection, automation, and control equipment on the 115kV system at Ignacio Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. The Ignacio 60kV MPAC project is planned to be executed concurrently with the Ignacio 115kV MPAC project. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.9486 | NA | 60 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112727 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-03-01 | NA | 2033-02-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 500 | 0 | 5000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1559 | LLAGAS SUB: INSTALL 115KV MPAC |  |  | Gilroy, Santa Clara | MPAC projects address deficiencies in transmission relays and life-cycle replacement of legacy relays while integrating SCADA into the scheme. Telecom circuits and battery systems are typically also upgraded concurrently. A significant section of the substation, usually by bus or bus section and all remote terminals are upgraded. Llagas MPAC project is part of the overall Llagas bus upgrade project, and both jobs must be executed concurrently. | Substation - Modular Protection and Automation Control Building | New | NA | T.0004271 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-04 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.3037 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5792891 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1250 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 250 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1560 | McCall: Install 115kV MPAC |  |  | Fresno | Install protection, automation, and control equipment on the 115kV system at McCall Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | T.0009584 ¦ T.0003305 ¦ EX112724 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 16.2494 | NA | 115 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112724 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 10500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 500 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1561 | Schindler: Install 115/70kV MPAC |  |  | Westside CDP, Fresno | Install protection, automation, and control equipment on the 115kV system at Schindler Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-04 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.9138 | NA | 115 ¦ 70 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112730 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 500 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1562 | Tulucay: Install 230/60kV MPAC |  |  | Napa | Install protection, automation, and control equipment on the 230kV system at Tulucay Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-04 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.1869 | NA | 230 ¦ 60 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112731 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 500 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 35.18% | 64.82% | [Primary Purpose] Infrastructure Enhancement
1563 | Tesoro: Install 230kV MPAC |  |  | Contra Costa | Install protection, automation, and control equipment on the 230kV system at Tesoro Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-02-03 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.6359 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | Ex112732 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7750 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 750 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement
1564 | Cottonwood: Install 60kV MPAC |  |  | Cottonwood CDP, Shasta | Install protection, automation, and control equipment on the 60kV system at Cottonwood Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. The Cottonwood 60kV MPAC project is planned to be executed concurrently with the Cottonwood 115kV MPAC project. | Substation - Modular Protection and Automation Control Building | New | NA | Ex112719 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 26.1945 | NA | 60 kV | NA | NA | NA | 5.1001 | Non-IGP | Ex112720 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | NA | 2034-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1565 | Cottonwood: Install 115kV MPAC |  |  | Cottonwood CDP, Shasta | Install protection, automation, and control equipment on the 115kV system at Cottonwood Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure installation is part of the overall MPAC Replacement Program to replace the initial MPAC MPAC-IPAC deployments prior to Y2010, where the existing MPAC relays have reached its intended life of expectancy. The Cottonwood 115kV MPAC project is planned to be executed concurrently with the Cottonwood 60kV MPAC project. | Substation - Modular Protection and Automation Control Building | New | NA | Ex112720 | Other [See Notes] | Modular Protection and Automation Control | NA | NA | 2026-03-19 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 26.1945 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | Ex112719 | TBD | TBD | TBD | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2033-12-01 | NA | 2035-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
1566 | Trans SCADA Replacement Bucket |  |  | NA | Bucket for SCADA/RTU replacements | Other - Operations Tech | Replace | NA | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 236 | 9. Reliability (Low Safety Risk) | NA | 5.1001 | Non-IGP | 5507180 | NA | NA | NA | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 11019.6999 | 34019.6999 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 3000 | 6000 | 6000 | 11019.6999 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1567 | OAKLAND D: Replace T-RTU |  |  | Oakland, Alameda | This job is to replace the SCADA RTU for the T&D equipment in Oakland D Substation. The project is necessary to improve the electric transmission system visibility and control, and help improve the distribution grid reliability and efficiency. | Other - Operations Tech | Replace | NA | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | NA | 2026-03-16 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.54348 | NA | 115 kV | 236 | 9. Reliability (Low Safety Risk) | 1 | NA | NA | 5781845 | T.0000010 | Oakland_D_D-RTU Replacement - concurrent | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-02-01 | 2019-04-03 | 2022-11-04 | Prioritization | NA | FALSE | 693 | NA ¦ NA | 1615.7833 | 1615.7833 | 497.4576 | 927.5613 | 2.5478 | 0.563 | 0 | 0 | 0 | 0 | 0 | 0 | 1615.7833 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 1509.0141 | 2.3724 | 0.52428 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1568 | BIG RIVER: Replace T-RTU |  |  | Mendocino CDP, Mendocino | This job is to install SCADA on all the transmission equipment in Big River Substation. Big River Substation currently has SCADA visibility, but the performing equipment has reached its end of life. This project will bring the station up to date with current standards. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | NA | 2026-03-16 | 10 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.73337 | NA | 60 kV | 236 | 3. Emergency Preparedness | NA | NA | Non-IGP | 5761804 | T.0001172 | BIG RIVER: REPLACE T-RTU | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-01 | 2022-08-31 | 2023-09-01 | Scope Change | NA | TRUE | 3090 | NA ¦ NA | 2894.0038 | 2946.9574 | 34.3661 | 185.9412 | 830.5341 | 289.1524 | 1450.273 | 88.0526 | 0 | 0 | 0 | 0 | 2854.4875 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 1046.0467 | 270.415 | 1356.2932 | 36.9556 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1569 | ELK: Replace T-RTU |  |  | Mendocino | Replace T-RTU, automatic feature cutouts for Circuit Breaker 12, 22 and 32 with new building and replace D-RTU and IPAC for Circuit Breaker 1101, Bank 1 meter and regulator, and replace the station service transformer at Elk Substation. This job includes replacing meters and switches with those capable of being SCADA operated. This job will also provide visibility of station annunciation. | Other - Operations Tech | Replace | NA | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | NA | 2026-02-12 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.0338 | NA | 60 kV | 236 | 3. Emergency Preparedness | 15 | NA | NA | 5765186 | T.0001189 | ELK: REPL T-RTU | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-08-25 | 2021-12-31 | 2021-12-16 | NA | NA | FALSE | 2210 | NA ¦ NA | 1887.6837 | 1887.6837 | 1311.2695 | 146.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1887.6837 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1689.4647 | 142.3443 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1570 | Millbrae: Replace T-RTU & FCOs |  |  | Millbrae, San Mateo | This job is to install SCADA on all the distribution equipment in Millbrae Substation. The project is necessary to improve the electric transmission system visibility and control, and help improve the distribution grid reliability and efficiency. | Other - Operations Tech | Replace | NA | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | NA | 2026-03-09 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.0501 | NA | 60 kV | 236 | 9. Reliability (Low Safety Risk) | 14 | NA | NA | 5785894 | T.0004846 | Millbrae: Replace D-Rtu & 4 Ipac | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-06-08 | 2021-09-18 | 2022-07-07 | Workforce | NA | FALSE | 2878 | NA ¦ NA | 1284.0794 | 1284.0794 | 980.5915 | 234.6912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1284.0794 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 1284.0794 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1571 | Los Esteros Sub: Replace RTU with D20MX |  |  | San Jose, Santa Clara | The project scope of work includes replacing the existing D20ME RTU with an D20MX RTU, retain all the peripheral boards and DNP devices, move critical alarms from D20S boards to the new C30 relays, migrate the AVC to the new RTU. This SCADA project is necessary to maintain the electric transmission system visibility and control and help improve the distribution grid reliability and efficiency | Other - Operations Tech | Replace | NA | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | NA | 2026-03-09 | 22 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.1703 | NA | 230 ¦ 115 kV | 236 | NA | NA | NA | NA | 5792890 | T.0006775 | Los Esteros Sub: Replace RTU with D20MX | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-10-03 | 2023-12-13 | 2023-12-02 | NA | NA | FALSE | 1395.84 | NA ¦ NA | 1087.3662 | 1087.3662 | 10.9444 | 425.0366 | 550.1559 | 101.2293 | 0 | 0 | 0 | 0 | 0 | 0 | 1087.3662 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 976.4809 | 100.1805 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1572 | Manteca Sub: Replace T-RTU & Rewire |  |  | Manteca, San Joaquin | Replace existing D20ME RTU and peripheral RTU boards (A,S,& K) with new Eaton SMP SG-4260 RTU & GE IO boards per PG&E standards. Install new Cisco Switch IE4010 and Ruggedcom terminal servers replacing existing SEL 2020/2031 and RFL 9660. This project will also eliminate daisy chaining issues and rewire per current standards. | Other - Operations Tech | Replace | NA | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | NA | 2026-03-14 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.8539 | NA | 115 kV | 236 | NA | NA | 5.1001 | Non-IGP | 5796825 | T.0007258 | Manteca: Replace T-RTU & Rewire | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-03-29 | 2024-12-31 | 2024-05-09 | NA | NA | FALSE | 1800 | NA ¦ NA | 1186.1249 | 1186.1249 | 68.7425 | 342.8407 | 87.8867 | 672.7543 | 13.9007 | 0 | 0 | 0 | 0 | 0 | 1186.1249 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1126.6312 | 13.3259 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1573 | LAMBIE SW STA: REPLACE RTU & SEL321 |  |  | Solano | This project will replace the RTU, including peripheral equipment, and SCADA system/equipment (TSRP), including installing ODN via VSAT, at Lambie Switching Station. Transmission Automation strategies aim to enhance O&M efficiency, safety, and compliance. Having a fully automated and integrated electric transmission and distribution grid will support value-added response capabilities and applications. To improve the quality and efficiency of our electric transmission system it is recommended to provide increased visibility at Lambie 230kV Switching Station. The scope of work will replace the legacy RTU and peripheral boards to maintain a reliable monitoring and control system for Grid Operations and replacing equipment to provide full SCADA monitoring and control to all breakers and switches (TSRP). While providing SCADA functionality is the driver, there may be additional justification to modernize the aging protection assets concurrently. The level of automation has been determined by the project team and approved by the System Automation department to include replacing the existing legacy D20++ RTU with an EATON 4260 and upgrading all SCADA peripheral as necessary. This includes installing ODN to the station control building through VSAT and replacing the SEL-321 relay on 230kV Line-1 to allow remote communication. | Other - Operations Tech | Replace | NA | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | NA | 2026-02-18 | 22 | Lifecycle Replacement Analysis | Other - Deferral | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3686 | NA | 230 kV | 236 | NA | NA | 5.1001 | Non-IGP | 5791840 | T.0007427 | Lambie SW Sta_Replace RTU & SEL321 | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-04-16 | 2024-05-28 | 2024-10-18 | NA | NA | TRUE | 800 | NA ¦ NA | 1460.0835 | 1550.5583 | 0.5014 | 168.7351 | 279.9224 | 982.755 | 28.1695 | 90.4749 | 0 | 0 | 0 | 0 | 1460.0835 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1346.7429 | 26.4105 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1574 | 2015 T-SCADA IT Decoupling |  |  | NA | Bucket for 2015 T-SCADA IT Decoupling | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 236 | 5a. Mitigates System Wide Failure Risk | NA | NA | NA | 5516256 | NA | NA | NA | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 5957.4201 | 5957.4201 | 12.5049 | 1.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5957.4201 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 12.5049 | 1.962 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1575 | Trans SCADA Installation Bucket |  |  | NA | Bucket for Transmission SCADA installation | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 236 | 9. Reliability (Low Safety Risk) | NA | 5.1001 | Non-IGP | 5507179 | NA | NA | NA | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 16720.6851 | 30720.6851 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 3000 | 3000 | 3000 | 16720.6851 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1576 | TEJON: Install T-SCADA on CB 12 22 32 |  |  | Kern | Install T-SCADA on CB 12, 22, & 32 at the Tejon Substation. This project’s scope is to install SCADA on circuit breaker 12, circuit breaker 22 and circuit breaker 32 to enhance efficiency, safety, and reliability. A Shoofly will be installed to obtain the required clearances and upon completion of the relay replacements, the old control building will be removed. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | 2026-03-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.0602 | NA | 70 kV | 236 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5755447 | T.0000160 | Tejon - Install SCADA on CB 12, 22, 32 | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-08-23 | 2019-06-07 | 2019-10-29 | NA | NA | FALSE | 3723 | NA ¦ NA | 1220.2178 | 1220.2178 | 8.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.2178 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 7.1484 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1577 | RESERVATION RD: Install T-SCADA |  |  | Monterey | Install new RTU & SCADA on SW37 & SW 39. Add motor operator to SW37 at Reservation Road Substation. This job includes replacing meters and switches with those capable of being SCADA operated. This job will also provide visibility of station annunciation. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | 2026-02-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.59657 | NA | 60 kV | 236 | 3. Emergency Preparedness | 16 | NA | NA | 5757521 | T.0000191 | Reservation Road_Install T-SCADA SW39 | 1 | 67 | NA ¦ 5767672 ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-05-11 | 2020-11-30 | 2020-12-03 | NA | NA | FALSE | 2575 | NA ¦ NA | 1830.3044 | 1830.3044 | 870.6339 | 0.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1830.3044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 837.3171 | 0.81264 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1578 | OROVILLE: INSTALL SCADA ON CB12-CB22 |  |  | Oroville, Butte | The scope of work will include adding full SCADA monitoring and control to Circuit Breakers 12, 22, and 32. This project will address the deficiency of transmission SCADA at this substation, installing the necessary equipment for remote status and operation of all transmission equipment that currently do not have SCADA.. The TSRP migration work is included in this project and involves revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | 2026-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.75208 | NA | 60 kV | 236 | 9. Reliability (Low Safety Risk) | 10 | 5.1001 | Non-IGP | 5738700 | T.0000324 | OROVILLE: T-SCADA CBs 12,22,32 &TSRP | 1 | 67 | NA ¦ 5769051 ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-07-30 | 2022-07-31 | 2027-12-13 | Bundling Dependencies | NA | TRUE | 1815 | NA ¦ NA | 1235.8058 | 3145.8707 | 211.2356 | 337.953 | 75.4545 | 8.4635 | 35.5817 | 157.4752 | 1121.9179 | 379.6032 | 0 | 0 | 1223.2866 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1579 | CUYAMA: Install T-SCADA |  |  | Cuyama CDP, Santa Barbara | This job is to install SCADA on all the transmission equipment in Cuyama | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | 2026-02-13 | 62 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.69685 | NA | 70 kV | 236 | 9. Reliability (Low Safety Risk) | 17 | NA | NA | 5755546 | T.0000771 | INSTALL SCADA - CUYAMA | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-09-04 | 2019-02-27 | 2022-11-03 | Scope Change | NA | FALSE | 1330 | NA ¦ NA | 1631.7702 | 1631.7702 | 107.2602 | 190.079 | 92.9763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1631.7702 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 1524.2902 | 91.6719 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1580 | HYAMPOM JCT: Install T-SCADA CB 62 |  |  | Trinity | This job is to install SCADA on all the transmission equipment in Hyampom Jct Substation. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | 2026-03-16 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.319 | NA | 60 kV | 236 | 3. Emergency Preparedness | NA | NA | NA | 5757493 | T.0000813 | HYAMPOM JCT: INSTALL T-SCADA CB 62 | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-10-15 | 2020-10-07 | 2019-03-22 | NA | NA | FALSE | 2606 | NA ¦ NA | 1634.32 | 1634.32 | 24.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1634.32 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 23.7296 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1581 | KILARC PH: Install T-SCADA |  |  | Shasta | This job is to install SCADA on all the transmission equipment in Kilarc PH Substation. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | 2026-03-04 | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.23969 | NA | 60 kV | 236 | NA | NA | NA | NA | 5757494 | T.0000814 | KILARC PH: INSTALL T-SCADA | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-09-24 | 2019-05-13 | 2018-12-10 | NA | NA | FALSE | 1103 | NA ¦ NA | 1698.7786 | 1698.7786 | 72.8465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1698.7786 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 30.5573 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1582 | OLEMA: Install T-SCADA on SW 27 & 29 |  |  | Marin | Install SCADA at Olema Substation on SW27 & 29, replace reclosing relay and add 60kV PT. This job includes replacing meters and switches with those capable of being SCADA operated. This job will also provide visibility of station annunciation. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | 2026-02-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.26483 | NA | 60 kV | 236 | 3. Emergency Preparedness | 17 | NA | NA | 5757520 | T.0000819 | OLEMA: INSTALL T-SCADA SW 27 & 29 | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-06-11 | 2019-12-31 | 2021-04-27 | Prioritization | NA | FALSE | 1621 | NA ¦ NA | 1866.6616 | 1866.6616 | 645.6538 | 102.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1866.6616 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1724.3299 | 100.3335 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1583 | HERDLYN: Install T-SCADA |  |  | Contra Costa | Install T-SCADA at Herdlyn Substation on CB 32, CB 62, MOAS 79, & TB 2 w/ new building, & battery upgrade. This job includes replacing meters and switches with those capable of being SCADA operated. This job will also provide visibility of station annunciation | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | 2026-02-03 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.81884 | NA | 60 kV | 236 | 9. Reliability (Low Safety Risk) | 17 | NA | NA | 5755313 | T.0003772 | HERDLYN SUB: INSTALL: T-SCADA | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-06-10 | 2021-04-30 | 2022-04-01 | Permitting | NA | FALSE | 2213 | NA ¦ NA | 2025.2425 | 2025.2425 | 482.2944 | 697.3246 | 16.3389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025.2425 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 2010.3481 | 16.3389 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1584 | CARIBOU PH 1 UPGRADE T SCADA |  |  | Plumas | This job is to install SCADA on all the transmission equipment in Caribou 1 PH Substation. • The project is necessary to improve the electric transmission system visibility and control, and help improve the distribution grid reliability and efficiency. | Other - Operations Tech | Upgrade/Retrofit | NA | NA | Reliability | Install SCADA/RTU | NA | NA | 2026-02-10 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.96252 | NA | 115 ¦ 60 kV | 236 | 3. Emergency Preparedness | 19 | NA | NA | 5779206 | T.0003784 | Caribou PH - TSCADA Upgrade | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-06-10 | 2019-12-31 | 2020-10-06 | Prioritization | NA | FALSE | 1536 | NA ¦ NA | 1041.8277 | 1041.8277 | 63.1422 | 16.9857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1041.8277 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 59.082 | 15.8934 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1585 | Trans SCADA Emergency Replacement Bucket |  |  | NA | Bucket for Emergency Transmission SCADA replacement | Other - Operations Tech | Replace | NA | NA | Emergency Event | Age/Condition - Replace SCADA/RTU | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 ¦ 115 ¦ 70 ¦ 60 kV | 236 | 5a.Mitigates System Wide Failure Risk | NA | 5.1001 | Non-IGP | 5506316 | NA | NA | NA | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 16750.0599 | 41969.3629 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 4753.2713 | 4936.7743 | 5127.3616 | 16750.0599 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1586 | Table Mountain: EM Repl Fail D20 Comm |  |  | Butte | The scope of work is to upgrade the SCADA system at Table Mountain Substation. There has been reliability issues with the SCADA system due to the high number of peripheral boards connected to the existing annunciator. | Other - Operations Tech | Replace | NA | NA | Emergency Event | SCADA Emergency Replacement | NA | NA | 2026-03-20 | 16 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 47.516 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5552661 | T.0009180 | Table Mountain: Em Repl Failed D20 Board | 1 | 67 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2024-09-03 | NA | 2026-08-31 | NA | NA | TRUE | NA | NA ¦ NA | 796.4726 | 1150.6199 | 0 | 0 | 69.7206 | 641.8335 | 84.8145 | 354.2513 | 0 | 0 | 0 | 0 | 796.3686 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 62.7485 | 577.6499 | 76.3328 | 0.09357 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1587 | Pit 1 PH: Inst 2411 Relays at Cottonwood |  |  | Cottonwood CDP, Shasta | Replace the 230/11kV Banks 1 and 2 at Pit PH No. 1 Substation | Substation - Protection Relay | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-03-19 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | 26.1945 | NA | 230 kV | NA | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5790208 | T.0002123 | Pit Powerhouse No1 Substation Replace Ba | 4 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-12-02 | 2021-08-31 | 2022-07-18 | Prioritization | NA | FALSE | 31400 | NA ¦ NA | 696.659 | 696.659 | 202.9703 | 470.6747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696.659 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 659.0183 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Replacement Alternative ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1588 | Pit 1 PH: Inst 2411 Relays at Pit 3 PH |  |  | Shasta | Replace the 230/11kV Banks 1 and 2 at Pit PH No. 1 Substation | Substation - Protection Relay | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-03-19 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | 1.3657 | NA | 230 kV | NA | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5790207 | T.0002123 | Pit Powerhouse No1 Substation Replace Ba | 4 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-08-08 | 2021-08-31 | 2022-10-31 | Prioritization | NA | FALSE | 31400 | NA ¦ NA | 376.8523 | 376.8523 | 159.253 | 166.4287 | 27.7718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376.8523 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 349.0804 | 27.7718 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Replacement Alternative ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1589 | Transmission Xfmr 500kV Banks Placeholder Planned Replacement |  |  | NA | Forecast placeholder for planned tranmission non-500 kV transformer replacements | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | IGP | EX139252 | NA | NA | NA | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 32000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 1000 | 1000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1590 | TABLE MOUNTAIN: Replace 500 KV BK 1 |  |  | Butte | PG&E is designing this project to minimize clearance requirements and impacts to the Pacific AC Intertie by installing the new 500/230kV transformer at a new location within the substation footprint, leaving the existing equipment in service during project construction. The new transformer connection will require swapping one of the 500kV transmission lines and installing an additional 500kV circuit breaker to connect. Installing the new Transformer first will minimize the clearance requirements to support the Pacific AC Intertie path. In addition, the project will upgrade the controls and protection scheme of the new transformer. | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | NA | 2026-03-20 | 56 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Subsidence |  | NA | 47.516 | NA | 500 ¦ 230 kV | 362 | 9. Reliability (Low Safety Risk) | 5 | 5.1001 | IGP | 5747877 | T.0000250 | Table Mountain 500/230kV Transformer Rep | 1 | 68 | NA ¦ 5767179 ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-08-31 | 2018-11-09 | 2021-11-17 | Prioritization | NA | TRUE | 54100 | NA ¦ NA | 48447.8974 | 48853.5119 | 18581.2151 | 2540.3746 | -85.32 | 10.802 | 193.5466 | 800.5693 | 0 | 0 | 0 | 0 | 48050.5193 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 42897.7655 | 2719.5789 | -80.8471 | 10.2356 | 183.3995 | 376.5448 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1591 | GATES: Replace BK 11 500/230 KV |  |  | Fresno | Replace three single-phase 500kV Gates Transformers Bank No. 11 (Bank 11) and associated equipment. This project will replace the deteriorated 500kV transmission transformer bank, which is at the end of its useful life. The loss of this transformer bank will require generation curtailment and impact service area reliability. Also, this transformer supports the Pacific 500kV AC Intertie, with connections to DCPP and North-to-South power flow, which is critical for grid stability. | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | NA | 2026-03-12 | 63 | Lifecycle Replacement Analysis | Other - Deferral | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 ¦ 230 kV | 319 | 9. Reliability (Low Safety Risk) | NA | 5.1001 | IGP | 5761816 | T.0001373 | Gates 500kV Bank 11 Replacement | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-09-07 | 2023-03-31 | 2023-06-05 | NA | NA | FALSE | 31500 | NA ¦ NA | 43542.8851 | 43542.8851 | 12462.5072 | 25171.2671 | 5092.2432 | 202.2155 | 21.6637 | 0 | 0 | 0 | 0 | 0 | 43542.8851 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 41892.9791 | 194.9556 | 20.886 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1592 | MOSS LANDING: Replace 500kV Bank 9 |  |  | Monterey | This project proposes to replace all four (4) phases of Moss Landing Bank 9 with four (4) new 500/230kV single-phase 374 MVA transformers under the Deteriorated Transformer Replacement Program. Moss Landing Bank 9 is composed of three (3) 1978-vintage 373MVA McGraw Edison single-phase transformers and one (1) 1997-vintage Pauwels unit of the same size. All four transformers will be replaced with a new bank of four (4) single-phase transformers. Bank 9 has a rank of #3 on the replacement list as of 2019. This bank has a RIBA score of 1,899, and RIBA Delta of 1,339. | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | NA | 2026-03-10 | 48 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 41.3213 | NA | 500 ¦ 230 kV | NA | 9. Reliability (Low Safety Risk) | 10 | 5.1001 | IGP | 5788362 | T.0005464 | Moss Landing-Replace 500kV Bank 9 | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 5 | 2037-04-02 | NA | 2037-10-01 | NA | NA | FALSE | NA | NA ¦ NA | 685.288 | 69619.6119 | 135.4685 | 287.3746 | 127.4444 | 87.8919 | 32.9661 | 42.9333 | 0 | 0 | 0 | 0 | 685.288 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1593 | Metcalf: Replace Bank 11 Phase B and C |  |  | Santa Clara | This project proposes to replace phases B and C of Metcalf Bank 11 with two (2) new 500/230kV single-phase 374 MVA transformers under the Deteriorated Transformer Replacement Program. Metcalf Bank 11 is composed of three (3) single-phase transformers and one (1) spare transformer, which is shared with Bank 12. | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | NA | 2026-03-05 | 58 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 500 ¦ 230 kV | 362 | 9. Reliability (Low Safety Risk) | NA | 5.1001 | IGP | 5790318 | T.0005835 | Metcalf: Replace Bank 11 Phase B and C | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2032-12-09 | NA | 2033-12-22 | NA | NA | FALSE | NA | NA ¦ NA | 19.1206 | 21905.7561 | 10.3736 | 6.81 | 1.2814 | 0.6555 | 0 | 1.2288 | 0 | 0 | 0 | 0 | 19.1206 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1594 | 500/230kV 1-ph 374MVA New CEM Bank |  |  | NA | Increase CEM stock for 500/230kV 374MVA single-phase transformer and install a new storage pad at Herndon substation. | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | NA | NA | NA | 5.1001 | IGP | 5555240 | T.0009784 | 500/230kV 1-ph 374MVA New CEM Bank | 2 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2027-12-30 | OAI | NA | NA | TRUE | 7540 | NA ¦ NA | 552.9182 | 6706.751 | 0 | 0 | 0 | 524.9898 | 27.9284 | 6153.8328 | 0 | 0 | 0 | 0 | 552.9182 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 524.9898 | 27.9284 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1595 | Transmission Mobile Transformer Purchase 2025 |  |  | NA | Forecast placeholder for Transmission Mobile Transformer Purchase 2025 to prepare for Emergency transformer failures | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | IGP | Ex112788 | NA | NA | NA | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8502.4882 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 8502.4882 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1596 | Transmission Xfmr Non 500kV Banks (6 Banks) Planned Replacement |  |  | NA | Forecast placeholder for planned tranmission non-500 kV transformer replacements | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 ¦ 70 ¦ 60 kV | NA | NA | NA | 5.1001 | IGP | EX139253 | NA | NA | NA | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 81000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 3000 | 9000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1597 | MARTIN: Replace 230/115 KV BK 7 |  |  | Brisbane, San Mateo | Replacement of the 230/115 kV Bank 7 spare at Martin Substation.This project proposes to replace the spare phase. | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-03-12 | 51 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 18.2105 | NA | 230 ¦ 115 kV | 227 | 9. Reliability (Low Safety Risk) | 4 | NA | NA | 5745519 | T.0000025 | SF H (Martin)-Replace 230/115KV Bank 7 | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-05-26 | 2021-02-01 | 2020-12-30 | NA | NA | FALSE | 11700 | NA ¦ NA | 16508.6502 | 16508.6502 | 2088.6989 | 444.2234 | 348.1036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16508.6502 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1906.7614 | 405.4976 | 317.7571 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $20 Mil - $30 Mil ¦ $15 Mil - $20 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1598 | PIT PH 1: Add BK 5 |  |  | Shasta | This project will replace the aging and deteriorated Bank 3 with a new transformer, as well as add a Bank 5 for redundancy and additional operational flexibility. The Load-Tap-Changer (LTC) built into Bank 3 will also provide flexibility in regulating voltage. The oil from the existing transformer banks will be disposed of per standard PG&E process; PSC, a contractor, will remove the oil from site and either recycle it (if low polychlorinated biphenyl (PCBs) count) or dispose of it at a hazardous waste facility (if high PCBs count). The project scope of work includes the following:  Install a new 30MVA, 60/11kV three-phase transformer with LTC, as replacement for Bank 3.  Install a new 70MVA, 230/60kV Bank 5.  Remove the existing Bank 3 and structures.  Install or upgrade spill prevention control and countermeasure (SPCC) as needed.  Install a new control building, protection package, and SCADA. | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-03-04 | NA | NA | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | 2.7679 | NA | 230 ¦ 60 kV | 202 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5768953 | T.0000623 | Pit No. 1 PH Transformer Upgrade | 2 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-12-03 | 2018-10-16 | 2020-01-13 | Bundling Dependencies | NA | FALSE | 27000 | NA ¦ NA | 26577.3006 | 26577.3006 | 90.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26577.3006 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 88.206 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1599 | Cascade - Repl 115/60kV Bk1 |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-02-16 | 64 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | NA | 115 ¦ 60 kV | 240 | 9. Reliability (Low Safety Risk) | NA | 5.1001 | IGP | 5777640 | T.0000651 | Cascade Substation Upgrade | 10 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-11-04 | 2022-01-31 | 2026-04-30 | Prioritization | NA | TRUE | 35800 | NA ¦ NA | 8673.497 | 10906.7506 | 1419.3423 | 2154.4417 | 358.604 | 366.1201 | 2357.9337 | 3321.5695 | 0.0002 | 0 | 0 | 0 | 7585.1809 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1600 | HOPLAND: REPLACE BK 2 |  |  | Mendocino | This project will replace the 115/60kV Bank 2 at Hopland Substation with a new three-phase, 100MVA, 115/60kV transformer bank with load tap-changer (LTC) | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-02-13 | 74 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.63377 | NA | 115 ¦ 60 kV | 202 | 9. Reliability (Low Safety Risk) | 11 | 5.1001 | IGP | 5748000 | T.0000830 | HOPLAND: REPL 115/60 KV BANK 2 | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2032-03-05 | 2018-08-14 | 2032-08-23 | Clearances | NA | FALSE | 4575 | NA ¦ NA | 5169.7417 | 10236.0039 | -1326.8534 | 413.3536 | 1636.2494 | 600.4231 | 184.7951 | 326.5949 | 0 | 0 | 0 | 0 | 5169.7417 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1601 | Reedley: Repl Bk 2 (115/70 kV) |  |  | Fresno | This planned project will replace Reedley Transformer #2 with one new 115/70 kV, 200 MVA transformer. This planned project is needed to maintain safe and reliable power to the greater Dinuba, Reedley and South Fresno area, and will provide the following benefits: Increase the existing transformer capacity from 90 MVA to 200 MVA and allow accommodation for future load growth. Provide a firm station (two T-banks banks in total) Improve employee safety by eliminating a possible catastrophic transformer failure due to equipment condition. Potential decrease in annual recurring maintenance costs by replacing the existing transformer and switches with newer equipment. | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-03-10 | 60 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.5939 | NA | 115 kV | 240 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5769944 | T.0001590 | Reedley: Repl Bk 2 (115/70 kV) | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-11-01 | 2021-12-04 | 2022-03-31 | NA | NA | FALSE | 5784 | NA ¦ NA | 7614.9521 | 7614.9521 | 4464.3355 | 1849.9598 | 451.3168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7614.9521 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 6747.6623 | 424.1875 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1602 | PEASE: Repl BK 2 |  |  | Sutter | This project will replace the 115/60kV Bank 2 at Pease Substation with a three-phase, 200 MVA, 115/60kV transformer bank with load tap-changer (LTC). | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-02-10 | 63 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.6809 | NA | 115 ¦ 60 kV | 240 | 9. Reliability (Low Safety Risk) | 14 | NA | NA | 5770141 | T.0001649 | PEASE: REPLACE 115/60KV BK2 | 1 | 68 | NA ¦ 5760984 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-01 | 2020-03-17 | 2022-04-07 | Clearances | NA | FALSE | 7958 | NA ¦ NA | 9716.9068 | 9716.9068 | 2457.9578 | 2645.9138 | -337.993 | 1.9753 | 0 | 0 | 0 | 0 | 0 | 0 | 9716.9068 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 9515.9439 | -318.1003 | 1.859 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1603 | CEM: Purch 115-60/70 KV 30MVA 1-Ph Mob |  |  | NA | This project will add a new single-phasetransmission mobile transformer 115-70/60 kV 30 MVA in our mobile fleet | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 115 ¦ 70 ¦ 60 kV | 76 | 3. Emergency Preparedness | NA | NA | NA | 5516564 | T.0001727 | MOBILE PROGRAM 2017-2018 | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | NA | 2019-10-30 | 2022-03-31 | Material | NA | FALSE | 2000 | NA ¦ NA | 1221.6037 | 1221.6037 | 692.7443 | 14.6227 | 0.7904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1221.6037 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 692.7443 | 14.6227 | 0.79038 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1604 | LOCKEFORD: Remove BK 1 |  |  | Lockeford CDP, San Joaquin | This project will remove the deteriorated 115/60 kV Transformer Bank 1 at Lockeford Substation | Substation - Transformer | Removal | NA | T.0008354 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-03-05 | 79 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2719 | NA | 115 ¦ 60 kV | 227 | NA | NA | 5.1001 | IGP | 5546019 | T.0002193 | LOCKEFORD SUB: REPLACE BANK 1 | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2033-11-22 | NA | 2033-12-21 | NA | NA | FALSE | NA | NA ¦ NA | 106.9731 | 1267.7341 | 49.6584 | 9.7986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9731 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 | 4.0877 | 0.01954 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1605 | Replace Sobrante Bank 1 (230/115 kV) |  |  | Orinda, Contra Costa | This project proposes to replace Sobrante Bank 1 (230/115 kV, 403MVA)with a new bank as part of the "Deteriorated Transmission Transformer Replaement Program". | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-03-04 | 61 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.0767 | NA | 115 kV | 240 | 9. Reliability (Low Safety Risk) | 3 | 5.1001 | IGP | 5760326 | T.0002845 | Sobrante: Replace Bank 1 | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2032-04-21 | NA | 2033-02-03 | NA | NA | FALSE | NA | NA ¦ NA | 345.8729 | 8210.6899 | 19.4636 | 21.0779 | 23.1802 | 11.8575 | 0 | 22.2274 | 0 | 0 | 0 | 0 | 345.8729 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1606 | Placer: Replace 115/60 kV Bank 1 |  |  | Placer | This project proposes to install Transformer 4 (1-3 phase with LTC, 200 MVA) and replace Bank 1 (1-3 phase with LTC, 200 MVA) at Placer Substation. Placer Bank 1 (3-1 phase, Westinghouse, 1962, 22.7 MVA/phase) was installed in 1962. Placer Bank 1 has been targeted for replacement as part of the PG&E Transmission Transformer Proactive Replacement Program. The prioritization criteria for this program is primarily based on technical assessments of the transmission transformer banks. The predominant factors include transformer condition per Dissolved Gas Analysis (DGA), age, and impact of consequence of an In-Service failure. In addition, recurring maintenance costs, availability of spare parts, and environmental issues are also taken into consideration. Specifically, Placer Bank 1 C, B, and A are ranked #57, #167, and #244 on 2021 Transmission Transformer Replacement List. Installation of the second Placer 115/60 kV transformer improves reliability and operational flexibility for customers in the area. Currently, with only one Placer 115/60 kV transformer, recommended clearance window for the bank 1 is limited to April to mid-May. An outage outside of this window could result in customers at risk. In addition, an outage of Placer 115/60 kV bank 1, could result in a sustained outage to customers served from Penryn, Auburn, Mountain Quarries and Halsey Substations (approximately 18,608 customers). | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-02-04 | 64 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 ¦ 60 kV | NA | NA | NA | 5.1001 | IGP | 5797893 | T.0005697 | Placer: Rebuild Substation | 10 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-05-20 | 2024-12-30 | 2027-10-27 | Prioritization | NA | TRUE | 17200 | NA ¦ NA | 5614.6805 | 9687.9304 | 14.7575 | 117.1233 | 3416.308 | 1867.8265 | 162.2549 | 455.6604 | 3473.6237 | 1186 | 23 | 0 | 5578.2701 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1607 | Placer Install 115/60 kV TXFMR 4 |  |  | Placer | This project proposes to install Transformer 4 (1-3 phase with LTC, 200 MVA) and replace Bank 1 (1-3 phase with LTC, 200 MVA) at Placer Substation. Placer Bank 1 (3-1 phase, Westinghouse, 1962, 22.7 MVA/phase) was installed in 1962. Placer Bank 1 has been targeted for replacement as part of the PG&E Transmission Transformer Proactive Replacement Program. The prioritization criteria for this program is primarily based on technical assessments of the transmission transformer banks. The predominant factors include transformer condition per Dissolved Gas Analysis (DGA), age, and impact of consequence of an In-Service failure. In addition, recurring maintenance costs, availability of spare parts, and environmental issues are also taken into consideration. Specifically, Placer Bank 1 C, B, and A are ranked #57, #167, and #244 on 2021 Transmission Transformer Replacement List. Installation of the second Placer 115/60 kV transformer improves reliability and operational flexibility for customers in the area. Currently, with only one Placer 115/60 kV transformer, recommended clearance window for the bank 1 is limited to April to mid-May. An outage outside of this window could result in customers at risk. In addition, an outage of Placer 115/60 kV bank 1, could result in a sustained outage to customers served from Penryn, Auburn, Mountain Quarries and Halsey Substations (approximately 18,608 customers). | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-02-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 ¦ 60 kV | NA | NA | NA | 5.1001 | IGP | 5797892 | T.0005697 | Placer: Rebuild Substation | 10 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-04-21 | 2024-12-30 | 2029-01-16 | Prioritization | NA | TRUE | 17200 | NA ¦ NA | 6063.3711 | 10817.9081 | 18.0752 | 132.731 | 3521.9433 | 1877.5794 | 436.027 | 910.5521 | 2105 | 1794 | 22 | 0 | 5986.356 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1608 | Tesla: Purchase Three-Phase Trans Mobile |  |  | Tracy, San Joaquin | This project will add a new 115/60x70 kV 90MVA three-phase transmission mobile to our mobile fleet. The new mobile transformer will be the first transmission 3-phase mobile transformer in the fleet. The existing three 115-60/70 kV 30 MVA single-phase mobiles can support loss of three single phase transformers or a whole 115-60/70kV bank. The loss of a three-phase bank would require all three of these mobile transformers, leaving 153 transmission transformers without backup for many months, or more than a year. The addition of this three-phase mobile transformer will greatly enhance our ability to recover from transmission transformer outages. | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 115 ¦ 70 ¦ 60 kV | NA | NA | NA | 5.1001 | IGP | 5540940 | T.0006112 | Tesla_Purchase Three-Phase Trans Mobile | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-07-01 | 2022-12-31 | 2024-07-29 | Material | NA | TRUE | 3800 | NA ¦ NA | 5549.8677 | 5549.8677 | 0 | 70.2671 | 2348.2586 | 2954.7493 | 160.7047 | 15.888 | 0 | 0 | 0 | 0 | 5533.9797 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 70.2671 | 2348.2586 | 2954.7493 | 160.7047 | 15.888 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1609 | CEM: xfmr 115/70x60 kV 100 MVA 3-ph w/ L |  |  | NA | Purchase a CEM 115/70 x 60 kV 100 MVA Transformer with load tap changer (LTC) to increase CEM transformer stock | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 115 ¦ 70 ¦ 60 kV | NA | NA | NA | 5.1001 | IGP | 5541679 | T.0006347 | CEM_xfmr 115_70x60 kV 100 MVA 3-ph w_LTC | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2022-12-31 | OAI | NA | NA | FALSE | 2600 | NA ¦ NA | 47.716 | 1204.344 | 23.8302 | -19.3451 | 43.2308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.716 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 23.8302 | -19.3451 | 43.2308 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1610 | 230/115kV 420MVA New CEM Bank 3 |  |  | NA | This project will procure three 230/115kV, 420MVA 3-phase transformer with LTC to support failure of existing three phase 230/115kV transmission transformers. | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | IGP | 5546162 | T.0007409 | 230 115kV 420MVA New CEM Bank 3 | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-12-04 | 2024-05-15 | 2024-01-19 | NA | NA | FALSE | 4270 | NA ¦ NA | 5644.8802 | 5644.8802 | 2.0738 | 804.4868 | 4621.1496 | 217.17 | 0 | 0 | 0 | 0 | 0 | 0 | 5644.8802 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 806.5606 | 4621.1496 | 217.17 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1611 | 230/115kV 420MVA New CEM Bank 2 |  |  | NA | This project will procure three 230/115kV, 420MVA 3-phase transformers with LTC to support failure of existing three phase 230/115kV transmission transformers. | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | IGP | 5546161 | T.0007410 | 230 115kV 420MVA New CEM Bank 2 | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-12-04 | 2023-05-15 | 2024-01-19 | Workforce | NA | FALSE | 4270 | NA ¦ NA | 5712.7115 | 5712.7115 | 0 | 807.0041 | 4657.0679 | 248.6396 | 0 | 0 | 0 | 0 | 0 | 0 | 5712.7115 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 807.004 | 4657.0679 | 248.6396 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1612 | 230/115kV 420MVA New CEM Bank 1 |  |  | NA | This project will procure three (3) 230/115 kV 420 MVA three-phase transformers with load tap changer (LTC) | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 kV | NA | NA | NA | 5.1001 | IGP | 5546160 | T.0007411 | 230/115kV 420MVA New CEM Bank 1 | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-09-06 | 2022-12-31 | 2023-10-03 | Material | NA | TRUE | 4500 | NA ¦ NA | 6763.8623 | 6763.8623 | 1.1183 | 2405.6018 | 3986.9486 | 220.5891 | 121.832 | 27.7726 | 0 | 0 | 0 | 0 | 6736.0897 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 2406.7201 | 3986.9485 | 220.5891 | 121.832 | 27.7726 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1613 | 115/60x70kV 100MVA New CEM Bank |  |  | Fresno, Fresno | This project proposes to procure one 115/70x60kV 100MVA 3 phase transformer to increase the CEM stock. Additional CEM is required due to the increase in failures and lack of planned replacement of the aging transformer fleet. | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | 2026-03-12 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.3414 | NA | 115 ¦ 70 ¦ 60 kV | NA | NA | NA | 5.1001 | IGP | 5555242 | T.0009786 | 115/60x70kV 100MVA New CEM Bank | 1 | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | 2027-12-31 | 2028-04-28 | NA | NA | FALSE | 2970 | NA ¦ NA | 519.0123 | 6009.2543 | 0 | 0 | 0 | 517.7249 | 1.2874 | 0 | 0 | 0 | 0 | 0 | 519.0123 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2028 | 0 | 0 | 0 | 517.7249 | 1.2874 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1614 | Transformer Refurbishments |  |  | NA | Forecast placeholder for transformer refurbishments. Refurbish tranformers to extend their service life, decrease operating costs, improve safety | Substation - Transformer | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | EX113775 | NA | NA | NA | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 15600 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 2400 | 2400 | 3300 | 3300 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1615 | Transmission Transformer online monitoring |  |  | NA | Forecast placeholder for Transmission Transformer online monitoring. Install 9 transmission transformer online monitors in 2025 and 10 per year for 2026-2035 (unit cost $120k) | Substation - Transformer | New | NA | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | EX113192 | NA | NA | NA | 68 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | 2029-05-31 | OAI | NA | NA | FALSE | 5940 | NA ¦ NA | 0 | 3600 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1200 | 1200 | 1200 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1616 | System Inspections TPTT |  |  | NA | Bucket for transmission pole test and treat inspections. These are intrusive wood pole inspections, conducted on a 10 year cycle. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.201 | Non-IGP | 5562465 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 1601.7949 | 1601.7949 | 0 | 0 | 0 | 0 | 1601.7948 | 0 | 0 | 0 | 0 | 0 | 1601.7949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1617 | Fiber Replacement/Support |  |  | NA | Forecast placeholder for Replacement of structures as required to support fiber asset replacement. Allows for reliability of telecom assets by facilitating degraded asset replacement by replacement of supporting structures | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | IGP | Ex112916 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 45000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 5000 | 10000 | 10000 | 10000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1618 | Pole Replacement Engineered |  |  | NA | Bucket for Pole Replacements | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 31 | NA | 1367 | NA | NA | 5515926 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 7505.93 | 7505.93 | 5.0077 | 34.481 | 536.9993 | 276.0507 | -847.9156 | 0 | 0 | 0 | 0 | 0 | 7505.93 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 ¦ 2025 ¦ 2026 | 5.0077 | 0 | 0 | 847.531 | -847.531 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1619 | System-Wide Generator Support - 70P |  |  | NA | Bucket for replacement of steel towers and wood poles based on asset health | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 81 | 9. Reliability (Low Safety Risk) | 151 | NA | NA | 5523002 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 3249.34 | 3249.34 | 10.8863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3249.34 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 9.7151 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1620 | Bucket for steel structure repairs |  |  | NA | Bucket created for steel structure repairs with high cost intended to extend the life of the structure 20+ years without having to replace it at a much higher cost | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.101 | IGP | EX113552 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 17500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 2500 | 5000 | 5000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1621 | Caribou-Palermo Replace 5 Damaged Towers |  |  | Palermo CDP, Butte ¦ Plumas | The Caribou-Palermo 115kV Line is located in the North Valley Division portion of Area 6. This line is approximately 55 miles long and is supported by 446 steel structures. From 22/87 to 23/92, 6 steel towers were damaged as a result of a storm that went through the area. In order to expedite placing the line back into service, a wood shoo-fly was installed and charged to the Emergency Major Work Category (MWC 92). Since the line is currently energized, the emergency condition has been resolved and the emergency event is effectively over. Therefore the work to replace the 6 damaged towers must be charged to MWC 70 – Replace Structures. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-03-20 | 76 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5755898 | P.07116 | CARIBOU-PALERMO RPLC 6 DMGD TWR | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 4256-E | 2013-07-16 | Approved | 2013 | Operational | 1 | 2016-05-31 | 2015-11-12 | 2016-06-27 | Project Design | NA | FALSE | 3424.5467 | NA ¦ NA | 3450.4376 | 3450.4376 | -15.6044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3450.4376 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 5.6365 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1622 | West Sac Brighton 115kV Twr Repl |  |  | Arden-Arcade CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento ¦ West Sacramento, Yolo | This project proposes to replace at least two aging deteriorated steel structure and/or foundation on the Pittsburg – San Mateo and Eastshore – San Mateo 230kV double circuit towers in order to maintain reliable service. This project will address the Bay Waters towers on the Pittsburg – San Mateo and Eastshore – San Mateo 230kV lines located in San Mateo County. These lines were built in 1952. These transmission lines share steel structure in this area. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-08 | 57 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 598 | 2. Overhead With Strong Safety Link | 574 | 5.101 | IGP | 5777913 | T.0003593 | West Sac - Brighton 115kV Twr Repl | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2030-08-20 | NA | 2031-09-24 | NA | NA | FALSE | NA | NA ¦ NA | 1394.791 | 8470.2274 | 227.889 | 209.0221 | 130.2058 | 0 | 8.5905 | 17.4917 | 2000 | 3000 | 100 | 0 | 1377.2993 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 10.67% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1623 | Metcalf-Edenvale |  |  | San Jose, Santa Clara ¦ Santa Clara | The purpose of this project is to replace all spans of the Metcalf -Edenvale 115kV and IBM Harry Road 115kV Tap non-track resistant ADSS fiber optic cable route that are within an excessively high E-fields with new 72 count OPGW fiber optic cable. The previously installed ADSS fiber optic cable on Metcalf-Edenvale #2 115 kV between Metcalf Sub and Edenvale Sub and the IBM Harry Road 115 kV Tap are non-track resistant. A span of that cable route failed and fell to the ground. Forensic investigation revealed that the cable had failed due to induced current on the cable jacket (tracking). Subsequently, E-field analysis was performed on the entire ADSS route. The analysis indicated that the ADSS on all spans must be removed and replaced with OPGW. In order to keep the enterprise operational during the transmission line outage, diverse paths with lease lines need to be established, and are included in the scope of this project. Associated lease line costs will be estimated once routes are designed. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-08-08 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | IGP | 5813170 | T.0006243 | IO - Fiber Optic Maintenance and Replace | 2 | 70 | NA ¦ Ex112916 ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-03-18 | 2022-08-31 | 2026-08-05 | Permitting | Project Design | TRUE | 3738 | NA ¦ NA | 5141.1395 | 6483.4576 | 0 | 0 | 0 | 1493.3521 | 3463.9955 | 1526.11 | 0 | 0 | 0 | 0 | 4957.3475 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1624 | Ravenswood - San Mateo 230kV 01/011 Rpr |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The project scope of work includes following: • Complete necessary immediate foundation replacement on Tower 001/011. • Replace Tower 001/011. • Replace old insulators, hardware, and equipment on Tower 001/011. • Coordinate transmission outages with T-line Operations, Grid Control, and impacted local stakeholders. • Manage any supporting purchase orders such as vegetation management and engineering. In January 2020, Maintenance and Construction (M&C) crews doing a site walk observed the legs of Tower 001/007 showing deterioration, and the tower required immediate attention. An emergency fix was done, and the tower was then replaced in late 2020. In June 2022, during a planned inspection on this line, a field crew observed significant degradation of the wooden piles and concrete foundation supporting structure 001/011 during a low-tide event. The conditions were reported, and T-Line engineering reviewed the situation and determined that the foundation was in need of immediate and urgent reinforcement, and that the structure as a whole needs to be replaced in order to permanently improve conditions at this location and offset future maintenance and repair costs. This project addresses the Electric Operations risk of Failure of Transmission Overhead Assets. This project will replace a structure with poor asset health to mitigate any potential safety incidents or unplanned outages to serve the electric customers of San Mateo County safely and reliably. Completion of this project will reduce the risk of losing these critical lines that help deliver power to customers in the northern San Francisco Peninsula area. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-19 | 60 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | NA | NA | NA | NA | NA | 5550228 | T.0008449 | Ravenswood-SanMateo 230kV 01/011 TRP RPR | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-07-25 | NA | 2022-08-27 | NA | NA | FALSE | 2134 | NA ¦ NA | 2335.0269 | 2335.0269 | 0 | 2318.0327 | 16.9943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2335.0269 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 2318.0327 | 16.9943 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1625 | Castro Valley-Newark 3/22 Retain Wall |  |  | Alameda ¦ Castro Valley CDP, Alameda ¦ Fairview CDP, Alameda ¦ Fremont, Alameda ¦ Hayward, Alameda ¦ Sunol CDP, Alameda ¦ Union City, Alameda | Due to landslide risks to tower 3/22 and exposed footings, PG&E is installing a retaining wall at tower 3/22 for the Castro Valley-Newark 230 kV Line. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-31 | NA | NA | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | NA | NA | 230 | NA | NA | NA | NA | 4.0121 | IGP | 5552101 | T.0008997 | Castro Valley-Newark 3/22 Retain Wall | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-06-01 | NA | 2028-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 2000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 | 0 | 0 | 66.9672 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 17.21% ¦ Electric Operations Risk Management | NA | 100% | 0% | NA
1626 | Monta Vista - Los Gatos |  |  | Cupertino, Santa Clara ¦ Los Gatos, Santa Clara ¦ Monte Sereno, Santa Clara ¦ Santa Clara ¦ Saratoga, Santa Clara | Replacing total of 12 overloaded transmission poles to install ADSS fiber on them. Monta Vista-Los Gatos line: Poles to be replaced: 003, 004, 005, 006 and 009 Monta Vista-Los Alto Line: Poles to be replaced: 016, 017, 018, 020, 020A, 021(reframe only) and 022. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-27 | 126 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ False | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | IGP | 5813162 | T.0009333 | Monta Vista-Los Altos/Gatos ADSS Install | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-05-05 | NA | 2026-05-18 | NA | NA | TRUE | NA | NA ¦ NA | 324.4842 | 653.5725 | 0 | 0 | 0 | 92.7829 | 132.0027 | 428.7868 | 0 | 0 | 0 | 0 | 224.7857 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1627 | Monta Vista - Los Gatos |  |  | Cupertino, Santa Clara ¦ Los Altos, Santa Clara ¦ Loyola CDP, Santa Clara ¦ Santa Clara | Replacing total of 12 overloaded transmission poles to install ADSS fiber on them. Monta Vista-Los Gatos line: Poles to be replaced: 003, 004, 005, 006 and 009 Monta Vista-Los Alto Line: Poles to be replaced: 016, 017, 018, 020, 020A, 021(reframe only) and 022. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-10-29 | 126 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | IGP | 5813163 | T.0009333 | Monta Vista-Los Altos/Gatos ADSS Install | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-05-12 | NA | 2026-07-07 | NA | NA | TRUE | NA | NA ¦ NA | 320.7346 | 537.2097 | 0 | 0 | 0 | 90.3401 | 154.6857 | 292.184 | 0 | 0 | 0 | 0 | 245.0258 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1628 | Palo Alto- Wood Pole - Ravenswood |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Palo Alto, Santa Clara | Wood pole replacement in support of installation of fiber optics cable. Planning, engineering and ordering of materials. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-10-07 | 53 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | IGP | 5813165 | T.0010750 | Palo Alto- Wood Pole- Cooley - Ravenwood | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-11-12 | NA | 2027-01-14 | NA | NA | TRUE | NA | NA ¦ NA | 124.7844 | 307.6735 | 0 | 0 | 0 | 31.9401 | 83.1175 | 180.9115 | 11.7044 | 0 | 0 | 0 | 115.0576 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1629 | Palo Alto- TSP - Ravenswood |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Palo Alto, Santa Clara | Wood pole replacement in support of installation of fiber optics cable. Planning, engineering and ordering of materials. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-07 | 55 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | IGP | 5813159 | T.0010750 | Palo Alto- Wood Pole- Cooley - Ravenwood | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-04-01 | NA | 2027-06-01 | NA | NA | TRUE | NA | NA ¦ NA | 241.3974 | 607.7078 | 0 | 0 | 0 | 104.8487 | 125.1337 | 93.401 | 284.3244 | 0 | 0 | 0 | 229.9824 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1630 | Palo Alto- Wood Pole - Cooley |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo | Wood pole replacement in support of installation of fiber optics cable. Planning, engineering and ordering of materials. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-10-22 | 54 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | IGP | 5813164 | T.0010750 | Palo Alto- Wood Pole- Cooley - Ravenwood | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-10-11 | NA | 2027-12-03 | NA | NA | TRUE | NA | NA ¦ NA | 524.1162 | 6422.2064 | 0 | 0 | 0 | 251.1448 | 246.508 | 605.7239 | 3318.8296 | 0 | 0 | 0 | 497.6529 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1631 | Sac SC to Sac BP (W Sac-Brighton) |  |  | Arden-Arcade CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento ¦ West Sacramento, Yolo | The project involves stringing in several spans of new OPGW on our existing transmission tower line (West Sac-Brighton). In addition to the new overhead fiber, several of the t-line towers will have foundation modifications and/or top cage extensions added. There will also be a new fiber vault installed on one end of the project where the fiber transitions from overhead back to underground. | Transmission Line - Other Equipment | New | NA | T.0010507 | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-12-08 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | IGP | 5813169 | T.0010756 | Sac SC to Sac BP (W Sac-Brighton) | 1 | 70 | NA ¦ Ex112916 ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-10-12 | 2026-12-08 | 2026-10-30 | NA | NA | TRUE | 2562 | NA ¦ NA | 1253.5534 | 3389.7892 | 0 | 0 | 0 | 938.3199 | 283.9906 | 2152.4787 | 15 | 0 | 0 | 0 | 1222.3104 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1632 | Moss-SLO Fiber Salinas Fiber Lateral |  |  | Boronda CDP, Monterey ¦ Elkhorn CDP, Monterey ¦ Monterey ¦ Prunedale CDP, Monterey ¦ Salinas, Monterey | This project will extend the PG&E IT ROADM network from Moss Landing Switchyard South to SLO SC via new ROADM network elements at Coburn Substation and Templeton Substation. SONET and Ethernet connectivity will be established. Several fiber laterals will be built to connect Lumen and Crown Castle long haul fibers. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-11-23 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | IGP | 5813167 | T.0010758 | Moss-SLO Fiber Coburn Fiber Lateral | 2 | 70 | NA ¦ Ex112916 ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-11-01 | 2025-11-26 | 2024-11-14 | NA | NA | TRUE | 17496 | NA ¦ NA | 742.8847 | 742.8847 | 0 | 0 | 0 | 659.2176 | 74.3508 | 9.3163 | 0 | 0 | 0 | 0 | 733.5684 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1633 | Moss-SLO Fiber Coburn Fiber Lateral |  |  | Elkhorn CDP, Monterey ¦ Monterey ¦ Prunedale CDP, Monterey ¦ San Benito | This project will extend the PG&E IT ROADM network from Moss Landing Switchyard South to SLO SC via new ROADM network elements at Coburn Substation and Templeton Substation. SONET and Ethernet connectivity will be established. Several fiber laterals will be built to connect Lumen and Crown Castle long haul fibers. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-12-04 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | NA | NA | NA | 5.101 | IGP | 5813166 | T.0010758 | Moss-SLO Fiber Coburn Fiber Lateral | 2 | 70 | NA ¦ Ex112916 ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-06-02 | 2025-11-26 | 2025-07-11 | NA | NA | TRUE | 17496 | NA ¦ NA | 1086.0224 | 1086.0224 | 0 | 0 | 0 | 941.8814 | 130.5215 | 13.6195 | 0 | 0 | 0 | 0 | 1072.4029 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1634 | Pittsburg-San Mateo Bay Towers FOND |  |  | Alameda ¦ Blackhawk CDP, Contra Costa ¦ Castro Valley CDP, Alameda ¦ Contra Costa ¦ Danville, Contra Costa ¦ Fairview CDP, Alameda ¦ Foster City, San Mateo ¦ Hayward, Alameda ¦ Pittsburg, Contra Costa ¦ San Mateo, San Mateo ¦ San Ramon, Contra Costa | The pile cap replacement work consists of total of 16 piers at 7 different towers, and the grade beam replacement consists of a total of 21 grade beams at 9 towers to improve the overall safety and reliability of the system due to the condition of the foundations on these towers. Pittsburg-San Mateo 230 kV towers 38/157 to 40/163, 41/165 to 42/168, and 43/171. This project will address the risk of failure to these structures due to deteriorated existing grade beams. All structures in scope are located in the San Francisco Bay and can only be accessed from water. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-01 | 25 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.101 | IGP | 5816400 | T.0011527 | Pittsburg-San Mateo Bay Towers FOND | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-06-05 | NA | 2026-11-09 | NA | NA | TRUE | NA | NA ¦ NA | 297.7667 | 24129.6462 | 0 | 0 | 0 | 0 | 214.9104 | 4395.1022 | 19519.6336 | 0 | 0 | 0 | 214.9104 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1635 | FT - BR/OPGW Replacement in San Bruno |  |  | Brisbane, San Mateo ¦ Burlingame, San Mateo ¦ Millbrae, San Mateo ¦ San Bruno, San Mateo ¦ San Mateo ¦ San Mateo, San Mateo ¦ South San Francisco, San Mateo | Replacement of OPGW on SAN MATEO-MARTIN #6 115 kV line | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-20 | 15 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 11.7 | NA | 115 | NA | NA | NA | NA | 5.101 | IGP | 5818241 | T.0011962 | FT - BR/OPGW Replacement in San Bruno | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2026-12-02 | NA | 2026-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 29.0579 | 1108.7572 | 0 | 0 | 0 | 0 | 0 | 1036.9306 | 71.6857 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1636 | Trans Replace Steel Structure - North |  |  | NA | Bucket for replacement of steel structures (North) | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 212 | 2. Overhead With Strong Safety Link | 39 | 3.0011 | IGP | 5510399 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 14618.2039 | 134618.2049 | 670.0788 | 1723.9128 | 973.6073 | 1193.0232 | 666.5529 | 217.4497 | 20000 | 0 | 0 | 0 | 14400.7552 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 548.154 | 1435.3342 | 875.2463 | 1059.197 | 634.739 | 209.2526 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1637 | Trans Replace Steel Structure - South |  |  | NA | Bucket for replacement of steel structures (South) | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | 77 | 4.0111 | IGP | 5504679 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 6618.7099 | 6618.7099 | -9.076 | 8.5389 | 18.425 | 356.4226 | 337.6751 | -30.5019 | 0 | 0 | 0 | 0 | 6649.2118 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 ¦ 2025 ¦ 2026 | -30.2247 | 0.87921 | 0 | 219.2272 | 185.3871 | 99.9835 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1638 | WMP - T Line Repl Steel Structures |  |  | NA | Bucket for replacement of transmission steel structures in support of WSIP | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | 4 | NA | NA | 5535225 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1237.5547 | 1237.5547 | 309.0334 | 12.6868 | 1.0764 | 0 | 1.45 | 0 | 0 | 0 | 0 | 0 | 1237.5547 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 ¦ 2026 | 309.6673 | 37.5544 | 1.0764 | 0 | 1.45 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1639 | HFTD - 70S - Monthly Forecast Only |  |  | NA | Bucket for HFTD Steel structure replacements for current year plan | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 4.0111 | IGP | 5562000 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 7109.6417 | 7109.6417 | 0 | 0 | 0 | 80.1429 | 7025.6322 | 3.8666 | 0 | 0 | 0 | 0 | 7105.7751 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 80.1429 | 7025.6323 | 3.8666 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1640 | Ravenswood Ames #1 Phase 1 |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Mountain View, Santa Clara ¦ Palo Alto, Santa Clara ¦ Santa Clara | The project scope of work includes following to eliminate NERC discrepancies over the Bay Waters: Replace eight lattice steel towers with taller towers, install one top cage, and install dampers at 17 locations. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-04 | 76 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | 2. Overhead With Strong Safety Link | 526 | 4.0111 | IGP | 5791338 | T.0000397 | RAVENSWOOD-AMES#1 TR PROJECT | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6599-E | 2022-05-19 | Approved | 2022 | Construction (over 75%) | 2 | 2024-09-11 | NA | 2026-06-23 | NA | NA | TRUE | NA | NA ¦ NA | 1258.0458 | 1489.3699 | 215.4995 | 685.7843 | 293.5182 | 0 | 0 | 247.9144 | 0 | 0 | 0 | 0 | 1241.4555 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1641 | RAVENSWOOD-AMES#1 |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Mountain View, Santa Clara ¦ Palo Alto, Santa Clara ¦ Santa Clara | The project scope of work includes following to eliminate NERC discrepancies over the Bay Waters: Replace eight lattice steel towers with taller towers, install one top cage, and install dampers at 17 locations. | Transmission Line - Pole/Tower | Replace | NA | T.0006761 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-04 | 76 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 228 | 2. Overhead With Strong Safety Link | 526 | 3.0011 | IGP | 5792377 | T.0000397 | RAVENSWOOD-AMES#1 TR PROJECT | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6599-E | 2022-05-19 | Approved | 2022 | On Hold | 5 | 2029-04-17 | NA | 2029-12-31 | NA | NA | FALSE | NA | NA ¦ NA | 2015.6249 | 32451.7654 | 755.2796 | 262.9554 | 0 | 44.9649 | 35.5911 | 0 | 250 | 7500 | 0 | 0 | 2015.6249 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 3.30% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1642 | San Bruno Interchange S 115kV Structures |  |  | San Mateo ¦ South San Francisco, San Mateo | This project will replace six corroded structures with three tubular steel poles at the San Bruno Interchange South Transition Station in San Mateo County | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-24 | 35 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 815 | NA | NA | NA | NA | 5771664 | T.0002114 | San Bruno Interchange S 115kV Structures | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2018-08-03 | 2019-02-20 | 2018-11-29 | NA | NA | FALSE | 5082 | NA ¦ NA | 5887.8949 | 5887.8949 | 504.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5887.8949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 493.3616 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1643 | RAVENSWOOD-SAN MATEO 115KV |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The Ravenswood-Bair No. 2 115 kV Line Segment 2 NERC Project (the “Project”) has identified approximately 30 towers for replacement. This project scope includes the replacement of 20 remaining towers identified as part of the North American Electric Reliability Corporation (NERC) remediation work not covered under the Segment 1 NERC project and 10 towers identified as part of the Tower Replacement Program. (All 10 towers were found as high priority from the asset strategy risk model, with 6 being confirmed as part of a 2017 special assessment and 4 that need further assessment.) | Transmission Line - Pole/Tower | Replace | NA | T.0006761 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-21 | 76 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 228 | 2. Overhead With Strong Safety Link | 504 | 4.0111 | IGP | 5792440 | T.0002155 | RAVENSWOOD-BAIR #2 115KV Ph2 TR PROJEC | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2038-03-19 | NA | 2038-07-15 | NA | NA | FALSE | NA | NA ¦ NA | 1538.4415 | 9621.5695 | 243.8471 | 102.3568 | 0 | 19.3832 | 44.7486 | 0 | 0 | 0 | 0 | 0 | 1538.4415 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1644 | RAVENSWOOD-BAIR #2 115KV PH2 |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Mountain View, Santa Clara ¦ Palo Alto, Santa Clara ¦ Santa Clara | The Ravenswood – San Mateo 115 kV Segment 2 NERC Project (the “Project”) has identified possibly 100 towers for replacement and the reconductoring of 4 spans of conductor on the towers that support the Ravenswood – San Mateo, the San Mateo – Belmont 115 kV and the Ravenswood – Bair No. 1 115 kV Lines. This project scope includes the replacement of 16 remaining towers identified as part of the North American Electric Reliability Corporation (NERC) remediation work not covered under the Segment 1 NERC project and 4 towers identified as part of the Tower Replacement Program. In addition, the project will need to evaluate another 80 towers to determine if those towers will need to replaced: 28 were identified through the coatings program, 45 through the asset strategy risk model, 2 from the NERC work, and 5 from the 2017 special assessment. To gain efficiencies in engineering, permitting, and construction, the NERC and Tower Replacement Program were merged into one scope of work. | Transmission Line - Pole/Tower | Replace | NA | T.0006761 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-04 | 76 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | 2. Overhead With Strong Safety Link | 896 | 4.0111 | IGP | 5792439 | T.0002156 | RAVENSWOOD-SAN MATEO 115KV Ph2 NERC PROJ | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2029-03-10 | NA | 2029-07-31 | NA | NA | FALSE | NA | NA ¦ NA | 804.1745 | 804.1745 | 51.3987 | 54.2983 | 0 | 15.19 | 23.391 | 0 | 0 | 0 | 0 | 0 | 804.1745 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1645 | SAN MATEO-BAYMDWS #1 & #2 PH2 |  |  | Foster City, San Mateo ¦ San Mateo, San Mateo | The Ravenswood – San Mateo 115 kV Segment 2 NERC Project (the “Project”) has identified possibly 100 towers for replacement and the reconductoring of 4 spans of conductor on the towers that support the Ravenswood – San Mateo, the San Mateo – Belmont 115 kV and the Ravenswood – Bair No. 1 115 kV Lines. This project scope includes the replacement of 16 remaining towers identified as part of the North American Electric Reliability Corporation (NERC) remediation work not covered under the Segment 1 NERC project and 4 towers identified as part of the Tower Replacement Program. In addition, the project will need to evaluate another 80 towers to determine if those towers will need to replaced: 28 were identified through the coatings program, 45 through the asset strategy risk model, 2 from the NERC work, and 5 from the 2017 special assessment. To gain efficiencies in engineering, permitting, and construction, the NERC and Tower Replacement Program were merged into one scope of work. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-18 | 89 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | 2. Overhead With Strong Safety Link | 1055 | 4.0111 | IGP | 5792442 | T.0002156 | RAVENSWOOD-SAN MATEO 115KV Ph2 NERC PROJ | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2029-08-31 | NA | 2029-12-21 | NA | NA | FALSE | NA | NA ¦ NA | 463.1872 | 1929.9652 | 76.6149 | 31.9804 | 0 | 13.2427 | 13.4727 | 0 | 0 | 0 | 0 | 0 | 463.1872 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 34.54% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1646 | RAVENSWOOD-BAIR #1 115KV PH2 |  |  | Menlo Park, San Mateo ¦ Redwood City, San Mateo | The Ravenswood – San Mateo 115 kV Segment 2 NERC Project (the “Project”) has identified possibly 100 towers for replacement and the reconductoring of 4 spans of conductor on the towers that support the Ravenswood – San Mateo, the San Mateo – Belmont 115 kV and the Ravenswood – Bair No. 1 115 kV Lines. This project scope includes the replacement of 16 remaining towers identified as part of the North American Electric Reliability Corporation (NERC) remediation work not covered under the Segment 1 NERC project and 4 towers identified as part of the Tower Replacement Program. In addition, the project will need to evaluate another 80 towers to determine if those towers will need to replaced: 28 were identified through the coatings program, 45 through the asset strategy risk model, 2 from the NERC work, and 5 from the 2017 special assessment. To gain efficiencies in engineering, permitting, and construction, the NERC and Tower Replacement Program were merged into one scope of work. | Transmission Line - Pole/Tower | Replace | NA | T.0006761 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-10 | 76 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | 2. Overhead With Strong Safety Link | 1253 | 4.0111 | IGP | 5792443 | T.0002156 | RAVENSWOOD-SAN MATEO 115KV Ph2 NERC PROJ | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2031-03-22 | NA | 2031-08-12 | NA | NA | FALSE | NA | NA ¦ NA | 2554.9687 | 285489.8426 | 582.6353 | 171.3748 | 0 | 54.7546 | 74.3162 | 0 | 0 | 0 | 0 | 0 | 2554.9687 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1647 | SAN MATEO-BELMONT 115KV PH2 |  |  | Belmont, San Mateo ¦ Foster City, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The San Mateo - Bay Meadows 115kV Segment 2 NERC Project (the “Project”) initially identified approximately 13 towers for replacement and the reconductoring of 1 section (7 spans) on the San Mateo – Bay Meadows Nos. 1 and 2 115 kV Lines. That scope included the replacement of 8 towers identified as part of the North American Electric Reliability Corporation (NERC) remediation work and the replacement of 5 towers as part of the Tower Replacement (TR) Program. However, the project scope is being expanded to include an evaluation of the condition of the 17 remaining towers. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-09 | 89 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 228 | 2. Overhead With Strong Safety Link | 1304 | 4.0111 | IGP | 5792441 | T.0002157 | SAN MATEO-BAYMDWS #1 & #2 TR Project | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2029-03-30 | NA | 2029-07-27 | NA | NA | FALSE | NA | NA ¦ NA | 1296.2979 | 41259.982 | 248.2161 | 86.5083 | 0 | 18.0004 | 37.7054 | 0 | 0 | 0 | 0 | 0 | 1296.2979 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 2.48% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1648 | Ignacio - Mare Island 115kV Twr Repl |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Ignacio-Mare Island 115 kV Priority Towers Replacement project. This project proposes to replace three transmission structures, Towers 013/093, 013/094, and 014/105 on the Ignacio – Mare Island 115 kV Lines, which have deteriorated steel components. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-04 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 1142 | 2. Overhead With Strong Safety Link | 295 | NA | NA | 5777902 | T.0002886 | IGNACIO-MARE ISL 115KV - Priority Towers | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-11-09 | 2021-04-21 | 2021-05-21 | NA | NA | FALSE | 56500 | NA ¦ NA | 62783.8951 | 62783.8951 | 42674.091 | 30.667 | 112.6981 | 0.1686 | 0 | 0 | 0 | 0 | 0 | 0 | 62783.8951 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 62640.9781 | 30.667 | 112.6981 | 0.16858 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1649 | Ignacio-Mare Island #1 115kV NERC |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Ignacio-Mare Island 115 kV Priority Towers Replacement project. This project proposes to replace three transmission structures, Towers 013/093, 013/094, and 014/105 on the Ignacio – Mare Island 115 kV Lines, which have deteriorated steel components. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-04 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 4.0111 | IGP | 5544374 | T.0002886 | IGNACIO-MARE ISL 115KV - Priority Towers | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-11-30 | 2021-04-21 | 2024-01-30 | Project Design | Scope Change | FALSE | 56500 | NA ¦ NA | 893.4023 | 893.4023 | 0 | 0.428 | 405.6261 | 397.2043 | 76.5115 | 13.6323 | 0 | 0 | 0 | 0 | 879.77 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 406.0542 | 397.2043 | 76.5115 | 13.6323 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1650 | Ignacio - Alto - Sausalito 60kV Twr Repl |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | This project proposes to replace at least three aging deteriorated steel structures and/or foundations on the Ignacio-Alto-Sausalito #1 and #2 60kV double circuit towers in order to maintain reliable service. Engineering evaluations will be performed to determine the level of upgrades required for each structure. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-07 | 94 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 598 | 1. Work that prevents fire ignition | 93 | 4.04 | IGP | 5777901 | T.0003580 | Ignacio - Alto - Sausalito 60kV | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | PTC | TBD | TBD | TBD | On Hold | 5 | 2036-03-04 | NA | 2037-03-02 | NA | NA | FALSE | NA | NA ¦ NA | 3356.043 | 153463.5903 | 597.6651 | 1054.789 | 499.3379 | 29.7631 | 97.6171 | 0 | 0 | 1000 | 2000 | 75463.5903 | 3356.043 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 474.23% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1651 | Aged TWR REP_ Rio Oso-Woodland #1 |  |  | East Nicolaus CDP, Sutter ¦ Madison CDP, Yolo ¦ Nicolaus CDP, Sutter ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ Woodland, Yolo ¦ Yolo | This project will proactively replace approximately 50 towers across entire PG&E Transmission grid identified based on a combination of age, deteriorated and obsolete designs that are difficult to maintain, as well as field inspection | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-30 | 71 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 | NA | 598 | 2. Overhead With Strong Safety Link | 592 | NA | NA | 5781721 | T.0003582 | Aged Tower Replacement Phase 1 | 6 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-03-20 | 2019-06-05 | 2020-06-10 | Construction Delays | NA | FALSE | 11965 | NA ¦ NA | 2522.8712 | 2522.8712 | 284.6935 | 1210.0062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2522.8712 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 386.4543 | 1155.0683 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1652 | Aged Tower Replacement Phase 1 |  |  | Auburn, Placer ¦ North Auburn CDP, Placer ¦ Placer | This project will proactively replace approximately 50 towers across entire PG&E Transmission grid identified based on a combination of age, deteriorated and obsolete designs that are difficult to maintain, as well as field inspection | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-09-08 | 71 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 598 | 2. Overhead With Strong Safety Link | 15 | NA | NA | 5777903 | T.0003582 | Aged Tower Replacement Phase 1 | 6 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-11-09 | 2020-06-05 | 2020-11-16 | NA | NA | FALSE | 11965 | NA ¦ NA | 1638.8396 | 1638.8396 | 96.8153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1638.8396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 1559.4699 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1653 | Aged TWR REP_ McCall-Kingsburg #1 |  |  | Fresno ¦ Kingsburg, Fresno ¦ Selma, Fresno | This project will proactively replace approximately 50 towers across entire PG&E Transmission grid identified based on a combination of age, deteriorated and obsolete designs that are difficult to maintain, as well as field inspection | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-07 | 71 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 598 | 2. Overhead With Strong Safety Link | 861 | NA | NA | 5781723 | T.0003582 | Aged Tower Replacement Phase 1 | 6 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-11 | 2019-06-05 | 2022-02-22 | Prioritization | NA | FALSE | 11965 | NA ¦ NA | 422.3436 | 422.3436 | 149.8839 | 209.6724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422.3436 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 370.8106 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1654 | Millbrae - San Mateo 115kV Twr Repl |  |  | Burlingame, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ San Mateo, San Mateo | This project proposes to replace 3 (1/14, 1/15, and 2/28) aging deteriorated steel structures and/or foundations on the Millbrae – San Mateo #1 115kV line. Engineering evaluations will be performed to determine the level of upgrades required for each structure. This project proposes to replace three aging deteriorated steel structures / foundations in order to maintain reliable service. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-05 | 79 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 598 | 2. Overhead With Strong Safety Link | 973 | 4.04 | IGP | 5777904 | T.0003583 | Millbrae - San Mateo 115kV Twr Repl | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2031-09-05 | NA | 2031-11-14 | NA | NA | FALSE | NA | NA ¦ NA | 647.1671 | 4501.2667 | 29.4894 | 202.2793 | 1.4268 | 14.2934 | 18.8241 | 0 | 0 | 0 | 0 | 0 | 647.1671 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 8.58% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1655 | SAN MATEO - MARTIN #3 115 KV TWR REP |  |  | Brisbane, San Mateo ¦ Burlingame, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ San Mateo, San Mateo ¦ South San Francisco, San Mateo | This project will address the Bay Waters towers on the San Mateo – Martin #3 and San Mateo – Martin #4 115kV lines located in San Mateo County. These lines were built in 1937. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-30 | 89 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 4.0111 | IGP | 5777909 | T.0003589 | San Mateo - Martin No3 115kV Twr Repl | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-09-29 | 2027-12-20 | 2027-11-17 | NA | NA | TRUE | 2950 | NA ¦ NA | 906.5437 | 11508.4657 | 102.9017 | 81.6259 | 156.73 | 28.9862 | 88.3791 | 406.1518 | 9536.1356 | 200 | 100 | 0 | 802.3139 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1656 | Newark - Ames 115kV Twr Repl |  |  | Fremont, Alameda ¦ Mountain View, Santa Clara ¦ Newark, Alameda ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Sunnyvale, Santa Clara | This project proposes to replace at least one aging deteriorated steel structure and/or foundation on the Newark – Ames #1 and #2 115kV double circuit towers, at least one tower on the Newark – Ames #3 and Newark – Ames Distribution 115kV double circuit towers, and at least one tower on the Newark – Applied Materials and Newark – Lawrence 115kV double circuit towers in order to maintain reliable service. Engineering evaluations will be performed to determine the level of upgrades required for each structure. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-18 | 100 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | NA | 115 | NA | 1142 | 2. Overhead With Strong Safety Link | 556 | 3.0011 | IGP | 5777910 | T.0003590 | Newark - Ames 115kV Twr Repl | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2028-02-22 | NA | 2028-04-28 | NA | NA | FALSE | NA | NA ¦ NA | 988.4537 | 60586.8855 | 181.3895 | -0.0791 | 89.5802 | 16.2424 | 28.7511 | 297.6599 | 750 | 8000 | 0 | 0 | 988.4537 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 38.08% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1657 | Pittsburg - San Mateo 230kV Twr Repl |  |  | Alameda ¦ Blackhawk CDP, Contra Costa ¦ Castro Valley CDP, Alameda ¦ Contra Costa ¦ Danville, Contra Costa ¦ Fairview CDP, Alameda ¦ Foster City, San Mateo ¦ Hayward, Alameda ¦ Pittsburg, Contra Costa ¦ San Mateo, San Mateo ¦ San Ramon, Contra Costa | The Pittsburg-San Mateo and Eastshore-San Mateo 230 kV Lines are supported by 47 lattice steel towers, with 29 of those towers in the Bay Waters. The current scope of the Pittsburg-San Mateo 230 kV Tower Replacement Project (the “Project”) includes the replacement of most of the towers in the Bay Waters. There is significant corrosion of the steel components on the towers and the pile caps supporting the tower foundations have many cracks, which is resulting in a deterioration of the foundation steel. This reauthorization is being requested so that the project team can evaluate whether a like-for-like replacement or other options, such as replacing the lines with submarine cables. are the best long-term solution for these critical lines. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-01 | 73 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | NA | 230 | NA | 598 | 1. Work that prevents fire ignition | 144 | 4.0111 | IGP | 5777912 | T.0003592 | Pittsburg - San Mateo 230kV Twr Repl | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2032-01-27 | NA | 2033-04-20 | NA | NA | FALSE | NA | NA ¦ NA | 1441.4813 | 384241.4813 | 77.9334 | 348.7397 | 364.9184 | -45.5363 | 41.9283 | 12000 | 3000 | 20000 | 147800 | 100000 | 1441.4813 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 764.15% ¦ Electric Operations Risk Management | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1658 | MIDDLE RIVER TAP 60KV MAST TRP PH2 |  |  | Contra Costa ¦ Discovery Bay CDP, Contra Costa ¦ San Joaquin | This project proposes to replace 11 mast towers and/or their anchors in the Sacramento Delta Area in order to maintain reliable service. 3 transmission lines are impacted: Rough and Ready 60kV Tap, McDonald 60kV Tap, and the Middle River 60kV Tap. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-04 | 25 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.0111 | IGP | 5816619 | T.0003734 | Sacramento Delta Area 60kV Mast Twr Repl | 4 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 4 | 2027-10-20 | NA | 2027-12-14 | NA | NA | TRUE | NA | NA ¦ NA | 12.8232 | 11308.7277 | 0 | 0 | 0 | 0 | 0.8429 | 209.5705 | 11079.8093 | 0 | 0 | 0 | 0.8429 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 0.28% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1659 | Middle River Tap 60kV Mast Twr |  |  | Contra Costa ¦ Discovery Bay CDP, Contra Costa ¦ San Joaquin | This project proposes to replace 11 mast towers and/or their anchors in the Sacramento Delta Area in order to maintain reliable service. 3 transmission lines are impacted: Rough and Ready 60kV Tap, McDonald 60kV Tap, and the Middle River 60kV Tap. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-04 | 76 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | 758 | 2. Overhead With Strong Safety Link | 1009 | 4.0111 | IGP | 5779000 | T.0003734 | Sacramento Delta Area 60kV Mast Twr Repl | 4 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-01-06 | NA | 2027-01-27 | NA | NA | TRUE | NA | NA ¦ NA | 1589.0123 | 7425.4392 | 235.9305 | 294.6765 | 168.1997 | 17.2007 | 354.3198 | 4384.4871 | 1564.0052 | 0 | 0 | 0 | 1476.947 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 0.30% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1660 | Almendra Jct 60k Mast Twr |  |  | East Nicolaus CDP, Sutter ¦ Nicolaus CDP, Sutter ¦ Sutter | This project proposes to replace 10 mast towers and/or their anchors in the Yuba Area in order to maintain reliable service. 3 transmission lines are impacted: Almendra Jct 60kV line, District 1500 60kV Tap, and the Colusa Jct #1 60kV line. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-23 | 101 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 60 | NA | 758 | 2. Overhead With Strong Safety Link | 298 | 4.0111 | IGP | 5779004 | T.0003735 | Yuba Area 60kV Mast Twr Repl | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2028-11-20 | NA | 2029-05-10 | NA | NA | FALSE | NA | NA ¦ NA | 1456.5044 | 1456.5044 | 230.4588 | 261.2392 | 227.3516 | 18.9153 | 42.3653 | 0 | 0 | 0 | 0 | 0 | 1456.5044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 193% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1661 | Colusa Jct No1 60kV Mast Twr |  |  | Colusa ¦ Grimes CDP, Colusa ¦ Meridian CDP, Sutter ¦ Sutter | This project proposes to replace 10 mast towers and/or their anchors in the Yuba Area in order to maintain reliable service. 3 transmission lines are impacted: Almendra Jct 60kV line, District 1500 60kV Tap, and the Colusa Jct #1 60kV line. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-15 | 82 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | 758 | 2. Overhead With Strong Safety Link | 628 | 4.0111 | IGP | 5779006 | T.0003735 | Yuba Area 60kV Mast Twr Repl | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2029-05-14 | NA | 2029-07-06 | NA | NA | FALSE | NA | NA ¦ NA | 555.3564 | 555.3564 | 77.3202 | 124.3882 | 83.4969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555.3564 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 10% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1662 | Christie-Willow 60kV Mast Twr |  |  | Bay Point CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa | This project proposes to replace 2 mast towers and/or their anchors on the Christie – Willow Pass 60kV line in order to maintain reliable service. Engineering evaluations will be performed to determine the level of upgrades required for each structure. This project proposes to replace either anchors or full structure replacement for 2 aging lattice-steel poles and/or their anchors in order to maintain reliable service. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-13 | 101 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | 758 | 1. Work that prevents fire ignition | 94 | 4.0111 | IGP | 5779001 | T.0003736 | Christie-Willow 60kV Mast Twr | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-01-05 | NA | 2027-02-02 | NA | NA | TRUE | NA | NA ¦ NA | 1560.1357 | 4059.2416 | 245.0282 | 212.9108 | 167.1476 | 17.091 | 332.8933 | 2444.2144 | 112.6734 | 0 | 0 | 0 | 1465.0271 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 5.39% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1663 | Vaca-Vacaville-Jameson-North Tower 115kV |  |  | Benicia, Solano ¦ Fairfield, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | In an effort to support PG&E top-level initiatives to manage asset risk for the benefit of public and employee safety, service reliability, operational flexibility, and cost reduction, the proposed Accelerated Obsolete and Deteriorated Tower Replacement projects will proactively replace approximately 150 towers across entire PG&E Transmission grid. This project is a subset identified for replacement to kick start the Tower Replacement Program. Additional towers besides the 150 will be identified and nominated for replacement based on results from Asset Strategy’s Risk Analytics Model, which prioritizes risk based on asset health and consequences. Typically towers with the highest risks from this model are in high atmospheric corrosion areas for which permits take a while to obtain. As such, it is proposed to start the program with high to medium risk assets where permits are less cumbersome to obtain. The replacement of approximately 150 towers will minimize the program implementation risk. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-18 | 76 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | 214 | 1. Work that prevents fire ignition | 11 | 3.0011 | IGP | 5781559 | T.0004170 | Vaca-Vacaville-Jameson-North Tower 115kV | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2029-07-31 | NA | 2030-01-10 | NA | NA | FALSE | NA | NA ¦ NA | 1999.1216 | 13678.2891 | 226.9576 | 367.9295 | 560.9261 | 56.7211 | 58.1484 | 0 | 0 | 0 | 0 | 0 | 1999.1216 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1664 | Lammers-Kasson 115kV Twr Repl |  |  | San Joaquin ¦ Tracy, San Joaquin | This project will replace 49 lattice steel towers on the Lammers-Kasson 115 kV Power Line with TSPs ahead or back of the existing structure locations and reconductor 3 spans of the line with new 477 ACSS (same as existing). This project will also improve safety and reliability for the customers served in San Joaquin County by mitigating the risk of failure from aged, corroded, and hard-to-maintain lattice steel towers. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-08-04 | 73 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 214 | 2. Overhead With Strong Safety Link | 748 | NA | NA | 5781560 | T.0004171 | Lammers-Kasson 115kV Twr Repl | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6507-E | 2022-02-18 | Approved | 2022 | Operational | 1 | 2022-10-11 | 2022-12-31 | 2022-12-23 | NA | NA | FALSE | 14906 | NA ¦ NA | 15991.7038 | 15991.7038 | 436.2332 | 12848.5951 | 1657.7312 | 44.6006 | 0 | 0 | 0 | 0 | 0 | 0 | 15991.7038 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 12599.8069 | 1384.6828 | 38.9763 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1665 | LAMMERS-KASSON 115KV TWR REPL - LAND |  |  | San Joaquin ¦ Tracy, San Joaquin | This project will replace 49 lattice steel towers on the Lammers-Kasson 115 kV Power Line with TSPs ahead or back of the existing structure locations and reconductor 3 spans of the line with new 477 ACSS (same as existing). This project will also improve safety and reliability for the customers served in San Joaquin County by mitigating the risk of failure from aged, corroded, and hard-to-maintain lattice steel towers. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-08-04 | NA | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5552800 | T.0004171 | Lammers-Kasson 115kV Twr Repl | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6507-E | 2022-02-18 | Approved | 2022 | Operational | 1 | 2023-10-27 | 2022-12-31 | 2023-12-31 | Prioritization | NA | TRUE | 14906 | NA ¦ NA | 827.5902 | 982.2296 | 0 | 0 | 374.7113 | 86.6116 | 136.7785 | 384.128 | 0 | 0 | 0 | 0 | 598.1015 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 374.7114 | 86.6116 | 136.7786 | 229.4887 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1666 | TESLA-SCHULTE SW STA #2 115KV SHOO-FLY |  |  | Alameda ¦ San Joaquin | This project will replace 34 lattice steel towers on the Tesla-Schulte #2 115 kV Power Line with 3 TSPs and 31 lattice steel towers ahead or back of the existing structure locations and reconductor 1.41 miles of conductor with new 477 ACSS (same as existing). This project will also improve safety and reliability for the customers served in San Joaquin County by mitigating the risk of failure from aged, corroded, and hard-to-maintain lattice steel towers. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-09-08 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5548808 | T.0004172 | Tesla-Schulte SW Sta #2 115kV Twr Repl | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6508-E | 2022-02-18 | Approved | 2022 | Operational | 1 | 2022-04-23 | 2022-11-30 | 2022-05-01 | NA | NA | FALSE | 15880 | NA ¦ NA | 41.7994 | 41.7994 | 0 | 41.7144 | 0 | 0.085 | 0 | 0 | 0 | 0 | 0 | 0 | 41.7994 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 ¦ 2026 | 0 | 34.7699 | 0 | 0.07085 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1667 | Tesla-Schulte SW Sta #2 115kV Twr Repl |  |  | Alameda ¦ San Joaquin | This project will replace 34 lattice steel towers on the Tesla-Schulte #2 115 kV Power Line with 3 TSPs and 31 lattice steel towers ahead or back of the existing structure locations and reconductor 1.41 miles of conductor with new 477 ACSS (same as existing). This project will also improve safety and reliability for the customers served in San Joaquin County by mitigating the risk of failure from aged, corroded, and hard-to-maintain lattice steel towers. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-09-08 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | 214 | 2. Overhead With Strong Safety Link | 995 | NA | NA | 5781561 | T.0004172 | Tesla-Schulte SW Sta #2 115kV Twr Repl | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6508-E | 2022-02-18 | Approved | 2022 | Operational | 1 | 2022-09-15 | 2022-11-30 | 2023-04-18 | NA | NA | FALSE | 15880 | NA ¦ NA | 6854.2077 | 6854.2077 | 437.2004 | 4639.5566 | 882.4607 | 22.6636 | 0 | 0 | 0 | 0 | 0 | 0 | 6854.2077 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 6514.2248 | 21.5559 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1668 | Gold Hill-Bellota-Lockeford 115kV |  |  | Clay CDP, Sacramento ¦ Dogtown CDP, San Joaquin ¦ Folsom, Sacramento ¦ Lockeford CDP, San Joaquin ¦ Sacramento ¦ San Joaquin | Gold Hill-Bellota-Lockeford 115kV Replacement Project, which plans to replace 13 deteriorated transmission line lattice-steel towers. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-02 | 76 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 | NA | 214 | 2. Overhead With Strong Safety Link | 652 | 3.0011 | IGP | 5781562 | T.0004173 | Gold Hill-Bellota-Lockeford 115kV | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2034-07-21 | NA | 2036-03-06 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 15250 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 250 | 7500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 2% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1669 | Ignacio-Alto 60kV Twr Repl 13/114 |  |  | Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin | This project proposes to replace two aging, deteriorated, steel structures, towers 13/113 and 13/114 on the Ignacio – Alto 60kV line, their associated foundations in order to maintain reliable service, and reconductor the associated conductor with a summer emergency (SE) rating of at least 1124 Amps. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-10-08 | 57 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 214 | 1. Work that prevents fire ignition | 7 | 4.0111 | IGP | 5781898 | T.0004219 | Ignacio-Alto 60kV Twr Repl 13/114 | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6645-E | 2022-07-07 | Approved | 2022 | Operational | 1 | 2021-03-01 | 2023-10-01 | 2024-01-11 | NA | NA | TRUE | 3902 | NA ¦ NA | 4851.0265 | 4851.0265 | 1393.4027 | 563.4045 | 1208.9658 | 794.674 | 350.3505 | 28.3339 | 0 | 0 | 0 | 0 | 4822.6926 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 2765.8733 | 203.58 | 16.4641 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1670 | DUMBARTON-NEWARK 115KV SALT POND TRP |  |  | Fremont, Alameda ¦ Newark, Alameda | The project scope of work includes following: Replace Dumbarton – Newark 115 kV Line aging tower Nos. 3/24, 4/30, 4/34, 4/35, 5/36, 5/37, and 6/43 with degradation issues categorized as high risk with lattice steel towers. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-04 | 76 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | 2. Overhead With Strong Safety Link | 520 | 3.0011 | IGP | 5782125 | T.0004260 | DUMBARTON-NEWARK 115KV Salt Pond TRP | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | PTC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2032-05-13 | NA | 2032-11-18 | NA | NA | FALSE | NA | NA ¦ NA | 2387.6819 | 12143.1891 | 898.3819 | 311.3367 | 344.5074 | 23.8894 | 68.5433 | 211.6951 | 255 | 2000 | 4000 | 2320 | 2356.494 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1671 | Ravenswood-San Mateo 230kV TWR 1/7 RPL |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | This project will proactively replace Tower 001/007 on the Ravenswood-San Mateo 230 kV Lines, which has deteriorated foundations and steel components | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-19 | 60 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | NA | 2. Overhead With Strong Safety Link | 880 | NA | NA | 5789620 | T.0005727 | Ravenswood-San Mateo 230kV TWR 1/7 RPL | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-11-01 | 2020-12-31 | 2020-11-18 | NA | NA | FALSE | 8900 | NA ¦ NA | 8863.4215 | 8863.4215 | -15.7765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8863.4215 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -15.7764 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1672 | Potter Valley-Mendocino 60 KV TWR RPL |  |  | Mendocino ¦ Potter Valley CDP, Mendocino | Four lattice steel tower replacements (w/new lattice steel towers), replace conductors, insulators and transmission line from Structures 000/004 to 000/007. Reconductoring approximately 0.42 miles. The existing 3/0 CU conductor will be replaced with 397 AAC 19 Strands “Canna” between 000/004 and 000/007. No new access roads will be constructed. A pull site may be used for reconductoring activities, the location of which is still being determined. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-10-30 | 89 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | 1. Work that prevents fire ignition | 301 | 4.0111 | IGP | 5541160 | T.0006100 | Potter Valley - Mendocino 60 KV TWR RPL | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-04-27 | 2025-12-31 | 2026-08-07 | Scope Change | NA | TRUE | 4700 | NA ¦ NA | 1921.3805 | 3249.9343 | 49.2709 | 579.9888 | 197.4649 | 169.2747 | 673.8802 | 1421.8043 | 0 | 0 | 0 | 0 | 1828.13 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 207.5215 | 579.9951 | 197.4649 | 169.2747 | 438.5424 | 81.2462 | 0% | NA ¦ NA | NA | 6.10% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1673 | Potter Valley-Mendocino Land Order |  |  | Mendocino ¦ Potter Valley CDP, Mendocino | Four lattice steel tower replacements (w/new lattice steel towers), replace conductors, insulators and transmission line from Structures 000/004 to 000/007. Reconductoring approximately 0.42 miles. The existing 3/0 CU conductor will be replaced with 397 AAC 19 Strands “Canna” between 000/004 and 000/007. No new access roads will be constructed. A pull site may be used for reconductoring activities, the location of which is still being determined. | Other | New | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-10-30 | NA | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ False | FALSE | Corrosion |  | NA | NA | NA | NA | NA | NA | NA | 4.0111 | IGP | 5800759 | T.0006100 | Potter Valley - Mendocino 60 KV TWR RPL | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | NA | NA | 2025-12-31 | OAI | NA | NA | FALSE | 4700 | NA ¦ NA | 5.2698 | 5.2698 | 0 | 0 | 0 | 0 | 5.2365 | 0.0333 | 0 | 0 | 0 | 0 | 5.2365 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1674 | BRIGHTON - GRAND ISLAND #1 115kV TWR RPL |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | The Brighton – Grand Island #1 115 kV Line is is located in the North Valley region. It is 24.99 miles long, with 205 structures. The following scope of work is proposed to mitigate structure and foundation issues identified in the field: Replacement of 5 structures and their foundations on the Brighton – Grand Island #1 115 kV circuit; Replacement of insulators, hardware, and equipment on these structures; and Replacement of conductor and splices around the (5) structure replacement locations. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-01 | 71 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 | NA | NA | 2. Overhead With Strong Safety Link | 388 | NA | NA | 5541336 | T.0006155 | BRIGHTON - GRAND ISLAND #1 115kV TWR RPL | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-11-30 | 2021-02-20 | 2021-02-25 | NA | NA | FALSE | 1130 | NA ¦ NA | 2717.821 | 2717.821 | 1533.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2717.821 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 2717.8211 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1675 | EBMUD 115 KV TAP POLE REPLACEMENT |  |  | Contra Costa Centre CDP, Contra Costa ¦ Walnut Creek, Contra Costa | The project scope of work includes the following: Replace three (3) existing poles and associated equipment along the EBMUD 115 kV Tap T-Line and redesign accordingly. The EBMUD 115 kV Tap is a high pressure nitrogen filled system transitioning from overhead to underground. As a result, the three (3) poles are going to introduce complexity and cost than a typical pole replacement. The project proposes to replace 3 existing poles and associated equipment along the EBMUD 115 kV Tap T-Line located in Contra Costa County, CA. This projects need is because the current condition of the three (3) poles are deteriorated and at risk of failure. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-02-23 | 49 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 | NA | NA | NA | NA | 5.4 | IGP | 5543819 | T.0006942 | EBMUD 115 kV Tap Pole Replacement | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-08-16 | NA | 2027-10-19 | NA | NA | TRUE | NA | NA ¦ NA | 567.3875 | 7911.5171 | 0 | 155.2084 | 310.4104 | 1.5474 | 57.7912 | 1367.112 | 5987.0011 | 300 | 0 | 0 | 524.9575 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 139.6875 | 278.8459 | 1.916 | 52.0121 | 38.187 | 0% | NA ¦ NA | NA | 30.06% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1676 | IGNACIO - SOBRANTE 230KV TWR RPL |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | In an effort to support PG&E top-level initiatives to manage asset risk for the benefit of public and employee safety, service reliability, operational flexibility, and cost reduction, the proposed Ignacio - Sobrante 230 kV Towers Replacement Project will proactively replace four towers on the line. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-25 | 43 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | NA | NA | 230 | NA | NA | NA | NA | NA | NA | 5795020 | T.0007002 | IGNACIO - SOBRANTE 230KV TWR RPL | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-03-01 | 2022-04-13 | 2022-04-18 | NA | NA | FALSE | 5583 | NA ¦ NA | 7689.8617 | 7689.8617 | 1670.8381 | 5903.9565 | 105.9001 | 9.167 | 0 | 0 | 0 | 0 | 0 | 0 | 7689.8617 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 6897.7577 | 96.3109 | 8.337 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1677 | Ignacio-Sobrante Twr 29/133 Replacement |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | In an effort to support PG&E top-level initiatives to manage asset risk for the benefit of public and employee safety, service reliability, operational flexibility, and cost reduction, the proposed Ignacio - Sobrante 230 kV Towers Replacement Project will proactively replace four towers on the line. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-25 | 42 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | NA | 230 | NA | NA | NA | NA | NA | NA | 5549227 | T.0007002 | IGNACIO - SOBRANTE 230KV TWR RPL | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-10-04 | 2022-04-13 | 2023-11-14 | Prioritization | NA | FALSE | 5583 | NA ¦ NA | 2299.6518 | 2299.6518 | 0 | 210.603 | 2061.0302 | 28.0187 | 0 | 0 | 0 | 0 | 0 | 0 | 2299.6518 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 210.603 | 1797.1659 | 24.7641 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1678 | Ignacio-Alto-Sausalito-Tower Replacement |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | The Ignacio - Alto – Sausalito 60 kV Line is is located in the North Coast region. It is 17.36 miles long, with 127 structures. In order to prevent the risk of structure failure, asset components on the line are being proposed to be replaced with the following scope of work: • Replacement of tower 009/064 and its foundation on the Ignacio - Alto – Sausalito 60 kV circuit; and • Replacement of old insulators, hardware, and equipment on the structure; | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-07 | 94 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | NA | NA | 5544414 | T.0007060 | Ignacio-Alto-Sausalito-Tower Replacement | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-05-31 | 2021-11-19 | 2022-06-10 | Project Design | NA | FALSE | 5315 | NA ¦ NA | 2987.559 | 2987.559 | 392.7716 | 2544.516 | 50.2715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2987.559 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 379.8169 | 2460.5908 | 48.6134 | -1e-05 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1679 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 34 deteriorated towers along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 34 towers in the scope of this project will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. Since the time of the initial Advance Authorization, the cage extensions and 14 miles of reconductoring have been removed from the scope. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-04 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 5.31 | IGP | 5792138 | T.0007072 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-02-28 | 2027-01-15 | 2023-03-20 | NA | NA | FALSE | 238200 | NA ¦ NA | 17864.8978 | 17864.8978 | -34.4686 | 6348.9479 | 9925.7336 | -737.9039 | 37.2256 | 0 | 0 | 0 | 0 | 0 | 17864.8978 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 17496.1508 | -693.6359 | 34.9924 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1680 | IGNACIO - MARE ISLAND TWR REPL PHASE 2 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 34 deteriorated towers along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 34 towers in the scope of this project will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. Since the time of the initial Advance Authorization, the cage extensions and 14 miles of reconductoring have been removed from the scope. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-04 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 | NA | NA | NA | NA | 5.31 | IGP | 5798400 | T.0007072 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-11-27 | 2027-01-15 | 2023-12-19 | NA | NA | FALSE | 238200 | NA ¦ NA | 20964.2536 | 20964.2536 | 0 | 0 | 19005.5176 | 1708.8227 | 249.2832 | 0.6301 | 0 | 0 | 0 | 0 | 20963.6235 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 19005.5176 | 1032.9344 | 241.0952 | 0.60938 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1681 | IGNACIO - MARE ISLAND TWR REPL PHASE 3 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 34 deteriorated towers along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 34 towers in the scope of this project will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. Since the time of the initial Advance Authorization, the cage extensions and 14 miles of reconductoring have been removed from the scope. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-04 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 5.31 | IGP | 5801466 | T.0007072 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-11-13 | 2027-01-15 | 2024-12-13 | NA | NA | TRUE | 238200 | NA ¦ NA | 12994.7601 | 12994.7601 | 0 | 0 | 58.7959 | 12144.1489 | 780.6839 | 11.1314 | 0 | 0 | 0 | 0 | 12983.6287 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 12202.9448 | 780.6839 | 11.1314 | 0% | NA ¦ NA | NA | 0% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1682 | Vaca-Vacaville-Jameson 115k TWR 8/63 |  |  | Benicia, Solano ¦ Fairfield, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | This project will replace Tower 008/063 which supports the Vaca-Vacaville-Jameson-North Tower and Vaca-Vacaville-Cordelia 115 kV lines with a tubular steel pole (TSP) structure in the same location as the existing structure. Currently, Tower 008/063 has been removed and the two circuits are supported by a shoofly. The replacement of Tower 008/063 was necessary because the top cage of the tower was twisted, and the engineering recommendation was to replace the whole structure and not only the top cage due to structural stability concerns. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-18 | 74 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5795883 | T.0007123 | Vaca-Vacaville -Jameson 115kV TWR 8/63 | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-05-06 | 2021-11-30 | 2022-05-11 | NA | NA | FALSE | 3131 | NA ¦ NA | 5650.1638 | 5650.1638 | 1444.3807 | 4167.8781 | 37.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5650.1638 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 4449.0396 | 29.9278 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1683 | Martin_SFAirport_Tower Replacement |  |  | Brisbane, San Mateo ¦ San Mateo ¦ South San Francisco, San Mateo | This project will proactively replace Tower 002/021 on the Martin-SF Airport 115kV Line, which has deteriorated steel components. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-30 | 34 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5544971 | T.0007173 | Martin_SFAirport_Tower Replacement | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6683-E | 2022-08-18 | Approved | 2022 | Operational | 1 | 2022-11-14 | 2021-10-31 | 2022-11-16 | Project Design | NA | FALSE | 1652 | NA ¦ NA | 2070.9217 | 2070.9217 | 777.2327 | 1361.906 | -69.4018 | 1.1848 | 0 | 0 | 0 | 0 | 0 | 0 | 2070.9217 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 636.8445 | 1115.9236 | -56.866 | 0.97084 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1684 | Essex Jct-Arcata-Fairhaven 60 kV |  |  | Arcata, Humboldt ¦ Humboldt ¦ Manila CDP, Humboldt ¦ Samoa CDP, Humboldt | This project will replace existing double circuit lattice steel tower #004/022 on the Essex Jct-Arcata-Fairhaven 60 kV Line in order to maintain reliable electric service for the customers in Humboldt County. Furthermore, we need to investigate an over-tensioning condition and an issue with a clearance for the double circuit transmission line. Resolving these problems are likely to require a shoo-fly and potentially replacement of one or two adjacent towers on this line. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-19 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | NA | NA | 5545379 | T.0007238 | Essex Jct-Arcata-Fairhaven 60 kV | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-05-20 | 2022-04-30 | 2022-05-23 | NA | NA | FALSE | 1682 | NA ¦ NA | 1865.2006 | 1865.2006 | 312.7093 | 1067.6586 | 317.4533 | 167.3793 | 0 | 0 | 0 | 0 | 0 | 0 | 1865.2006 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 300.6822 | 1026.5977 | 305.2437 | 160.9417 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1685 | Sobrante-Moraga 115 kV Tower Replacement |  |  | Orinda, Contra Costa | This project will replace 7 lattice steel poles on 2 transmission lines: Poles #00/001A, 00/002A, 00/003A, 00/005A on the Sobrante-Moraga 115 kV Line; and Poles #00/001B, 00/002B, 00/003B on the Moraga-Lakewood 115 kV Line. All 7 structures will be replaced with TSP’s per engineering recommendations. These replacements will be made in order to maintain reliable electric service for the customers in Contra Costa County. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-06 | 73 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5797568 | T.0007396 | Sobrante-Moraga 115 kV Tower Replacement | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6644-E | 2022-07-07 | Approved | 2022 | Operational | 1 | 2022-12-01 | 2022-12-31 | 2022-12-16 | NA | NA | FALSE | 2813 | NA ¦ NA | 2027.6724 | 2027.6724 | 164.5531 | 1728.5483 | 134.5709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027.6724 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 1679.2472 | 119.0951 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1686 | IAS 4/37 & 4/38 Veg Restoration |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | The target structures of this project, 004/037 and 004/038, have been determined to require replacement via B-Tag assignment post inspection. This project will aim to replace both structures with new lattice steel design towers and engineered piling or pier foundations. This work, when complete, will mitigate all currently assigned B-tags on the two structures and enable PG&E to maintain compliance on this segment of the line. This project, when combined with other ongoing efforts to improve the functionality and dependency of the line, will allow PG&E to continue safe and reliable electric operation in the region. This project proposes to : • Replace foundations and lattice steel towers at locations 004/037 and 004/038 with new foundations and lattice steel towers ahead or back in line from original structure locations. • To mitigate B-Tags which have been assigned to each of these structures post inspection. • Completion of this work will mitigate all currently assigned B-Tags and improve system reliability in this segment of the line. • This work will be executed by an Engineer, Procure, Construction (EPC) contract. Awarded prime contractor will be responsible for the completion of the T-line and Civil engineering, material procurement, equipment procurement, construction and post-construction cleanup efforts. • PG&E will assist in customer outreach, permit application and attainment, land acquisition as needed, environmental clearances for work and confirmation of completion of work per scope. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-07 | 94 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 4.0111 | IGP | 5562204 | T.0007460 | Ignacio-Alto-Sausalito B Tag Projects | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-06-01 | EIR | NA | CDFW | NA | NOC: AL 6970-E | 2023-06-26 | Approved | 2023 | Engineering more than 50% complete | 3 | NA | 2023-12-29 | OAI | NA | NA | TRUE | 18460 | NA ¦ NA | 4.8281 | 179.1466 | 0 | 0 | 0 | 0 | 0.0979 | 59.752 | 0 | 0 | 0 | 0 | 0.098 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1687 | Ignacio-Alto-Sausalito 4/37 & 4/38 B Tag |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | The target structures of this project, 004/037 and 004/038, have been determined to require replacement via B-Tag assignment post inspection. This project will aim to replace both structures with new lattice steel design towers and engineered piling or pier foundations. This work, when complete, will mitigate all currently assigned B-tags on the two structures and enable PG&E to maintain compliance on this segment of the line. This project, when combined with other ongoing efforts to improve the functionality and dependency of the line, will allow PG&E to continue safe and reliable electric operation in the region. This project proposes to : • Replace foundations and lattice steel towers at locations 004/037 and 004/038 with new foundations and lattice steel towers ahead or back in line from original structure locations. • To mitigate B-Tags which have been assigned to each of these structures post inspection. • Completion of this work will mitigate all currently assigned B-Tags and improve system reliability in this segment of the line. • This work will be executed by an Engineer, Procure, Construction (EPC) contract. Awarded prime contractor will be responsible for the completion of the T-line and Civil engineering, material procurement, equipment procurement, construction and post-construction cleanup efforts. • PG&E will assist in customer outreach, permit application and attainment, land acquisition as needed, environmental clearances for work and confirmation of completion of work per scope. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-07 | 94 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 4.0111 | IGP | 5797979 | T.0007460 | Ignacio-Alto-Sausalito B Tag Projects | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-06-01 | EIR | NA | CDFW | NA | NOC: AL 6970-E | 2023-06-26 | Approved | 2023 | Operational | 1 | 2024-11-11 | 2023-12-29 | 2024-11-26 | Prioritization | NA | TRUE | 18460 | NA ¦ NA | 19720.7893 | 19721.3791 | 104.6644 | 381.5838 | 1178.2879 | 17260.6861 | 794.0499 | 2.1069 | 0 | 0 | 0 | 0 | 19719.2721 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 18417.2837 | 772.416 | 1.4758 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1688 | Wheeler Ridge-Tejon - Pole Replacement |  |  | Kern | The project will address California Public Utilities Commission (CPUC) General Order (GO)-95 and Pacific Gas and Electric Company (PG&E) standard requirements, in addition increase system performance in Kern County by performing the following work: • Replace forty-six (46) wood structures on the Wheeler Ridge – Tejon 70 kV Line; • Replacement of old insulators, hardware, and equipment on the structure; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-03 | 48 | Lifecycle Replacement Analysis | Other - Deferral | $2 Mil - $3 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | NA | NA | NA | 4.0111 | NA | 5798379 | T.0007564 | Wheeler Ridge-Tejon - Pole Replacement | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6632-E | 2022-05-19 | Approved | 2022 | Operational | 1 | 2022-10-01 | 2023-12-01 | 2024-01-25 | NA | NA | FALSE | 3447 | NA ¦ NA | 4841.9616 | 4841.9616 | 7.1413 | 2069.0544 | 2394.7967 | 370.9692 | 0 | 0 | 0 | 0 | 0 | 0 | 4841.9616 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 4668.666 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1689 | Newark-Livermore 60 kV Tower Replacement |  |  | Alameda ¦ Fremont, Alameda ¦ Livermore, Alameda ¦ Sunol CDP, Alameda | This project proposes to replace towers 08/051 and 08/052 on the Newark-Livermore 60 kV Line to address aging transmission assets and maintain reliable service. Towers 08/051 and 08/052 were not originally issued replacement tags, but rather a maintenance crew observed the rust while performing a routine cleaning of the nearby transmission facilities. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-20 | 107 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | NA | NA | 60 | NA | NA | NA | NA | NA | NA | 5548162 | T.0007858 | Newark-Livermore 60 kV Tower Replacement | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-10-09 | 2023-07-15 | 2023-10-13 | NA | NA | FALSE | 2206 | NA ¦ NA | 1546.4316 | 1546.4316 | 0 | 361.0978 | 1167.727 | 17.6068 | 0 | 0 | 0 | 0 | 0 | 0 | 1546.4316 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 327.3557 | 1073.4691 | 16.1327 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1690 | Tidewater-Sobrante 230 kV TR |  |  | Alhambra Valley CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa ¦ Orinda, Contra Costa ¦ Vine Hill CDP, Contra Costa | This project proposes to replace seven line structures (014/068, 014/069, 014/070, 014/071, 014/072, 014/073, and 015/074) on the Tidewater-Sobrante 230 kV Line in order to maintain reliable service and reduce the potential public safety risk due to hardware failures on the structures. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-07-09 | 53 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 230 | NA | NA | NA | NA | NA | NA | 5799458 | T.0007860 | Tidewater-Sobrante 230 kV TR | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6717-E | 2022-09-30 | Approved | 2022 | Operational | 1 | 2023-03-31 | 2023-05-24 | 2023-04-10 | NA | NA | FALSE | 14000 | NA ¦ NA | 2881.4085 | 2881.4085 | 0 | 1149.8515 | 1741.0678 | -9.5107 | 0 | 0 | 0 | 0 | 0 | 0 | 2881.4085 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 2866.6487 | -9.4288 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1691 | Tidewater-Sobrante 230 kV TR PH2 |  |  | Alhambra Valley CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa ¦ Orinda, Contra Costa ¦ Vine Hill CDP, Contra Costa | This project proposes to replace seven line structures (014/068, 014/069, 014/070, 014/071, 014/072, 014/073, and 015/074) on the Tidewater-Sobrante 230 kV Line in order to maintain reliable service and reduce the potential public safety risk due to hardware failures on the structures. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-07-09 | 53 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 230 | NA | NA | NA | NA | 4.0111 | NA | 5805660 | T.0007860 | Tidewater-Sobrante 230 kV TR | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6717-E | 2022-09-30 | Approved | 2022 | Operational | 1 | 2024-03-01 | 2023-05-24 | 2024-03-10 | Scope Change | NA | FALSE | 14000 | NA ¦ NA | 1879.9468 | 1879.9468 | 0 | 0 | 650.7834 | 1139.2433 | 75.0789 | 14.8412 | 0 | 0 | 0 | 0 | 1865.1056 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1756.2724 | 73.6442 | 14.8412 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1692 | Tidewater-Sobrante 230 kV TR PH3 |  |  | Alhambra Valley CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa ¦ Orinda, Contra Costa ¦ Vine Hill CDP, Contra Costa | This project proposes to replace seven line structures (014/068, 014/069, 014/070, 014/071, 014/072, 014/073, and 015/074) on the Tidewater-Sobrante 230 kV Line in order to maintain reliable service and reduce the potential public safety risk due to hardware failures on the structures. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-07-09 | 54 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 230 | NA | NA | NA | NA | 4.06 | IGP | 5809400 | T.0007860 | Tidewater-Sobrante 230 kV TR | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6717-E | 2022-09-30 | Approved | 2022 | Operational | 1 | 2025-10-14 | 2023-05-24 | 2025-11-14 | Scope Change | NA | TRUE | 14000 | NA ¦ NA | 4337.329 | 4716.5806 | 0 | 0 | 0 | 502.9409 | 3633.903 | 579.7368 | 0 | 0 | 0 | 0 | 4136.8438 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 4099.6714 | 198.6344 | 0% | NA ¦ NA | NA | 8% ¦ Electric Operations Risk Management | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1693 | RAVENSWOOD-AMES #1 115 KV: SALT POND |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Mountain View, Santa Clara ¦ Palo Alto, Santa Clara ¦ Santa Clara | The California State Coastal Conservancy (SCC) has a project to breach the levee for Salt Pond A2W. That will increase the water levels around the 18 towers in that area. Their plan is to breach the levee in 2023. Engineering has determined that adding cathodic protection, tower coating, and grouting on the towers will address that issue. | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-04 | 74 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5800218 | T.0008192 | RAVENSWOOD-COOLEY-NEWARK-AMES SALT POND | 4 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-12-19 | 2023-03-20 | 2023-10-26 | Prioritization | NA | FALSE | 6362 | NA ¦ NA | 6417.5939 | 6417.5939 | 0 | 695.4606 | 5583.5908 | 138.5425 | 0 | 0 | 0 | 0 | 0 | 0 | 6417.5939 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 6279.0514 | 138.5425 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1694 | Martin-Millbrae #1 Tower Replacements |  |  | Brisbane, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ South San Francisco, San Mateo | In March 2022, transmission line maintenance crews identified severe corrosion on Martin-Millbrae No. 1 115 kV Towers 002/020 and 002/021. The crews made repairs, but were not able to address all of the deterioration. Given the severity of the corrosion on these structures, Asset Strategy and T-Line Civil Engineering has recommended these towers be replaced. These tower replacements have been assigned to the 70S Tower Replacement Program because they are beyond repair and a current safety and reliability concern. The project scope of work includes the following: • Replacement of Martin – Millbrae No. 1 115 kV Towers 002/020 and 002/021 and associated foundations; • Replacement of old insulators, hardware, and equipment; • Construction will require a temporary shoofly to keep the existing circuits in service during installation of the new structures. This work will be completed under a single line or dual line clearance based on consultation with Transmission Operations | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-30 | 34 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5548880 | T.0008193 | Martin-Millbrae #1 Tower Replacements | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6683-E | 2022-08-18 | Approved | 2022 | Operational | 1 | 2022-11-14 | 2022-12-31 | 2022-11-23 | NA | NA | FALSE | 4300 | NA ¦ NA | 3114.7964 | 3114.7964 | 0 | 2838.3075 | 276.4889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3114.7964 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 2668.8619 | 259.9826 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1695 | Kearney-Biola Pole Replacement |  |  | Biola CDP, Fresno ¦ Fresno ¦ Fresno, Fresno | The Kearney-Biola 70 kV Line located in Fresno County, is approximately 19 miles long and supported by 348 overhead structures. Structure 018/016 is one of the Lattice Steel Poles (LSP) supporting this line located within the Biola Substation fence. The structure was assessed due to a bent distribution underbuild cross-arm at which point the entire pole was found to be in poor condition due to lack of a reinforced foundation, direct embeded along with limited documentation on the asset. After reviewing possible repair options, the project team recommended to replace the existing LSP with Tubular Steel Pole (TSP), due to relatively high foundation retro-fit and corresponding repair costs. The project will also address possible touch-potential issues due to the existing metallic substation fence beng in close proximity to the existing metallic structure. This work is needed to maintain reliable electric service for the customers in Fresno County who are experiencing outages due to circuit unrealiability. In addition, substation clearance issues will reduce safety concerns related to touch potential. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-08-20 | 55 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | NA | NA | NA | NA | NA | 5549361 | T.0008283 | Kearney-Biola Pole Replacement | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-09-19 | 2023-10-31 | 2023-11-22 | NA | NA | FALSE | 1341 | NA ¦ NA | 1218.1186 | 1218.1186 | 0 | 172.1001 | 871.9043 | 179.927 | -5.8128 | 0 | 0 | 0 | 0 | 0 | 1218.1186 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 149.8551 | 856.3056 | 173.405 | -5.6021 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1696 | IGNACIO - SOBRANTE 230KV TRP PH3 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The project scope of work includes following: • Replace structures IG004/025, IG004/024, IG004/023, IG004/022, IG004/021, and IG003/020 and their foundations under phase 2. • Replace structures IG003/015 through IG002/010 and their foundations under phase 3. • Replace old insulators, hardware, and equipment on these structures. • Coordinate transmission outages with T-line Operations, Grid Control, and impacted local stakeholders. • Manage any supporting purchase orders such as engineering, Geotech, and construction. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-25 | 43 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | NA | NA | NA | 4.0111 | IGP | 5800802 | T.0008284 | IGNACIO - SOBRANTE 230KV TRP PH2 & PH3 | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7580-E | 2025-04-25 | Approved | 2025 | Operational | 1 | 2025-08-21 | 2022-12-31 | 2025-10-11 | Scope Change | NA | TRUE | 11907 | NA ¦ NA | 10692.4316 | 10919.8435 | 0 | 116.5431 | 454.9508 | 336.2143 | 9835.144 | 176.9912 | 0 | 0 | 0 | 0 | 10742.8523 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 10020.9883 | -46.9505 | 0% | NA ¦ NA | NA | 7% ¦ Electric Operations Risk Management | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1697 | IGNACIO - SOBRANTE 230KV TRP PH2 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The project scope of work includes following: • Replace structures IG004/025, IG004/024, IG004/023, IG004/022, IG004/021, and IG003/020 and their foundations under phase 2. • Replace structures IG003/015 through IG002/010 and their foundations under phase 3. • Replace old insulators, hardware, and equipment on these structures. • Coordinate transmission outages with T-line Operations, Grid Control, and impacted local stakeholders. • Manage any supporting purchase orders such as engineering, Geotech, and construction. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-25 | 41 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | NA | NA | NA | NA | NA | 5800801 | T.0008284 | IGNACIO - SOBRANTE 230KV TRP PH2 & PH3 | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-03 | 2022-12-31 | 2022-11-21 | NA | NA | FALSE | 11907 | NA ¦ NA | 10020.4865 | 10020.4865 | 0 | 9890.6442 | 125.2901 | 4.5522 | 0 | 0 | 0 | 0 | 0 | 0 | 10020.4865 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 9890.6442 | -777.0053 | 4.1394 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1698 | Jefferson-Stanford 60kV Rep Pole 06/157 |  |  | Atherton, San Mateo ¦ Emerald Lake Hills CDP, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo ¦ Santa Clara ¦ Stanford CDP, Santa Clara ¦ Woodside, San Mateo | This project proposes to: • Replace wood Pole 006/157 on the Jefferson-Stanford 60kV line that is severely deteriorating due to underbuild tension. The Jefferson-Stanford 60kV Line is a Pacfic Gas and Electric (PG&E) owned transmission line in San Mateo County. The line normally provides service to Stanford University and Emerald Lake Substation (1,530 customers), and it provides back-up service to the Stanford Linear Accelerator Center (SLAC) and other distribution substations serving customers in Menlo Park, Atherton and Woodside. The line is 9.1 miles long, with 7.6 miles of the line overhead and 1.5 miles underground. It is located in a densely populated area, and approximately 2.6 miles of the line runs through a Tier 2 High Fire Threat District (HFTD). The line transitions from an overhead section to an underground section at Pole 006/157 on Alameda de las Pulgas near Las Lomitas Elementary School in Menlo Park. Inspections by overhead and underground line inspectors have concluded that the structural integrity of the pole has been severely compromised and requires immediate mitigation. As a result of these inspections, a Notification ‘A’ Tag (#122795422) was completed to stub Pole 006/157. However, a more permanent solution is required to replace the deteriorated pole. This project is needed now to meet PG&E’s standard requirement to maintain assets. Mainaining aging assets is not viable. And there is a significant risk of failure on this 60kV transmission line, which could potentially impact electric service and presents a safety hazard to local customers in Menlo Park. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2025-11-09 | 76 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.42 | IGP | 5801179 | T.0008334 | Jefferson-Stanford 60kV Rep Pole 06/157 | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-11-01 | NA | 2027-12-13 | NA | NA | TRUE | NA | NA ¦ NA | 584.0089 | 9477.8482 | 0 | 0 | 72.7808 | 26.3184 | 419.3241 | 1659.4249 | 5792.5626 | 300 | 0 | 0 | 518.4233 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 0.34% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1699 | Vaca-Vacaville -Jameson 115kV TWR 24/171 |  |  | Benicia, Solano ¦ Fairfield, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | This project proposes to replace 2 severely rusted lattice steel towers with 2 new lattice steel towers (LST’s) to improve asset health and maintain reliable service. Tower 24/171 was removed and replaced with a two-pole shoofly in July 2022 to avoid structure failure. This tower replacement project will replace that tower and the preceding structure, 24/170. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-18 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5550039 | T.0008400 | Vaca-Vacaville -Jameson 115kV 24/170-171 | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-07-17 | 2023-07-30 | 2023-07-20 | NA | NA | FALSE | 1146 | NA ¦ NA | 1082.5467 | 1082.5467 | 0 | 274.238 | 808.3087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1082.5467 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 208.3223 | 645.1395 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1700 | Ravenswood - San Mateo 230kV 01/011 TRP |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The project scope of work includes following: • Complete necessary immediate foundation replacement on Tower 001/011. • Replace Tower 001/011. • Replace old insulators, hardware, and equipment on Tower 001/011. • Coordinate transmission outages with T-line Operations, Grid Control, and impacted local stakeholders. • Manage any supporting purchase orders such as vegetation management and engineering. In January 2020, Maintenance and Construction (M&C) crews doing a site walk observed the legs of Tower 001/007 showing deterioration, and the tower required immediate attention. An emergency fix was done, and the tower was then replaced in late 2020. In June 2022, during a planned inspection on this line, a field crew observed significant degradation of the wooden piles and concrete foundation supporting structure 001/011 during a low-tide event. The conditions were reported, and T-Line engineering reviewed the situation and determined that the foundation was in need of immediate and urgent reinforcement, and that the structure as a whole needs to be replaced in order to permanently improve conditions at this location and offset future maintenance and repair costs. This project addresses the Electric Operations risk of Failure of Transmission Overhead Assets. This project will replace a structure with poor asset health to mitigate any potential safety incidents or unplanned outages to serve the electric customers of San Mateo County safely and reliably. Completion of this project will reduce the risk of losing these critical lines that help deliver power to customers in the northern San Francisco Peninsula area. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-19 | 62 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | NA | NA | NA | 4.0111 | IGP | 5801779 | T.0008449 | Ravenswood-SanMateo 230kV 01/011 TRP RPR | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-11-17 | NA | 2026-12-31 | NA | NA | TRUE | NA | NA ¦ NA | 1184.0571 | 11021.9311 | 0 | 130.8998 | 390.1518 | 183.2208 | 338.9315 | 9606.0014 | 372.7259 | 0 | 0 | 0 | 1043.2038 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 10.38% ¦ Electric Operations Risk Management | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1701 | PARKWAY-MORAGA 230kV 5/34-35-36 TRP |  |  | Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Orinda, Contra Costa ¦ Solano ¦ Vallejo, Solano | This project will replace three transmission line structures, 005/034, 006/035 and 006/036, that support the Parkway -Moraga 230kV and the Bahia – Moraga 230kV lines in order to maintain reliable electric service for customers in Solano County. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-08-20 | 81 | Lifecycle Replacement Analysis | Wires - Location/Route Alternative | $125 Mil - $150 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 4.03 | IGP | 5802143 | T.0008555 | PARKWAY-MORAGA 230kV 5/34-35-36 TRP | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-10-04 | 2028-05-19 | 2028-05-31 | NA | NA | FALSE | 89000 | NA ¦ NA | 2806.7297 | 88874.8616 | 0 | 93.5901 | 342.4753 | 400.5029 | 1599.9174 | 3126.2501 | 32000 | 0 | 0 | 0 | 2436.4857 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 0.76% ¦ Electric Operations Risk Management | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1702 | DUMBARTON-NEWARK 115KV TWR 6/48 TRP |  |  | Fremont, Alameda ¦ Newark, Alameda | The project scope of work includes following: • Complete any necessary temporary repairs to the Tower 06/048. • Replace Tower 06/048. In November 2019, an F-priority maintenance tag (118145965) was created and labelled tower 6/48 on the Dumbarton – Newark 115 kV to be replaced. The tag indicates that the Face struts and center plates have been replaced after the tower was inspected also cleaned and galvanized. Pack rust on shims throughout the tower. Spliced rusted through flat stock on first and second level of C face. Installed a strong back plate on C leg 8ft above pier and also above second splice. The engineering recommendation following July 2022 engineering review was the replacement of the tower. Tower #6/48 is under an elevated risk level of failure if the tower is not replaced within the next 2 years. Field crews will continue to FSR the structure every 90 days until the tower is replaced. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-04 | 99 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5550450 | T.0008563 | DUMBARTON-NEWARK 115KV TWR 6/48 TRP | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-12-01 | 2023-10-21 | 2023-12-09 | NA | NA | FALSE | 1350 | NA ¦ NA | 1675.3736 | 1675.3736 | 0 | 108.1605 | 1480.4292 | 86.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 1675.3736 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 108.1605 | 1394.2401 | 82.0754 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1703 | MARTIN-DALY CITY #1 115KV 3/20 TRP |  |  | Brisbane, San Mateo ¦ Daly City, San Mateo ¦ San Mateo | The project scope of work includes following: • Complete any necessary temporary repairs to the Tower 003/020. • Replace Tower 003/020. The Martin-Daly City Nos. 1 and 2 115 kV Lines supply power to Daly City Substation, which serves over 50,500 customers in Daly City and the southwestern portion of San Francisco. The No. 2 Line has a tap connection at Tower 002/014 that supplies power to Serramonte Substation, which serves over 9,200 customers. In September 2022, Transmission Engineering and Design South raised that three E-priority maintenance tags were created and evaluated by Tower, Engineering and Tower Coating on the Martin-Daly City Lines. The outcome of the review indicated that Tower 003/020 (122986585) needs immediate replacement and Tower 002/013 (123028780) and Tower 002/014 (122986380) can be replaced in a few years. The E-priority tag (122986585) for Tower 003/020 indicates several issues on the tower: minor cracks on the foundation, 15% material loss on stub on the tower’s D-Leg, no ground wire on the tower, a lot of surface rust, and the truss members have holes and need to be replaced. Refer to Attachment 2 for pictures for Tower 003/20. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-24 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 4.0111 | IGP | 5551123 | T.0008714 | MARTIN-DALY CITY #1 115KV 3/20 | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-03-22 | NA | 2027-04-16 | NA | NA | TRUE | NA | NA ¦ NA | 1189.0041 | 4478.7104 | 0 | 105.4276 | 1046.853 | 5.9813 | 3.5949 | 216.8535 | 1202.4365 | 100 | 0 | 0 | 1161.8568 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 105.4276 | 968.9248 | -41.5019 | 3.2056 | 24.2079 | 0% | NA ¦ NA | NA | 99.83% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1704 | Ignacio-Alto-Sausalito 115 kV 7/54 TRP |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | Tower 7/54 has an open E-priority tag, 119375345. In 2018/19 modifications were made to the supports of the tower. This tower has been identified as one to be in need to be repaired or replaced mainly due to the heavy rust around the anchor connections and top cage. Additional inspections were completed in September 2022 and again in January 2023. Engineering design need to be completed to determine what is needed to be done for the tower. Additionally, the Tiscornia Marsh restoration project, led by the city of San Rafael and Marin Audubon Society are planning to add about 5.5ft of fill material at the base of tower 08/046 on Ignacio-San Rafael 115 kV which could cause serious damage to the existing foundation pile caps. Additional Geotech studies need to be completed to determine the effects of this added fill material. Finally, this Marsh Restoration project might cause PG&E to replace or relocate the existing boardwalks to access these 2 towers. • Complete any necessary temporary repairs to the Tower 07/054. • Replace top cage if needed. • Coordinate with City of San Rafael and Audubon Society on tower access/boardwalks. • Review fill material to be added to the base of tower 08/046 on Ignacio-San Rafael 115 kV | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-07 | 94 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 4.0111 | IGP | 5804586 | T.0008733 | Ignacio-Alto-Sausalito 60 kV 7/54 TRP | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7246-E | 2024-04-26 | Approved | 2024 | Operational | 1 | 2024-11-15 | 2024-12-13 | 2024-11-25 | NA | NA | TRUE | 2500 | NA ¦ NA | 10549.4723 | 10549.4723 | 0 | 0 | 120.9573 | 9613.6322 | 814.8828 | 0 | 0 | 0 | 0 | 0 | 10549.4723 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 9538.5537 | 798.3586 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1705 | Cortina-Mendocino 115 kV - Twr 46/225 |  |  | Clearlake Oaks CDP, Lake ¦ Colusa ¦ Lake ¦ Lucerne CDP, Lake ¦ Mendocino ¦ Nice CDP, Lake | This project will replace the old double-circuit lattice steel tower #46/225 on the Cortina-Mendocino 115 kV and Mendocino-Redbud 115 kV Line The tower is situated on a slope that is prone to mudslides and posed an immediate safety threat during the recent heavy rains in December 2022 and January 2023. The tower footings were found to be in such critical condition that an emergency 4-pole shoofly was installed, and the tower was removed before a full failure occurred. The shoofly was only an immediate mitigation, so the project team is currently designing 2 permanent TSP’s offset to either side of the old tower location in order to reduce the likelihood of these being affected by future land/mudslides. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-08-18 | 46 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 3.0011 | IGP | 5804087 | T.0008942 | Cortina-Mendocino 115 kV - Twr 46/225 | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-06-10 | 2024-02-06 | 2024-06-14 | NA | NA | TRUE | 1802.928 | NA ¦ NA | 2056.0173 | 2104.2673 | 0 | 0 | 645.0941 | 1328.8919 | 71.0495 | 59.2317 | 0 | 0 | 0 | 0 | 2045.0356 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1899.2136 | 68.2672 | 10.5517 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1706 | Ignacio-Alto-Sausalito 115 kV 13/94 TRP |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | It has been determined by recent field inspections and confirmed by the Transmission and Civil Engineering group that Tower 013/094 on the Ignacio - Alto – Sausalito 60 kV circuit must be replaced due to the current condition and structural integrity of the structure. The Ignacio - Alto – Sausalito 60 kV Line is located in the North Coast region. It is 17.36 miles long, with 127 structures. The line was constructed in 1930 and is the only source of power to Sausalito Substation, which serves over 7,400 customers. In order to prevent the risk of structure failure, asset components on the line are being proposed to be replaced with the following scope of work: • Replacement of tower 013/094 and its foundation on the Ignacio - Alto – Sausalito 60 kV circuit; and • Replacement of old insulators, hardware, and equipment on the structure. | Transmission Line - Pole/Tower | Replace | NA | T.0008733 I T.0007460 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-04-07 | 94 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 4.04 | IGP | 5804688 | T.0009146 | Ignacio-Alto-Sausalito 60 kV 13/94 TRP | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7290-E | 2024-06-07 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-07-10 | 2024-03-31 | 2026-08-07 | Prioritization | NA | TRUE | 2900 | NA ¦ NA | 2080.6571 | 4684.4584 | 0 | 0 | 572.0826 | 1117.5687 | 332.1765 | 2658.6306 | 4 | 0 | 0 | 0 | 2021.8278 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 175% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1707 | Rio Dell RPLC 002/001 to 002/004 STRW |  |  | Humboldt ¦ Hydesville CDP, Humboldt ¦ Rio Dell, Humboldt | The proposed project scope of work includes: • Replace Rio Dell Tap 002/003 3 pole wood structure with a 3 pole TSP approximately 800 feet from the edge of the Van Duzen River Bank (~ 530’ NE of the existing Rio Dell Tap). • Remove Rio Dell Tap 002/001 (Existing 70Y Not 120823607), 002/002 (Existing 70Y Not 120823604), and 002/003 (Existing 70Y Not 128072140, 128593667, 128593668 DURA notifications) • Replace Rio Dell Tap 002/004 3 pole wood structure with with a new H-frame structure to address new tension (Existing 70Y Not 126587773, 126587754, 126587728, WMP 7/14/2024 due date) • Secure necessary ROWs, easements, environmental permits • Perform necessesary geoscience evaluations as well as hydrology and risk studies • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-08-18 | 124 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 1.0001 | IGP | 5810922 | T.0010353 | Rio Dell RPLC 002/001 to 002/004 STRW | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-06-16 | 2025-06-30 | 2025-08-27 | NA | NA | TRUE | 3600 | NA ¦ NA | 5052.2733 | 5072.7215 | 0 | 0 | 0 | 132.4065 | 4859.7715 | 80.5434 | 0 | 0 | 0 | 0 | 4992.178 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 4992.1781 | 60.0953 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1708 | Moraga-Oakland X Twr Repl |  |  | Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa ¦ Piedmont, Alameda | It has been determined by the Transmission and Civil Engineering group that Towers 002/017 and 002/019 on Moraga – Oakland #3 & #4 115 kV must be replaced due to their current condition and structural integrity of the structures. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-10-31 | 95 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 4.0111 | IGP | 5810879 | T.0010439 | Moraga-Oakland X Twr Repl | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-10-29 | NA | 2026-12-01 | NA | NA | TRUE | NA | NA ¦ NA | 725.5906 | 4834.2393 | 0 | 0 | 0 | 192.8813 | 491.0096 | 4098.8647 | 51.4837 | 0 | 0 | 0 | 683.8909 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1709 | IGNACIO - MARE ISLAND TWR REPL PHASE 4 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 15 lattice steel structures, install 1 cage extension, and reconductor 16 spans along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 15 towers and modification of 1 tower in the 2025 scope of this program will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. The greatest positive effect of this program will be mitigating the risk of potential structural failure that would cause sustained, unplanned outages to Substations Skaggs, Highway, Carquinez, Jameson Canyon Pumps, and Mare Island (Solano County, CA). | Transmission Line - Pole/Tower | Replace | NA | T.0000415 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-04 | 98 | Lifecycle Replacement Analysis | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 4.0111 | IGP | 5801467 | T.0011035 | IGNACIO - MARE ISLD TWR REP PHASE 4 | 1 | 70 | NA ¦ NA ¦ T.0007072 ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7650-E | 2025-07-17 | Approved | 2025 | Operational | 1 | 2025-11-12 | 2026-01-15 | 2025-12-22 | NA | NA | TRUE | 56000 | NA ¦ NA | 47139.2724 | 48182.2928 | 0 | 0 | 0 | 229.127 | 42626.3284 | 5326.8374 | 0 | 0 | 0 | 0 | 42855.4554 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 42855.4554 | 3853.6776 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1710 | IGNACIO - MARE ISLAND TWR REPL PHASE 5 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 10 lattice steel structures, remove 1 lattice steel pole, and reconductor 1.2 miles. The replacement of 10 lattice steel towers (015/108, 015/110, 015/111, 015/112, 016/113, 016/114, 016/115, 016/116, 016/117, and 016/118), removal of 1 lattice steel pole (015/109) and replacement of approximately 1.2 miles of conductor in the 2026 scope of this program (Phase 5) will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. The greatest positive effect of this program will be mitigating the risk of potential structural failure that would cause sustained, unplanned outages to Substations Skaggs, Highway, Carquinez, Jameson Canyon Pumps, and Mare Island (Solano County, CA). | Transmission Line - Pole/Tower | Replace | NA | T.0000415 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-04 | 99 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1.2 | NA | 115 | NA | NA | NA | NA | 5.31 | IGP | 5806102 | T.0011036 | IGNACIO - MARE ISLAND TWR REPL PHASE 5 | 1 | 70 | NA ¦ NA ¦ T.0007072 ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-11-17 | NA | 2027-01-15 | NA | NA | TRUE | NA | NA ¦ NA | 580.0827 | 43430.4417 | 0 | 0 | 0 | 0 | 412.7396 | 36305.0826 | 6712.6195 | 0 | 0 | 0 | 412.7396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1711 | IGNACIO - MARE ISLAND TWR REPL PHASE 6 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 34 deteriorated towers along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 34 towers in the scope of this project will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. Since the time of the initial Advance Authorization, the cage extensions and 14 miles of reconductoring have been removed from the scope. | Transmission Line - Pole/Tower | Replace | NA | T.0000415 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-12-04 | 99 | Lifecycle Replacement Analysis | Other - Deferral | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 5.31 | IGP | 5806103 | T.0011037 | IGNACIO - MARE ISLAND TWR REPL PHASE 6 | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-12-21 | 2027-01-15 | 2026-12-31 | NA | NA | TRUE | 46500 | NA ¦ NA | 0 | 67050 | 0 | 0 | 0 | 0 | 0 | 0 | 49669.5652 | 13000 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1712 | MONTA VISTA-HICKS 230 KV TRP |  |  | Campbell, Santa Clara ¦ Cupertino, Santa Clara ¦ Los Gatos, Santa Clara ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Saratoga, Santa Clara | This project proposes to replace two hairpin structures, VASONA-METCALF 009/040A (SAP ID 40576207) and MONTA VISTA-HICKS 009/040B (SAP ID 41168961) with new TSPs to improve the overall safety and reliability of the system due to the condition of these towers. | Transmission Line - Pole/Tower | Replace | NA | T.0011275 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-10-16 | 66 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ False | FALSE | NA |  | NA | NA | 230 | NA | NA | NA | NA | 4.0111 | IGP | 5815463 | T.0011262 | MONTA VISTA-HICKS 230 KV TRP | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-12-29 | NA | 2027-01-14 | NA | NA | TRUE | NA | NA ¦ NA | 335.8305 | 3010.877 | 0 | 0 | 0 | 0 | 238.0506 | 2060.6565 | 712.1699 | 0 | 0 | 0 | 238.0506 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 0.46% ¦ Electric Operations Risk Management | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1713 | DIABLO UNIT #2 - 500 KV #05/004 TRP |  |  | San Luis Obispo | This project proposes to replace lattice tower 005/004 on the Diablo Unit #2 – 500kV circuit to address the asset’s deteriorating structural health and maintain reliable service on one of two crucial 500 kV transmission circuits out of DCPP. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-04 | 124 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme | FALSE ¦ TRUE ¦ False | FALSE | NA |  | NA | NA | 500 | NA | NA | NA | NA | 4.0111 | IGP | 5815746 | T.0011292 | DIABLO UNIT #2 - 500 KV #05/004 TRP | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-04-12 | NA | 2027-04-21 | NA | NA | TRUE | NA | NA ¦ NA | 315.9135 | 3236.7874 | 0 | 0 | 0 | 0 | 193.2356 | 1704.9027 | 1338.6491 | 0 | 0 | 0 | 193.2356 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1714 | MARTIN-SF AIRPORT 115KV 2/19 TRP |  |  | Brisbane, San Mateo ¦ San Mateo ¦ South San Francisco, San Mateo | This project aims to replace tower 002/019 on the Martin-SF Airport 115 kV circuit with a new lattice steel tower to improve the overall safety and reliability of the system due to the condition of this structure. This project will address the risk of asset failure due to advanced corrosion and pack rust at primary and secondary members on Martin-SF Airport 002/019 (SAP ID 40594884), thus increasing the reliability and structural integrity of this structure on the Martin-SF Airport 115 kV circuit. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-30 | 37 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | 115 | NA | NA | NA | NA | 4.0111 | IGP | 5815907 | T.0011376 | MARTIN-SF AIRPORT 115KV 2/19 TRP | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-10-27 | NA | 2027-11-23 | NA | NA | TRUE | NA | NA ¦ NA | 9.5789 | 4371.88 | 0 | 0 | 0 | 0 | 0.447 | 213.4388 | 4133.9882 | 2500 | 0 | 0 | 0.4469 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 94.89% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1715 | MARTIN-MILLBRAE#1 115 kV 2/19 & 3/28 |  |  | Brisbane, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ South San Francisco, San Mateo | This project aims to replace tower 002/019 on the Martin-SF Airport 115 kV circuit with a new lattice steel tower to improve the overall safety and reliability of the system due to the condition of this structure. This project will address the risk of asset failure due to advanced corrosion and pack rust at primary and secondary members on Martin-SF Airport 002/019 (SAP ID 40594884), thus increasing the reliability and structural integrity of this structure on the Martin-SF Airport 115 kV circuit. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-30 | 37 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 115 | NA | NA | NA | NA | 4.0111 | IGP | 5817719 | T.0011376 | MARTIN-SF AIRPORT 115KV 2/19 TRP | 2 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2026 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-11-01 | NA | 2027-12-24 | NA | NA | TRUE | NA | NA ¦ NA | 7.1898 | 7452.8234 | 0 | 0 | 0 | 0 | 0 | 188.7511 | 7227.3562 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1716 | CARUTHERS-LEMOORE NAS 70 KV TRP |  |  | Fresno ¦ Kings ¦ Lemoore Station CDP, Kings ¦ Riverdale CDP, Fresno | Replace roughly 13 miles of 1/0-7 Cu conductor along Caruthers-Lemoore NAS-Camden 70 kV with higher ampacity conductor (TBD during design). Replace structures along 13-mile span as needed accordingly per new conductor loading conditions, and transfer/replace distribution underbuild as needed. Reconductoring this transmission line will increase the capacity and reliability of the line and prevent future wire-down events. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-12-08 | 109 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | 13 | NA | 70 | NA | NA | NA | NA | 4.0111 | IGP | 5816046 | T.0011391 | CARUTHERS-LEMOORE NAS 70 KV TRP | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-10-30 | NA | 2027-03-29 | NA | NA | TRUE | NA | NA ¦ NA | 617.0935 | 18135.5526 | 0 | 0 | 0 | 0 | 352.1938 | 9722.9986 | 8060.3602 | 0 | 0 | 0 | 352.1938 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1717 | VACA-PARKWAY-Structure 023/124 (SAP#40756456) |  |  | Fairfield, Solano ¦ Green Valley CDP, Solano ¦ Hartley CDP, Solano ¦ Napa ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | Replace degraded VACA-PARKWAY-Structure 023/124 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-04 | 80 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 230 | NA | NA | NA | NA | 4.0111 | IGP | EX113556 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-02-01 | NA | 2028-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2250 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 250 | 2000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 1.16% ¦ Electric Operations Risk Management | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1718 | Newark-Vallecitos Structure Replacement |  |  | Fremont, Alameda ¦ Sunol CDP, Alameda | Replace Degraded structures within 5 years based on Civil Priority 4. Structures 094/612 and 094/613. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-02 | 126 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | 60 | NA | NA | NA | NA | 3.0011 | IGP | EX130532 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-02-01 | NA | 2028-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 3250 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 250 | 3000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1719 | MENDOCINO-PHILO JCT-HOPLAND Multiple Structures |  |  | Calpella CDP, Mendocino ¦ Mendocino ¦ Talmage CDP, Mendocino ¦ Ukiah, Mendocino | Replace 22 structures on MENDOCINO-PHILO JCT-HOPLAND line due to Foundation type is direct embed grillage with a pin head and has no rotational strength and very limited bearing capacity. Pole leaning and lateral deflection. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-08-18 | 125 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.0111 | IGP | EX113555 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 15600 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 350 | 15000 | 250 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1720 | VASONA-METCALF-Structure 009/040A (SAP#40576207) |  |  | Los Gatos, Santa Clara ¦ San Jose, Santa Clara ¦ Santa Clara | Replace degraded VASONA-METCALF-Structure 009/040A | Transmission Line - Pole/Tower | Replace | NA | T.0009169 ¦ T.0003803 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-01 | 69 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 4.0111 | IGP | EX113564 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1600 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 150 | 1300 | 150 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 1.00% ¦ Electric Operations Risk Management | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1721 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1-Structure 044/281 (SAP#40593743) |  |  | Monterey ¦ Prunedale CDP, Monterey ¦ Salinas, Monterey ¦ Soledad, Monterey | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1-Structure 044/281 is recommended to be replaced within 5 years due to the severity of the recent impact from farm equipment that generated an A tag. The tower has an observable, permanent lean as a result of the impact. The tower lean is unable to be corrected. Tower is 94 years old. | Transmission Line - Pole/Tower | Replace | NA | 5811930 | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2026-03-31 | 95 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion ¦ Weather |  | NA | NA | 115 | NA | NA | NA | NA | 4.0111 | IGP | EX113567 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-02-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1600 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 300 | 1300 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 73.50% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1722 | NICOLAUS-CATLETT JCT-Structures 074/547 and 073/544 (SAP#40755067,40904630) |  |  | East Nicolaus CDP, Sutter ¦ Elverta CDP, Sacramento ¦ Sacramento ¦ Sutter ¦ Trowbridge CDP, Sutter | Replace degraded NICOLAUS-CATLETT JCT-Structures 074/547 and 073/544 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-11-01 | 126 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.0111 | IGP | EX113553 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-12-01 | NA | 2033-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8850 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 350 | 1500 | 3500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 0.17% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1723 | STOCKTON-NEWARK-Structures 064/015 and 064/016 (SAP# 44314844, 44314846) |  |  | Contra Costa ¦ San Joaquin | Replace degraded STOCKTON-NEWARK-Structures 064/015 and 064/016 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2025-09-10 | 123 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 4.0111 | IGP | EX113566 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-12-01 | NA | 2035-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1050 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 350 | 350 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 30.15% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1724 | MAT 70Y: E/F Non-HFTD/HFRA |  |  | NA | Completion of priority E/F tags (within the 12mo-60mo time frame) to mitigate asset conditions that may pose a safety or wildfire risk. In accordance with ETPM TD-1001M, TD-8123P-101, and TD-8123P-103. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.201 | IGP | EX111042 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 485793.3408 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 93274.3073 | 191665.6394 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1725 | MAT 70Y: E/F HFTD/HFRA |  |  | NA | Completion of priority E/F tags (within the 12mo-60 mo time frame) to mitigate asset conditions that may pose a safety or wildfire risk. In accordance with ETPM TD-1001M, TD-8123P-101, and TD-8123P-103. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.301 | IGP | EX111043 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 431500.3901 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 92049.6146 | 63543.6714 | 99485.5272 | 104030.2332 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1726 | 70Y: PTT Forecast for Poles Requiring Replacement due to New TD-2325 Revisions |  |  | NA | Replacement of 1807 poles rejected for repalcement as result of 2022 pole test and treat inspections, which are conducted in accordance with TD-2325 Rev 3 from Nov 2021. Approximately 619 poles are in HFTD 2 or 3 and thus cannot be deferred. Prior to the new revision, only 50 to 70 poles would be rejected for replacement annually. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.201 | IGP | Ex112925 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 55000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 11000 | 11000 | 11000 | 11000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1727 | MAT 70Y: Backlog Non-HFTD/HFRA |  |  | NA | Completion of non-HFTD backlogged tags. This backlog must be cleared in order to reach steady-state compliance with GO-95. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.201 | IGP | Ex112933 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 269229.913 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 86358.268 | 135292.558 | 47579.087 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1728 | MAT 70Y: Short Durn E HFTD/HFRA |  |  | NA | Completion of short duration tags (typically 3 or 6 months priority) to mitigate conditions that may pose urgent risk. In accordance with ETPM TD-1001M, TD-8123P-101, and TD-8123P-103 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.301 | IGP | Ex112935 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 6952.4332 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 2504.4231 | 2813.8499 | 483.4794 | 309.4268 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1729 | MAT 70Y: Short Durn E Non-HFTD/HFRA |  |  | NA | Completion of short duration tags (typically 3 or 6 months priority) to mitigate conditions that may pose urgent risk. In accordance with ETPM TD-1001M, TD-8123P-101, and TD-8123P-103 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.301 | IGP | Ex112936 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 20808.9518 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 3809.8174 | 4873.472 | 4312.6359 | 3500.3906 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1730 | Pole Replacement - South Coast Region |  |  | NA | Bucket for replacement of wood poles in the south coast region | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 31 | NA | 13 | 5.42 | IGP | 5502913 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 234379.549 | 234379.549 | 3616.8407 | 14916.7131 | 28860.1514 | 15978.7695 | 11431.1852 | 2873.0929 | 0 | 0 | 0 | 0 | 231506.4561 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 2913.1082 | 13479.5118 | 25416.5264 | 13413.4828 | 10861.9759 | 2177.4885 | 0% | NA ¦ NA | NA | 1% ¦ Electric Operations Risk Management | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1731 | Pole Replacement Service Ter - NHFTD |  |  | NA | Bucket for replacement of wood poles across the service territory | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 197 | NA | 1 | 5.301 | IGP | 5508619 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 205381.0452 | 205381.0452 | 14289.9254 | 48547.8314 | 42817.6125 | 17907.2165 | 29904.2745 | 3991.7816 | 0 | 0 | 0 | 0 | 201389.2636 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 11657.4659 | 43172.7899 | 37403.2397 | 14384.7366 | 27961.4017 | 1901.1953 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1732 | Pole Replacement - North Valley - NHFTD |  |  | NA | Bucket for pole replacements in the North Valley region. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | NA | NA | NA | 31 | NA | 4 | 5.301 | IGP | 5509219 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 413047.9504 | 413047.9504 | 34758.3577 | 106699.6602 | 98288.3149 | 38463.5691 | 34173.5423 | 7873.8213 | 0 | 0 | 0 | 0 | 405174.1291 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 29431.0289 | 98334.1329 | 86866.8628 | 27366.7226 | 30825.2385 | 4313.5114 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1733 | Pole Replacement - North Bay/Coast NHFTD |  |  | NA | Bucket for Pole Replacements in North Bay/Coast | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion ¦ Weather |  | NA | NA | NA | NA | 31 | NA | 39 | 5.301 | IGP | 5509220 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 44346.555 | 44346.555 | 736.9348 | 2934.3303 | 4738.8174 | 11291.6962 | 21428.2475 | 1915.5092 | 0 | 0 | 0 | 0 | 42431.0458 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 553.5918 | 2651.2204 | 3833.4749 | 9297.4046 | 20112.5798 | 962.3407 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1734 | TLine Construction Contractor-Eng Poles |  |  | NA | Bucket for contractor replacement of wood poles | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 31 | NA | 167 | NA | NA | 5513319 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 17938.6842 | 17938.6842 | -5.9271 | 0.494 | -9.0414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17938.6842 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | -5.6369 | 0.43709 | -9.67 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1735 | Pole Replacement - Eureka BL - NHFTD |  |  | NA | Bucket for replacement of wood poles in Eureka area | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | NA | NA | 39 | 5.301 | IGP | 5519159 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 3511.8817 | 3511.8817 | 606.5095 | 832.9478 | 17.7643 | 1.3511 | 0.3326 | 30.7468 | 0 | 0 | 0 | 0 | 3481.1349 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 527.0837 | 860.0859 | 17.5748 | -276.9034 | 0.33262 | 30.7468 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1736 | 70Y 2020 Planning and Construction |  |  | NA | Bucket for replacement of wood poles in 2020 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 31 | 2. Overhead With Strong Safety Link | 4 | 5.301 | IGP | 5529956 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 10786.0523 | 10786.0523 | 4101.4883 | 1619.656 | 597.9136 | 164.1928 | 77.9484 | -9.705 | 0 | 0 | 0 | 0 | 10795.7573 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 3581.2929 | 1513.7577 | 528.5662 | 137.0106 | 66.328 | -8.2994 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1737 | WMP - Pole Replacements - NHFTD |  |  | NA | Bucket for replacement of wood poles in Tier 2 & 3 HFTDs | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3563 | 1. Work that prevents fire ignition | 1 | 5.301 | IGP | 5533586 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 562211.4544 | 562211.4544 | 160068.7414 | 42576.7301 | 16664.0892 | 3581.1784 | 2350.4707 | 520.3328 | 0 | 0 | 0 | 0 | 561691.1216 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 147493.597 | 38979.7556 | 14600.1649 | -6965.8001 | 1762.772 | 326.419 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1738 | WMP - MWC 70Y Forecast - NHFTD |  |  | NA | Bucket for MWC 70 WSIP Work | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3563 | NA | 106 | 1.0001 | IGP | 5534223 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 5283.1732 | 5283.1732 | 1795.7657 | 3215.5147 | 0.2835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5283.1732 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1400.9321 | 2470.165 | 0.22679 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1739 | HFTD-Pole Replacement-South Coast Region |  |  | NA | Bucket for HFTD Pole Replacement in South Coast Region | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.42 | IGP | 5562019 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 52217.2596 | 52217.2596 | 55.0507 | 1701.0462 | 6146.0424 | 22565.933 | 20689.9003 | 1059.5729 | 0 | 0 | 0 | 0 | 51157.6867 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 16.9157 | 1511.9365 | 5199.9258 | 19999.2623 | 19195.0035 | 1054.4123 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1740 | HFTD-Pole Replacement Service |  |  | NA | Bucket for HFTD-Pole Replacement Service | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.42 | IGP | 5562020 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 55487.312 | 55487.312 | 7.2052 | 1012.5145 | 14215.6705 | 23401.7283 | 16509.2481 | 340.9152 | 0 | 0 | 0 | 0 | 55146.3968 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 853.7922 | 12549.5202 | 20485.2587 | 16426.8483 | 272.5113 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1741 | HFTD-Pole Replacement-North Valley |  |  | NA | Bucket for HFTD Pole Replacement in North Valley Region | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.42 | IGP | 5562021 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 196492.2786 | 196492.2786 | 1281.3437 | 12289.898 | 58849.071 | 67416.6539 | 54098.6445 | 2608.8768 | 0 | 0 | 0 | 0 | 193883.4018 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 1092.1327 | 11362.3191 | 52344.2853 | 58524.3942 | 52672.047 | 2197.7597 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1742 | HFTD-Pole Replacement-NBC |  |  | NA | Bucket for HFTD Pole Replacement in North Bay North Coast Region | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.42 | IGP | 5562022 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 59762.7642 | 59762.7642 | 0 | 11.6814 | 3398.7385 | 18637.9526 | 37253.5712 | 391.967 | 0 | 0 | 0 | 0 | 59370.7972 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 9.7524 | 2440.9811 | 15787.0058 | 35124.2213 | 389.4454 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1743 | HFTD 2020 Planning and Construction |  |  | NA | Bucket for HFTD Wood Pole Replacements - 2020 Planning and Construction | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.42 | IGP | 5562026 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 3865.9406 | 3865.9406 | 2117.4658 | 138.024 | 152.584 | 133.5828 | 115.6917 | 2.4614 | 0 | 0 | 0 | 0 | 3863.4792 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 1930.034 | 124.9954 | 138.8966 | 118.6962 | 103.7961 | 2.2435 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1744 | HFTD WMP Pole Replacements |  |  | NA | Bucket for HFTD Wildfire Mitigation Plan Pole Replacement | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ False | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.42 | IGP | 5562027 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 22984.3586 | 22984.3586 | 5293.8935 | 4100.8416 | 5355.555 | 2042.4709 | 571.2015 | 0.9206 | 0 | 0 | 0 | 0 | 22983.438 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 4888.6798 | 3773.2746 | 4971.9471 | 1006.8677 | 835.3049 | 0.82479 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1745 | Composite Poles |  |  | NA | Increase pole replacements from wood to composite. This line item if for the delta: unit cost wood pole =96K , composite unit cost 100K, 175 poles minimum. 96k-100K=4K 4K x 175=700K minimum requested but ideally would like to get 1M to allow for more composite units ~250 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.02 | IGP | EX130520 | NA | NA | NA | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 17500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 3500 | 3500 | 3500 | 3500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1746 | Jessup Tap 115kV |  |  | Shasta | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2025-06-27 | 48 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5541501 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 7 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6191-E | 2021-05-12 | Approved | 2021 | Operational | 1 | 2021-08-09 | 2021-11-30 | 2021-10-27 | NA | NA | FALSE | 18400 | NA ¦ NA | 1282.869 | 1282.869 | 1204.2576 | 52.0778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1282.869 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1086.3758 | 45.9802 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1747 | Woodleaf-Palermo 115kV-Structure Replac |  |  | Butte ¦ Forbestown CDP, Butte ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte | This project proposes to replace aging structures and insulators on the Woodleaf – Palermo 115 kV Line and associated 115 kV Tap lines to help mitigate high-risk components on these line. Scope in details: • Replace 124 of the 232 structures on the Woodleaf – Palermo 115 kV Line with steel structures; • Replace 69 insulators on the Woodleaf – Palermo 115 kV Line; • Perform field analysis on existing structures, Nos. 000/005, 006/053, and 013/128 on the Woodleaf – Palermo 115 kV Line to verify if replacements are needed; • Perform field analysis on 0.02 miles of Sly Creek Tap 115 kV from pole no. 000/006 to 000/008 to verify the age of the conductor and to determine if reconductor is needed; • Replace 3 structures, pole nos. 003/031A, 003/031B, and 003/031C and perform field analysis on 3 structures, pole nos. 002/019, 003/032, and 004/038 to determine if structure and insulator replacements are needed on the Sly Creek Tap 115 kV; • Replace all insulators on the Sly Creek Tap 115 kV; • Replace 1 structure, pole no. 004/039 and conduct field analysis on 3 structures, pole nos. 000/001A, 000/001B, and 000/001C to determine if structure and insulator replacements are needed on the Forbestown Tap 115 kV; • Perform field analysis on 9 structures, pole nos. 000/002, 001/008B, 001/008C, 001/010C, 001/011, 002/015, 002/016, 002/018A, and 002/018C, to verify if structure and insulator replacements are needed on the Kanaka Tap 115 kV; • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2025-07-14 | 64 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 4703 | 2. Overhead With Strong Safety Link | 151 | 3.0011 | IGP | 5789804 | T.0005758 | Woodleaf-Palermo 115kV-Structure & Insul | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2033-04-20 | NA | 2033-05-17 | NA | NA | FALSE | NA | NA ¦ NA | 18.1902 | 5097.1621 | 1.3537 | 8.8893 | 7.3235 | 0.6236 | 0 | 1.2111 | 0 | 0 | 900 | 2000 | 18.1902 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 607% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1748 | HARDING: REARRANGE 60KV T-LINE |  |  | Kennedy CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | This project proposes to replace Bank 1 with a 16 MVA 60/12x4 kV dual winding transformer, enhance the ground grid, implement a Shakespeare Wall, install neutral reactors, deploy a 12 kV Shelter Aisle Switchgear, and complete necessary civil construction for the project. | Transmission Line - Multiple | Relocate | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2025-10-30 | NA | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 4.02 | IGP | 5564717 | T.0007980 | HARDING: REBUILD SUBSTATION | 3 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-06-30 | 2028-02-29 | 2027-05-26 | NA | NA | TRUE | 35600 | NA ¦ NA | 936.8314 | 1300.8805 | 0 | 0 | 0 | 29.5936 | 426.5893 | 731.357 | 14.035 | 0 | 0 | 0 | 456.1829 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 228.0912 | 240.3239 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1749 | T-LINE INDUSTRIAL ACRES RE-BUIL |  |  | Monterey ¦ Salinas, Monterey | This project proposes to replace Industrial Acres Transformer Bank 1 under the MWC 59 program (emergency), and install a new distribution 12kV switchgear, cutover part of existing 4kV feeders, and install two (2) 12-4kV distribution stepdowns under the MWC 46 and MWC 06 programs (capacity). The distribution work will support the emergency rebuild of Industrial Acres Substation as well as eliminate a 20 percent normal forecasted overload of Buena Vista Bank 1 and 57 percent normal forecasted overload of Buena Vista 1106 feeder. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2025-11-20 | 126 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | 60 | NA | NA | NA | NA | 4.03 | IGP | 5813425 | T.0009160 | INDUSTRIAL ACRES: EM REBLD SUB | 1 | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-03-22 | NA | 2027-08-11 | NA | NA | TRUE | NA | NA ¦ NA | 31.0182 | 3944.6871 | 0 | 0 | 0 | 0 | 27.762 | 141.5557 | 3775.3694 | 0 | 0 | 0 | 27.762 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1750 | LAYTONVILLE-WILLITS Repl Wood Structures |  |  | Laytonville CDP, Mendocino ¦ Mendocino | LAYTONVILLE-WILLITS has a high Probability of failure. Currently 127 wood poles on the line, with 36 existing and 6 recently completed 70Y Tags in the past year (~30%). Average age is 42.76 years old, with nearly 30% of the pole line over 70 years old. Approximately 43% of poles have a TCM Annual Probability of Failure of over 10%. Average annual probability of failure TCM is 15.57%. Average pole condition score is 1.76 and number of condition scores of 3 or higher is 30% (Top 15%). | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2025-06-05 | 72 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 4.031 | IGP | Ex112932 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-03-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1152.872 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 1152.872 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 94.52% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1751 | Contra Costa - Pittsburg Pole Relocation (024/034 to 025/019) |  |  | Antioch, Contra Costa ¦ Pittsburg, Contra Costa | Contra Costa-Pittsburg 60kV – ETL.6540, has approximately 34 wood poles between 024/024 to, and including 025/019, many of which are tagged as in swamp. Seven of these poles failed PTT in Sept 2022 and cannot be restored. We have a 5700’ Boardwalk construction project proposed for Contra Costa – Pittsburg between structures 024/034 and 025/019, but it makes more sense to relocate the line out of the marshland which has 33% soil corrosivity and lies underwater much of the time.. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2025-11-02 | 82 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence ¦ Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 4.01 | IGP | EX112653 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-12-01 | NA | 2031-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 14500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 2000 | 3500 | 4000 | 4000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 330.50% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1752 | CHRISTIE-WILLOW PASS Structure REplacement |  |  | Bay Point CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa | CHRISTIE-WILLOW PASS has a high Probability of failure. Per Maintenance this is a worst acting line with areas that are inaccessible and have high environmental requirements. Currently 270 wood poles on the line, with approximately 5% having existing 70Y tags or recently completed 70Y tags. Average age is 37 years old (third quartile). Approximately 42% of poles have a TCM Annual Probability of Failure of over 10%. Average annual probability of failure TCM is 16.93%. The oldest poles appear to be in the first two miles, but they are not the poles with the highest risk. A spot check on the inspection reports is spotty at best. Recommend new project in the 2 to 5 year plan for at the worst actors. The first two miles have very old poles, although they do not rank high on the TCM. A spot check on the inspection reports show that the conditions reported is the condition for the worst acting component on the line, not the wood structure. This likely impacted many of the younger poles with higher POFs. Propose a targeted replacement for worst actors. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2025-11-13 | 39 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.03 | IGP | Ex112926 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-12-01 | NA | 2031-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 3700 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 300 | 1700 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 4575.78% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1753 | Colgate - Alleghany Wood Structure Repalcement |  |  | Alleghany CDP, Sierra ¦ Nevada ¦ Pike CDP, Sierra ¦ Sierra ¦ Yuba | Colgate - Alleghany current has 80 open and 13 recently closed 70Y tags. This is a Tier 2/3 area, so this will be a 2023 requirement. The 80 outstanding tags equates to $6.8 million in work. This was noted as a worst acting line for North Valley. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2026-02-16 | 72 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.0111 | IGP | Ex112927 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-12-01 | NA | 2032-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 20257.608 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 0 | 7411.32 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 30% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1754 | KING CITY-COBURN #1 Wood Structures |  |  | Greenfield, Monterey ¦ King City, Monterey ¦ Monterey ¦ Soledad, Monterey | KING CITY-COBURN #1, Over 15% of this line has less than 100% remaining strength per intrusive PTT inspections. Average age is 47 years old (second quartile). Approximately 94% of poles have a TCM Annual Probability of Failure of over 10% , which is significant considering there are over 350 wood poles on this line. Average annual probability of failure TCM is 22.94%, accounting for 14.8% of the entire line. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2025-12-04 | 49 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 4.03 | IGP | Ex112931 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-03-01 | NA | 2032-12-31 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 11250 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 750 | 5250 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | 7000% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1755 | 70Y COBURN-BASIC ENERGY ETL.6400 |  |  | King City, Monterey ¦ Monterey | Reduce risk by replacing wood poles experiencing severe bending & potential hardware failure due to the bundled conductor. Line has multiple tags 70Y and ICW (repair hardware, guy wire, etc.) it will be beneficial to bundle the tags | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | 2025-11-23 | 124 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | 60 | NA | NA | NA | NA | 5.21 | IGP | EX130529 | TBD | TBD | TBD | 70 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-02-01 | NA | 2027-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1000 | 0 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1756 | Newark Replace Boardwalk 2022 -2023 |  |  | Fremont, Alameda ¦ Mountain View, Santa Clara ¦ Newark, Alameda ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Sunnyvale, Santa Clara | Replace approximately 2.4 miles of existing boardwalk for Newark-Ames #2, Newark-Ames #1, and Newark-Ames #3. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | 2025-11-18 | 51 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 2.4 | NA | 115 | NA | NA | NA | NA | NA | NA | 5802621 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-12-21 | 2023-03-16 | 2023-12-22 | Weather | NA | TRUE | 6629 | NA ¦ NA | 8384.2289 | 8782.8449 | 0 | 23.9956 | 5139.849 | 42.3801 | 3152.0198 | 424.6005 | 0 | 0 | 0 | 0 | 8358.2444 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2025 ¦ 2026 | 0 | 0 | 4617.8514 | 0 | 3150.5398 | 69.8446 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1757 | Boardwalks Planning |  |  | NA | Forecast placeholder for replacement of boardwalks for t-line access | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.202 | Non-IGP | 5549695 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 0 | 72413.6984 | 0 | 0 | 0 | 0 | 0 | 31529.9244 | 23285 | 9574 | 3574 | 6574 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1758 | Replace Deteriorated Boardwalks - 2018 |  |  | NA | Bucket for replacement of deteriorated boardwalks in 2018 & 2019 | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Salt Pond |  | NA | NA | NA | NA | 190 | NA | 7 | NA | NA | 5507682 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 49338.6856 | 49338.6856 | -10.7452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49338.6856 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 441.9375 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1759 | Replace Deteriorated Boardwalks 2020 |  |  | NA | Bucket for replacement of deteriorated boardwalks in 2020 | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Salt Pond |  | NA | NA | NA | NA | NA | 9. Reliability (Low Safety Risk) | NA | 5.202 | Non-IGP | 5790558 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 37498.9472 | 37498.9472 | 7246.4127 | 1026.0985 | -0.4178 | 4827.0805 | 11866.7202 | 490.9232 | 0 | 0 | 0 | 0 | 37008.024 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 12809.0672 | 5464.7182 | -0.41779 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1760 | Ravenswood Replace Boardwalk 2022 |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Mountain View, Santa Clara ¦ Palo Alto, Santa Clara ¦ Santa Clara | Replace boardwalks on Ravenswood-Ames #1 115 kV line | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | 2025-11-04 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 4.58 | NA | 115 | NA | NA | NA | NA | NA | NA | 5800399 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-06-23 | NA | 2022-01-14 | NA | NA | FALSE | NA | NA ¦ NA | 15549.1617 | 15549.1617 | 13075.5308 | 2471.813 | 1.8179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15549.1617 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 15516.0819 | 1.8179 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1761 | Ignacio Replace Boardwalk 2022 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace boardwalks on Ignacio-Sobrante 230 kV line | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | 2025-11-25 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 0.3 | NA | 230 | NA | NA | NA | NA | NA | NA | 5800400 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-13 | NA | 2022-10-13 | NA | NA | FALSE | NA | NA ¦ NA | 1482.729 | 1482.729 | 440.89 | 1041.5746 | 0.2643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1482.729 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 1419.9319 | 0.25259 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1762 | Pittsburg Replace Boardwalk 2022 |  |  | Bay Point CDP, Contra Costa ¦ Contra Costa ¦ Pittsburg, Contra Costa | The work will replace approximately 4,910 linear feet existing boardwalk to Pittsburg-Tidewater 230kV Towers 000/002, 000/003, and 000/004, and adjacent structures on Pittsburg-Eastshore 230kV, Pittsburg-Tesla #1 230kV, Pittsburg-San Ramon 230kV, Pittsburg-Martinez #1 115kV, Pittsburg-Clayton #1 115kV, Pittsburg-Clayton #3 115kV, and Pittsburg-Columbia Steel 115kV. Approximately 2,020 feet of existing boardwalk will be replaced in place, and 2,820 feet require replacement of cross braces, planks, and handrails on top of existing pilings that will remain. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | 2026-02-24 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.93 | NA | 230 | NA | NA | NA | NA | NA | NA | 5800398 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-02-07 | NA | 2022-10-18 | NA | NA | FALSE | NA | NA ¦ NA | 2301.8044 | 2301.8044 | 79.7683 | 2221.8699 | 0.1662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2301.8044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 1931.3802 | 0.13844 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1763 | Ravenswood San Mateo #2 - Repl Boardwalk |  |  | Bay Point CDP, Contra Costa ¦ Contra Costa ¦ Pittsburg, Contra Costa | Scope of work for construction services includes full boardwalk replacement, disposal, and installation of new 3X plastic. The existing boardwalk is located off Hwy 84 at the Ravenswood substation and would address a total of 33 towers. It will start from the West side of the substation at tower 000/001 and from the East side at tower 000/002. The existing wood boardwalk is mainly composed of a 2X planking system with some existing 3X planking sections with single handrailing. This boardwalk is all lumber. boardwalk of approximately 14,221 lineal feet (LF). Removal | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | 2026-02-24 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 3.07 | NA | 230 | NA | NA | NA | NA | NA | NA | 5799001 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-01 | NA | 2022-12-28 | NA | NA | FALSE | NA | NA ¦ NA | 6921.0178 | 6921.0178 | 0 | 7042.5152 | -121.4975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6921.0178 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 6918.329 | -119.3378 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1764 | Repl Deteriorated Boardwalks - Ignacio |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace deteriorated wooden boardwalk (access) with new plastic lumber based boardwalk. (Ignacio Sobrante between TWR 16/69 and 23/69.) | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | 2025-11-25 | 31 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 ¦ 115 ¦ 60 | NA | 190 | NA | 15 | NA | NA | 5786498 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-02-13 | 2019-12-31 | 2020-02-28 | NA | NA | FALSE | 8500 | NA ¦ NA | 7960.9067 | 7960.9067 | 7.8 | 0.0222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7960.9067 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 5.6301 | 0.01604 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1765 | TLINE Emergent Access Road Capital Support outside of HFTD Areas |  |  | NA | Forecast Placeholder for TLINE Emergent Access Road Capital Support outside of HFTD Areas. Provides safe access to Transmission facilities where access roads, culverts and/or gates are damaged or missing. Increases employee safety and improves access reliability for multiple functional areas. This work WILL support the reduction of wildfire risk and spread. First responders also depending on these access routes often. Work to encompass tags created outside of Tier 2 and 3 areas | Other | Replace | NA | NA | Other [See Notes] | Construct Roads/Gates/Culverts | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.211 | Non-IGP | Ex112913 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 37000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 3000 | 7000 | 7000 | 10000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1766 | TLINE Emergent Access Road Capital Support within HFTD areas |  |  | NA | Forecast Placeholder for TLINE Emergent Access Road Capital Support within HFTD areas. for Provides safe access to Transmission facilities where access roads, culverts and/or gates are damaged or missing. Increases employee safety and improves access reliability for multiple functional areas. This work WILL support the reduction of wildfire risk and spread. First responders also depending on these access routes often. Work to encompass tags created inside tier 2 and 3 areas | Other | Replace | NA | NA | Other [See Notes] | Construct Roads/Gates/Culverts | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.211 | Non-IGP | Ex112914 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 54000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 4000 | 12000 | 8000 | 15000 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1767 | TLine Access Road Work - Base Capital |  |  | NA | Bucket for T-line access road work | Other | Replace | NA | NA | Other [See Notes] | Construct Roads/Gates/Culverts | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 100 | 9. Reliability (Low Safety Risk) | NA | 4.0103 | Non-IGP | 5502914 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 88741.792 | 142520.694 | 8855.2211 | 7946.1203 | 7204.3687 | 19248.3324 | 12396.7181 | 16913.9666 | 13005.615 | 1500 | 8500 | 13404 | 87798.7274 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 8856.0281 | 7658.1265 | 7691.9889 | 19212.9781 | 12196.6248 | 813.1302 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1768 | TLine Access Road Work |  |  | NA | Bucket for TLine Access Road Work | Other | Replace | NA | NA | Other [See Notes] | Construct Roads/Gates/Culverts | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.0103 | Non-IGP | 5547687 | NA | NA | NA | 71 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 5101.9333 | 5101.9333 | 1010.4871 | 657.7747 | 816.806 | 52.5904 | 9.8196 | -14.3103 | 0 | 0 | 0 | 0 | 5116.2436 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 1008.4352 | 648.6625 | 827.9701 | 52.5904 | 9.8196 | -14.3103 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1769 | Improve Cathodic Protection |  |  | NA | Bucket for cathodic protection improvements for underground transmission circuits | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 739 | 4. Underground / Network (Strong Safety Link) | NA | 4.02 | Non-IGP | 5505219 | NA | NA | NA | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1160.8611 | 5200 | 8.0867 | 97.3899 | 1.5254 | 0 | 0 | 0 | 1200 | 1000 | 1000 | 1000 | 1160.8611 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 1.4007 | 104.0759 | 1.5254 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1770 | ETL UG Replace System_Planning |  |  | NA | Forecast placeholder for replacement of underground system | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.02 | Non-IGP | 5543226 | NA | NA | NA | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 3200 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1000 | 1000 | 600 | 300 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1771 | Transmission Underground Capital Projects |  |  | NA | Forecast placeholder for Transmission Underground Capital Projects | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.02 | Non-IGP | EX112180 | NA | NA | NA | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 0 | 500 | 500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1772 | Low Pressure Trip Cabinet replacement |  |  | NA | Forecast placeholder for Low Pressure Trip Cabinet replacement | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.02 | Non-IGP | Tx001999 | NA | NA | NA | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1000 | 1000 | 0 | 0 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1773 | Repl Trans Line UG-ETM (System |  |  | NA | Forecast placeholder for replacement of underground transmission line | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.021 | Non-IGP | 5502935 | NA | NA | NA | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2013 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 24340 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 4868 | 4868 | 4868 | 4868 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 433.5481 | 76.2187 | 65.4439 | 191.4478 | 393.194 | 27.6091 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1774 | External Corrosion Direct Assessment |  |  | NA | Bucket placeholder for External Corrosion Direct Assessment for underground transmission lines. ECDA for each line will be assigned a specific PM# under this planning order #. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.02 | Non-IGP | Tx001998 | NA | NA | NA | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 7500 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 1500 | 1500 | 1500 | 1500 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1775 | Los Esteros-Metcalf Cable Rack Work |  |  | Fremont, Alameda | The Los Esteros 230 kV Cable Rack Replacement Project will reduce the risk of a failure of the UG cable section on the Newark-Los Esteros and the Los Esteros-Metcalf 230 kV Lines by performing the following work: Replace all cable racks in the 10 manholes on both 230 kV lines, and Add sacrificial anodes onto the racks to prolong the cable rack life expectancy.Maintenance inspections of the underground cable sections have found that the cable racks in the manholes have severe corrosion. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | 2026-01-01 | 20 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 2.8 | NA | 230 | NA | 240 | 4. Underground / Network (Strong Safety Link) | 1459 | NA | NA | 5790378 | T.0005870 | Los Esteros 230kV Cable Rack Replacement | 2 | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-03-14 | 2022-05-11 | 2022-04-26 | NA | NA | FALSE | 5710 | NA ¦ NA | 2521.362 | 2521.362 | 1899.6614 | 596.8137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2521.362 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 2521.362 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1776 | NEWARK-LOS ESTEROS CABLE RACK WORK |  |  | Fremont, Alameda | The Los Esteros 230 kV Cable Rack Replacement Project will reduce the risk of a failure of the UG cable section on the Newark-Los Esteros and the Los Esteros-Metcalf 230 kV Lines by performing the following work: Replace all cable racks in the 10 manholes on both 230 kV lines, and Add sacrificial anodes onto the racks to prolong the cable rack life expectancy.Maintenance inspections of the underground cable sections have found that the cable racks in the manholes have severe corrosion. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | 2026-01-01 | 21 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 2.8 | NA | 230 | NA | 240 | 4. Underground / Network (Strong Safety Link) | 1459 | NA | NA | 5790379 | T.0005870 | Los Esteros 230kV Cable Rack Replacement | 2 | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-27 | 2022-05-11 | 2022-06-07 | NA | NA | FALSE | 5710 | NA ¦ NA | 2420.6901 | 2420.6901 | 1234.2831 | 1163.2185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2420.6901 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 2420.6901 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1777 | Jefferson-Las Pulgas Cable Replacement |  |  | San Mateo | The Jefferson-Las Pulgas Cable Replacement Project is located in San Mateo County. This 1100-foot long, cross-linked polyethylene (XLPE) 60 kV underground cable is located where the Jefferson-Las Pulgas Line crosses Alameda de las Pulgas. This project will replace the old cableconductor and the connections at the riser poles on Woodside Road and Hull Avenue, where the linetransitions from overhead to underground. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | 2026-01-01 | 38 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 0.18 | NA | 60 | NA | NA | NA | NA | 4.06 | Non-IGP | 5793678 | T.0006738 | Jefferson-Las Pulgas Cable Replacement | 1 | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-10-02 | NA | 2028-12-29 | NA | NA | FALSE | NA | NA ¦ NA | 96.1878 | 18172.3672 | 33.9579 | 26.2219 | 11.8808 | 10.7393 | 12.1816 | 1636.6411 | 442 | 0 | 0 | 0 | 94.9815 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1778 | East Grand-San Mateo Cable Replacement |  |  | San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | 2026-03-03 | 53 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.22 | NA | 115 | NA | NA | NA | NA | 4.02 | Non-IGP | 5793679 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-06-11 | NA | 2028-08-10 | NA | NA | FALSE | NA | NA ¦ NA | 2125.3795 | 20551.3921 | 560.3938 | 409.0965 | 620.5019 | 150.3043 | 152.8594 | 461.9656 | 8500 | 9000 | 500 | 0 | 2089.4265 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1779 | San Bruno Interchange 115 kV Land Rights |  |  | Burlingame, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ San Mateo, San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | 2025-11-05 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 115 | NA | NA | NA | NA | 4.02 | Non-IGP | 5798128 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-06-11 | NA | 2032-02-02 | NA | NA | FALSE | NA | NA ¦ NA | 117.6005 | 445.4904 | 26.8098 | 22.6864 | 30.6575 | 30.9469 | 4.9729 | 38.7456 | 4 | 4 | 0 | 0 | 116.0735 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1780 | San Mateo-Martin No. 3 Cable Relocation |  |  | San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | 2026-03-03 | 53 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 0.21 | NA | 115 | NA | NA | NA | NA | 4.02 | Non-IGP | 5798140 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-02-25 | NA | 2028-08-16 | NA | NA | FALSE | NA | NA ¦ NA | 569.8928 | 18840.6195 | 0 | 99.0178 | 398.5833 | 54.6087 | 13.2346 | 275.1749 | 8500 | 9000 | 500 | 0 | 565.4445 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1781 | San Mateo-Martin No. 6 Cable Relocation |  |  | San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | 2026-03-03 | 53 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 0.23 | NA | 115 | NA | NA | NA | NA | 4.02 | Non-IGP | 5798141 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-11-23 | NA | 2028-08-28 | NA | NA | FALSE | NA | NA ¦ NA | 558.7242 | 18829.1109 | 0 | 99.6999 | 367.2191 | 74.5182 | 12.9764 | 274.6972 | 8500 | 9000 | 500 | 0 | 554.4137 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1782 | Martin-SF Airport Cable Replacement |  |  | San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | 2026-03-03 | 53 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 0.23 | NA | 115 | NA | NA | NA | NA | 4.02 | Non-IGP | 5798143 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-12-06 | NA | 2033-08-18 | NA | NA | FALSE | NA | NA ¦ NA | 29.9145 | 18265.9992 | 0 | 3.7745 | 16.4212 | 7.2363 | 0.6574 | 237.9099 | 8500 | 9000 | 500 | 0 | 28.0894 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1783 | Martin-Millbrae No. 1 Cable Replacement |  |  | San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | 2026-03-03 | 53 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 0.22 | NA | 115 | NA | NA | NA | NA | 4.02 | Non-IGP | 5798142 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Planning | 5 | 2033-01-18 | NA | 2033-06-22 | NA | NA | FALSE | NA | NA ¦ NA | 28.064 | 18635.8089 | 0 | 2.5191 | 17.0432 | 6.9053 | 0.6344 | 608.7071 | 8500 | 9000 | 500 | 0 | 27.1019 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1784 | ETL CEM Stock |  |  | NA | PG&E’s Transmission Line Asset Management team is proposing purchasing and properly storing emergency stock of the Electric Transmission Underground cables and associated hardware: cable splices cable terminations, etc. (further as hardware). Such cables and associated hardware are considered “long lead items” and not readily available in case of emergency. | Transmission Line - Underground | Replace | NA | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.23 | Non-IGP | 5802562 | T.0009802 | CEM for ETU Cables | 1 | 72 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 18031.7222 | 31031.7222 | 0 | 0 | 2.3759 | 9950.8456 | 7852.3697 | 226.131 | 6000 | 4000 | 1000 | 1000 | 17805.5912 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1785 | SMARTVILLE-MARYSVILLE 60KV LEVEE 3 |  |  | Marysville, Yuba ¦ Smartsville CDP, Yuba ¦ Yuba | Relocate the Smartville – Marysville and Pease – Marysville – Harter 60 kV lines to support the Marysville Ring Levee Phase 3 Project by the Marysville Levee District in Marysville, CA. | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-09-12 | 59 | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 1.7 | NA | 60 | NA | NA | NA | NA | NA | NA | 5539441 | T.0003956 | Pease-Marysville-Harter 60kV Levee 3 | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6187-E | 2021-05-05 | Approved | 2021 | Operational | 1 | 2022-12-03 | 2021-06-30 | 2022-12-31 | Permitting | NA | FALSE | 13800 | NA ¦ NA | 205.893 | 205.893 | 0 | 200.5265 | 3.6085 | 1.5529 | 0.2051 | 0 | 0 | 0 | 0 | 0 | 205.893 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 191.3126 | 3.4427 | 1.4815 | 0.19572 | 0 | 0% | 17% ¦ $206 | NA | NA ¦ NA | NA | 0% | 100% | NA
1786 | ROUGH & READY TAP 60KV: CAPACITY INCREAS |  |  | Stockton, San Joaquin | The Port of Stockton (Customer) has submitted an application to Pacific Gas and Electric (PG&E) for plans to increase electric load (Project) at their existing facilities in Stockton, California. The Customer is currently interconnected to PG&E’s existing transmission system near Rough & Ready Substation via PG&E’s Rough & Ready 60 kV Tap Line. This has triggered a network upgrade to reconductor sections of the Stockton A No. 1 60 kV Line and Rough & Ready 60 kV Tap with 715 AAC. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-09-27 | 57 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 1 | NA | 60 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5780438 | T.0003979 | Rough & Ready Tap 60kV: Capacity Increas | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5482-E | 2019-02-25 | Approved | 2019 | Operational | 1 | 2019-05-31 | 2019-04-15 | 2020-01-13 | Workforce | NA | FALSE | 9795 | NA ¦ NA | 8424.1012 | 8424.1012 | -237.9835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8424.1012 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -237.9835 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1787 | Private Load Interconnection Project |  |  |  | The following scope of work is required to interconnect the Customer's data center into PG&E’s Los Esteros Substation: • Construct two, 2000-foot 115 kV underground cables from Los Esteros Substation to Customer’s McCarthy Substation. The cables will have normal and emergency ratings of 500 Amps (= 100 MVA). • Connect riser structures for the two 115 kV cables at Los Esteros Substation and connect the lines into 115 kV Bays 7 and 8. Install Circuit Breakers 772 and 872 and Disconnect Switches 773 and 783 to complete the break-and-a-half bay configuration. • Install 115 kV metering equipment at Micosoft’s McCarthy Substation. • Install protective relay packages at Los Esteros and McCarthy Substations for line protection. • Install fiber line for communication between Los Esteros and McCarthy Substations. | Substation - Circuit Breaker | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-09 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5790382 | T.0005903 | Private Load Interconnection Project | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2024-04-08 | EIR | NA | San Jose City | NA | NOC: AL 7349-E | 2024-08-09 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-06-15 | 2023-08-30 | 2027-01-13 | Prioritization | NA | TRUE | 18600 | NA ¦ NA | 2369 | 4599 | 125.6244 | -1391.9745 | 1010.6371 | 2125.1469 | 423 | 2308 | 0 | 0 | 0 | 0 | 2291 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 0 | 144.3086 | 16.406 | 1.063 | 0 | 0 | 0% | 50% ¦ $4,599 | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1788 | Private Load Interconnection Project |  |  |  | Construct new switching station and install additional conductor on the Morgan Hill-Llagas 115 kV tower line to a new switching station at the customer site | Transmission Line - Conductor | New | NA | T.0004271 | Work Requested by Others | Load Interconnection | NA | NA | 2025-10-21 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.2 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5547567 | T.0007676 | Private Load Interconnection Project | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2025-03-26 | EIR | NA | City of Gilroy | NA | NOC: AL 7687-E | 2025-08-29 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-08-27 | 2026-10-14 | 2027-03-26 | NA | NA | TRUE | 18000 | NA ¦ NA | 906.8019 | 4527.8457 | 10.8115 | 129.0337 | 23.7731 | 169.1029 | 409.0119 | 3232.6863 | 553.4262 | 0 | 0 | 0 | 741.7331 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 139.8687 | 23.7731 | 169.1029 | 409.0119 | 165.0688 | 0% | 100% ¦ $4,528 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1789 | Private Load Interconnection Project |  |  |  | The Customer is planning on constructing a large data center facility, expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Trimble 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Loop the Newark-Trimble 115 kV Line into the new PG&E Switching Station; ● Reconductoring of 12.1 miles of the Newark-Trimble 115 kV Line from Newark to TSP 012/082; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The Customer has also requested that the two connections from the Newark-Trimble Line be routed separately from the PG&E switching station to the existing line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-11-18 | 52 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | 12.1 | NA | 115 | NA | NA | NA | NA | 5.301 | Non-IGP | 5804165 | T.0009031 | Private Load Interconnection Project | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2031-11-13 | NA | 2032-05-07 | NA | NA | FALSE | NA | NA ¦ NA | 929.4295 | 1442.1401 | 0 | 0 | 394.6072 | 807.898 | -284.4082 | 67.756 | 72.2735 | 77.5708 | 83.2564 | 89.3588 | 918.0969 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 50% ¦ $1,442 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1790 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC), has submitted an application to Pacific Gas and Electric Company (PG&E) to interconnect a data center to PG&E’s transmission system through discrete 230kV service from Egbert Switching Station. The site is currently served from PG&E’s 12kV feeder H1112 from Martin Substation. The IC expects their load to ramp up to 48 MW in 2031, and therefore requested transmission service. | Transmission Line - Multiple | New | NA | T.0000159 | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-04 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 1.7 | NA | 230 | NA | NA | NA | NA | 5.301 | Non-IGP | 5804590 | T.0009133 | Private Load Interconnection Project | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-11-14 | NA | 2029-03-01 | NA | NA | FALSE | NA | NA ¦ NA | 65.8174 | 5993.2347 | 0 | 0 | 7.4022 | 60.1641 | -6.4357 | 267.0569 | 3383.4774 | 927.1394 | 1354.4303 | 0 | 61.1306 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 48% ¦ $5,993 (Subject to change) | Type 2 | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1791 | Private Load Interconnection Project |  |  |  | The project scope of work includes following: Install Gas Insulated Switchgear (GIS) Switching Station • Install two (2) GIS BAAH switching station looping into Grant-Eastshore #2 115kV Line • Provide dual 115kV service from a new GIS Switching station. • Install Station Service Voltage Transformer (SSVT) • Install a new MPAC building to accommodate the protective relays for the GIS and SSVT • Install access roads, grading, fencing and security Install T-Line • Two 115 kV Overhead (OH) Transmission lines will be built to interconnect 115 kV GIS switching station to Eastshore & Grant’s 115 kV bus. The new double circuit line would consist of new tubular steel poles(TSP) supporting approximately 0.40 double circuit miles of aluminum concentric stranded conductor. Eastshore: Remote End Upgrade • Install SMP breaker & Line package for CB 312 • Establish redundant communication path. Grant: Remote End Upgrade • Install SMP breaker & Line package for CB 122 • Establish redundant communication path. Direct Assignment • Install necessary relay upgrades. Metering • Add telemetry from Customer’s substation to PG&E system | Transmission Line - Conductor | New | NA | T.0004580 | Work Requested by Others | Load Interconnection | NA | NA | 2025-11-09 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.8 | NA | 115 | NA | NA | NA | NA | 5.301 | Non-IGP | 5807592 | T.0009652 | Private Load Interconnection Project | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-04-29 | 2027-11-19 | 2028-01-27 | NA | NA | FALSE | 3400 | NA ¦ NA | 878.5427 | 3443.364 | 0 | 0 | 30.7358 | 312.6038 | 468.4234 | 461.4323 | 2004.4129 | 165.7558 | 0 | 0 | 811.7629 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,443 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1792 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC or Customer), has submitted an application to Pacific Gas and Electric Company (PG&E) to interconnect a data center load to PG&E’s Transmission system. Preliminary Engineering Study report was signed in April 2024 Direct Assignment • Review and accept customer design and testing protocols • Witness/complete final testing for interconnection Component 115kV BAAH • Two new bays and provision for 3rd bay in new Component Switching Station • Install two(2) new 115kV complete BAAH Bay 1 & 2 o Six 115kV breakers o Twelve 115kV disconnects o Two 115kV line disconnect switches o Two 115kV underground line termination structures • Install protective relaying for the new breakers/lines in the existing control enclosure • Install new SMP relay package(s) for the 115kV CBs. 115kV T-Line • Install two 115kV underground lines between Component Switching Station and Customer substation • Install two fiber communication lines between Component Switching Station and Customer substation Land Rights • Land rights for Component Switching station and transmission line parcels Metering • Install two CT/PT combo units and metering enclosure equipment at Customer facility | Transmission Line - Multiple | Relocate | NA | T.0009031 | Work Requested by Others | Load Interconnection | NA | NA | 2025-11-18 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 115 | NA | NA | NA | NA | 3.002 | Non-IGP | 5817742 | T.0010520 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-04-30 | 2028-09-29 | 2028-09-29 | NA | NA | FALSE | 89700 | NA ¦ NA | 11.8216 | 4354.0252 | 0 | 0 | 0 | 0 | 3.8176 | 319.632 | 1419.2639 | 2386.0335 | 210.0157 | 15.2625 | 3.8177 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 9% ¦ $4,354 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1793 | SVP Interconnection - POCO Switch |  |  | San Jose, Santa Clara ¦ Santa Clara, Santa Clara | IC has forecasted that their load will double in the upcoming years. To support the large load growth, IC is pursuing a series of expansion projects. There are four major projects involved: Scott Receiving Station (SRS), Kifer Receiving Station (KRS), Northern Receiving Station (NRS), and NRS-KRS 115kV Transmission Line. PG&E is obligated support them in these upgrades to ensure continued safe and reliable transmission from PG&E to IC. Project scope is the following: • Remote end upgrades at three (3) substations which includes: Newark (Newark – Kifer & Newark - NRS #1 & #2 115 kV lines), Nortech (Nortech - NRS 115 kV line), Zanker (San Jose Regional Water Facility SJRWF tap from Newark - Kifer 115 kV line) • Four (4) Point Of Customer Ownership (POCO) outside of the receiving stations (Scott & Northern Receiving Stations) | Transmission Line - Switch | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-08-28 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5813219 | T.0010764 | SVP Interconnection - POCO Switch | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-03-24 | 2027-08-04 | 2027-08-13 | NA | NA | TRUE | 24420 | NA ¦ NA | 503.1657 | 7994.5142 | 0 | 0 | 0 | 0 | 405.0292 | 3320.595 | 4260.6283 | 8.2617 | 0 | 0 | 405.0292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1794 | Private Load Interconnection Project |  |  |  | Interconnect a 250 MW data center to PG&E's Los Esteros Substation. This project proposes to connect new large load (new data center and / or R&D facilities) to 230kV bay 4 at Los Esteros substation by installing a new breaker. | Transmission Line - Multiple | New | NA | T.0011326 | Work Requested by Others | Load Interconnection | NA | NA | 2025-10-23 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1 | NA | 230 | NA | NA | NA | NA | 3.002 | Non-IGP | 5816379 | T.0010864 | Private Load Interconnection Project | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-12-01 | NA | 2027-05-01 | NA | NA | TRUE | NA | NA ¦ NA | 9.9029 | 9311.3336 | 0 | 0 | 0 | 0 | 9.7787 | 1674.6828 | 7024.7987 | 602.0734 | 0 | 0 | 9.7787 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 3 | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1795 | Private Load Interconnection Project |  |  |  | Interconnect data center to Garlic 115kV Switching Station on Morgan Hill-Llagas 115kV line 115kV Garlic Switching Station • Install Three (3) 115kV, 3000A, 63kA Circuit Breakers, associated switches and bus structures for Bay 3 • Install breaker failure and reclosing relays for all new Circuit Breakers • Install Line Current Differential scheme for Garlic-LC24-1 115kV Line #1 & #2 AWS Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV line that PG&E will own, operate, and maintain • Install Remote Terminal Unit(RTU) for PG&E visibility • Install revenue metering Transmission Line • Relocate 115kV Garlic-LC24-24 #2 line terminal to Bay 3 and install LC24-1 115kV Line #2 • Install approximately 1 mile long single circuit 115kV Overhead Transmission Line to customer site from Garlic Switching Station | Transmission Line - Multiple | Relocate | NA | T.0010873 ¦ T.0010874 ¦ T.0010875 ¦ T.0010876 ¦ T.0010908 | Work Requested by Others | Load Interconnection | NA | NA | 2025-07-25 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | NA | 115 | NA | NA | NA | NA | 5.301 | Non-IGP | 5816147 | T.0010902 | Private Load Interconnection Project | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-09-13 | 2029-10-01 | 2028-10-25 | NA | NA | FALSE | 3600 | NA ¦ NA | 3.734 | 1099.3579 | 0 | 0 | 0 | 0 | 3.4389 | 284.9002 | 295.4624 | 451.8139 | 63.7425 | 0 | 3.4389 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 6% ¦ $1,099 (Subject to change) | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1796 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install a new two (2) bay BAAH GIS Switching station and the existing Trimble-Montague 115kV line will be looped through the new switching station. New 115kV Charcot Switching Station • Install a new 115kV two (2) bay Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with the land provision for ultimate four (4) bay. • Install Breaker failure and Reclosing relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install line current differential relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. Trimble Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Trimble – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 312. Montague Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Montague – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 142. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Trimble-Montague 115kV line through the new 115kV Switching Station • Install approximately 0.80 mile two line extension using underground cables | Transmission Line - Multiple | New | NA | T.0010902 ¦ T.0010873 ¦ T.0010874 ¦ T.0010875 ¦ T.0010876 | Work Requested by Others | Load Interconnection | NA | NA | 2025-08-19 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | 0.8 | NA | 115 | NA | NA | NA | NA | 5.301 | Non-IGP | 5813934 | T.0010908 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-06-15 | NA | 2030-03-01 | NA | NA | FALSE | NA | NA ¦ NA | 385.8511 | 52223.7263 | 0 | 0 | 0 | 0 | 310.9184 | 774.8944 | 2990.2656 | 7922.7504 | 21690.6949 | 18482.975 | 310.9184 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1797 | Caltrain IC - T-Line Site 1 (82) |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-24 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.25 | NA | 115 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5766382 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | NA ¦ 5763023 ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-05-08 | 2021-06-30 | 2022-03-13 | Construction Delays | NA | FALSE | 46700 | NA ¦ NA | 1491.2176 | 1491.2176 | -39.5173 | 50.0447 | 2.4087 | -41.7715 | 0 | 0 | 0 | 0 | 0 | 0 | 1491.2176 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 1503.0812 | 2.3386 | -40.5551 | 0 | 0 | 0% | 60% ¦ $1,491 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1798 | Caltrain IC - Desgn-Bld Supp Site 1 (82) |  |  | Burlingame, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ San Mateo, San Mateo ¦ South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Transmission Line - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-11-05 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5773283 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-24 | 2021-06-30 | 2022-03-13 | Construction Delays | NA | FALSE | 46700 | NA ¦ NA | 11.5643 | 11.5643 | -2.6618 | 7.5033 | -8.7007 | -0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5643 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 20.5592 | -8.7007 | -0.42 | 0 | 0 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1799 | HSR Interconnection ET Sites 4-7 (82) |  |  | TBD | TPS Sites 4 to 7 will power the section of the rail line that connects the Bay Area with the Central Valley. When the CHSR Project is completed and in-service, the CHSR substation at Sites 4 to 7 will have a total power demand of over 230 megawatts (MW). The interconnections at Sites 4 to 7 will consist of the major work components shown below. There will be other system work needed to address protection and automation upgrades needed for the system reconfigurations resulting from the interconnections. Generally, “Network Upgrades” will be performed by PG&E, and work for new “Interconnection Facilities” will be performed by CHSRA or its contractors. | Transmission Line - Conductor | New | NA | T.0000006 ¦ T.0002127 ¦ T.0004116 ¦ T.0002231 | Work Requested by Others | Load Interconnection | NA | NA | NA | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 41 | NA | 230 ¦ 115 | NA | 3 | 6. Customer commitments | NA | 5.211 | Non-IGP | 5766463 | T.0000005 | CHSR Interconnections, Sites 4-7 | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2017 | 2018 | FALSE | NA | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2034-03-13 | 2020-12-01 | 2036-06-11 | Customer Action | Scope Change | FALSE | 285000 | NA ¦ NA | 277.1478 | 62914.6139 | 18.2979 | 15.2051 | 22.1339 | 23.9948 | 4.8597 | 18.7984 | 38.4337 | 46.4406 | 49.8054 | 51.6767 | 275.2178 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 (Final allocation not yet finalized with CPUC & FERC) | NA | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1800 | HSR Interconnection ET Sites 8-13 (82) |  |  | TBD | California High Speed Rail (CHSR) Transmission Power Delivery Project – Sites 8 through 13. The Project will require the installation of a 25 kV AC Traction Electrification System (TES) to power the electric trains. In order to have adequate capacity for train operations, the proposed TES will interconnect into local utility networks at 115 kV or 230 kV, with approximately 30-mile intervals between the traction power substations. This substation spacing results in twelve (12) traction power substations for the 345-mile portion of the line running in PG&E’s service territory.There are six (6) interconnection sites located in the Madera to Bakersfield section. These sites have been designated as Sites 8 through 13. | Transmission Line - Conductor | New | NA | T.0000005 ¦ T.0001650 ¦ T.0000924 ¦ T.0000204 ¦ T.0000980 ¦ T.0003202 ¦ T.0000220 ¦ T.0000143 ¦ T.0000156 | Work Requested by Others | Load Interconnection | NA | NA | NA | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 61 | NA | 230 ¦ 115 | NA | 3 | 6. Customer commitments | NA | 5.211 | Non-IGP | 5766318 | T.0000006 | CHSR Interconnections, Sites 8-13 | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2017 | 2018 | FALSE | NA | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2034-10-20 | 2020-12-01 | 2036-09-10 | Customer Action | Scope Change | FALSE | 454000 | NA ¦ NA | 419.2744 | 98725.05 | 25.899 | 22.7949 | 41.9545 | 35.0537 | 0 | 31.6296 | 32.6015 | 34.9912 | 37.5558 | 40.3085 | 413.1635 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 (Final allocation not yet finalized with CPUC & FERC) | NA | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1801 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 100 megawatt (MW) (net output) solar-based generation facility to the Pacific Gas and Electric Company’s (PG&E’s) new 230 kV Bitterwater Switching Station which connects to the Midway – Wheeler Ridge 230 kV Line No.2 in Kern County, California. | Transmission Line - Conductor | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.02 | 10.403 | 230 | NA | 3 | 6. Customer commitments | NA | 5.3 | Non-IGP | 5768562 | T.0001353 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2017 | 2015 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6634-E | 2022-06-30 | Approved | 2022 | Operational | 1 | 2024-02-27 | 2018-12-01 | 2024-04-24 | Customer Action | NA | FALSE | 19820 | NA ¦ NA | 2321.1601 | 2321.1601 | 4.7713 | 109.3635 | 495.477 | 1814.7857 | -127.497 | 0 | 0 | 0 | 0 | 0 | 2321.1601 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 2323.0583 | -120.8111 | 0 | 0% | 100% ¦ $2,321 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1802 | Caltrain Transition Sta Kifer-FMC |  |  | San Jose, Santa Clara ¦ Santa Clara, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-11-19 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | 6. Customer commitments | NA | NA | NA | 5784664 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 1 | 2021-03-01 | 2021-06-30 | 2021-04-18 | NA | NA | FALSE | 64500 | NA ¦ NA | 120.897 | 120.897 | 75.8617 | -1.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.897 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 121.9758 | -1.1032 | 0 | 0 | 0 | 0 | 0% | 60% ¦ $121 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1803 | Caltrain Transition Sta Trimble-SanJoseB |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-11-12 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | 6. Customer commitments | NA | NA | NA | 5784663 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 1 | 2021-04-01 | 2021-06-30 | 2021-05-18 | NA | NA | FALSE | 64500 | NA ¦ NA | 96.5626 | 96.5626 | 58.5323 | 0.6538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5626 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 95.8862 | 0.65392 | 0 | 0 | 0 | 0 | 0% | 60% ¦ $97 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1804 | Caltrain IC - Desgn-Bld Supp Site 3 (82) |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Transmission Line - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-11-05 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5773284 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 1 | 2020-11-03 | 2021-06-30 | 2022-02-19 | Construction Delays | NA | FALSE | 64500 | NA ¦ NA | -2.4699 | 0 | 22.4704 | -25.5166 | -0.229 | -0.42 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4699 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | -1.8763 | -0.22896 | -0.42 | 0 | 0 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1805 | Caltrain IC - T-Line Site 3 (82) |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Transmission Line - Conductor | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-11-05 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.25 | NA | 115 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5772269 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2018 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 1 | 2019-05-13 | 2021-06-30 | 2022-08-29 | Construction Delays | NA | FALSE | 64500 | NA ¦ NA | 1497.4875 | 1497.4875 | 196.6122 | 52.6397 | 8.726 | -39.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 1497.4875 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 1455.0135 | 8.215 | -37.2462 | 0 | 0 | 0% | 60% ¦ $1,497 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1806 | Los Banos - Padre Flat 20074: Recon-Land |  |  | Fresno ¦ Merced | Reconductor 4.5 miles of the Los Banos - Padre Flat Switching Station 230 kV Line No. 1 with 1113 ACSS conductor. Upgrade associated equipment to 1,900 Amps to match the new conductor rating, as needed. Replace structures, as needed | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-10-30 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | NA | 230 | NA | NA | NA | NA | NA | NA | 5536583 | T.0003016 | Los Banos - Padre Flat SS 20266: Recon. | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2022 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6527-E | 2022-03-11 | Approved | 2022 | Operational | 1 | NA | 2021-09-30 | 2022-10-31 | Land Rights | NA | FALSE | 14300 | NA ¦ NA | 57.5161 | 57.5161 | 0 | 57.5161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5161 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 57.5161 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $58 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1807 | LOS BANOS - PADRE FLAT SS 20266: RECON - |  |  | Fresno ¦ Merced | Reconductor 4.5 miles of the Los Banos - Padre Flat Switching Station 230 kV Line No. 1 with 1113 ACSS conductor. Upgrade associated equipment to 1,900 Amps to match the new conductor rating, as needed. Replace structures, as needed | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-10-30 | 70 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | 3.7 | NA | 230 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5774966 | T.0003016 | Los Banos - Padre Flat SS 20266: Recon. | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2019 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6527-E | 2022-03-11 | Approved | 2022 | Operational | 1 | 2022-10-31 | 2021-09-30 | 2022-12-24 | Material | NA | FALSE | 14300 | NA ¦ NA | 5220.7914 | 5220.7914 | 513.4248 | 4070.6732 | 119.9182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5220.7914 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 4920.6048 | 115.5057 | 0 | 0 | 0 | 0% | 100% ¦ $5,221 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1808 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | T.0009188 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 2 | 26.1945 | 230 | NA | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5775143 | T.0003035 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2018 | 2017 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2028-05-25 | 2020-06-01 | 2028-09-05 | Customer Action | NA | FALSE | 31980 | NA ¦ NA | 153.3297 | 183.5825 | 68.1018 | 27.1872 | 7.1982 | 16.1835 | 4.4599 | 9.3323 | 11.9225 | 8.9981 | 0 | 0 | 153.3297 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $184 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1809 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 300 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) new Switching Station looped into the Quinto Switching Station - Westley 230 kV Line, in Stanislaus County, California. | Transmission Line - Conductor | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-09-29 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 0.02 | NA | 230 | NA | 3 | NA | NA | NA | NA | 5779143 | T.0003770 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6529-E | 2022-03-16 | Approved | 2022 | Operational | 1 | 2023-10-23 | 2020-01-10 | 2023-12-13 | Prioritization | NA | FALSE | 25500 | NA ¦ NA | 3314.8732 | 3314.8732 | 170.5564 | 510.2092 | 2478.2453 | 97.4996 | 0 | 0 | 0 | 0 | 0 | 0 | 3314.8732 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 3126.2272 | 94.571 | 0 | 0 | 0% | 100% ¦ $3,315 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1810 | LOS BANOS-QUINTO SS 20244: RECON. |  |  | Merced | Reconductor 6.11 miles of the Los Banos - Quinto Switching Station 230 kV Line with super bundled 795 ACSS conductor. Upgrade associated terminal equipment at Los Banos and Quinto Switching Station to match the new conductor rating as needed. Replace structures as needed | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-07-24 | 60 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | 12 | NA | 230 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5779031 | T.0003789 | Los Banos - Quinto SS 20244: EGI Recon. | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2019 | 2018 | FALSE | NA | NA | NA | TRUE | Final Certified | 2012-11-06 | EIR | NA | Merced County | NA | NOC: AL 4180-E | 2013-01-17 | Approved | 2013 | Operational | 1 | 2023-03-06 | 2020-04-30 | 2023-05-08 | Material | NA | FALSE | 12430 | NA ¦ NA | 13835.8986 | 13835.8986 | 545.8126 | 3907.6373 | 8797.5818 | -8.1745 | 0 | 0 | 0 | 0 | 0 | 0 | 13835.8986 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 13621.2672 | -8.0379 | 0 | 0 | 0% | 100% ¦ $13,836 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1811 | Padre Flat - Panoche#1 20074: Recon-Land |  |  | Fresno ¦ Merced | Reconductor 32.59 miles of the Padre Flat Switching Station - Panoche 230 kV Line No. 1 with 795 ACSS conductor. Upgrade associated equipment and structures to match the new conductor rating, as needed. | Other | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-10-30 | NA | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 32.6 | NA | 230 | NA | NA | NA | NA | 5.4 | NA | 5536585 | T.0003792 | Padre Flat SS - Panoche #1 20267: Recon. | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2022 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6857-E | 2022-11-21 | Approved | 2023 | Operational | 1 | NA | 2021-09-30 | 2024-02-23 | Land Rights | NA | FALSE | 49490 | NA ¦ NA | 1385.4967 | 1385.4967 | 0 | 271.3618 | 1130.3071 | -16.086 | -0.0862 | 0 | 0 | 0 | 0 | 0 | 1385.4967 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 246.6925 | 1027.5519 | 111.3385 | -0.08625 | 0 | 0% | 100% ¦ $1,385 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1812 | PADRE FLAT- PANOCHE#1 20267: RECON - EGI |  |  | Fresno ¦ Merced | Reconductor 32.59 miles of the Padre Flat Switching Station - Panoche 230 kV Line No. 1 with 795 ACSS conductor. Upgrade associated equipment and structures to match the new conductor rating, as needed. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-10-30 | 72 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 33.5 | NA | 230 | NA | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5779058 | T.0003792 | Padre Flat SS - Panoche #1 20267: Recon. | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6857-E | 2022-11-21 | Approved | 2023 | Operational | 1 | 2023-11-02 | 2021-09-30 | 2025-03-31 | Material | NA | TRUE | 49490 | NA ¦ NA | 40675.3053 | 40675.3053 | 369.2148 | 1259.4602 | 14346.6458 | 14162.8738 | 9839.6154 | 33.8449 | 0 | 0 | 0 | 0 | 40641.4604 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 37883.0954 | 31.3805 | 0% | 100% ¦ $40,675 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1813 | WRO Generator Network Upgrades |  |  |  | To fulfill the Utility’s obligation to serve, the company will interconnect the Project to the Pacific Gas and Electric Company (PG&E)’s non-CAISO controlled Transmission system for a 99 MW Wind Generation tapping into the Manville Tap 115 kV Transmission Line in Lompoc, CA. In order for the interconnection customer to interconnect their 99 MW to PG&E’s Manville Tap, it’s required that the customer reconductor 0.62 miles of the Manville 115 kV Tap Line to mitigate an overload issue when generation is tapped to the Manville 115kV Tap Line. Reliability Network Upgrades Scope of work • Install one (1) direct transfer trip (DTT) transmitter at Divide Substation; • Modify existing under voltage load shedding (UVLS) protection scheme to include tripping CB142 at Divide Substation; • Install one (1) direct transfer trip (DTT) transmitter at Cabrillo Substation; • Install new IT T1 infrastructure for the DTT communication circuit at Cabrillo Substation. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.9377 | 115 | NA | NA | 6. Customer commitments | NA | NA | NA | 5780280 | T.0004006 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2024 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 5755-E | 2020-02-05 | Approved | 2020 | Operational | 1 | 2020-02-18 | 2020-03-16 | 2022-11-15 | Prioritization | Project Design | FALSE | 3460 | NA ¦ NA | 821.5142 | 821.5142 | 111.3965 | 127.3811 | 59.2408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 821.5142 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 758.7861 | 58.883 | 0 | 0 | 0 | 0% | 100% ¦ $822 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1814 | WRO Generator Network Upgrades |  |  |  | To fulfill the Utility’s obligation to serve, the company will interconnect the Project to the Pacific Gas and Electric Company (PG&E)’s non-CAISO controlled Transmission system for a 99 MW Wind Generation tapping into the Manville Tap 115 kV Transmission Line in Lompoc, CA. In order for the interconnection customer to interconnect their 99 MW to PG&E’s Manville Tap, it’s required that the customer reconductor 0.62 miles of the Manville 115 kV Tap Line to mitigate an overload issue when generation is tapped to the Manville 115kV Tap Line. Reliability Network Upgrades Scope of work • Install one (1) direct transfer trip (DTT) transmitter at Divide Substation; • Modify existing under voltage load shedding (UVLS) protection scheme to include tripping CB142 at Divide Substation; • Install one (1) direct transfer trip (DTT) transmitter at Cabrillo Substation; • Install new IT T1 infrastructure for the DTT communication circuit at Cabrillo Substation. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.3073 | 115 | NA | NA | NA | NA | NA | NA | 5789342 | T.0004006 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2020 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 5755-E | 2020-02-05 | Approved | 2020 | Operational | 1 | 2020-08-18 | 2020-03-16 | 2022-11-15 | Prioritization | Project Design | FALSE | 3460 | NA ¦ NA | 436.4186 | 436.4186 | 77.7628 | 61.916 | 4.8034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.4186 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 431.6289 | 4.8034 | 0 | 0 | 0 | 0% | 100% ¦ $436 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1815 | DOS AMIGOS PP-PANOCHE #3 20232: RECON. |  |  | Fresno ¦ Merced | The Project proposes to reconductor 23.63 miles of the Pacific Gas and Electric Company’s (PG&E’s) Dos Amigos - Panoche 230 kV Line No. 3 with a higher capacity conductor, in Merced and Fresno Counties, California. During the Cluster 9 Phase I Fresno Area Interconnection Study, the Dos Amigos - Panoche 230 kV Line No. 3 was found to be overloaded by roughly 84%. To eliminate this deliverability constraint, the CAISO requires reconductoring the overloaded line and the costs are allocated among multiple full capacity generation projects identified by the CAISO. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-14 | 78 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 23.6 | NA | 230 | NA | 3 | 6. Customer commitments | 1162 | 3.002 | Non-IGP | 5782110 | T.0004255 | Dos Amigos PP-Panoche #3 230 kV Recondu. | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7392-E | 2024-10-02 | Approved | 2024 | Construction (over 75%) | 2 | 2025-04-01 | 2021-09-30 | 2026-05-04 | Prioritization | NA | TRUE | 66420 | NA ¦ NA | 17129.9068 | 24739.084 | 160.507 | 866.9159 | 492.4483 | 2315.9413 | 8764.1825 | 11545.0693 | 0 | 0 | 0 | 0 | 13194.0146 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $24,739 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1816 | Dos Amigos - Panoche T-line Land Acq. |  |  | Fresno ¦ Merced | The Project proposes to reconductor 23.63 miles of the Pacific Gas and Electric Company’s (PG&E’s) Dos Amigos - Panoche 230 kV Line No. 3 with a higher capacity conductor, in Merced and Fresno Counties, California. During the Cluster 9 Phase I Fresno Area Interconnection Study, the Dos Amigos - Panoche 230 kV Line No. 3 was found to be overloaded by roughly 84%. To eliminate this deliverability constraint, the CAISO requires reconductoring the overloaded line and the costs are allocated among multiple full capacity generation projects identified by the CAISO. | Other | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-14 | NA | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 23.6 | NA | 230 | NA | NA | NA | NA | 5.4 | Non-IGP | 5547947 | T.0004255 | Dos Amigos PP-Panoche #3 230 kV Recondu. | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2022 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7392-E | 2024-10-02 | Approved | 2024 | Operational | 1 | NA | 2021-09-30 | 2024-04-12 | Prioritization | NA | FALSE | 66420 | NA ¦ NA | 983.4092 | 983.4092 | 0 | 152.5812 | 780.4905 | 50.3376 | 0 | 0 | 0 | 0 | 0 | 0 | 983.4092 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 152.5812 | 780.4905 | 50.3375 | 0 | 0 | 0% | 100% ¦ $983 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1817 | WRO Generator Network Upgrades |  |  |  | The project is to accommodate the Energy Storage Project, which proposes to install 13 inverters rated at 1.9385 MW each with a maximum gross output of 25.2 MW. Auxiliary load of 0 MW and estimated losses of 0.2 MW. The net output is 25 MW to the CAISO Controlled Grid. This Generating Facility and the associated Interconnection Facilities plan to connect to Weber 60 kV Substation in San Joaquin County. Reconductor 0.9 mi of Stockton A0Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-11-25 | 13 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 0.9 | NA | 60 | NA | NA | NA | NA | NA | NA | 5783875 | T.0004561 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 5770-E | 2020-02-25 | Approved | 2020 | Operational | 1 | 2022-01-18 | 2021-11-01 | 2022-02-28 | NA | NA | FALSE | 8650 | NA ¦ NA | 1796.4792 | 1796.4792 | 351.4127 | 1333.445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1796.4792 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | 1688.8083 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,796 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1818 | WRO Generator Network Upgrades |  |  |  | The project is to accommodate the Energy Storage Project, which proposes to install 13 inverters rated at 1.9385 MW each with a maximum gross output of 25.2 MW. Auxiliary load of 0 MW and estimated losses of 0.2 MW. The net output is 25 MW to the CAISO Controlled Grid. This Generating Facility and the associated Interconnection Facilities plan to connect to Weber 60 kV Substation in San Joaquin County. Reconductor 0.9 mi of Stockton A0Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC | Transmission Line - Conductor | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-11-25 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 0.15 | NA | 60 | NA | NA | NA | NA | NA | NA | 5783874 | T.0004561 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 5770-E | 2020-02-25 | Approved | 2020 | Operational | 1 | 2022-04-09 | 2021-11-01 | 2022-04-11 | NA | NA | FALSE | 8650 | NA ¦ NA | 680.2713 | 680.2713 | 143.2857 | 472.6748 | 12.3925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680.2713 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 664.1785 | 12.3121 | 0 | 0 | 0 | 0% | 100% ¦ $680 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1819 | Grizzly PH Reconnect T-Line Work NU |  |  | Butte ¦ Plumas | The Caibou-Palermo 115 kV line, which connected the Powerhouse to the transmission grid, has been taken out of service for an extended timeframe in the aftermath of the November 2018 Camp Fire. This outage has disabled the Powerhouse’s ability to transmit power to SVP. The Powerhouse is currently generating a small amount to only provide station service. PG&E is obligated under the Agreement to transmit the power generated by the Powerhouse to SVP. The Agreement states that in the event of a transmission line outage, PG&E must work diligently to restore service on the same value-based schedule and priority as if it were a PG&E-owned facility. This project will provide an alternative interconnection for the Powerhouse. This project will connect the Powerhouse to the Bucks Creek-Rock Creek-Cresta 230 kV Line and install a 230/115kV step-up transformer at Bucks Creek Switchyard to facilitate the interconnection to the 230kV grid. | Transmission Line - Conductor | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-08-26 | NA | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 0.1 | NA | 230 ¦ 115 | NA | NA | 6. Customer commitments | NA | NA | NA | 5785300 | T.0004715 | Bucks Creek PH-Grizzly PH Reconnection | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-07-11 | 2021-12-31 | 2023-12-19 | Weather | NA | TRUE | 19981 | NA ¦ NA | 2625.046 | 2677.0427 | 630.146 | 776.6927 | 986.0629 | 63.2633 | 9.4539 | 52.2282 | 0 | 0 | 0 | 0 | 2624.8146 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 2164.393 | 52.6318 | 7.8651 | 0.19253 | 0% | 100% ¦ $2,677 | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1820 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 70.9 MW. This Generating Facility and the associated Interconnection Facilities plan connect to PG&E’s Lakeview Substation in Bakersfield, in Kern County. | Transmission Line - Conductor | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-14 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.5 | NA | 70 | NA | NA | NA | NA | 3.002 | Non-IGP | 5791725 | T.0006097 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2022 | 2020 | FALSE | NA | NA | NA | TRUE | Final Certified | 2024-03-12 | EIR | NA | Kern County | NA | NOC: AL 7247-E | 2024-04-26 | Approved | 2024 | Construction (25%-50%) | 2 | 2026-03-04 | 2024-07-07 | 2026-04-03 | Prioritization | NA | TRUE | 10000 | NA ¦ NA | 461.9721 | 1649.4748 | 5.1638 | 89.0225 | 78.9231 | 78.8729 | 176.7591 | 1210.6127 | 10.1206 | 0 | 0 | 0 | 428.7414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,649 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1821 | GATES BUS SECTION "E" LINE RELOCATIONS |  |  | Fresno | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Transmission Line - Conductor | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-20 | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | 3 | NA | NA | NA | NA | 5738327 | T.0006452 | GATES BUS SECTION "E" | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-03-08 | 2023-08-15 | 2021-04-08 | NA | NA | FALSE | 20060 | NA ¦ NA | 1506.3775 | 1506.3775 | 1280.856 | 21.4777 | 33.0253 | 66.2897 | 0 | 0 | 0 | 0 | 0 | 0 | 1506.3775 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 1279.8631 | 19.8379 | 30.5043 | 61.2315 | 0 | 0 | 0% | 100% ¦ $1,506 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1822 | Gates-Panoche 230 Line Relocation |  |  | Fresno | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Transmission Line - Conductor | Relocate | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-09-16 | 77 | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 0.02 | NA | 230 | NA | NA | NA | NA | NA | NA | 5795899 | T.0006452 | GATES BUS SECTION "E" | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-01-09 | 2023-08-15 | 2023-04-17 | NA | NA | FALSE | 20060 | NA ¦ NA | 4648.1683 | 4648.1683 | 2920.1463 | 1347.7281 | 356.9053 | 23.3885 | 0 | 0 | 0 | 0 | 0 | 0 | 4648.1683 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 4430.8688 | 22.3174 | 0 | 0 | 0% | 100% ¦ $4,648 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1823 | Castanea Line Relocation |  |  | Fresno | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Transmission Line - Conductor | Relocate | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-09-16 | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.02 | NA | 230 | NA | NA | NA | NA | NA | NA | 5795825 | T.0006452 | GATES BUS SECTION "E" | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-03-13 | 2023-08-15 | 2023-05-23 | NA | NA | FALSE | 20060 | NA ¦ NA | 2977.8583 | 2977.8583 | 109.4504 | 2064.435 | 779.2812 | 24.6918 | 0 | 0 | 0 | 0 | 0 | 0 | 2977.8583 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 2883.4314 | 24.086 | 0 | 0 | 0% | 100% ¦ $2,978 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1824 | Borden - Gregg#1 20009: Recon-Land |  |  | Madera | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-23 | 95 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.2 | NA | 230 | NA | 776 | NA | NA | 3.002 | Non-IGP | 5536587 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7393-E | 2024-10-02 | Approved | 2024 | Construction (over 75%) | 2 | 2025-07-07 | 2020-09-30 | 2026-03-30 | Land Rights | NA | TRUE | 41660 | NA ¦ NA | 1737.9744 | 3737.9744 | 0.3098 | 0 | 0.0392 | 0.5045 | 1741.1478 | 1995.9731 | 0 | 0 | 0 | 0 | 1742.0013 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0.30982 | 0.0392 | 0.50447 | 1741.1478 | -4.0269 | 0% | 100% ¦ $3,738 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1825 | BORDEN-GREGG #2 20162: RECON. |  |  | Madera | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-23 | 95 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.25 | NA | 230 | NA | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5779060 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7393-E | 2024-10-02 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-01-19 | 2020-09-30 | 2027-05-12 | Land Rights | NA | TRUE | 41660 | NA ¦ NA | 805.9629 | 13120.7905 | 61.2768 | 34.3647 | 37.1246 | 131.7581 | 111.793 | 5468.6799 | 6875.2493 | 0 | 0 | 0 | 776.8613 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $13,121 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1826 | BORDEN-GREGG #1 20009: RECON. |  |  | Madera | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-23 | 95 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.2 | NA | 230 | NA | 776 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5779059 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7393-E | 2024-10-02 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-12-18 | 2020-09-30 | 2027-06-22 | Land Rights | NA | TRUE | 41660 | NA ¦ NA | 3065.5702 | 24416.3821 | 278.6062 | 357.1707 | 359.6946 | 723.3425 | 707.2584 | 12186.7734 | 9246.7053 | 0 | 0 | 0 | 2982.9035 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $24,416 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1827 | WRO Generator Network Upgrades |  |  |  | Install a storage generation plant with a net output of 24.5 MW PG&Es 60 kV Tulucay Substation in Napa County, California. Tulucay Substation: • Extend maiNAux bus with DBSB, install aux switch, fence and grading • Install 2 DTT Receivers with new DTT panel Vaca-Dixon Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit Lakeville Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit | Transmission Line - Conductor | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-10-20 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 2 | NA | 60 | NA | NA | NA | NA | 3.002 | Non-IGP | 5798546 | T.0007591 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | CEQA Final Published | 2024-04-15 | IS/MND | NA | County of Napa | NA | NOC: AL 7472-E | 2025-01-02 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-09-21 | 2025-10-10 | 2027-07-09 | Customer Action | NA | TRUE | 5750 | NA ¦ NA | 263.9751 | 1376.0726 | 0 | 19.9692 | 98.1176 | 79.2851 | 57.7867 | 642.0676 | 478.8464 | 0 | 0 | 0 | 255.1586 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,376 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1828 | FULTON-HOPLAND RECON (HOPLAND-GEYSERS) |  |  | Fulton CDP, Sonoma ¦ Healdsburg, Sonoma ¦ Larkfield-Wikiup CDP, Sonoma ¦ Mendocino ¦ Sonoma ¦ Windsor, Sonoma | The project scope of work includes the following: Local Delivery Network Upgrade: Reconductor Fulton-Hopland 60kV Line (Fitch Mountain Jct-Geysers Jct): • Reconductor Fulton-Hopland 60kV Line (Fitch Mountain Jct 009/005A – Geysers Jct 016/004) ~7 miles total length with 715 AAC. Reconductor Fulton-Hopland 60kV Line (Geysers Jct-Cloverdale Jct-Hopland): • Reconductor Fulton-Hopland 60kV Line (Geysers Jct 016/003A-Cloverdale Jct 026/002-Hopland) ~ 24.21 miles total length with 715 AAC and upgrade any limiting equipment. This Local Delivery Upgrade project is tied to following electric generation interconnection projects: • Janus Solar PV, LLC (Q1455), • Beauchamp Solar (Q1444), and • Walker Ridge Wind Energy Park (Q1284). The project proposes to reconductor 31.21 miles of Fulton-Hopland 60kV Line with a higher capacity conductor. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0008218 ¦ T.0006968 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-26 | 95 | Interconnection System Impact/Facilities Studies | Other - Deferral | $50 Mil – $75 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | 24.21 | NA | 60 | NA | NA | NA | NA | 3.002 | Non-IGP | 5798940 | T.0007629 | Fulton-Hopland 60 kV Reconductor (EGI) | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2022 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7532-E | 2025-03-11 | Approved | 2025 | Construction (25%-50%) | 2 | 2025-11-03 | 2027-03-31 | 2027-02-02 | NA | NA | TRUE | 70000 | NA ¦ NA | 21065.9311 | 41142.8082 | 0 | 0 | 831.1307 | 529.7017 | 9163.974 | 24098.4796 | 6471.1936 | 48.3287 | 0 | 0 | 10524.8063 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $41,143 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1829 | FULTON-HOPLAND RECON (GEYSERS-FITCH MTN) |  |  | Fulton CDP, Sonoma ¦ Healdsburg, Sonoma ¦ Larkfield-Wikiup CDP, Sonoma ¦ Mendocino ¦ Sonoma ¦ Windsor, Sonoma | The project scope of work includes the following: Local Delivery Network Upgrade: Reconductor Fulton-Hopland 60kV Line (Fitch Mountain Jct-Geysers Jct): • Reconductor Fulton-Hopland 60kV Line (Fitch Mountain Jct 009/005A – Geysers Jct 016/004) ~7 miles total length with 715 AAC. Reconductor Fulton-Hopland 60kV Line (Geysers Jct-Cloverdale Jct-Hopland): • Reconductor Fulton-Hopland 60kV Line (Geysers Jct 016/003A-Cloverdale Jct 026/002-Hopland) ~ 24.21 miles total length with 715 AAC and upgrade any limiting equipment. This Local Delivery Upgrade project is tied to following electric generation interconnection projects: • Janus Solar PV, LLC (Q1455), • Beauchamp Solar (Q1444), and • Walker Ridge Wind Energy Park (Q1284). The project proposes to reconductor 31.21 miles of Fulton-Hopland 60kV Line with a higher capacity conductor. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0008218 ¦ T.0006968 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-26 | 95 | Interconnection System Impact/Facilities Studies | Other - Deferral | $50 Mil – $75 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | 7 | NA | 60 | NA | NA | NA | NA | 3.002 | Non-IGP | 5798804 | T.0007629 | Fulton-Hopland 60 kV Reconductor (EGI) | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2022 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7532-E | 2025-03-11 | Approved | 2025 | Engineering more than 50% complete | 3 | 2027-02-03 | 2027-03-31 | 2027-03-31 | NA | NA | TRUE | 70000 | NA ¦ NA | 1849.074 | 12684.504 | 0 | 9.2205 | -67.9531 | 1843.4232 | -9.8148 | 1090.999 | 9763.0136 | 55.6156 | 0 | 0 | 1774.8758 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $12,685 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1830 | WRO Generator Network Upgrades |  |  |  | The project scope of work includes the following: Local Delivery Network Upgrade: Reconductor North Dublin – Cayetano 230kV Line: • Reconductor underground and overhead portion of the North Dublin – Cayetano 230kV line. Overhead and underground portions are 2.6 miles and 2.8 miles, respectivlety for a total of approximately 5.4 miles with 2000A capacity. This Local Delivery Upgrade project is tied to following Electric Generation Interconnection (EGI) project: • Solano 4 (Q1463) The project proposes to reconductor 5.4 miles of North Dublin – Cayetano 230kV Line with a higher capacity conductor. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004421 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-21 | 19 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | 5.4 | NA | 230 | NA | NA | NA | NA | 3.002 | Non-IGP | 5799480 | T.0007846 | WRO Generator Network Upgrades | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-09-02 | 2025-03-31 | 2026-03-06 | Clearances | NA | TRUE | 46380 | NA ¦ NA | 22144.3008 | 24577.1801 | 0 | 168.0676 | 392.3385 | 8087.8385 | 12348.9947 | 3579.9408 | 0 | 0 | 0 | 0 | 20997.2393 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $24,577 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1831 | WRO Generator Network Upgrades |  |  |  | The project proposes to reconductor 45 miles of 115kV Line upgrades with a higher capacity conductor and is a Local Delivery Network Upgrade (LDNU) project tied to the Q1557 electric generation interconnection project. The project scope of work includes the following: • Ripon-Manteca 115 kV Line Reconductor: Reconductor Ripon-Manteca 115 kV Line 2/0 CU and 4/0 ACSR sections with 715.5 AAC, 126/148 MVA • Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line Reconductor: Reconductor Ripon -Manteca 115 kV Line 2/0 CU and 4/0 ACSR sections with 715.5 AAC, 126/148 MVA • Bellota-Riverbank-Melones Sw Sta 115 kV Line 115 kV Line Reconductor: Reconductor 17 miles of Bellota-Riverbank-Melones Sw Sta 115 kV Line (Riverbank Tap to Tulloch Tap) with 477 ACSS 224/224/245/245 MVA. • Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line Reconductor: Reconductor 7.49 miles of Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line from :000/001 to :007/043 with 715 AAC, 126/148 MVA. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0007445 ¦ T.0004515 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-11-10 | 69 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | 17 | NA | 115 | NA | NA | NA | NA | 3.002 | Non-IGP | 5799800 | T.0007979 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ T.0007445 ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2021 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7787-E | 2025-12-17 | Approved | 2026 | Engineering more than 50% complete | 3 | 2026-04-08 | 2025-01-10 | 2027-01-28 | Prioritization | NA | TRUE | 136800 | NA ¦ NA | 4522.5286 | 25141.468 | 0 | 0 | 94.8738 | 403.2569 | 3724.0345 | 16164.7556 | 4754.5473 | 0 | 0 | 0 | 4222.1651 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $25,141 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1832 | WRO Generator Network Upgrades |  |  |  | The project proposes to reconductor 45 miles of 115kV Line upgrades with a higher capacity conductor and is a Local Delivery Network Upgrade (LDNU) project tied to the Q1557 electric generation interconnection project. The project scope of work includes the following: • Ripon-Manteca 115 kV Line Reconductor: Reconductor Ripon-Manteca 115 kV Line 2/0 CU and 4/0 ACSR sections with 715.5 AAC, 126/148 MVA • Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line Reconductor: Reconductor Ripon -Manteca 115 kV Line 2/0 CU and 4/0 ACSR sections with 715.5 AAC, 126/148 MVA • Bellota-Riverbank-Melones Sw Sta 115 kV Line 115 kV Line Reconductor: Reconductor 17 miles of Bellota-Riverbank-Melones Sw Sta 115 kV Line (Riverbank Tap to Tulloch Tap) with 477 ACSS 224/224/245/245 MVA. • Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line Reconductor: Reconductor 7.49 miles of Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line from :000/001 to :007/043 with 715 AAC, 126/148 MVA. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0007445 ¦ T.0004515 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-22 | 8 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 0.9 | NA | 115 | NA | NA | NA | NA | 3.002 | Non-IGP | 5799798 | T.0007979 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ T.0007445 ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2021 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-03-01 | 2025-01-10 | 2027-04-13 | Prioritization | NA | TRUE | 136800 | NA ¦ NA | 1645.6155 | 24264.5062 | 0 | 0 | 208.5399 | 547.8744 | 680.737 | 10056.4306 | 12724.6676 | 46.2567 | 0 | 0 | 1437.1513 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $24,265 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1833 | WRO Generator Network Upgrades |  |  |  | The project proposes to reconductor 45 miles of 115kV Line upgrades with a higher capacity conductor and is a Local Delivery Network Upgrade (LDNU) project tied to the Q1557 electric generation interconnection project. The project scope of work includes the following: • Ripon-Manteca 115 kV Line Reconductor: Reconductor Ripon-Manteca 115 kV Line 2/0 CU and 4/0 ACSR sections with 715.5 AAC, 126/148 MVA • Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line Reconductor: Reconductor Ripon -Manteca 115 kV Line 2/0 CU and 4/0 ACSR sections with 715.5 AAC, 126/148 MVA • Bellota-Riverbank-Melones Sw Sta 115 kV Line 115 kV Line Reconductor: Reconductor 17 miles of Bellota-Riverbank-Melones Sw Sta 115 kV Line (Riverbank Tap to Tulloch Tap) with 477 ACSS 224/224/245/245 MVA. • Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line Reconductor: Reconductor 7.49 miles of Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line from :000/001 to :007/043 with 715 AAC, 126/148 MVA. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0007445 ¦ T.0004515 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-10-21 | 90 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | 25.23 | NA | 115 | NA | NA | NA | NA | 3.002 | Non-IGP | 5799799 | T.0007979 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ T.0007445 ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2021 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-03-02 | 2025-01-10 | 2028-03-30 | Prioritization | NA | FALSE | 136800 | NA ¦ NA | 1893.1907 | 43382.1778 | 0 | 0 | 142.277 | 635.0324 | 954.3675 | 787.3919 | 11046.15 | 29722.6855 | 94.2734 | 0 | 1731.677 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $43,382 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1834 | WRO Generator Network Upgrades |  |  |  | The Project is a combined photovoltaic solar and battery energy storage technology-based generation facility with a net output of 500.0 MW to the CAISO controlled grid. The Large Generating Facility and associated Interconnection Facilities connects to the new 230kV switching station (or the new “Q1593 Switching Station”) along PG&E’s Gates-Midway 230kV transmission line in Kettleman City, Kings County, California (the “Project”). | Transmission Line - Other Equipment | Upgrade/Retrofit | NA | T.0008543 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 10 | 94.5324 | 230 | NA | NA | NA | NA | 3.002 | Non-IGP | 5803144 | T.0008735 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | NA | NA | NA | TRUE | Final Certified | 2023-12-01 | EIR | NA | Kern County | NA | NOC: AL 7236-E | 2024-04-05 | Approved | 2024 | Construction (over 75%) | 2 | 2025-11-03 | 2026-09-22 | 2026-03-13 | NA | NA | TRUE | 30284 | NA ¦ NA | 4229.7778 | 4758.9012 | 0 | 0 | 322.4595 | 1316.0645 | 1996.2148 | 1124.1624 | 0 | 0 | 0 | 0 | 3634.7388 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,759 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1835 | SS Loop-in Dos Amigos-Panoche 230kV |  |  | Fresno ¦ Merced | The high level project scope of work includes following: • Build a new 3-bay BAAH, 230 kV Switching Station (SS) near the existing Dos Amigos Pumping Plant (PP). The ultimate bus arrangement should be 6-bay BAAH. • Build the Switching Station with enough room for future installation of two 230/70 kV transformers, a 70 kV bus and line terminations for future connection to the Mercy Springs Switching Station (this is a separate project submitted by PG&E to CAISO through the TPP process). • Disconnect the Los Banos-Dos Amigos PP 230 kV and the Dos Amigos PP-Panoche 230 kV line terminals at Dos Amigos PP. • Build two 230 kV lines (less than 2 miles each) to loop the Los Banos-Dos Amigos PP and the Dos Amigos PP-Panoche 230 kV Lines into the new Switching Station • Build two 230 kV lines from the new Switching Station to Dos Amigos PP. • Upgrade associated equipment at Los Banos and Panoche substations to meet the required ampacity of the lines. • Acquire land for the new Switching Station | Transmission Line - Multiple | New | NA | T.0009550 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-14 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Corrosion |  | 4 | NA | 230 | NA | NA | NA | NA | 3.002 | Non-IGP | 5804624 | T.0009177 | New SS for Los Banos-Panoche 230kV | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-02-28 | 2028-05-01 | 2030-03-27 | Scope Change | NA | FALSE | $50,000 ¦ $100,000 | NA ¦ NA | 9.7321 | 7157.9572 | 0 | 0 | 0 | 0 | 0 | 448.9506 | 747.358 | 1031.825 | 3359.1783 | 1570.6453 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $7,158 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1836 | SS Loop-in Los Banos-Dos Amigos 230kV |  |  | Fresno ¦ Merced | The high level project scope of work includes following: • Build a new 3-bay BAAH, 230 kV Switching Station (SS) near the existing Dos Amigos Pumping Plant (PP). The ultimate bus arrangement should be 6-bay BAAH. • Build the Switching Station with enough room for future installation of two 230/70 kV transformers, a 70 kV bus and line terminations for future connection to the Mercy Springs Switching Station (this is a separate project submitted by PG&E to CAISO through the TPP process). • Disconnect the Los Banos-Dos Amigos PP 230 kV and the Dos Amigos PP-Panoche 230 kV line terminals at Dos Amigos PP. • Build two 230 kV lines (less than 2 miles each) to loop the Los Banos-Dos Amigos PP and the Dos Amigos PP-Panoche 230 kV Lines into the new Switching Station • Build two 230 kV lines from the new Switching Station to Dos Amigos PP. • Upgrade associated equipment at Los Banos and Panoche substations to meet the required ampacity of the lines. • Acquire land for the new Switching Station | Transmission Line - Multiple | New | NA | T.0009550 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-14 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Corrosion |  | NA | NA | 230 | NA | NA | NA | NA | 3.002 | Non-IGP | 5804623 | T.0009177 | New SS for Los Banos-Panoche 230kV | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2031-04-30 | 2028-05-01 | 2031-05-28 | Scope Change | NA | FALSE | $50,000 ¦ $100,000 | NA ¦ NA | 12.6165 | 7541.8358 | 0 | 0 | 0 | 0 | 0 | 330.6352 | 784.7897 | 1207.3227 | 656.2079 | 2923.7443 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $7,542 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1837 | Dos Amigos Line Mod (2 ckts into new SS) |  |  | Fresno ¦ Merced | The high level project scope of work includes following: • Build a new 3-bay BAAH, 230 kV Switching Station (SS) near the existing Dos Amigos Pumping Plant (PP). The ultimate bus arrangement should be 6-bay BAAH. • Build the Switching Station with enough room for future installation of two 230/70 kV transformers, a 70 kV bus and line terminations for future connection to the Mercy Springs Switching Station (this is a separate project submitted by PG&E to CAISO through the TPP process). • Disconnect the Los Banos-Dos Amigos PP 230 kV and the Dos Amigos PP-Panoche 230 kV line terminals at Dos Amigos PP. • Build two 230 kV lines (less than 2 miles each) to loop the Los Banos-Dos Amigos PP and the Dos Amigos PP-Panoche 230 kV Lines into the new Switching Station • Build two 230 kV lines from the new Switching Station to Dos Amigos PP. • Upgrade associated equipment at Los Banos and Panoche substations to meet the required ampacity of the lines. • Acquire land for the new Switching Station | Transmission Line - Multiple | New | NA | T.0009550 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-14 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 4 | NA | 230 | NA | NA | NA | NA | 3.002 | Non-IGP | 5804625 | T.0009177 | New SS for Los Banos-Panoche 230kV | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-01-05 | 2028-05-01 | 2027-01-08 | NA | NA | TRUE | $50,000 ¦ $100,000 | NA ¦ NA | 2.2587 | 147.0413 | 0 | 0 | 0 | 0 | 0 | 80.6253 | 66.416 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $147 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1838 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-21 | 60 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 104.5 | NA | 500 | NA | NA | NA | NA | 3.002 | Non-IGP | 5805808 | T.0009383 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2023 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7656-E | 2025-07-30 | Approved | 2025 | Construction (10%-25%) | 2 | 2026-03-16 | 2028-08-01 | 2027-02-16 | NA | NA | TRUE | 94899 | NA ¦ NA | 1438.9286 | 4283.5579 | 0 | 0 | 2.0038 | 365.3038 | 850.65 | 2686.8617 | 155.8148 | 93.7141 | 106.3734 | 22.8362 | 1217.9577 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 1379.3805 | 0% | 100% ¦ $4,284 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1839 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Transmission Line - Conductor | New | NA | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-21 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 15 | NA | 500 | NA | NA | NA | NA | 3.002 | Non-IGP | 5809671 | T.0009383 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2023 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7656-E | 2025-07-30 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-08-07 | 2028-08-01 | 2027-06-22 | NA | NA | TRUE | 94899 | NA ¦ NA | 459.1608 | 8867.0678 | 0 | 0 | 0 | 170.8396 | 256.0991 | 1515.7459 | 6924.3831 | 0 | 0 | 0 | 426.9387 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $8,867 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1840 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Energy Storage System (BESS) Large Generating Facility with a net output of 500MW connecting to Pacific Gas and Electric Company’s (PG&E’s) Tesla Substation in Tracy, San Joaquin County, CA. The project scope of work includes following: Interconnection Reliability Network Upgrades (IRNU-A): Tesla Substation: Outdoor work: • Install 500 kV circuit breaker (CB) and associated equipment to complete existing Bay 4. • Modify Bay 3 for Q1922 Terminal • Install Wave Trap and Line Tuner for relocated Tesla – Metcalf 500 kV line. • Modify existing 500 kV building to accommodate Set B and D line relays in a different section of the building to comply with PG&E 500 kV building standard (i.e., firewall). Indoor work： • Replace the existing Bay 4 CB 542 & 642 Breaker Failure/Reclosing relays with new SEL-451 relays. • Relocate Bay 5 relays to allow Bay 4 expansion. T-Line work: • Relocate the 500 kV Tesla - Metcalf line terminal to the Bay 4 with one (1) single circuit 3-phase structure and conductors • Raise Tesla - Tracy 500 kV and Tesla - Los Banos 500 kV lines to allow the Customer’s Gen-Tie line to cross underneath | Transmission Line - Multiple | New | NA | T.0010881 ¦ T.0010880 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-12-08 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 500 | NA | NA | NA | NA | 3.002 | Non-IGP | 5813446 | T.0010805 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-05-08 | 2031-04-21 | 2030-08-30 | NA | NA | FALSE | 22977 | NA ¦ NA | 8.6797 | 1549.4302 | 0 | 0 | 0 | 0 | 1.8899 | 102.2 | 128.229 | 139.176 | 134.0576 | 1043.8777 | 1.8899 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,549 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1841 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA 94085. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-11-17 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 11.37 | NA | 115 | NA | NA | NA | NA | 3.002 | Non-IGP | 5810600 | T.0010809 | Private Load Interconnection Project | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | On Hold | 4 | 2030-08-23 | NA | 2030-09-18 | NA | NA | FALSE | NA | NA ¦ NA | 269.3326 | 23106.7206 | 0 | 0 | 0 | 242.6692 | 26.6634 | 1217.0741 | 5169.8742 | 2097.5724 | 1292.7355 | 12741.6444 | 269.3326 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $23,107 | Type 4 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1842 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA 94085. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2025-10-29 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 7.17 | NA | 115 | NA | NA | NA | NA | 3.002 | Non-IGP | 5810602 | T.0010809 | Private Load Interconnection Project | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | On Hold | 4 | 2031-01-16 | NA | 2031-12-10 | NA | NA | FALSE | NA | NA ¦ NA | 250.6539 | 24773.5106 | 0 | 0 | 0 | 141.9403 | 105.5702 | 83.7381 | 3496.7953 | 1510.2355 | 2086.3963 | 7067.7045 | 247.5105 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $24,774 | Type 4 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1843 | WRO Generator Network Upgrades |  |  |  | The Project is a combination of solar and Battery Energy Storage System (BESS) 250 MW Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) new 230kV Switching Station in Linden, San Joaquin County, CA. Below is the high-level project scope to loop in a new 230kV switching station on existing 230kV Racho Seco PP - Bellota #1 line and associated work to interconnect a 350MW generation. Reliability Network Upgrades (RNU): New 230kV Switching Station: • Two (2) 230kV Breaker-and-a-half (BAAH) bays with ultimate arrangement of five (5) bays. o Install five (5) 230kV circuit breakers (CB) with breaker and line disconnects. o Install four (4) dead-end structures, bus support structures, foundation, grounding system. • Install one (1) 98” Modular Protection Automation and Control (MPAC) building with line, breaker and bus differential relay panels. • Install One (1) stand-alone 34’ battery building including all necessary concrete foundations, rebar and anchor bolts. • Clear, Grade, and improve approximately 1 mile of roadway for access road to the switching station. • Install redundant communication paths between the switching stations and remote ends as necessary including the microwave tower. Rancho-Seco PP Substation: • Install Direct Transfer Trip (DTT) scheme between from Switching Station and Rancho-Seco PP Substation including new IT T1 infrastructure for the communication circuits. Bellota Substation: • Replace the existing line and breaker relays for the 230kV Switching Station - Bellota line. • Install redundant communication paths between the Switching Station and any remote ends as necessary including the microwave tower. • Install a DTT scheme between Switching Station and Bellota Substation including new IT T1 infrastructure for the communication circuits. T-Line work: • PG&E T-Line to install six (6) TSPs and conductor to route the following two (2) 230 kV lines into Switching Station: o Switching Station - Bellota Substation 230 kV. o Switching Station - Rancho-Seco PP Substation 230 kV. | Transmission Line - Conductor | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-12-04 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 0.1 | NA | 230 | NA | NA | NA | NA | 3.002 | Non-IGP | 5813738 | T.0010853 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-03-13 | 2030-11-04 | 2030-10-11 | NA | NA | FALSE | 1914 | NA ¦ NA | 37.1913 | 2440.0187 | 0 | 0 | 0 | 0 | 25.511 | 13.9442 | 314.8965 | 1794.8757 | 157.5474 | 133.2439 | 25.5109 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,440 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1844 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Energy Storage System (BESS) Large Generating Facility with a net output of 300MW connecting to Pacific Gas and Electric Company’s (PG&E’s) Templeton-Gates 230kV line looped into a new Switching Station, Fresno County, CA. | Transmission Line - Multiple | Relocate | NA | T.0010031 ¦ T.0001650 ¦ T.0007722 ¦ T.0010879 ¦ T.0000154 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 3.002 | Non-IGP | 5813917 | T.0010878 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-06-06 | 2030-08-18 | 2030-09-30 | NA | NA | FALSE | 34420 | NA ¦ NA | 1.0784 | 94.0776 | 0 | 0 | 0 | 0 | 0.0889 | 66.5077 | 12.1094 | 5.3312 | 5.722 | 4.3185 | 0.0889 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $94 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1845 | Tesla-Tracy 230kV Line #1 Relocation |  |  | San Joaquin | The project scope of work includes following: General Reliability Network Upgrades (GRNU): Tesla Substation: • Relocate a Tesla – Tracy #2 230kV line to Bus Section C into BAAH Bay position where Tesla- Newark #2 line resides today and shift Tesla - Newark #2 line to a new BAAH bay. • Install nine (9) 230kV T-line structures (4000 feet of new line). • Install two (2) circuit breakers and associated equipment in the new BAAH bay. • Install new relays and revise existing relay schemes as needed. | Transmission Line - Multiple | Relocate | NA | T.0011168 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.2961 | 230 | NA | NA | NA | NA | 3.002 | Non-IGP | 5816100 | T.0010881 | Tesla 230kV & 500kV Mitigation | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-10-12 | 2031-04-18 | 2031-04-18 | NA | NA | FALSE | 30878 | NA ¦ NA | 12.3332 | 6167.5587 | 0 | 0 | 0 | 0 | 4.4707 | 208.9062 | 403.8876 | 525.2831 | 3711.5228 | 971.1985 | 4.4707 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $6,168 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1846 | WRO Generator Network Upgrades |  |  |  | The Project is a Solar PV and Battery Energy Storage System (BESS) Large Generating Facility with a net output of 125MW connecting to Pacific Gas and Electric Company’s (PG&E’s) Excelsior 115kV Switching Station in Fresno County, CA. | Transmission Line - Multiple | New | NA | T.0009194 ¦ T.0009177 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-13 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 3.002 | Non-IGP | 5560567 | T.0010887 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-04-12 | 2029-04-18 | 2028-05-03 | NA | NA | FALSE | 2176 | NA ¦ NA | 0 | 6673.7703 | 0 | 0 | 0 | 0 | 0 | 400.3248 | 3640.3564 | 2198.8738 | 434.2153 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $6,674 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1847 | WRO Generator Network Upgrades |  |  |  | The IC plans to install a Solar PV and Storage generation plant, comprised of 12 Solar PV Inverters each rated at 3.465 MW and a Battery Energy Storage System (“BESS”) comprised of 12 Inverters each rated at 3.465 MW, with a maximum gross output of 37.464 MW. • This project will build out a 3rd BAAH bay (Bay 3) at Crescent SW Sta. This bay will include two breakers and one line. This bay will follow the existing PGE Electrical Design Standard drawing 4042040. • Reconductor 4.7 miles rated ampacity 1400amp • Gentie line design with two TSP • Replace CB 22 at Helm Sub to meet 1400amp rating | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-04-03 | 62 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ False | FALSE | NA |  | 4.7 | NA | 70 | NA | NA | NA | NA | 3.002 | Non-IGP | 5814038 | T.0010934 | WRO Generator Network Upgrades | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-10-28 | 2027-12-03 | 2027-11-29 | NA | NA | TRUE | 13963 | NA ¦ NA | 172.4474 | 9279.8983 | 0 | 0 | 0 | 0 | 136.3209 | 549.245 | 8579.1719 | 15.1604 | 0 | 0 | 136.321 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $9,280 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1848 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Hybrid project, which is a Solar PV and Storage generation plant, with a net output of 110 MW to the CAISO Controlled Grid. The Large Generating Facility connects to PG&E's New 115kV Switching Station looped into Crazy Horse Canyon Sw Sta —Hollister 115 kV line in San Benito County, California. | Transmission Line - Multiple | Relocate | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-01 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 3.002 | Non-IGP | 5814525 | T.0011010 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-06-24 | 2030-09-19 | 2030-10-15 | NA | NA | FALSE | 36997 | NA ¦ NA | 21.9771 | 2187.2627 | 0 | 0 | 0 | 0 | 16.8032 | 39.2258 | 337.09 | 354.1647 | 710.8242 | 729.1549 | 16.8032 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,187 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1849 | Partially Reimbursed Elec Trans WRO |  |  | NA | Bucket for WRO relocation work. | Substation - Multiple | New | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5716640 | NA | NA | NA | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 6614.8309 | 6614.8309 | -29.3011 | 0.665 | 0.4508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6614.8309 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | -29.4082 | 0.56305 | 0.38164 | 0 | 0 | 0 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1850 | 82-WRO Partially Reimb - PRJ |  |  | NA | Bucket for partially reimbursable WRO work | Substation - Multiple | Relocate | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | NA | 5509302 | NA | NA | NA | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 4981.4623 | 4981.4623 | -42.7795 | 0.7084 | 0.0564 | 0 | -104.864 | 0 | 0 | 0 | 0 | 0 | 4981.4623 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 ¦ 2026 | -42.8289 | 0.51715 | 0.05345 | 0 | -95.5845 | 0 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1851 | Fully Reimbursed ElecTransmission WRO |  |  | NA | Bucket for fully reimbursable WRO work | Substation - Multiple | New | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | NA | NA | 5716639 | NA | NA | NA | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 9816.6684 | 9816.6684 | -23.229 | -32.6412 | -1.4265 | 0 | 110.2435 | 0 | 0 | 0 | 0 | 0 | 9816.6684 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | -39.3451 | -31.0872 | -1.4265 | -0.00085 | 92.5714 | 0 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1852 | SMARTVILLE-MARYSVILLE 60KV RELO-LOMARICA |  |  | Marysville, Yuba ¦ Smartsville CDP, Yuba ¦ Yuba | Caltrans has a proposed project to upgrade SR 20 in Yuba County. The project will upgrade the roadway alignment by widening existing roadway shoulders. Caltrans has requested the Utility to relocate approximately 2.1 miles of Smartville - Marysville 60kv with 12 kV underbuild from Pole No. 011/214 to 012/251, which runs along SR 20 near Loma Rica Road. Work consists of installation of 39 transmission poles (3 TPD, 3 HPD, 33 T1), 2 distribution poles, 4 guy stubs, 1 clearance pole with all associated framing and guying, and removal of 40 wood poles and 2 LDSPs | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-09-12 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 2.1 | NA | 60 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5774833 | T.0002940 | SMARTVILLE-MARYSVILLE 60KV RELO-LOMARICA | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2016-08-17 | IS/MND | NA | CalTrans | NA | NOC: AL 5438-E | 2018-12-07 | Approved | 2019 | Operational | 1 | 2020-05-01 | 2019-06-30 | 2020-06-02 | Customer Action | NA | FALSE | 1914 | NA ¦ NA | 3429.2982 | 3429.2982 | 220.5562 | 0 | 0 | 0 | 32.3974 | 4.07 | 0 | 0 | 0 | 0 | 3425.2282 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2025 ¦ 2026 | 205.3166 | 0 | 0 | 0 | 30.1588 | 3.7888 | 0% | 100% ¦ $3,429 | NA | NA ¦ NA | NA | 0% | 100% | NA
1853 | KASSON-CARBONA 60KV RELO MACARTHUR DR |  |  | San Joaquin ¦ Tracy, San Joaquin | The City of Tracy is performing a road widening project on MacArthur Drive between Schulte Road and Valpico Road in Tracy, CA. In order to accommodate the City of Tracy’s project, Pacific Gas and Electric Company (PG&E) will need to relocate 16 transmission poles on the Kasson – Carbona 60 kV Line and a total of 10 distribution poles, guy stubs, and service poles. This project precedes the Corral Hollow Relocation Project, which proposes to relocate 12 wood poles on the Kasson – Carbona 60 kV line due to the widening of Corral Hollow Road beteween West Schulte Road and West Linne Road in the City of Tracy, California. The Corral Hollow Relocation Project has a Q4 2019 forecasted construction date. | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-10-24 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 1 | NA | 60 | NA | 3 | NA | NA | NA | NA | 5526124 | T.0003061 | Kasson-Carbona - Macarthur Blvd Tracy | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 4838-E | 2016-05-05 | Approved | 2016 | Operational | 1 | 2019-01-07 | 2019-01-31 | 2019-02-15 | NA | NA | FALSE | 1659 | NA ¦ NA | 2379.1262 | 2379.1262 | 0 | -58.1861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2379.1262 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2026 | 0 | -54.3793 | 0 | 0 | 0 | 0 | 0% | 75% ¦ $2,379 | NA | NA ¦ NA | NA | 0% | 100% | NA
1854 | SR 120 Manteca #1 60 kV Relo |  |  | Grayson CDP, Stanislaus ¦ Manteca, San Joaquin ¦ San Joaquin ¦ Stanislaus | The project proposes to relocate a section of the Manteca #1 60 kV Line to accommodate the Caltrans and the City of Manteca’s planned overcrossing widening project at the overcrossing of SR 120 at Union St, in Manteca, California. The project will need to relocate approximately 0.4 miles of the Manteca #1 60 kV Line, and its associated distribution under-build, from Pole Nos. 1/27 to 1/31. | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-08-22 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.4 | NA | 60 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5777125 | T.0003411 | Manteca #1 60 kV Relo- SR 120 TSP PL_ENG | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5488-E | 2019-03-06 | Approved | 2019 | Operational | 1 | 2020-02-14 | 2019-06-21 | 2020-02-20 | Customer Action | NA | FALSE | 3700 | NA ¦ NA | 1063.6643 | 1063.6643 | -91.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063.6643 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -91.4956 | 0 | 0 | 0 | 0 | 0 | 0% | 50% ¦ $1,064 | NA | NA ¦ NA | NA | 0% | 100% | NA
1855 | TESLA-STOCKTON 115KV TRACY REPLACEMENT |  |  | Alameda ¦ Lathrop, San Joaquin ¦ Manteca, San Joaquin ¦ Ripon, San Joaquin ¦ San Joaquin ¦ Tracy, San Joaquin | Replace 5 wood poles on Corral Hollow Road with wood poles and Tubular Steel Poles. Relocate the Tesla-Stockton Cogen Jct 115kV Line to support the City of Tracy’s road widening project in San Joaquin County, CA. | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-11-10 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.5 | NA | 115 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5528514 | T.0003697 | TESLA-STOCKTON 115KV TRACY REPLACEMENT | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5687-E | 2019-11-15 | Approved | 2020 | Operational | 1 | 2020-09-23 | 2020-09-17 | 2020-10-12 | NA | NA | FALSE | 2560 | NA ¦ NA | 1439.3398 | 1439.3398 | 29.0227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1439.3398 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | 28.6054 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,439 | NA | NA ¦ NA | NA | 0% | 100% | NA
1856 | PEASE-MARYSVILLE-HARTER 60KV LEVEE 2B |  |  | Marysville, Yuba ¦ Smartsville CDP, Yuba ¦ Yuba | The Marysville Levee District is initiating Phase B of their Marysville Ring Levee Project, which will upgrade an approximately 1-mile section of the levee between Highway 70 and Ramirez Street in Marysville, CA. This levee upgrade project is in conflict with facilities on three of PG&E’s transmission lines in the area: the Nicolaus – Marysville, Smartville – Marysville and Pease – Marysville – Harter 60 kV lines. Four transmission line structures will need to be relocated to accommodate the levee upgrade project. In addition, a 3-wood pole structure is expected to be replaced with tubular steel pole at the toe of the levee. | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-09-12 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 0.12 | NA | 60 | NA | 3 | 6. Customer commitments | NA | 5.1001 | Non-IGP | 5528516 | T.0003703 | Pease-Marysville-Harter 60kV Levee 2B | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6187-E | 2021-05-05 | Approved | 2021 | Operational | 1 | 2024-04-08 | 2022-08-31 | 2024-11-22 | Prioritization | NA | FALSE | 3500 | NA ¦ NA | 2087.3741 | 2087.3741 | 127.3449 | 353.9298 | 426.5024 | 911.7752 | 67.8136 | 82.3774 | 0 | 0 | 0 | 0 | 2004.9967 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 113.177 | 314.6311 | 331.003 | 767.6119 | 57.0913 | 69.3525 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | NA
1857 | PEASE-MARYSVILLE-HARTER 60KV LEVEE 3 |  |  | Marysville, Yuba ¦ Sutter ¦ Yuba ¦ Yuba City, Sutter | Relocate the Smartville – Marysville and Pease – Marysville – Harter 60 kV lines to support the Marysville Ring Levee Phase 3 Project by the Marysville Levee District in Marysville, CA. | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-09-15 | 59 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 1.7 | NA | 60 | NA | 3 | 6. Customer commitments | NA | 5.1001 | Non-IGP | 5530048 | T.0003956 | Pease-Marysville-Harter 60kV Levee 3 | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6187-E | 2021-05-05 | Approved | 2021 | Operational | 1 | 2024-04-08 | 2021-06-30 | 2024-11-22 | Permitting | NA | TRUE | 13800 | NA ¦ NA | 7760.8971 | 7765.6401 | 434.3083 | 600.0252 | 85.8423 | 4009.625 | 1540.9616 | 29.8095 | 0 | 0 | 0 | 0 | 7735.8306 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 406.3209 | 549.1137 | 79.8094 | 3727.8372 | 1432.6662 | 23.3048 | 0% | 17% ¦ $7,766 | NA | NA ¦ NA | NA | 0% | 100% | NA
1858 | TABLE MOUNTAIN-PEACHTON 60 KV RELOCATION |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Durham CDP, Butte | The project proposes to remove and relocate 11 transmission poles along State Road 99 at the Cottonwood Creek Bridge. The project scope of work includes the following: Remove and relocate 11 transmission poles staying within the Caltrans ROW. Engineering will determine if alterations of transmission poles adjacent to these three poles will be required due to altered forces from this project. . | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2026-03-18 | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 1 | NA | 60 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5530519 | T.0004028 | Table Mountain-Peachton 60kV:Relocation | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-09 | 2019-12-31 | 2020-10-12 | Customer Action | NA | FALSE | 945 | NA ¦ NA | 1138.1046 | 1138.1046 | -9.4746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1138.1046 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2026 | -7.6474 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,138 | NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1859 | SALINAS_LAURELESS_60kV-RELO-S_DAVIS_RD |  |  | Boronda CDP, Monterey ¦ Carmel Valley Village CDP, Monterey ¦ Monterey ¦ Monterey, Monterey ¦ Salinas, Monterey | Relocate transmission poles on the Salinas-Laureles 60 kV Line to facilitate Monterey County’s SR 20 road widening and bridge reconstruction. | Transmission Line - Pole/Tower | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-12-10 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 3 | 6. Customer commitments | 13 | 3.002 | Non-IGP | 5531823 | T.0004279 | Salinas-Laureles 60kV Pole Relo Davis Rd | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7841-E | 2026-02-17 | Approved | 2026 | Engineering more than 50% complete | 3 | 2026-08-18 | 2020-11-30 | 2026-12-01 | Prioritization | NA | TRUE | 3500 | NA ¦ NA | 306.9017 | 1825.9917 | 27.6126 | 2.7726 | -417.974 | 11.9654 | 162.7008 | 1510.2186 | 25.9749 | 0 | 0 | 0 | 289.7982 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 21.813 | 2.1902 | -330.1852 | 31.6917 | 156.9973 | 16.5039 | 0% | 50% ¦ $1,346 | NA | NA ¦ NA | NA | 0% | 100% | NA
1860 | Lakeville #2 60kV RELO Novato Caltrans |  |  | Marin ¦ Novato, Marin ¦ Petaluma, Sonoma ¦ Sonoma | The project scope of work addresses Poles A006/126 to A009/167 on the Lakeville #2 60kV line: • Relocate and replace forty (40) existing wood transmission poles with new wood transmission poles. • Relocate and upgrade two (2) wood transmission poles with new tubular steel poles (TSP). • Relocate 13,943 circuit feet of 1/0-7 CU and 397.5-19 AAC 60 kV conductor. o Note, no changes to existing conductor size. • Relocate distribution under-build. • Relocate and replace four (4) field switches. Caltrans has initiated the Highway 101 Improvement Project in Marin County, which proposes improvements to a segment of Highway 101, in Novato, CA. These improvements are in conflict with 42 overhead transmission poles on PG&E’s Lakeville #2 60 kV Line. This project proposes to relocate PG&E’s transmission infrastructure in conflict | Transmission Line - Pole/Tower | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-03-24 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 3.002 | Non-IGP | 5555990 | T.0004281 | Lakeville #2 60kV Pole Relo Novato CT | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-11-02 | 2024-05-31 | 2026-11-23 | Prioritization | NA | TRUE | 6235 | NA ¦ NA | 14.2052 | 460.2441 | 0 | 0 | 0 | 0 | 12.8891 | 461.103 | -13.748 | 0 | 0 | 0 | 12.8891 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 12.1979 | 1.2455 | 0% | 50% ¦ $1,346 | NA | NA ¦ NA | NA | 0% | 100% | NA
1861 | LAKEVILLE_#2_60kV-RELO-NOVATO_CALTRNS101 |  |  | Marin ¦ Novato, Marin ¦ Petaluma, Sonoma ¦ Sonoma | The project scope of work addresses Poles A006/126 to A009/167 on the Lakeville #2 60kV line: • Relocate and replace forty (40) existing wood transmission poles with new wood transmission poles. • Relocate and upgrade two (2) wood transmission poles with new tubular steel poles (TSP). • Relocate 13,943 circuit feet of 1/0-7 CU and 397.5-19 AAC 60 kV conductor. o Note, no changes to existing conductor size. • Relocate distribution under-build. • Relocate and replace four (4) field switches. Caltrans has initiated the Highway 101 Improvement Project in Marin County, which proposes improvements to a segment of Highway 101, in Novato, CA. These improvements are in conflict with 42 overhead transmission poles on PG&E’s Lakeville #2 60 kV Line. This project proposes to relocate PG&E’s transmission infrastructure in conflict | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-03-24 | 100 | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | 3 | NA | 60 | NA | 3 | 6. Customer commitments | NA | 5.1001 | Non-IGP | 5531919 | T.0004281 | Lakeville #2 60kV Pole Relo Novato CT | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-04-23 | 2024-05-31 | 2026-05-04 | Prioritization | NA | TRUE | 6235 | NA ¦ NA | 1525.0359 | 1279.5701 | 165.4202 | 108.0173 | 70.4747 | 107.9346 | 353.9563 | -33.7374 | 0 | 0 | 0 | 0 | 1313.3075 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 165.4202 | 62.7959 | 66.3935 | 101.6842 | 340.7284 | 200.6392 | 0% | 50% ¦ $1,346 | NA | NA ¦ NA | NA | 0% | 100% | NA
1862 | Lincoln Pleas. Grove - Pole Replace |  |  | Lincoln, Placer ¦ Placer | The County of Placer is proposing the Placer Parkway project in Placer County which will construct a new transportation facility connecting State Route (SR) 65 to SR 99. The alignment of the new transportation facility is in conflict with the height of the existing fiberglass pole 006/132 and Tubular Steel Pole 006/133 on the Lincoln-Pleasant Grove 115 kV Line. To mitigate this conflict, this project proposes to replace Poles 006/132 and 006/133 with Tubular Steel Poles, approximately 10’ from the existing location. Pole 006/133 currently supports three transmission line switches (including Switch 117, 119, and 145), which is not allowed under current PG&E transmission line standards (TD-1006S). To address the non-compliance, Switch 145 will be relocated to Pole 000/001 on the Rio Bravo 115 kV Tap Line and Switch 119 will be relocated to Pole 006/132 on the Lincoln-Pleasant Grove 115kV line. Switch 117 will remain on Pole 006/133 on the Lincoln-Pleasant Grove 115kV line. All three inline switches will be replaced with SCADA SEECO side-by phase switches per PG&E switch standards (TD-1006S). Furthermore, to support Switch 145, the existing wood transmission Pole 000/001 will be replaced with a new TSP. The new transportation facility will also affect the grading elevation of the wood transmission Poles impacting Rio Bravo (Rocklin) 115 kV Tap Line (000/002, 000/003, and 000/004) Poles. This will be addressed by rerouting Rio Bravo (Rocklin) 115kv Tap and replacing these poles with three new LDSPs. Note, as a separate project, the existing distribution underbuilt between Lincoln – Pleasant Grove 115kV Line (006/132, and 006/133) Poles will be relocated underground. | Transmission Line - Pole/Tower | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2026-04-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | 6. Customer commitments | NA | 5.211 | Non-IGP | 5535360 | T.0004688 | Lincoln Pleasant Grove & Rio Bravo Relo | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7768-E | 2025-11-26 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-04-17 | 2026-04-15 | 2026-04-24 | NA | NA | TRUE | 3720 | NA ¦ NA | 205.9578 | 54.8133 | 19.8434 | 0 | -243.3059 | 52.8038 | -38.6876 | 7.9733 | 0 | 0 | 0 | 0 | 46.84 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 19.8434 | 0 | -243.3059 | 52.8038 | -40.1774 | 154.0571 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | NA
1863 | Rio Bravo Tap 115 kV - Poles Repl |  |  | Placer | The County of Placer is proposing the Placer Parkway project in Placer County which will construct a new transportation facility connecting State Route (SR) 65 to SR 99. The alignment of the new transportation facility is in conflict with the height of the existing fiberglass pole 006/132 and Tubular Steel Pole 006/133 on the Lincoln-Pleasant Grove 115 kV Line. To mitigate this conflict, this project proposes to replace Poles 006/132 and 006/133 with Tubular Steel Poles, approximately 10’ from the existing location. Pole 006/133 currently supports three transmission line switches (including Switch 117, 119, and 145), which is not allowed under current PG&E transmission line standards (TD-1006S). To address the non-compliance, Switch 145 will be relocated to Pole 000/001 on the Rio Bravo 115 kV Tap Line and Switch 119 will be relocated to Pole 006/132 on the Lincoln-Pleasant Grove 115kV line. Switch 117 will remain on Pole 006/133 on the Lincoln-Pleasant Grove 115kV line. All three inline switches will be replaced with SCADA SEECO side-by phase switches per PG&E switch standards (TD-1006S). Furthermore, to support Switch 145, the existing wood transmission Pole 000/001 will be replaced with a new TSP. The new transportation facility will also affect the grading elevation of the wood transmission Poles impacting Rio Bravo (Rocklin) 115 kV Tap Line (000/002, 000/003, and 000/004) Poles. This will be addressed by rerouting Rio Bravo (Rocklin) 115kv Tap and replacing these poles with three new LDSPs. Note, as a separate project, the existing distribution underbuilt between Lincoln – Pleasant Grove 115kV Line (006/132, and 006/133) Poles will be relocated underground. | Transmission Line - Pole/Tower | Replace | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-07-19 | 39 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 | NA | NA | 6. Customer commitments | NA | 5.211 | Non-IGP | 5538680 | T.0004688 | Lincoln Pleasant Grove & Rio Bravo Relo | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL 7768-E | 2025-11-26 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-04-17 | 2026-04-15 | 2026-04-24 | NA | NA | TRUE | 3720 | NA ¦ NA | 70.517 | 1255.555 | 3.0394 | 0 | -87.8419 | 49.4384 | -47.9651 | 1252.6348 | 0 | 0 | 0 | 0 | 2.9202 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 2.783 | 0 | -80.4274 | 45.2655 | -43.9165 | 61.8911 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | NA
1864 | PALERMO-OROVILLE#2 60KV: RELO CALT HW162 |  |  | Butte ¦ Oroville East CDP, Butte ¦ Oroville, Butte ¦ Palermo CDP, Butte ¦ South Oroville CDP, Butte | Relocate and replace 18 wood poles, 4 guy stubs, and add 2 wood poles on the Palermo - Oroville #2 60 kV line. Caltrans is proposing to widen SR 162 from Foothill Boulevard in Oroville, California to the east for approximately 1.4 miles. The route widening plans are in conflict with PG&E’s Palermo-Oroville #2 60KV line in approximately 18 locations, and with an Electric Distribution (ED) line along the same route. This project will relocate the facilities onto a new Electric Transmission (ET) line with ED underbuilt to support Caltrans widening plans on Hwy 162. Caltrans has requested PG&E to relocate 18 conflicting wood poles on the Palermo-Oroville #2 60KV line to accommodate the road widening project. Some poles will be replaced in the same location while others will be replaced and relocated. The two new poles will be wood poles. | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-08-28 | 56 | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Subsidence |  | 1.4 | NA | 60 | NA | NA | 6. Customer commitments | NA | NA | NA | 5531454 | T.0004918 | Palermo-Oroville#2 60kV: Relo CalT HW162 | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5982-E | 2020-10-26 | Approved | 2020 | Operational | 1 | 2021-05-06 | 2022-05-01 | 2022-05-13 | NA | NA | FALSE | 1692 | NA ¦ NA | 1375.7685 | 1375.7685 | 263.4262 | 1710.1765 | -842.5373 | 0.5744 | 1.7169 | 0.2908 | 0 | 0 | 0 | 0 | 1375.4777 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 235.5736 | 1530.2592 | -753.9324 | 0.514 | 1.5363 | 0.26022 | 0% | 50% ¦ $1,376 | NA | NA ¦ NA | NA | 0% | 100% | NA
1865 | WHEELER RIDGE-WEEDPATCH 70:Relo-184 |  |  | Bakersfield, Kern ¦ Kern ¦ Weedpatch CDP, Kern | This project proposes to relocate seven (7) transmission wood poles on Wheeler Ridge – Weedpatch 70 kV Line in support of Caltrans’ roundabout project on Sunset Boulevard in Bakersfield, CA | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-11-26 | 71 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.25 | NA | 70 | NA | NA | 6. Customer commitments | NA | NA | NA | 5536900 | T.0004942 | Wheeler Ridge-Weepatch 70 kV: Relo-184 | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5944-E | 2020-09-10 | Approved | 2020 | Operational | 1 | 2021-11-15 | 2020-11-01 | 2021-11-23 | Customer Action | NA | FALSE | 920 | NA ¦ NA | 1001.4398 | 1001.4398 | 665.1398 | 29.5542 | 0 | 0.3957 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.4398 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 ¦ 2026 | 546.46 | 24.2809 | 0 | 0.32507 | 0 | 0 | 0% | 100% ¦ $1,001 | NA | NA ¦ NA | NA | 0% | 100% | NA
1866 | Atwater - El Capitan 115 kV Relocation |  |  | Atwater, Merced ¦ Merced ¦ Merced, Merced | Merced County is requesting the relocation of the towers 011/080 and 01/081 on the Atwater-El Capitan 115kV line located in Merced, CA as a part of their Atwater-Merced Expressway Project. | Transmission Line - Pole/Tower | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-11-10 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 3.002 | Non-IGP | 5546480 | T.0007496 | Atwater - El Capitan 115 kV Relocation | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-05-28 | NA | 2027-06-11 | NA | NA | TRUE | NA | NA ¦ NA | 328.8041 | 1283.0247 | -3.7919 | 2.9312 | 44.6662 | 110.1923 | 154.7898 | 411.927 | 562.3102 | 0 | 0 | 0 | 308.7875 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | -3.7919 | 2.9324 | 44.6662 | 110.1923 | 154.7898 | 20.0166 | 0% | 50% ¦ $1,346 | NA | NA ¦ NA | NA | 0% | 100% | NA
1867 | Stockton A-Weber #2 60kV Pole Relo |  |  | Kennedy CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | San Joaquin Regional Rail Commission (SJRRC) is shifting 2 railroad lines and will be constructing a flyover bridge for their grade separation project in Stockton, California. Preliminary customer designs indicate that the shifting of the 2 railroad lines and the new flyover bridge will result into insufficient electrical clearances between the existing T-Line and the upcoming infrastructure. To mitigate clearance issues, the T-Line poles 000/019, 000/020, 000/021 and 000/027, 000/028 of Stockton A-Weber #3 and Stockton A-Weber #2 lines respectively are required to be relocated, replaced, and raised. The relocation of distribution facilities will be addressed on a separate order number. Project Scope: The project scope of work includes following: • Relocate poles 000/028 and 000/027 on the Stockton A-Weber #2 line • Relocate poles 000/019, 000/020, and 000/021 on the Stockton A-Weber #3 line • Additional poles may need to be raised or relocated based on engineering review | Transmission Line - Pole/Tower | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-10-30 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.5 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5549362 | T.0008287 | Stockton A-Weber #2 60kV Pole Relo | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-10-02 | 2023-06-30 | 2026-10-22 | Customer Action | NA | TRUE | 975 | NA ¦ NA | 870.2061 | 1669.9003 | 0 | 57.6982 | 86.4553 | 380.6734 | 303.3665 | 828.4926 | 13.2143 | 0 | 0 | 0 | 828.1935 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 52.9824 | 79.3894 | 349.5605 | 324.2038 | 40.8938 | 0% | 100% ¦ $1,670 | NA | NA ¦ NA | NA | 0% | 100% | NA
1868 | Stockton A-Weber #2 Hazelton Crossing |  |  | Kennedy CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | San Joaquin Regional Rail Commission (SJRRC) is shifting 2 railroad lines and will be constructing a flyover bridge for their grade separation project in Stockton, California. Preliminary customer designs indicate that the shifting of the 2 railroad lines and the new flyover bridge will result into insufficient electrical clearances between the existing T-Line and the upcoming infrastructure. To mitigate clearance issues, the T-Line poles 000/019, 000/020, 000/021 and 000/027, 000/028 of Stockton A-Weber #3 and Stockton A-Weber #2 lines respectively are required to be relocated, replaced, and raised. The relocation of distribution facilities will be addressed on a separate order number. Project Scope: The project scope of work includes following: • Relocate poles 000/028 and 000/027 on the Stockton A-Weber #2 line • Relocate poles 000/019, 000/020, and 000/021 on the Stockton A-Weber #3 line • Additional poles may need to be raised or relocated based on engineering review | Transmission Line - Pole/Tower | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-10-30 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.211 | Non-IGP | 5561925 | T.0008287 | Stockton A-Weber #2 60kV Pole Relo | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-12-21 | 2023-06-30 | 2026-12-21 | Customer Action | NA | TRUE | 975 | NA ¦ NA | 48.9921 | 707.311 | 0 | 0 | 0 | 0 | 40.0095 | 667.3014 | 0 | 0 | 0 | 0 | 40.0096 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 50% ¦ $1,346 | NA | NA ¦ NA | NA | 0% | 100% | NA
1869 | Stockton A-Weber #2 Shoo Fly |  |  | Kennedy CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | San Joaquin Regional Rail Commission (SJRRC) is shifting 2 railroad lines and will be constructing a flyover bridge for their grade separation project in Stockton, California. Preliminary customer designs indicate that the shifting of the 2 railroad lines and the new flyover bridge will result into insufficient electrical clearances between the existing T-Line and the upcoming infrastructure. To mitigate clearance issues, the T-Line poles 000/019, 000/020, 000/021 and 000/027, 000/028 of Stockton A-Weber #3 and Stockton A-Weber #2 lines respectively are required to be relocated, replaced, and raised. The relocation of distribution facilities will be addressed on a separate order number. Project Scope: The project scope of work includes following: • Relocate poles 000/028 and 000/027 on the Stockton A-Weber #2 line • Relocate poles 000/019, 000/020, and 000/021 on the Stockton A-Weber #3 line • Additional poles may need to be raised or relocated based on engineering review | Transmission Line - Pole/Tower | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-10-30 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | 0.1 | NA | 60 | NA | NA | NA | NA | 3.002 | Non-IGP | 5561924 | T.0008287 | Stockton A-Weber #2 60kV Pole Relo | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-01-19 | 2023-06-30 | 2027-04-19 | Customer Action | NA | TRUE | 975 | NA ¦ NA | 103.2946 | 340.3515 | 0 | 0 | 0 | 0 | 103.2946 | 7.4891 | 229.5678 | 0 | 0 | 0 | 103.2946 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2027 | 0 | 0 | 0 | 0 | 100.5436 | 0 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | NA
1870 | Martin-Hunters Point Shoofly Project |  |  | San Francisco, San Francisco | The scope of work includes removing the two towers supporting the HP-3 line above ground to an underground system. The lattice structure provides power along the HP-3 line to the Hunters Point Switchyard. The plan is to tie into an existing vault located on Hawes St and run the 115 KV HPGF HP-3 line underground into the Hunters Point Switchyard. A new termination structure will dead end the underground system and tie into the existing tower at the switchyard. The majority of this work originally falls under the Hunters Point GIS Substation Project, while the scope of this project involves adding a shoofly/cutover at the corner of Hunters Point Blvd and Evans from the original route to the switchyard HP-3 termination point. A vault will be added at this corner for the future connection to the GIS substation along Evans Ave. | Transmission Line - Conductor | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-11-16 | NA | NA | Wires - Location/Route Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 23.6 | NA | 230 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5803358 | T.0008764 | Martin-Hunters Point Shoofly Project | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | BCDC | NA | NOC: AL 7127-E | 2024-01-10 | Approved | 2024 | Construction (over 75%) | 2 | 2025-10-13 | 2025-04-01 | 2026-03-25 | Prioritization | NA | TRUE | 19500 | NA ¦ NA | 14955.2745 | 18163.4035 | 0 | 0 | 540.0005 | 4450.4487 | 8273.4622 | 4390.4016 | 509.0906 | 0 | 0 | 0 | 13263.9113 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $18,163 | NA | NA ¦ NA | NA | 100% | 0% | NA
1871 | Dixon - Vaca #1 60kV Pole Relo |  |  | Dixon, Solano ¦ Elmira CDP, Solano ¦ Fairfield, Solano ¦ Solano ¦ Vacaville, Solano | Relocate, replace and/or raise four poles, 006/154 thru 007/157, on the Dixon – Vaca #1 60 kV transmission line and four poles, 006/156 thru 007/159, on the Dixon – Vaca #2 60 kV transmission line located in Solano County, CA. The work is needed to accommodate a proposed overpass along, Porter Road between Pitt School Road and South Lincoln Street in the City of Dixon. | Transmission Line - Pole/Tower | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-12-01 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5551704 | T.0008895 | Dixon - Vaca #1 60kV Pole Relo | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7154-E | 2024-02-25 | Approved | 2024 | Construction (50%-75%) | 2 | 2026-01-12 | 2024-06-01 | 2026-04-17 | Customer Action | NA | TRUE | 900 | NA ¦ NA | 965.9615 | 1260.658 | 0 | 13.7596 | 254.7262 | 109.1099 | 190.2829 | 692.7793 | 0 | 0 | 0 | 0 | 567.8787 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 228.6395 | 92.9168 | 162.0427 | 339.0028 | 0% | 100% ¦ $1,261 | NA | NA ¦ NA | NA | 0% | 100% | NA
1872 | BORDEN-COPPERMINE 70KV POLE RELO AV12 |  |  | Fresno ¦ Fresno, Fresno ¦ Madera ¦ Madera Ranchos CDP, Madera ¦ Rolling Hills CDP, Madera | The Borden-Coppermine 70kV Pole Relo AV12 project is located on Avenue 12, from Riverwalk Blvd to Road 39-1/2. This project plans to relocate existing poles on the Borden-Coppermine 70kV line at the request of the County of Madera as a part of the Avenue 12 widening effort. The scope will include relocating 30 wood poles on the Borden-Coppermine 70kV Transmission Line. | Transmission Line - Pole/Tower | Relocate | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | 2025-09-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 2 | NA | 70 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5556282 | T.0010475 | BORDEN-COPPERMINE 70KV POLE RELO AV12 | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC: AL-7703-E | 2025-09-24 | Approved | 2025 | Construction (over 75%) | 2 | 2025-11-12 | 2025-12-31 | 2026-04-17 | NA | NA | TRUE | 4720 | NA ¦ NA | 2745.7028 | 2919.7272 | 0 | 0 | 0 | 160.3171 | 2025.7822 | 733.6277 | 0 | 0 | 0 | 0 | 2186.0994 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 160.3171 | 2025.7822 | 559.6034 | 0% | 100% ¦ $2,920 | NA | NA ¦ NA | NA | 0% | 100% | NA
1873 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC or Customer), has submitted an application to Pacific Gas and Electric Company (PG&E) to interconnect a data center load to PG&E’s Transmission system. Preliminary Engineering Study report was signed in April 2024 Direct Assignment • Review and accept customer design and testing protocols • Witness/complete final testing for interconnection Component 115kV BAAH • Two new bays and provision for 3rd bay in new Component Switching Station • Install two(2) new 115kV complete BAAH Bay 1 & 2 o Six 115kV breakers o Twelve 115kV disconnects o Two 115kV line disconnect switches o Two 115kV underground line termination structures • Install protective relaying for the new breakers/lines in the existing control enclosure • Install new SMP relay package(s) for the 115kV CBs. 115kV T-Line • Install two 115kV underground lines between Component Switching Station and Customer substation • Install two fiber communication lines between Component Switching Station and Customer substation Land Rights • Land rights for Component Switching station and transmission line parcels Metering • Install two CT/PT combo units and metering enclosure equipment at Customer facility | Other | New | NA | T.0009031 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 1.8982 | NA | NA | NA | NA | NA | 5.1001 | Non-IGP | 5558521 | T.0010520 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Programmatic Work | NA | NA | 2028-09-29 | OAI | NA | NA | TRUE | 89700 | NA ¦ NA | 30.9739 | 880.0771 | 0 | 0 | 0 | 0 | 28.3533 | 542.4527 | 309.2712 | 0 | 0 | 0 | 28.3533 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1874 | 82S Plan - Load |  |  | NA | Forecast placeholder for load interconnection projects | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | NA | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | NA | False ¦ False ¦ False | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | 5555047 | NA | NA | NA | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 22487 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 113008.5451 | 41959.3049 | 65715.0053 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 2-4 | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1875 | Regulatory Amount MWC 82 |  |  | NA | Bucket for regulatory related WRO work | Substation - Multiple | New | NA | NA | Work Requested by Others | Facility Relocation | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | 5.1001 | Non-IGP | 5505967 | NA | NA | NA | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2885.9279 | 2885.9279 | 8.8683 | 9.6039 | 10.5618 | 5.4028 | 0 | 0 | 0 | 0 | 0 | 0 | 2885.9279 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | NA | NA ¦ NA | NA | 0% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1876 | MWC82 Post-COD Work PG&E Funded |  |  | NA | Bucket for regulatory related WRO work | Transmission Line/Substation | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | NA | NA | 5.1001 | NA | 5759001 | NA | NA | NA | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1909.7027 | 1909.7027 | 83.1851 | 90.0846 | 99.296 | 50.6858 | 0 | 0 | 0 | 0 | 0 | 0 | 1909.7027 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 421.5692 | 0 | 0% | 23% ¦ $1,910 | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
1877 | Caltrain Interconnections CPUC Audit |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Other | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-08 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.0642 | NA | 115 kV | NA | NA | NA | NA | NA | 5550360 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2022 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 1 | 2022-08-17 | 2021-06-30 | 2022-09-14 | Construction Delays | NA | FALSE | 64500 | NA ¦ NA | 314.5958 | 314.5958 | 0 | 249.6645 | 0 | 24.45 | 40.4813 | 0 | 0 | 0 | 0 | 0 | 314.5958 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 224.6981 | 0 | 22.005 | 36.4331 | 0 | 0% | 100% ¦ $315 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1878 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC) has requested PG&E to serve the proposed data center. The project scope of work includes following: SUBSTATION • Relocate Bank #2 230 kV line to make room for the double circuit IC lines o Install two TSP’s and remove one TSP o Install three spans of conductor to reconnect the bank #2 • Install 230 kV complete BAAH Bay #5 o Three 230 kV breakers o Six 230 kV disconnects o Two 230 kV line disconnect switches o Wave-trap with 3 CCVT’s, with line tuner accessories o With an additional dead-end on the West side terminal for the IC • Install all line relays and controls for Bay #5 o Install additional conduits as needed o Install control wiring to all BAAH Bay #5 elements • Install 230 kV Dead-end East of bay #5 for the line disconnect switch and CCVT’s location for IC #2 line • Remove Line Trap and CCVT’s from Bay #4 • Install conduit extensions for fiber optic communications (protection) between PG&E and IC T-LINE • Two 230 kV Overhead (OH) Transmission lines made of 715.5 AAC conductor will be built to interconnect IC’s 230 kV substation to Eastshore 230 kV bus. The project will consist of 9 new Tubular Steel Poles (TSP) on drilled pier foundations, and about 0.5 double circuit miles of 230 kV transmission lines. TELEMETRY • Add telemetry from IC’s substation to PG&E system | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-04 | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 9.9849 | NA | 230 kV | NA | NA | NA | 5.1001 | Non-IGP | 5795285 | T.0006960 | Private Load Interconnection Project | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6570-E | 2022-04-22 | Approved | 2022 | Operational | 1 | 2023-01-23 | 2023-06-30 | 2024-05-17 | Workforce | NA | TRUE | 26700 | NA ¦ NA | 9846.3859 | 9846.3859 | -1787.5666 | -618.4225 | -1631.0763 | 13925.424 | -41.9728 | 0 | 0 | 0 | 0 | 0 | 9846.3859 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 9868.9871 | -41.8904 | 0 | 0% | 70% ¦ $9,846 | Type 2 | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - New Substation Alternative [Alternative Solutions and Costs - Costs] $15 Mil - $20 Mil ¦ $20 Mil - $30 Mil
1879 | Private Load Interconnection Project |  |  |  | Construct new switching station and install additional conductor on the Morgan Hill-Llagas 115 kV tower line to a new switching station at the customer site | Substation - Other Equipment | New | NA | T.0004271 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.8017 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5800024 | T.0007676 | Private Load Interconnection Project | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2025-03-26 | EIR | NA | City of Gilroy | NA | NOC: AL 7687-E | 2025-08-29 | Approved | 2025 | Construction (under 10%) | 2 | 2026-02-23 | 2026-10-14 | 2027-03-26 | NA | NA | TRUE | 18000 | NA ¦ NA | 1036.8704 | 5607.4749 | 0 | 15.4679 | 92.1555 | 105.5712 | 689.7882 | 4328.3062 | 376.1861 | 0 | 0 | 0 | 902.9826 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $5,607 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1880 | Private Load Interconnection Project |  |  |  | Construct new switching station and install additional conductor on the Morgan Hill-Llagas 115 kV tower line to a new switching station at the customer site | Substation - Other Equipment | New | NA | T.0004271 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.3037 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5800025 | T.0007676 | Private Load Interconnection Project | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2025-03-26 | EIR | NA | City of Gilroy | NA | NOC: AL 7687-E | 2025-08-29 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-06-10 | 2026-10-14 | 2027-03-26 | NA | NA | TRUE | 18000 | NA ¦ NA | 2055.1432 | 9518.7948 | 0 | 32.95 | 137.1638 | 109.8293 | 1433.8821 | 7187.8079 | 617.1617 | 0 | 0 | 0 | 1713.8252 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $9,519 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1881 | Private Load Interconnection Project |  |  |  | Construct new switching station and install additional conductor on the Morgan Hill-Llagas 115 kV tower line to a new switching station at the customer site | Substation - Multiple | New | NA | T.0004271 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.3037 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5799024 | T.0007676 | Private Load Interconnection Project | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2025-03-26 | EIR | NA | City of Gilroy | NA | NOC: AL 7687-E | 2025-08-29 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-04-08 | 2026-10-14 | 2027-04-02 | NA | NA | TRUE | 18000 | NA ¦ NA | 1396.9155 | 26014.4112 | 0.8316 | -6724.1085 | 58.8132 | 7131.8599 | 711.2006 | 26831.6869 | -1995.8726 | 0 | 0 | 0 | 1178.5968 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 86% ¦ $26,014 | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1882 | Private Load Interconnection Project |  |  |  | Construct new switching station and install additional conductor on the Morgan Hill-Llagas 115 kV tower line to a new switching station at the customer site | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.3037 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5547486 | T.0007676 | Private Load Interconnection Project | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2025-03-26 | EIR | NA | City of Gilroy | NA | NOC: AL 7687-E | 2025-08-29 | Approved | 2025 | Programmatic Work | NA | NA | 2026-10-14 | OAI | NA | NA | TRUE | 18000 | NA ¦ NA | 536.1381 | 1080.1105 | 0 | 0 | 0.5761 | 17.6576 | 440.6155 | 102.1598 | 519.1016 | 0 | 0 | 0 | 458.8492 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 412.9643 | 69.5601 | 0% | 100% ¦ $1,080 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1883 | Private Load Interconnection Project |  |  |  | The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Milpitas No. 2 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Construction of two, new 1000-foot 115 kV line sections from the Newark-Milpitas No. 2 Line to the new PG&E-owned 115 kV switching station; ● Two 115 kV connectins to the Customer-owned substation; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The data center is expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. | Substation - Other Equipment | New | NA | T.0009536 | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 27.7611 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804014 | T.0008046 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7280-E | 2024-05-23 | Approved | 2024 | Construction (25%-50%) | 2 | 2025-12-22 | 2026-04-30 | 2026-08-31 | NA | NA | TRUE | 34800 | NA ¦ NA | 300.4049 | 691.8144 | 0 | 0 | 16.7958 | 119.7952 | 138.389 | 398.5283 | 18.3061 | 0 | 0 | 0 | 274.9799 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $692 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1884 | Private Load Interconnection Project |  |  |  | The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Milpitas No. 2 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Construction of two, new 1000-foot 115 kV line sections from the Newark-Milpitas No. 2 Line to the new PG&E-owned 115 kV switching station; ● Two 115 kV connectins to the Customer-owned substation; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The data center is expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. | Substation - Other Equipment | New | NA | T.0009536 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 1.2309 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5555821 | T.0008046 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7280-E | 2024-05-23 | Approved | 2024 | Construction (50%-75%) | 2 | 2025-12-08 | 2026-04-30 | 2026-05-13 | NA | NA | TRUE | 34800 | NA ¦ NA | 452.8961 | 934.9929 | 0 | 0 | 0 | 70.4371 | 295.7083 | 568.8475 | 0 | 0 | 0 | 0 | 366.1454 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 70.4371 | 295.7083 | 86.7507 | 0% | 100% ¦ $935 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1885 | Private Load Interconnection Project |  |  |  | The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Milpitas No. 2 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Construction of two, new 1000-foot 115 kV line sections from the Newark-Milpitas No. 2 Line to the new PG&E-owned 115 kV switching station; ● Two 115 kV connectins to the Customer-owned substation; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The data center is expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. | Substation - Multiple | New | NA | T.0009536 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-02 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 3.3452 | NA | 115 kV | NA | NA | NA | 5.301 | Non-IGP | 5799905 | T.0008046 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7280-E | 2024-05-23 | Approved | 2024 | Construction (over 75%) | 2 | 2025-01-13 | 2026-04-30 | 2026-06-03 | NA | NA | TRUE | 34800 | NA ¦ NA | 4326.756 | 31117.6001 | 0 | -343.6689 | 436.8111 | 1039.0758 | 2699.0383 | 27286.3437 | 0 | 0 | 0 | 0 | 3831.2564 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 48% ¦ $31,118 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1886 | Private Load Interconnection Project |  |  |  | The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Milpitas No. 2 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Construction of two, new 1000-foot 115 kV line sections from the Newark-Milpitas No. 2 Line to the new PG&E-owned 115 kV switching station; ● Two 115 kV connectins to the Customer-owned substation; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The data center is expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. | Substation - Protection Relay | Upgrade/Retrofit | NA | T.0009536 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-02 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 3.3452 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5804015 | T.0008046 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7280-E | 2024-05-23 | Approved | 2024 | Construction (under 10%) | 2 | 2026-03-04 | 2026-04-30 | 2026-06-01 | NA | NA | TRUE | 34800 | NA ¦ NA | 3204.8271 | 5789.1877 | 0 | 0 | 25.6152 | 170.2644 | 1173.5256 | 4419.7825 | 0 | 0 | 0 | 0 | 1369.4052 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $5,789 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1887 | Private Load Interconnection Project |  |  |  | The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Milpitas No. 2 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Construction of two, new 1000-foot 115 kV line sections from the Newark-Milpitas No. 2 Line to the new PG&E-owned 115 kV switching station; ● Two 115 kV connectins to the Customer-owned substation; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The data center is expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | T.0009536 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 2.1012 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5564281 | T.0008046 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7280-E | 2024-05-23 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-04-10 | 2026-04-30 | 2026-05-23 | NA | NA | TRUE | 34800 | NA ¦ NA | 28.4608 | 257.4593 | 0 | 0 | 0 | 0 | 1.051 | 254.8047 | 1.6036 | 0 | 0 | 0 | 1.051 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | Type 4 | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1888 | Private Load Interconnection Project |  |  |  | The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Milpitas No. 2 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Construction of two, new 1000-foot 115 kV line sections from the Newark-Milpitas No. 2 Line to the new PG&E-owned 115 kV switching station; ● Two 115 kV connectins to the Customer-owned substation; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The data center is expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | T.0009536 | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-05 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5816404 | T.0008046 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7280-E | 2024-05-23 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-08-14 | 2026-04-30 | 2026-12-31 | Customer Action | NA | TRUE | 34800 | NA ¦ NA | 103.2776 | 759.5072 | 0 | 0 | 0 | 0 | 20.1622 | 331.0969 | 408.2481 | 0 | 0 | 0 | 20.1622 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | Type 4 | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1889 | L0009: VTA 115KV_FMC INTERCONNECTION |  |  | San Jose, Santa Clara | The project scope of work includes following: Substation:  Install new 115kV circuit breaker in BAAH Bay 5, disconnect switches, line CCVTs, and H-frame dead end structures. Includes breaker relays and overhead conductor and drops between Bay 5 and new 115kV line termination structure  Install new line current differential relays and Digital Fault Recorder in FMC 115kV MPAC building  Install new line current differential relays in PG&E metering building located at VTA 115kV substation  Install fully redundant communication paths between FMC substation 115kV MPAC building, and PG&E metering building located at VTA 115kV substation. Physically separated independent communication paths required for set A and set B protection relaying  Install PG&E RTU at proposed VTA substation  Install PG&E meter and 115kV PT/CT combination metering transformers. Includes pulling secondary wires and installing one electronic meter Transmission Line:  Install approximately 300 circuit-feet of a new single-circuit 115 kV transmission line from PG&E’s FMC Substation Bay 5 to the proposed VTA substation. The new line will support the expected temporary load of 24.8 MVA | Substation - Circuit Breaker | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-08 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.0642 | NA | 115 kV | NA | NA | NA | 5.301 | Non-IGP | 5800518 | T.0008309 | FMC: VTA 115kV Interconnect | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-05-01 | 2024-12-31 | 2024-10-19 | NA | NA | TRUE | 11560 | NA ¦ NA | 6.4289 | 2597.3621 | 0 | -547.7853 | 637.794 | -80.7831 | 0.1599 | 545.4062 | 2041.2949 | 1.2755 | 0 | 0 | 9.3855 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 9.2256 | 0.15992 | -2.9566 | 0% | 0% ¦ $0 | Type 2 | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1890 | Oakland Sub J Relay Upgrade |  |  | Oakland, Alameda | Oakland J-Alameda 115 kV line relay upgrade and fiber connection extension from Oakland J to Oakland C in PG&E's facilities per work agreement with Alameda Municipal Power (AMP) | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-09 | 19 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 2.5059 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5552179 | T.0009027 | Oakland J to Alameda 115kV Relay Upgrade | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-12-03 | NA | 2027-02-22 | NA | NA | TRUE | NA | NA ¦ NA | 165.3219 | 2400.6303 | 0 | 0 | 75.2138 | 10.7169 | 58.9178 | 1143.9829 | 1111.7989 | 0 | 0 | 0 | 144.8485 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 67.6925 | 9.6453 | 53.0259 | 18.426 | 0% | 0% ¦ $0 | Type 3 | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1891 | Private Load Interconnection Project |  |  |  | The Customer is planning on constructing a large data center facility, expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Trimble 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Loop the Newark-Trimble 115 kV Line into the new PG&E Switching Station; ● Reconductoring of 12.1 miles of the Newark-Trimble 115 kV Line from Newark to TSP 012/082; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The Customer has also requested that the two connections from the Newark-Trimble Line be routed separately from the PG&E switching station to the existing line. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5805817 | T.0009031 | Private Load Interconnection Project | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | CEC | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-03-10 | NA | 2025-07-01 | NA | NA | FALSE | NA | NA ¦ NA | -1.537 | -1.537 | 0 | 0 | 13.2473 | 76.6859 | -91.4701 | 0 | 0 | 0 | 0 | 0 | -1.537 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ -$2 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1892 | Private Load Interconnection Project |  |  |  | The Customer is planning on constructing a large data center facility, expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Trimble 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Loop the Newark-Trimble 115 kV Line into the new PG&E Switching Station; ● Reconductoring of 12.1 miles of the Newark-Trimble 115 kV Line from Newark to TSP 012/082; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The Customer has also requested that the two connections from the Newark-Trimble Line be routed separately from the PG&E switching station to the existing line. | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5805814 | T.0009031 | Private Load Interconnection Project | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | CEC | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-06-17 | NA | 2025-07-31 | NA | NA | FALSE | NA | NA ¦ NA | 12.389 | 12.389 | 0 | 0 | 35.6831 | 163.3389 | -192.666 | 6.0329 | 0 | 0 | 0 | 0 | 6.3561 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 95% ¦ $12 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1893 | Private Load Interconnection Project |  |  |  | The Customer is planning on constructing a large data center facility, expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Trimble 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Loop the Newark-Trimble 115 kV Line into the new PG&E Switching Station; ● Reconductoring of 12.1 miles of the Newark-Trimble 115 kV Line from Newark to TSP 012/082; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The Customer has also requested that the two connections from the Newark-Trimble Line be routed separately from the PG&E switching station to the existing line. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5805815 | T.0009031 | Private Load Interconnection Project | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | CEC | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-09-25 | NA | 2025-07-31 | NA | NA | FALSE | NA | NA ¦ NA | 52.6622 | 52.6622 | 0 | 0 | 41.2358 | 122.7631 | -115.4643 | 4.1275 | 0 | 0 | 0 | 0 | 48.5347 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $53 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1894 | Private Load Interconnection Project |  |  |  | The Customer is planning on constructing a large data center facility, expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Trimble 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Loop the Newark-Trimble 115 kV Line into the new PG&E Switching Station; ● Reconductoring of 12.1 miles of the Newark-Trimble 115 kV Line from Newark to TSP 012/082; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The Customer has also requested that the two connections from the Newark-Trimble Line be routed separately from the PG&E switching station to the existing line. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 27.7611 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5805816 | T.0009031 | Private Load Interconnection Project | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | CEC | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-16 | NA | 2025-07-31 | NA | NA | FALSE | NA | NA ¦ NA | -2.2652 | -2.2652 | 0 | 0 | 24.6746 | 100.1526 | -127.0924 | 0 | 0 | 0 | 0 | 0 | -2.2652 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ -$2 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1895 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC), has submitted an application to Pacific Gas and Electric Company (PG&E) to interconnect a data center to PG&E’s transmission system through discrete 230kV service from Egbert Switching Station. The site is currently served from PG&E’s 12kV feeder H1112 from Martin Substation. The IC expects their load to ramp up to 48 MW in 2031, and therefore requested transmission service. | Substation - Multiple | New | NA | T.0000159 | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 230 kV | NA | NA | NA | 5.211 | Non-IGP | 5804558 | T.0009133 | Private Load Interconnection Project | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-12-12 | NA | 2029-03-01 | NA | NA | FALSE | NA | NA ¦ NA | -67.4256 | 8584.0932 | 0 | 0 | -489.0317 | 349.3578 | 52.5491 | 117.1422 | 59.6977 | 6788.2783 | 1706.0999 | 0 | -87.1249 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 48% ¦ $8,584 (Subject to change) | Type 3 | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1896 | Private Load Interconnection Project |  |  |  | IC has applied for a total of 37 MW of capacity from the distribution system. Transmission Substation Work: T.0010081.02: MAT 82N, Planning Order 5809167, OAA 74058607 • Extend the 115 kV bus to build Bus Section F with five bay spaces • Install two 115 kV bus sectionalizing breaker with disconnects • Install one 115 kV MPAC building • Upgrade Ravenswood 230 kV BAAH with redundant relays to mitigate against thermal overload on San Mateo-Belmont 115 kV Line caused by failure of non-redundant relay at Ravenswood 230 kV BAAH Bus #2 (TBD) | Substation - Multiple | New | NA | T.0006761 | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5809167 | T.0010081 | Private Load Interconnection Project | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-09-20 | NA | 2027-11-05 | NA | NA | TRUE | NA | NA ¦ NA | 260.5105 | 2813.3229 | 0 | 0 | 0 | 27.6922 | 191.9193 | 559.1274 | 1535.5091 | 499.075 | 0 | 0 | 219.6114 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1897 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.1069 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5815037 | T.0010100 | Private Load Interconnection Project | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-12-01 | 2027-07-31 | 2027-05-01 | NA | NA | TRUE | 16400 | NA ¦ NA | 5.1669 | 5402.8056 | 0 | 0 | 0 | 0 | 3.7651 | 599.2362 | 4799.8043 | 0 | 0 | 0 | 3.7651 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 14% ¦ $5,403 (Subject to change. Agreements are not finalized.) | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1898 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA 94085. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.0337 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5810601 | T.0010100 | Private Load Interconnection Project | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-04-19 | 2027-07-31 | 2027-05-12 | NA | NA | TRUE | 16400 | NA ¦ NA | 123.6684 | 1324.6627 | 0 | 0 | 0 | 12.0853 | 63.7901 | 832.4617 | 396.2246 | 20.101 | 0 | 0 | 75.8753 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,325 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1899 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA 94085. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.0337 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5810527 | T.0010100 | Private Load Interconnection Project | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-04-20 | 2027-07-31 | 2027-06-09 | NA | NA | TRUE | 16400 | NA ¦ NA | 148.5616 | 1641.071 | 0 | 0 | 0 | 11.0563 | 86.0956 | 1019.2467 | 497.6707 | 27.0018 | 0 | 0 | 97.1518 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,641 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1900 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.1069 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5563280 | T.0010100 | Private Load Interconnection Project | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-04-26 | 2027-07-31 | 2027-06-22 | NA | NA | TRUE | 16400 | NA ¦ NA | 30.6427 | 692.2441 | 0 | 0 | 0 | 0 | 10.0884 | 325.0098 | 357.1459 | 0 | 0 | 0 | 10.0884 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 14% ¦ $692 (Subject to change. Agreements are not finalized.) | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1901 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA 94085. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.0337 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5810528 | T.0010100 | Private Load Interconnection Project | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-12-10 | 2027-07-31 | 2027-06-25 | NA | NA | TRUE | 16400 | NA ¦ NA | 1272.2116 | 7420.8832 | 0 | 0 | 0 | 76.6671 | 1102.0187 | 3293.3302 | 2837.7962 | 111.071 | 0 | 0 | 1178.6858 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $7,421 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1902 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-08 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.0642 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5561948 | T.0010100 | Private Load Interconnection Project | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-05-03 | 2027-07-31 | 2027-06-29 | NA | NA | TRUE | 16400 | NA ¦ NA | 35.6712 | 674.3259 | 0 | 0 | 0 | 0 | 13.1663 | 365.9324 | 295.2271 | 0 | 0 | 0 | 13.1663 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 3% ¦ $674 (Subject to change. Agreements are not finalized.) | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1903 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA 94085. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.0337 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5810599 | T.0010100 | Private Load Interconnection Project | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-06-30 | 2027-07-31 | 2027-07-26 | NA | NA | TRUE | 16400 | NA ¦ NA | 107.2634 | 945.8133 | 0 | 0 | 0 | 10.936 | 64.3434 | 503.3279 | 353.5632 | 13.6428 | 0 | 0 | 75.2794 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $946 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1904 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA 94085. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.0337 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5810598 | T.0010100 | Private Load Interconnection Project | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-06-08 | 2027-07-31 | 2027-07-28 | NA | NA | TRUE | 16400 | NA ¦ NA | 124.1805 | 1378.122 | 0 | 0 | 0 | 10.8908 | 75.6933 | 672.2144 | 542.4956 | 76.828 | 0 | 0 | 86.584 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,378 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1905 | Private Load Interconnection Project |  |  |  | The Interconnection Customer has requested PG&E to increase load located in Santa Clara County, CA 94085. The proposed scope will add an additional 14MW, 23MW & 15MW in Phase 1, Phase 2 & Phase 3 respectively to the existing 20MW. IC Switching Station • Upgrade existing 115kV bus protection for bus section D & E • Upgrade Newark-Applied Materials 115kV line to a 3-terminal Line Current Differential (LCD) • Relocate existing station battery to a n control room enclosure • Install Microwave tower Lockheed 2 Substation • Install two (2) 115kV Circuit Breaker (CB) and associated equipment replacing the existing Circuit Switchers (326 & 346) • Relocate the existing station batter to a new control room enclosure • Install LCD for Newark-Applied Materials 115kV line & Lockheed 2 115kV tap • Install Bus total overcurrent relay scheme on Lockheed #2 Bus • Install Microwave tower Lockheed 1 Substation • Install CB and LCD relays with fully redundant communication channels for the 3-terminal LCD scheme involving Applied Materials and Lockheed 2 substations. • Install Microwave tower Newark Substation • Install LCD for Lockheed 2 115kV tap Britton Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Newark-Lockheed #2 transmission line Monta Vista Substation • Upgrade Britton-Monta Vista 115kV line protection to 2-terminal LCD • Reconductor Monta Vista-Britton transmission line | Substation - Protection Relay | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.0337 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5810526 | T.0010100 | Private Load Interconnection Project | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-12-11 | 2027-07-31 | 2027-07-30 | NA | NA | TRUE | 16400 | NA ¦ NA | 383.6 | 8981.4843 | 0 | 0 | 0 | 73.2814 | 236.8794 | 2335.8044 | 4956.6558 | 1378.8633 | 0 | 0 | 310.1608 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $8,981 | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1906 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC or Customer), has submitted an application to Pacific Gas and Electric Company (PG&E) to interconnect a data center load to PG&E’s Transmission system. Preliminary Engineering Study report was signed in April 2024 Direct Assignment • Review and accept customer design and testing protocols • Witness/complete final testing for interconnection Component 115kV BAAH • Two new bays and provision for 3rd bay in new Component Switching Station • Install two(2) new 115kV complete BAAH Bay 1 & 2 o Six 115kV breakers o Twelve 115kV disconnects o Two 115kV line disconnect switches o Two 115kV underground line termination structures • Install protective relaying for the new breakers/lines in the existing control enclosure • Install new SMP relay package(s) for the 115kV CBs. 115kV T-Line • Install two 115kV underground lines between Component Switching Station and Customer substation • Install two fiber communication lines between Component Switching Station and Customer substation Land Rights • Land rights for Component Switching station and transmission line parcels Metering • Install two CT/PT combo units and metering enclosure equipment at Customer facility | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0009031 | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 27.7611 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5815560 | T.0010520 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-04-18 | 2028-09-29 | 2028-09-29 | NA | NA | FALSE | 89700 | NA ¦ NA | 260.2739 | 3066.6591 | 0 | 0 | 0 | 0 | 242.6227 | 370.8543 | 281.9578 | 2018.1857 | 153.0387 | 0 | 242.6227 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 6% ¦ $3,067 | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1907 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC or Customer), has submitted an application to Pacific Gas and Electric Company (PG&E) to interconnect a data center load to PG&E’s Transmission system. Preliminary Engineering Study report was signed in April 2024 Direct Assignment • Review and accept customer design and testing protocols • Witness/complete final testing for interconnection Component 115kV BAAH • Two new bays and provision for 3rd bay in new Component Switching Station • Install two(2) new 115kV complete BAAH Bay 1 & 2 o Six 115kV breakers o Twelve 115kV disconnects o Two 115kV line disconnect switches o Two 115kV underground line termination structures • Install protective relaying for the new breakers/lines in the existing control enclosure • Install new SMP relay package(s) for the 115kV CBs. 115kV T-Line • Install two 115kV underground lines between Component Switching Station and Customer substation • Install two fiber communication lines between Component Switching Station and Customer substation Land Rights • Land rights for Component Switching station and transmission line parcels Metering • Install two CT/PT combo units and metering enclosure equipment at Customer facility | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0009031 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5815561 | T.0010520 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-03-31 | 2028-09-29 | 2028-09-29 | NA | NA | FALSE | 89700 | NA ¦ NA | 132.7509 | 4410.5978 | 0 | 0 | 0 | 0 | 124.4759 | 214.2521 | 1306.4406 | 2612.3905 | 153.0387 | 0 | 124.4759 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 13% ¦ $4,411 | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1908 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC or Customer), has submitted an application to Pacific Gas and Electric Company (PG&E) to interconnect a data center load to PG&E’s Transmission system. Preliminary Engineering Study report was signed in April 2024 Direct Assignment • Review and accept customer design and testing protocols • Witness/complete final testing for interconnection Component 115kV BAAH • Two new bays and provision for 3rd bay in new Component Switching Station • Install two(2) new 115kV complete BAAH Bay 1 & 2 o Six 115kV breakers o Twelve 115kV disconnects o Two 115kV line disconnect switches o Two 115kV underground line termination structures • Install protective relaying for the new breakers/lines in the existing control enclosure • Install new SMP relay package(s) for the 115kV CBs. 115kV T-Line • Install two 115kV underground lines between Component Switching Station and Customer substation • Install two fiber communication lines between Component Switching Station and Customer substation Land Rights • Land rights for Component Switching station and transmission line parcels Metering • Install two CT/PT combo units and metering enclosure equipment at Customer facility | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0009031 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5815559 | T.0010520 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-04-14 | 2028-09-29 | 2028-09-29 | NA | NA | FALSE | 89700 | NA ¦ NA | 353.0201 | 1240.9869 | 0 | 0 | 0 | 0 | 326.8879 | 174.342 | 501.3134 | 164.9013 | 73.5423 | 0 | 326.8879 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 3% ¦ $1,241 | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1909 | SVP: Nortech Remote End |  |  | San Jose, Santa Clara | IC has forecasted that their load will double in the upcoming years. To support the large load growth, IC is pursuing a series of expansion projects. There are four major projects involved: Scott Receiving Station (SRS), Kifer Receiving Station (KRS), Northern Receiving Station (NRS), and NRS-KRS 115kV Transmission Line. PG&E is obligated support them in these upgrades to ensure continued safe and reliable transmission from PG&E to IC. Project scope is the following: • Remote end upgrades at three (3) substations which includes: Newark (Newark – Kifer & Newark - NRS #1 & #2 115 kV lines), Nortech (Nortech - NRS 115 kV line), Zanker (San Jose Regional Water Facility SJRWF tap from Newark - Kifer 115 kV line) • Four (4) Point Of Customer Ownership (POCO) outside of the receiving stations (Scott & Northern Receiving Stations) | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-08 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.6495 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813840 | T.0010764 | SVP Interconnection - POCO Switch | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-02-24 | 2027-08-04 | 2027-09-23 | NA | NA | TRUE | 24420 | NA ¦ NA | 104.8525 | 2877.9704 | 0 | 0 | 0 | 0 | 83.9996 | 357.4239 | 2422.1449 | 14.402 | 0 | 0 | 83.9995 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1910 | SVP: Newark Remote End |  |  | Fremont, Alameda | IC has forecasted that their load will double in the upcoming years. To support the large load growth, IC is pursuing a series of expansion projects. There are four major projects involved: Scott Receiving Station (SRS), Kifer Receiving Station (KRS), Northern Receiving Station (NRS), and NRS-KRS 115kV Transmission Line. PG&E is obligated support them in these upgrades to ensure continued safe and reliable transmission from PG&E to IC. Project scope is the following: • Remote end upgrades at three (3) substations which includes: Newark (Newark – Kifer & Newark - NRS #1 & #2 115 kV lines), Nortech (Nortech - NRS 115 kV line), Zanker (San Jose Regional Water Facility SJRWF tap from Newark - Kifer 115 kV line) • Four (4) Point Of Customer Ownership (POCO) outside of the receiving stations (Scott & Northern Receiving Stations) | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Corrosion |  | NA | 27.7611 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813841 | T.0010764 | SVP Interconnection - POCO Switch | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-01-22 | 2027-08-04 | 2027-09-30 | NA | NA | TRUE | 24420 | NA ¦ NA | 140.7201 | 4836.5203 | 0 | 0 | 0 | 0 | 123.041 | 2060.1522 | 2646.5089 | 6.8183 | 0 | 0 | 123.0409 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1911 | SVP: Zanker Remote End |  |  | San Jose, Santa Clara | IC has forecasted that their load will double in the upcoming years. To support the large load growth, IC is pursuing a series of expansion projects. There are four major projects involved: Scott Receiving Station (SRS), Kifer Receiving Station (KRS), Northern Receiving Station (NRS), and NRS-KRS 115kV Transmission Line. PG&E is obligated support them in these upgrades to ensure continued safe and reliable transmission from PG&E to IC. Project scope is the following: • Remote end upgrades at three (3) substations which includes: Newark (Newark – Kifer & Newark - NRS #1 & #2 115 kV lines), Nortech (Nortech - NRS 115 kV line), Zanker (San Jose Regional Water Facility SJRWF tap from Newark - Kifer 115 kV line) • Four (4) Point Of Customer Ownership (POCO) outside of the receiving stations (Scott & Northern Receiving Stations) | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814479 | T.0010764 | SVP Interconnection - POCO Switch | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-03-24 | 2027-08-04 | 2027-09-30 | NA | NA | TRUE | 24420 | NA ¦ NA | 88.0788 | 4291.8934 | 0 | 0 | 0 | 0 | 58.3496 | 960.2158 | 2600.4521 | 671.8912 | 0.9846 | 0 | 58.3497 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1912 | Private Load Interconnection Project |  |  |  | Interconnect a 250 MW data center to PG&E's Los Esteros Substation. This project proposes to connect new large load (new data center and / or R&D facilities) to 230kV bay 4 at Los Esteros substation by installing a new breaker. | Substation - Circuit Breaker | New | NA | T.0011326 | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.1997 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5816368 | T.0010864 | Private Load Interconnection Project | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-03-02 | NA | 2028-03-30 | NA | NA | FALSE | NA | NA ¦ NA | 82.372 | 11914.1376 | 0 | 0 | 0 | 0 | 51.949 | 2014.2664 | 8064.652 | 1783.2702 | 0 | 0 | 51.949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 2 | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1913 | Private Load Interconnection Project |  |  |  | Interconnect a 49MW data center to PG&E's Lockheed #1 substation. This project proposes to include an element to the existing ring bus and will install a 115kV Circuit Breaker, associated switches and bus structure at Lockeheed #1. | Substation - Other Equipment | New | NA | T.0011626 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-02 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3387 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5561126 | T.0010873 | Private Load Interconnection Project | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-09-11 | 2027-06-01 | 2028-11-03 | Customer Action | NA | FALSE | 10100 | NA ¦ NA | 6.4293 | 33.3842 | 0 | 0 | 0 | 0 | 0 | 6.4291 | 26.9551 | -0.0001 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1914 | Private Load Interconnection Project |  |  |  | Interconnect a 49MW data center to PG&E's Lockheed #1 substation. This project proposes to include an element to the existing ring bus and will install a 115kV Circuit Breaker, associated switches and bus structure at Lockeheed #1. | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-02 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.3387 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5813904 | T.0010873 | Private Load Interconnection Project | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-09-24 | 2027-06-01 | 2027-06-01 | NA | NA | TRUE | 10100 | NA ¦ NA | 521.1689 | 5538.2927 | 0 | 0 | 0 | 0 | 446.0386 | 4100.3128 | 991.9414 | 0 | 0 | 0 | 446.0386 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $5,538 | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1915 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (“IC), has signed Preliminary Engineering Study (PES) with Pacific Gas and Electric Company (PG&E) for LC24-26 (“Project”) to interconnect a data center load to PG&E’s Transmission system. This project proposes to install a partial Breaker-And-Half (BAAH) to support the data center load. San Jose A Substation • Install partial Breaker-And-A-Half (BAAH) bay on the existing Gas Insulated Switchgear(GIS) • Install breaker failure & reclosing relays for new Circuit Breakers following PG&E’s SMP relay standards • Install Line Current Differential scheme for San Jose A-IC 115kV Line • Install line current differential relays with fully redundant communication channels for the transmission line sources from El Patio, and San Jose B substations. IC Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV line that PG&E will own, operate, and maintain • Install Remote Terminal Unit(RTU) for PG&E visibility • Install revenue metering | Substation - Other Equipment | New | NA | T.0010902 ¦ T.0010873 ¦ T.0010875 ¦ T.0010876 ¦ T.0010908 ¦ T.0010465 ¦ T.0011286 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 3.392 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5814484 | T.0010874 | Private Load Interconnection Project | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-05-03 | NA | 2028-08-30 | NA | NA | FALSE | NA | NA ¦ NA | 3.8664 | 4901.3178 | 0 | 0 | 0 | 0 | 3.8179 | 198.5742 | 613.2591 | 4080.1104 | 5.5562 | 0 | 3.8179 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,901 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1916 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (“IC), has signed Preliminary Engineering Study (PES) with Pacific Gas and Electric Company (PG&E) for LC24-26 (“Project”) to interconnect a data center load to PG&E’s Transmission system. This project proposes to install a partial Breaker-And-Half (BAAH) to support the data center load. San Jose A Substation • Install partial Breaker-And-A-Half (BAAH) bay on the existing Gas Insulated Switchgear(GIS) • Install breaker failure & reclosing relays for new Circuit Breakers following PG&E’s SMP relay standards • Install Line Current Differential scheme for San Jose A-IC 115kV Line • Install line current differential relays with fully redundant communication channels for the transmission line sources from El Patio, and San Jose B substations. IC Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV line that PG&E will own, operate, and maintain • Install Remote Terminal Unit(RTU) for PG&E visibility • Install revenue metering | Substation - Other Equipment | New | NA | T.0010902 ¦ T.0010873 ¦ T.0010875 ¦ T.0010876 ¦ T.0010908 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 2.1017 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814485 | T.0010874 | Private Load Interconnection Project | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-04-14 | NA | 2028-09-20 | NA | NA | FALSE | NA | NA ¦ NA | 3.0132 | 813.7124 | 0 | 0 | 0 | 0 | 2.9754 | 44.576 | 132.8364 | 603.6754 | 29.6492 | 0 | 2.9754 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $814 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1917 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (“IC), has signed Preliminary Engineering Study (PES) with Pacific Gas and Electric Company (PG&E) for LC24-27 (“Project”) to interconnect a data center load to PG&E’s Transmission system. This project proposes to install a partial Breaker-And-Half (BAAH) to support the data center load. San Jose A Substation • Install partial Breaker-And-A-Half (BAAH) bay on the existing Gas Insulated Switchgear(GIS) • Install breaker failure & reclosing relays for new Circuit Breakers following PG&E’s SMP relay standards • Install Line Current Differential scheme for San Jose A-IC 115kV Line • Install line current differential relays with fully redundant communication channels for the transmission line sources from El Patio, and San Jose B substations. IC Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV line that PG&E will own, operate, and maintain • Install Remote Terminal Unit(RTU) for PG&E visibility • Install revenue metering Transmission Line • Install approx. 1.5 miles long single service underground 115kV transmission line to customer site from San Jose A El Patio Substation • Install breaker and line relay package with fully redundant communication channels for the 115kV transmission line terminal at El Patio substation. San Jose B Substation • Install breaker and line relay package with fully redundant communication channels for the 115kV transmission line terminal at San Jose B substation. | Substation - Other Equipment | New | NA | T.0010902 ¦ T.0010873 ¦ T.0010874 ¦ T.0010876 ¦ T.0010908 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 3.392 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5814482 | T.0010875 | Private Load Interconnection Project | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-11-19 | NA | 2028-05-19 | NA | NA | FALSE | NA | NA ¦ NA | 6.8424 | 1325.2142 | 0 | 0 | 0 | 0 | 3.4955 | 185.3001 | 648.8382 | 292.3453 | 195.235 | 0 | 3.4955 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,325 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1918 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (“IC), has signed Preliminary Engineering Study (PES) with Pacific Gas and Electric Company (PG&E) for LC24-27 (“Project”) to interconnect a data center load to PG&E’s Transmission system. This project proposes to install a partial Breaker-And-Half (BAAH) to support the data center load. San Jose A Substation • Install partial Breaker-And-A-Half (BAAH) bay on the existing Gas Insulated Switchgear(GIS) • Install breaker failure & reclosing relays for new Circuit Breakers following PG&E’s SMP relay standards • Install Line Current Differential scheme for San Jose A-IC 115kV Line • Install line current differential relays with fully redundant communication channels for the transmission line sources from El Patio, and San Jose B substations. IC Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV line that PG&E will own, operate, and maintain • Install Remote Terminal Unit(RTU) for PG&E visibility • Install revenue metering Transmission Line • Install approx. 1.5 miles long single service underground 115kV transmission line to customer site from San Jose A El Patio Substation • Install breaker and line relay package with fully redundant communication channels for the 115kV transmission line terminal at El Patio substation. San Jose B Substation • Install breaker and line relay package with fully redundant communication channels for the 115kV transmission line terminal at San Jose B substation. | Substation - Other Equipment | New | NA | T.0010902 ¦ T.0010873 ¦ T.0010874 ¦ T.0010876 ¦ T.0010908 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 2.1017 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814483 | T.0010875 | Private Load Interconnection Project | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-01-18 | NA | 2028-09-12 | NA | NA | FALSE | NA | NA ¦ NA | 5.75 | 1107.4903 | 0 | 0 | 0 | 0 | 3.1639 | 240.1826 | 189.9223 | 656.6708 | 17.5507 | 0 | 3.1639 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,107 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1919 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (“IC), has signed Preliminary Engineering Study (PES) with Pacific Gas and Electric Company (PG&E) for LC24-28 (“Project”) to interconnect a data center load to PG&E’s Transmission system. This project proposes to install a partial Breaker-And-Half (BAAH) to support the data center load. San Jose A Substation • Install partial Breaker-And-A-Half (BAAH) bay on the existing Gas Insulated Switchgear(GIS) • Install breaker failure & reclosing relays for new Circuit Breakers following PG&E’s SMP relay standards • Install Line Current Differential scheme for San Jose A-IC 115kV Line • Install line current differential relays with fully redundant communication channels for the transmission line sources from El Patio, and San Jose B substations. IC Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV line that PG&E will own, operate, and maintain • Install Remote Terminal Unit(RTU) for PG&E visibility • Install revenue metering Transmission Line • Install approx. 1.5 miles long single service (combination of underground & overhead) 115kV transmission line to customer site from San Jose A El Patio Substation • Install breaker and line relay package with fully redundant communication channels for the 115kV transmission line terminal at El Patio substation. San Jose B Substation • Install breaker and line relay package with fully redundant communication channels for the 115kV transmission line terminal at San Jose B substation. | Substation - Other Equipment | New | NA | T.0010902 ¦ T.0010873 ¦ T.0010874 ¦ T.0010875 ¦ T.0010908 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 3.392 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5814498 | T.0010876 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-12-22 | 2028-12-01 | 2027-06-21 | NA | NA | TRUE | 91000 | NA ¦ NA | 6.1885 | 738.5731 | 0 | 0 | 0 | 0 | 2.9754 | 156.4243 | 558.3229 | 14.5608 | 6.2897 | 0 | 2.9754 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $739 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1920 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (“IC), has signed Preliminary Engineering Study (PES) with Pacific Gas and Electric Company (PG&E) for LC24-28 (“Project”) to interconnect a data center load to PG&E’s Transmission system. This project proposes to install a partial Breaker-And-Half (BAAH) to support the data center load. San Jose A Substation • Install partial Breaker-And-A-Half (BAAH) bay on the existing Gas Insulated Switchgear(GIS) • Install breaker failure & reclosing relays for new Circuit Breakers following PG&E’s SMP relay standards • Install Line Current Differential scheme for San Jose A-IC 115kV Line • Install line current differential relays with fully redundant communication channels for the transmission line sources from El Patio, and San Jose B substations. IC Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV line that PG&E will own, operate, and maintain • Install Remote Terminal Unit(RTU) for PG&E visibility • Install revenue metering Transmission Line • Install approx. 1.5 miles long single service (combination of underground & overhead) 115kV transmission line to customer site from San Jose A El Patio Substation • Install breaker and line relay package with fully redundant communication channels for the 115kV transmission line terminal at El Patio substation. San Jose B Substation • Install breaker and line relay package with fully redundant communication channels for the 115kV transmission line terminal at San Jose B substation. | Substation - Other Equipment | New | NA | T.0010902 ¦ T.0010873 ¦ T.0010874 ¦ T.0010875 ¦ T.0010908 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 2.1017 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814499 | T.0010876 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2026 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-08-17 | 2028-12-01 | 2027-11-05 | NA | NA | TRUE | 91000 | NA ¦ NA | 6.0658 | 1431.5355 | 0 | 0 | 0 | 0 | 3.684 | 242.4575 | 814.5743 | 207.7632 | 163.0565 | 0 | 3.6839 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,432 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1921 | Private Load Interconnection Project |  |  |  | Interconnect data center to Garlic 115kV Switching Station on Morgan Hill-Llagas 115kV line 115kV Garlic Switching Station • Install Three (3) 115kV, 3000A, 63kA Circuit Breakers, associated switches and bus structures for Bay 3 • Install breaker failure and reclosing relays for all new Circuit Breakers • Install Line Current Differential scheme for Garlic-LC24-1 115kV Line #1 & #2 AWS Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV line that PG&E will own, operate, and maintain • Install Remote Terminal Unit(RTU) for PG&E visibility • Install revenue metering Transmission Line • Relocate 115kV Garlic-LC24-24 #2 line terminal to Bay 3 and install LC24-1 115kV Line #2 • Install approximately 1 mile long single circuit 115kV Overhead Transmission Line to customer site from Garlic Switching Station | Substation - Multiple | New | NA | T.0010873 ¦ T.0010874 ¦ T.0010875 ¦ T.0010876 ¦ T.0010908 | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 2.3037 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5813930 | T.0010902 | Private Load Interconnection Project | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-10-30 | 2029-10-01 | 2029-10-01 | NA | NA | FALSE | 3600 | NA ¦ NA | 269.9871 | 11884.336 | 0 | 0 | 0 | 0 | 208.9578 | 1520.793 | 1612.087 | 4656.4153 | 3561.0565 | 325.0265 | 208.9577 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 54% ¦ $11,884 (Subject to change) | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1922 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install new 115kV BAAH GIS switching station with four (4) bays and the existing Swift-Metcalf 115kV line and Piercy-Metcalf 115kV lines will be looped through the new switching station. New 115kV GIS Switching Station • Acquire land less than a mile from Piercy substation and Construct a new 115kV Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with four (4) bays. • Install a new 115kV GIS/MPAC enclosure. • Install HVAC systems for GIS/MPAC enclosure. • Install Breaker failure and Reclosing relays using relays consistent with PG&E protection standards for breakers associated with Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install Line Current Differential line relay scheme using relays consistent with PG&E protection standards on the Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. • Install new battery, battery charger & battery monitoring system. Metcalf Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on New Switching station – Metcalf #1 Line. • Install Breaker Failure and Reclosing relays for breakers CB 422. • Install Line Current Differential scheme on New Switching Station – Metcalf #2 Line. • Install Breaker Failure and Reclosing relays for breakers CB 412. Swift Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Swift – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 142. Piercy Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Piercy – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 122. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Piercy-Metcalf and Swift-Metcalf 115kV lines into the New Switching Station. • Install approximately 0.86 mile two line extension using underground cables to customer site from the new switching station. | Other | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 7.3776 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5561439 | T.0010903 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | NA | NA | 2026-10-20 | NA | NA | TRUE | NA | NA ¦ NA | 74.9609 | 16868.7707 | 0 | 0 | 0 | 0 | 60.6315 | 16795.4615 | 12.6777 | 0 | 0 | 0 | 60.6315 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 60.6315 | 14.3294 | 0% | 100% ¦ $16,869 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1923 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install new 115kV BAAH GIS switching station with four (4) bays and the existing Swift-Metcalf 115kV line and Piercy-Metcalf 115kV lines will be looped through the new switching station. New 115kV GIS Switching Station • Acquire land less than a mile from Piercy substation and Construct a new 115kV Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with four (4) bays. • Install a new 115kV GIS/MPAC enclosure. • Install HVAC systems for GIS/MPAC enclosure. • Install Breaker failure and Reclosing relays using relays consistent with PG&E protection standards for breakers associated with Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install Line Current Differential line relay scheme using relays consistent with PG&E protection standards on the Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. • Install new battery, battery charger & battery monitoring system. Metcalf Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on New Switching station – Metcalf #1 Line. • Install Breaker Failure and Reclosing relays for breakers CB 422. • Install Line Current Differential scheme on New Switching Station – Metcalf #2 Line. • Install Breaker Failure and Reclosing relays for breakers CB 412. Swift Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Swift – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 142. Piercy Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Piercy – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 122. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Piercy-Metcalf and Swift-Metcalf 115kV lines into the New Switching Station. • Install approximately 0.86 mile two line extension using underground cables to customer site from the new switching station. | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.3509 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814133 | T.0010903 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-06-26 | NA | 2030-02-12 | NA | NA | FALSE | NA | NA ¦ NA | 543.5865 | 101924.2268 | 0 | 0 | 0 | 0 | 404.3302 | 19114.618 | 33502.9743 | 26270.6049 | 17085.2055 | 5506.2235 | 404.3301 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 57% ¦ $101,924 (Subject to change) | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1924 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install new 115kV BAAH GIS switching station with four (4) bays and the existing Swift-Metcalf 115kV line and Piercy-Metcalf 115kV lines will be looped through the new switching station. New 115kV GIS Switching Station • Acquire land less than a mile from Piercy substation and Construct a new 115kV Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with four (4) bays. • Install a new 115kV GIS/MPAC enclosure. • Install HVAC systems for GIS/MPAC enclosure. • Install Breaker failure and Reclosing relays using relays consistent with PG&E protection standards for breakers associated with Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install Line Current Differential line relay scheme using relays consistent with PG&E protection standards on the Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. • Install new battery, battery charger & battery monitoring system. Metcalf Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on New Switching station – Metcalf #1 Line. • Install Breaker Failure and Reclosing relays for breakers CB 422. • Install Line Current Differential scheme on New Switching Station – Metcalf #2 Line. • Install Breaker Failure and Reclosing relays for breakers CB 412. Swift Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Swift – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 142. Piercy Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Piercy – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 122. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Piercy-Metcalf and Swift-Metcalf 115kV lines into the New Switching Station. • Install approximately 0.86 mile two line extension using underground cables to customer site from the new switching station. | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.3509 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814127 | T.0010903 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-07-30 | NA | 2030-02-20 | NA | NA | FALSE | NA | NA ¦ NA | 38.5441 | 926.8949 | 0 | 0 | 0 | 0 | 44.1088 | 896.0972 | -224.0272 | 85.098 | 103.5597 | 22.0584 | 44.1088 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | Type 3 | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1925 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install new 115kV BAAH GIS switching station with four (4) bays and the existing Swift-Metcalf 115kV line and Piercy-Metcalf 115kV lines will be looped through the new switching station. New 115kV GIS Switching Station • Acquire land less than a mile from Piercy substation and Construct a new 115kV Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with four (4) bays. • Install a new 115kV GIS/MPAC enclosure. • Install HVAC systems for GIS/MPAC enclosure. • Install Breaker failure and Reclosing relays using relays consistent with PG&E protection standards for breakers associated with Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install Line Current Differential line relay scheme using relays consistent with PG&E protection standards on the Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. • Install new battery, battery charger & battery monitoring system. Metcalf Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on New Switching station – Metcalf #1 Line. • Install Breaker Failure and Reclosing relays for breakers CB 422. • Install Line Current Differential scheme on New Switching Station – Metcalf #2 Line. • Install Breaker Failure and Reclosing relays for breakers CB 412. Swift Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Swift – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 142. Piercy Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Piercy – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 122. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Piercy-Metcalf and Swift-Metcalf 115kV lines into the New Switching Station. • Install approximately 0.86 mile two line extension using underground cables to customer site from the new switching station. | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3509 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5816399 | T.0010903 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-08-24 | NA | 2030-02-22 | NA | NA | FALSE | NA | NA ¦ NA | 14.2477 | 208.6719 | 0 | 0 | 0 | 0 | 1.2388 | 365.7655 | -333.5724 | 39.5627 | 201.8162 | -66.1389 | 1.2388 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD ¦ TBD | Type 2 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1926 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install new 115kV BAAH GIS switching station with four (4) bays and the existing Swift-Metcalf 115kV line and Piercy-Metcalf 115kV lines will be looped through the new switching station. New 115kV GIS Switching Station • Acquire land less than a mile from Piercy substation and Construct a new 115kV Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with four (4) bays. • Install a new 115kV GIS/MPAC enclosure. • Install HVAC systems for GIS/MPAC enclosure. • Install Breaker failure and Reclosing relays using relays consistent with PG&E protection standards for breakers associated with Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install Line Current Differential line relay scheme using relays consistent with PG&E protection standards on the Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. • Install new battery, battery charger & battery monitoring system. Metcalf Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on New Switching station – Metcalf #1 Line. • Install Breaker Failure and Reclosing relays for breakers CB 422. • Install Line Current Differential scheme on New Switching Station – Metcalf #2 Line. • Install Breaker Failure and Reclosing relays for breakers CB 412. Swift Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Swift – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 142. Piercy Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Piercy – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 122. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Piercy-Metcalf and Swift-Metcalf 115kV lines into the New Switching Station. • Install approximately 0.86 mile two line extension using underground cables to customer site from the new switching station. | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814793 | T.0010903 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-08-13 | NA | 2026-09-18 | NA | NA | TRUE | NA | NA ¦ NA | 23.0188 | 0 | 0 | 0 | 0 | 0 | 30.1973 | -12.4841 | -40.9549 | 0 | 0 | 0 | 30.1972 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | Type 3 | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1927 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install new 115kV BAAH GIS switching station with four (4) bays and the existing Swift-Metcalf 115kV line and Piercy-Metcalf 115kV lines will be looped through the new switching station. New 115kV GIS Switching Station • Acquire land less than a mile from Piercy substation and Construct a new 115kV Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with four (4) bays. • Install a new 115kV GIS/MPAC enclosure. • Install HVAC systems for GIS/MPAC enclosure. • Install Breaker failure and Reclosing relays using relays consistent with PG&E protection standards for breakers associated with Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install Line Current Differential line relay scheme using relays consistent with PG&E protection standards on the Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. • Install new battery, battery charger & battery monitoring system. Metcalf Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on New Switching station – Metcalf #1 Line. • Install Breaker Failure and Reclosing relays for breakers CB 422. • Install Line Current Differential scheme on New Switching Station – Metcalf #2 Line. • Install Breaker Failure and Reclosing relays for breakers CB 412. Swift Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Swift – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 142. Piercy Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Piercy – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 122. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Piercy-Metcalf and Swift-Metcalf 115kV lines into the New Switching Station. • Install approximately 0.86 mile two line extension using underground cables to customer site from the new switching station. | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814794 | T.0010903 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-08-13 | NA | 2026-09-18 | NA | NA | TRUE | NA | NA ¦ NA | 16.1015 | 0 | 0 | 0 | 0 | 0 | 33.7164 | -6.1398 | -32.4713 | 0 | 0 | 0 | 33.7164 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | Type 3 | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1928 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install new 115kV BAAH GIS switching station with four (4) bays and the existing Swift-Metcalf 115kV line and Piercy-Metcalf 115kV lines will be looped through the new switching station. New 115kV GIS Switching Station • Acquire land less than a mile from Piercy substation and Construct a new 115kV Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with four (4) bays. • Install a new 115kV GIS/MPAC enclosure. • Install HVAC systems for GIS/MPAC enclosure. • Install Breaker failure and Reclosing relays using relays consistent with PG&E protection standards for breakers associated with Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install Line Current Differential line relay scheme using relays consistent with PG&E protection standards on the Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. • Install new battery, battery charger & battery monitoring system. Metcalf Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on New Switching station – Metcalf #1 Line. • Install Breaker Failure and Reclosing relays for breakers CB 422. • Install Line Current Differential scheme on New Switching Station – Metcalf #2 Line. • Install Breaker Failure and Reclosing relays for breakers CB 412. Swift Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Swift – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 142. Piercy Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Piercy – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 122. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Piercy-Metcalf and Swift-Metcalf 115kV lines into the New Switching Station. • Install approximately 0.86 mile two line extension using underground cables to customer site from the new switching station. | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.3509 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814131 | T.0010903 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-07-02 | NA | 2026-09-28 | NA | NA | TRUE | NA | NA ¦ NA | 45.0275 | 0 | 0 | 0 | 0 | 0 | 206.6412 | -104.8658 | -119.2623 | 0 | 0 | 0 | 206.6412 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | Type 3 | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1929 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install new 115kV BAAH GIS switching station with four (4) bays and the existing Swift-Metcalf 115kV line and Piercy-Metcalf 115kV lines will be looped through the new switching station. New 115kV GIS Switching Station • Acquire land less than a mile from Piercy substation and Construct a new 115kV Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with four (4) bays. • Install a new 115kV GIS/MPAC enclosure. • Install HVAC systems for GIS/MPAC enclosure. • Install Breaker failure and Reclosing relays using relays consistent with PG&E protection standards for breakers associated with Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install Line Current Differential line relay scheme using relays consistent with PG&E protection standards on the Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. • Install new battery, battery charger & battery monitoring system. Metcalf Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on New Switching station – Metcalf #1 Line. • Install Breaker Failure and Reclosing relays for breakers CB 422. • Install Line Current Differential scheme on New Switching Station – Metcalf #2 Line. • Install Breaker Failure and Reclosing relays for breakers CB 412. Swift Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Swift – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 142. Piercy Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Piercy – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 122. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Piercy-Metcalf and Swift-Metcalf 115kV lines into the New Switching Station. • Install approximately 0.86 mile two line extension using underground cables to customer site from the new switching station. | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 7.3776 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814470 | T.0010903 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-12-27 | NA | 2030-02-08 | NA | NA | FALSE | NA | NA ¦ NA | 69.2698 | 1438.001 | 0 | 0 | 0 | 0 | 29.459 | 338.1642 | 185.3612 | 197.8333 | 362.5491 | 324.6342 | 29.4589 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,438 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1930 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install new 115kV BAAH GIS switching station with four (4) bays and the existing Swift-Metcalf 115kV line and Piercy-Metcalf 115kV lines will be looped through the new switching station. New 115kV GIS Switching Station • Acquire land less than a mile from Piercy substation and Construct a new 115kV Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with four (4) bays. • Install a new 115kV GIS/MPAC enclosure. • Install HVAC systems for GIS/MPAC enclosure. • Install Breaker failure and Reclosing relays using relays consistent with PG&E protection standards for breakers associated with Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install Line Current Differential line relay scheme using relays consistent with PG&E protection standards on the Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. • Install new battery, battery charger & battery monitoring system. Metcalf Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on New Switching station – Metcalf #1 Line. • Install Breaker Failure and Reclosing relays for breakers CB 422. • Install Line Current Differential scheme on New Switching Station – Metcalf #2 Line. • Install Breaker Failure and Reclosing relays for breakers CB 412. Swift Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Swift – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 142. Piercy Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Piercy – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 122. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Piercy-Metcalf and Swift-Metcalf 115kV lines into the New Switching Station. • Install approximately 0.86 mile two line extension using underground cables to customer site from the new switching station. | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814471 | T.0010903 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2029-12-27 | NA | 2030-02-08 | NA | NA | FALSE | NA | NA ¦ NA | 43.7555 | 1505.4448 | 0 | 0 | 0 | 0 | 26.6988 | 360.5517 | 196.5144 | 209.9262 | 302.474 | 409.2798 | 26.6987 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,505 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1931 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install new 115kV BAAH GIS switching station with four (4) bays and the existing Swift-Metcalf 115kV line and Piercy-Metcalf 115kV lines will be looped through the new switching station. New 115kV GIS Switching Station • Acquire land less than a mile from Piercy substation and Construct a new 115kV Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with four (4) bays. • Install a new 115kV GIS/MPAC enclosure. • Install HVAC systems for GIS/MPAC enclosure. • Install Breaker failure and Reclosing relays using relays consistent with PG&E protection standards for breakers associated with Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install Line Current Differential line relay scheme using relays consistent with PG&E protection standards on the Piercy – New switching station, Swift – New Switching station, New Switching Station – Metcalf #1, New Switching Station – Metcalf #2 and New Switching Station – Prologis LC24-13 115kV Lines • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. • Install new battery, battery charger & battery monitoring system. Metcalf Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on New Switching station – Metcalf #1 Line. • Install Breaker Failure and Reclosing relays for breakers CB 422. • Install Line Current Differential scheme on New Switching Station – Metcalf #2 Line. • Install Breaker Failure and Reclosing relays for breakers CB 412. Swift Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Swift – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 142. Piercy Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install Line Current Differential scheme on Piercy – New Switching Station 115kV Line. • Install Breaker Failure and Reclosing relays for breakers CB 122. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Piercy-Metcalf and Swift-Metcalf 115kV lines into the New Switching Station. • Install approximately 0.86 mile two line extension using underground cables to customer site from the new switching station. | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3509 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5816398 | T.0010903 | Private Load Interconnection Project | 15 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-08-01 | NA | 2026-09-28 | NA | NA | FALSE | NA | NA ¦ NA | 270.4166 | 270.4166 | 0 | 0 | 0 | 0 | 26.8983 | 243.5183 | 0 | 0 | 0 | 0 | 26.8983 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | Type 4 | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1932 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install a new two (2) bay BAAH GIS Switching station and the existing Trimble-Montague 115kV line will be looped through the new switching station. New 115kV Charcot Switching Station • Install a new 115kV two (2) bay Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with the land provision for ultimate four (4) bay. • Install Breaker failure and Reclosing relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install line current differential relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. Trimble Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Trimble – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 312. Montague Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Montague – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 142. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Trimble-Montague 115kV line through the new 115kV Switching Station • Install approximately 0.80 mile two line extension using underground cables | Other | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 1.2309 | NA | NA | NA | NA | NA | 5.211 | Non-IGP | 5561482 | T.0010908 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | NA | NA | 2026-11-09 | NA | NA | TRUE | NA | NA ¦ NA | 100.2915 | 57501.3006 | 0 | 0 | 0 | 0 | 84.0046 | 57416.671 | 0.6251 | 0 | 0 | 0 | 84.0046 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 84.0046 | 16.2869 | 0% | 100% ¦ $57,501 | Type 3 | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1933 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install a new two (2) bay BAAH GIS Switching station and the existing Trimble-Montague 115kV line will be looped through the new switching station. New 115kV Charcot Switching Station • Install a new 115kV two (2) bay Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with the land provision for ultimate four (4) bay. • Install Breaker failure and Reclosing relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install line current differential relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. Trimble Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Trimble – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 312. Montague Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Montague – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 142. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Trimble-Montague 115kV line through the new 115kV Switching Station • Install approximately 0.80 mile two line extension using underground cables | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814562 | T.0010908 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-01-10 | NA | 2030-02-25 | NA | NA | FALSE | NA | NA ¦ NA | 68.376 | 2424.5006 | 0 | 0 | 0 | 0 | 40.3674 | 409.6912 | 464.1558 | 478.8664 | 513.8219 | 517.598 | 40.3674 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,425 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1934 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install a new two (2) bay BAAH GIS Switching station and the existing Trimble-Montague 115kV line will be looped through the new switching station. New 115kV Charcot Switching Station • Install a new 115kV two (2) bay Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with the land provision for ultimate four (4) bay. • Install Breaker failure and Reclosing relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install line current differential relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. Trimble Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Trimble – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 312. Montague Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Montague – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 142. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Trimble-Montague 115kV line through the new 115kV Switching Station • Install approximately 0.80 mile two line extension using underground cables | Substation - Other Equipment | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.2309 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5814561 | T.0010908 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-01-30 | NA | 2030-03-14 | NA | NA | FALSE | NA | NA ¦ NA | 65.6952 | 1724.96 | 0 | 0 | 0 | 0 | 35.2893 | 265.0096 | 374.7163 | 302.8165 | 325.0891 | 422.0392 | 35.2893 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,725 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1935 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install a new two (2) bay BAAH GIS Switching station and the existing Trimble-Montague 115kV line will be looped through the new switching station. New 115kV Charcot Switching Station • Install a new 115kV two (2) bay Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with the land provision for ultimate four (4) bay. • Install Breaker failure and Reclosing relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install line current differential relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. Trimble Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Trimble – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 312. Montague Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Montague – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 142. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Trimble-Montague 115kV line through the new 115kV Switching Station • Install approximately 0.80 mile two line extension using underground cables | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 5.1001 | Non-IGP | 5813933 | T.0010908 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-12-21 | NA | 2030-04-08 | NA | NA | FALSE | NA | NA ¦ NA | 414.7332 | 39787.4675 | 0 | 0 | 0 | 0 | 330.5067 | 3657.2172 | 19945.2339 | 7604.2181 | 5120.5629 | 3082.2087 | 330.5067 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 76% ¦ $39,787 (Subject to change) | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1936 | Private Load Interconnection Project |  |  |  | This project proposes to interconnect a data center and install a new two (2) bay BAAH GIS Switching station and the existing Trimble-Montague 115kV line will be looped through the new switching station. New 115kV Charcot Switching Station • Install a new 115kV two (2) bay Breaker-And-A-Half (BAAH) Gas Insulated Switchgear (GIS) switching station with the land provision for ultimate four (4) bay. • Install Breaker failure and Reclosing relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install line current differential relays using PG&E protection standards for breakers associated with Trimble – New Switching Station 115 kV, Montague – New Switching Station 115 kV and New Switching Station – L24-3 115 kV #1 & #2 lines. • Install SMP High Impedance Bus Differential Scheme on Bus 1 and Bus 2. Trimble Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Trimble – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 312. Montague Substation • Replace existing line and breaker relay schemes to coordinate with the new Current Differential scheme at the New Switching Station. • Install control building extension to accommodate line relay upgrades needed to connect the new Switching Station to the PG&E System. • Install Line Current Differential scheme on Montague – New Switching Station 115 kV Line. • Install Breaker Failure and Reclosing relays for breakers 142. Prologis Site • Install a PG&E Metering Building to house major PG&E equipment • Install protective relays for the 115kV lines that PG&E will own, operate, and maintain • Install Remote Terminal Unit (RTU) for PG&E visibility • Install revenue metering Transmission Line • Loop in the existing Trimble-Montague 115kV line through the new 115kV Switching Station • Install approximately 0.80 mile two line extension using underground cables | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.8982 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5813935 | T.0010908 | Private Load Interconnection Project | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-12-24 | NA | 2027-07-14 | NA | NA | TRUE | NA | NA ¦ NA | 45.0085 | 538.8017 | 0 | 0 | 0 | 0 | 53.4044 | 73.6795 | 113.0178 | 95.1522 | 89.3133 | 114.2344 | 53.4044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $539 | Type 3 | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1937 | Private Load Interconnection Project |  |  |  | This project proposes to install a new 230/34.5kV substation with a 230kV GIS, (3) 230/34.5kV 150MVA transformers, (2) 34.5 kV 3000A switchgears, and distribution feeders to the customer sites and the Newark-NRS 230kV line will be looped through the new Substation. | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-08 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.6495 | NA | 230 kV | NA | NA | NA | 5.211 | Non-IGP | 5815018 | T.0011156 | Private Load Interconnection Project | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-01-01 | NA | 2029-01-09 | NA | NA | FALSE | NA | NA ¦ NA | 414.1759 | 61915.6473 | 0 | 0 | 0 | 0 | 375.7127 | 88.9266 | 615.8273 | 610.0651 | 60225.1157 | 0 | 375.7127 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 97% ¦ $61,916 (Subject to change) | Type 3 | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1938 | 82W Plan - EGI |  |  | NA | Forecast placeholder for generation interconnection projects | Substation - Multiple | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | False ¦ False ¦ False | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 1.0001 | Non-IGP | 5554999 | NA | NA | NA | 82 | NA ¦ 5533304 ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 389354 | 0 | 0 | 0 | 0 | 0 | 0.3381 | 0 | 155365.2425 | 22851.6549 | 178583.0994 | -0.3381 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $389,354 | NA | NA ¦ NA | NA | 35.18% | 64.82% | [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
1939 | Caltrain IC - Substation Site 1 (82) |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-18 | 68 | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.3775 | NA | 115 kV | 3 | 6. Customer commitments | NA | 5.211 | Non-IGP | 5766383 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | NA ¦ 5743532 ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2017 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-05-08 | 2021-06-30 | 2021-03-23 | NA | NA | FALSE | 46700 | NA ¦ NA | 27641.4141 | 27641.4141 | -9107.0438 | 2580.1411 | 1399.4282 | -875.1187 | -90.0019 | 0 | 0 | 0 | 0 | 0 | 27641.4141 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 24458.1622 | 2560.5445 | 1390.0049 | -869.2258 | -89.3962 | 0 | 0% | 60% ¦ $27,641 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1940 | Caltrain IC - Remote End at Martin (82) |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-18 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.3775 | NA | 115 kV | 3 | 6. Customer commitments | NA | NA | NA | 5776103 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2018 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-02-01 | 2021-06-30 | 2021-03-23 | NA | NA | FALSE | 46700 | NA ¦ NA | 1060.8973 | 1060.8973 | 672.2738 | -25.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060.8973 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1078.9708 | -25.7234 | 0 | 0 | 0 | 0 | 0% | 60% ¦ $1,061 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1941 | Caltrain IC - Remote End at MA (82) |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-18 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.3775 | NA | 115 kV | 3 | 6. Customer commitments | NA | NA | NA | 5776102 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-01 | 2021-06-30 | 2021-09-23 | NA | NA | FALSE | 46700 | NA ¦ NA | 825.1741 | 825.1741 | 486.568 | 59.3309 | 6.3978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 825.1741 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 744.483 | 58.1472 | 6.2615 | 0 | 0 | 0 | 0% | 60% ¦ $825 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1942 | Caltrain IC - Remote End San Mateo (82) |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-18 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.3775 | NA | 115 kV | 3 | 6. Customer commitments | NA | NA | NA | 5776104 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-04-01 | 2021-06-30 | 2021-09-23 | NA | NA | FALSE | 46700 | NA ¦ NA | 998.7229 | 998.7229 | 755.7955 | -29.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998.7229 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 1014.3341 | -28.6057 | 0 | 0 | 0 | 0 | 0% | 60% ¦ $999 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1943 | Caltrain IC - VGVVRAS (82) |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Multiple | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-18 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.3775 | NA | 115 kV | 3 | 6. Customer commitments | NA | NA | NA | 5776106 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-01-01 | 2021-06-30 | 2023-01-25 | Construction Delays | NA | FALSE | 46700 | NA ¦ NA | 199.7926 | 199.7926 | -17.5503 | 100.1409 | -5.3262 | -5.582 | 0 | 0 | 0 | 0 | 0 | 0 | 199.7926 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 195.5193 | -5.2616 | 0 | 0 | 0% | 60% ¦ $200 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1944 | Caltrain South San Francisco TPS |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Bus Arrangement | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-18 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.3775 | NA | 115 kV | NA | 6. Customer commitments | NA | NA | NA | 5779702 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2021 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-10-11 | 2021-06-30 | 2023-09-01 | Construction Delays | NA | FALSE | 46700 | NA ¦ NA | 301.5831 | 301.5831 | 357.7868 | -178.0148 | 131.7527 | -10.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 301.5831 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 311.5453 | -10.0261 | 0 | 0 | 0% | 60% ¦ $302 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1945 | CALTRAIN S. SAN FRANCISCO TPS1 BATTERY |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-18 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.3775 | NA | 115 kV | NA | NA | NA | NA | NA | 5804778 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2023 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-09-18 | 2021-06-30 | 2023-11-10 | Construction Delays | NA | FALSE | 46700 | NA ¦ NA | 42.9828 | 42.9828 | 0 | 0 | 50.4029 | -7.635 | 0.2148 | 0 | 0 | 0 | 0 | 0 | 42.9828 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 49.5034 | -7.4971 | 0.21093 | 0 | 0% | 60% ¦ $43 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1946 | HSR Interconnection Sub Sites 4-7 (82) |  |  | TBD | TPS Sites 4 to 7 will power the section of the rail line that connects the Bay Area with the Central Valley. When the CHSR Project is completed and in-service, the CHSR substation at Sites 4 to 7 will have a total power demand of over 230 megawatts (MW). The interconnections at Sites 4 to 7 will consist of the major work components shown below. There will be other system work needed to address protection and automation upgrades needed for the system reconfigurations resulting from the interconnections. Generally, “Network Upgrades” will be performed by PG&E, and work for new “Interconnection Facilities” will be performed by CHSRA or its contractors. | Substation - Multiple | New | NA | T.0000006 ¦ T.0002127 ¦ T.0004116 ¦ T.0002231 | Work Requested by Others | Load Interconnection | NA | NA | NA | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | TBD | NA | 230 ¦ 115 kV | 3 | 6. Customer commitments | NA | 5.211 | Non-IGP | 5766464 | T.0000005 | CHSR Interconnections, Sites 4-7 | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2017 | 2018 | FALSE | NA | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-04-02 | 2020-12-01 | 2032-03-16 | Customer Action | Scope Change | FALSE | 285000 | NA ¦ NA | 5903.7396 | 216084.7558 | 410.4698 | 459.078 | 564.9902 | 549.4863 | 477.5572 | 612.1667 | 1465.3318 | 3770.7523 | 48860.582 | 15878.1446 | 5824.5804 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 (Final allocation not yet finalized with CPUC & FERC) | NA | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1947 | HSR Interconnection Sub Sites 8-13 (82) |  |  | TBD | California High Speed Rail (CHSR) Transmission Power Delivery Project – Sites 8 through 13. The Project will require the installation of a 25 kV AC Traction Electrification System (TES) to power the electric trains. In order to have adequate capacity for train operations, the proposed TES will interconnect into local utility networks at 115 kV or 230 kV, with approximately 30-mile intervals between the traction power substations. This substation spacing results in twelve (12) traction power substations for the 345-mile portion of the line running in PG&E’s service territory.There are six (6) interconnection sites located in the Madera to Bakersfield section. These sites have been designated as Sites 8 through 13. | Substation - Multiple | New | NA | T.0000005 ¦ T.0001650 ¦ T.0000924 ¦ T.0000204 ¦ T.0000980 ¦ T.0003202 ¦ T.0000220 ¦ T.0000143 ¦ T.0000156 | Work Requested by Others | Load Interconnection | NA | NA | NA | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | TBD | NA | 230 ¦ 115 kV | 3 | 6. Customer commitments | NA | 5.211 | Non-IGP | 5766319 | T.0000006 | CHSR Interconnections, Sites 8-13 | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2017 | 2018 | FALSE | NA | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2034-07-05 | 2020-12-01 | 2036-11-11 | Customer Action | Scope Change | FALSE | 454000 | NA ¦ NA | 5621.2922 | 348121.1578 | 390.468 | 438.9385 | 573.4193 | 555.087 | 454.7504 | 560.4467 | 1017.2596 | 2578.8544 | 8385.7015 | 57718.1614 | 5543.3895 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 (Final allocation not yet finalized with CPUC & FERC) | NA | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1948 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 100 megawatt (MW) (net output) solar-based generation facility to the Pacific Gas and Electric Company’s (PG&E’s) new 230 kV Bitterwater Switching Station which connects to the Midway – Wheeler Ridge 230 kV Line No.2 in Kern County, California. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5798626 | T.0001353 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2022 | 2015 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6634-E | 2022-06-30 | Approved | 2022 | Engineering more than 50% complete | 3 | 2027-12-22 | 2018-12-01 | 2028-03-21 | Customer Action | NA | FALSE | 19820 | NA ¦ NA | 62.4128 | 2983.5691 | 0 | 25.0837 | 16.6295 | 7.2806 | 9.8677 | 524.088 | 611.667 | 1642.2627 | 146.6898 | 0 | 58.8615 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,984 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1949 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 100 megawatt (MW) (net output) solar-based generation facility to the Pacific Gas and Electric Company’s (PG&E’s) new 230 kV Bitterwater Switching Station which connects to the Midway – Wheeler Ridge 230 kV Line No.2 in Kern County, California. | Substation - Multiple | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | 3 | 6. Customer commitments | NA | 5.3 | Non-IGP | 5768563 | T.0001353 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2017 | 2015 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6634-E | 2022-06-30 | Approved | 2022 | Operational | 1 | 2023-02-14 | 2018-12-01 | 2024-04-20 | Customer Action | NA | TRUE | 19820 | NA ¦ NA | 3310.0832 | 3310.0832 | 17.3905 | 174.9436 | 1895.0635 | 1016.0626 | 179.3907 | 11.1749 | 0 | 0 | 0 | 0 | 3298.9083 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 3119.5305 | 179.3907 | 11.1749 | 0% | 100% ¦ $3,310 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1950 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 100 megawatt (MW) (net output) solar-based generation facility to the Pacific Gas and Electric Company’s (PG&E’s) new 230 kV Bitterwater Switching Station which connects to the Midway – Wheeler Ridge 230 kV Line No.2 in Kern County, California. | Substation - Multiple | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.4 | NA | 230 kV | 3 | 6. Customer commitments | NA | 5.3 | Non-IGP | 5768561 | T.0001353 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2017 | 2015 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6634-E | 2022-06-30 | Approved | 2022 | Operational | 1 | 2024-04-08 | 2018-12-01 | 2024-04-22 | Customer Action | NA | FALSE | 19820 | NA ¦ NA | 597.7088 | 597.7088 | 3.4212 | 141.5169 | 245.4593 | 182.4542 | 10.3936 | 0 | 0 | 0 | 0 | 0 | 597.7088 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 587.1975 | 10.3936 | 0 | 0% | 100% ¦ $598 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1951 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 100 megawatt (MW) (net output) solar-based generation facility to the Pacific Gas and Electric Company’s (PG&E’s) new 230 kV Bitterwater Switching Station which connects to the Midway – Wheeler Ridge 230 kV Line No.2 in Kern County, California. | Substation - Multiple | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5768560 | T.0001353 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2017 | 2015 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6634-E | 2022-06-30 | Approved | 2022 | Operational | 1 | 2024-04-09 | 2018-12-01 | 2024-04-23 | Customer Action | NA | TRUE | 19820 | NA ¦ NA | 478.7517 | 478.7517 | 23.6691 | 118.5132 | 192.8326 | 124.1944 | 15.129 | 0 | 0 | 0 | 0 | 0 | 478.7517 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 463.5557 | 15.129 | 0 | 0% | 100% ¦ $479 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1952 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 100 megawatt (MW) (net output) solar-based generation facility to the Pacific Gas and Electric Company’s (PG&E’s) new 230 kV Bitterwater Switching Station which connects to the Midway – Wheeler Ridge 230 kV Line No.2 in Kern County, California. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5798542 | T.0001353 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2022 | 2015 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6634-E | 2022-06-30 | Approved | 2022 | Operational | 1 | 2024-04-08 | 2018-12-01 | 2024-04-23 | Customer Action | NA | FALSE | 19820 | NA ¦ NA | 436.0817 | 436.0817 | 0 | 22.9262 | 266.1341 | 133.4392 | 13.5823 | 0 | 0 | 0 | 0 | 0 | 436.0817 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 422.4995 | 13.5823 | 0 | 0% | 100% ¦ $436 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1953 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 100 megawatt (MW) (net output) solar-based generation facility to the Pacific Gas and Electric Company’s (PG&E’s) new 230 kV Bitterwater Switching Station which connects to the Midway – Wheeler Ridge 230 kV Line No.2 in Kern County, California. | Other | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 230 kV | NA | NA | NA | 3.002 | NA | 5556763 | T.0001353 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2024 | 2015 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6634-E | 2022-06-30 | Approved | 2022 | Operational | 1 | NA | 2018-12-01 | OAI | NA | NA | FALSE | 19820 | NA ¦ NA | 11000 | 11000 | 0 | 0 | 0 | 11000 | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 11000 | 0 | 0 | 0% | 100% ¦ $11,000 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1954 | WRO Generator Network Upgrades |  |  |  | Interconnect a 150 megawatt (MW) (net output) solar-based generation facility to Gates 230 kV BAAH Switchyard, in Fresno County, California. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | 3 | 6. Customer commitments | NA | NA | NA | 5757640 | T.0001403 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2018 | 2015 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2019-04-01 | 2017-12-01 | 2023-02-17 | Customer action | NA | FALSE | 2510 | NA ¦ NA | 2770.2344 | 2770.2344 | 208.2452 | 264.7772 | 60.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2770.2344 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 2442.4284 | -2442.4284 | 2767.2534 | 0 | 0 | 0 | 0% | 100% ¦ $2,770 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1955 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 12 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) Woodland – Davis 115 kV Line, in Yolo County, California. Network Upgrades Scope of work • Install two (2) DTT receivers and perform associated relay setting changes at Woodland and Davis. • Install (1) new light duty steel pole to be used as the tap structure • Install (2) new SCADA Switches on the Woodland – Davis 115 kV Line, one on each side of the tap structure • Install (2) new TSPs on the Woodland – Davis 115 kV Line, one on each side of the tap structure | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7115 | NA | 115 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5770164 | T.0001728 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2015 | Project Management Governance Standard | 2018 | 2014 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 2 | 2017-02-13 | 2015-11-01 | 2024-09-30 | Customer Action | NA | TRUE | 2920 | NA ¦ NA | 899.0967 | 1080.8496 | 47.6972 | 51.6534 | 90.5041 | 46.8621 | 0 | 60.2151 | 77.2811 | 44.2566 | 0 | 0 | 899.0967 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,081 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1956 | Caltrain IC - Remote End at Kifer (82) |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-08 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.0642 | NA | 115 kV | 3 | 6. Customer commitments | NA | NA | NA | 5776108 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 1 | 2021-02-15 | 2021-06-30 | 2021-06-16 | NA | NA | FALSE | 64500 | NA ¦ NA | 817.0994 | 817.0994 | 126.2249 | 10.8998 | 442.4216 | 0.3769 | 0 | 0 | 0 | 0 | 0 | 0 | 817.0994 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 356.7026 | 10.6636 | 432.8362 | 0.36877 | -2e-05 | 0 | 0% | 60% ¦ $817 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1957 | Caltrain IC-Remote End at San JoseB (82) |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-08 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.0642 | NA | 115 kV | 3 | 6. Customer commitments | NA | NA | NA | 5776109 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 1 | 2021-03-01 | 2021-06-30 | 2021-07-22 | NA | NA | FALSE | 64500 | NA ¦ NA | 868.6165 | 868.6165 | 648.2438 | -25.5757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 868.6165 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 883.8674 | -25.2528 | 0 | 0 | 0 | 0 | 0% | 60% ¦ $869 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1958 | Caltrain IC - Substation Site 3 (82) |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-08 | 25 | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.0642 | NA | 115 kV | 3 | 6. Customer commitments | NA | 5.211 | Non-IGP | 5772270 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2018 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 1 | 2019-05-13 | 2021-06-30 | 2022-02-19 | Construction Delays | NA | FALSE | 64500 | NA ¦ NA | 27610.9449 | 27610.9449 | -12980.2996 | 5723.1113 | 656.6039 | -736.0819 | -90.2531 | 0 | 0 | 0 | 0 | 0 | 27610.9449 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 27585.1078 | 652.3603 | -731.3246 | -89.6698 | 0 | 0% | 60% ¦ $27,611 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1959 | Caltrain San Jose TPS |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Multiple | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-08 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.0642 | NA | 115 kV | NA | 6. Customer commitments | NA | NA | NA | 5779707 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2020 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 1 | 2021-06-08 | 2021-06-30 | 2022-08-29 | Construction Delays | NA | FALSE | 64500 | NA ¦ NA | 749.5145 | 749.5145 | 495.2607 | 251.3454 | 19.4025 | -20.5502 | 0 | 0 | 0 | 0 | 0 | 0 | 749.5145 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 750.5119 | 19.4025 | -20.5502 | 0 | 0 | 0% | 60% ¦ $750 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1960 | CALTRAIN SAN JOSE TPS2 BATTERY |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-08 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.0642 | NA | 115 kV | NA | NA | NA | NA | NA | 5804779 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2017 | Project Management Governance Standard | 2023 | 2017 | FALSE | NA | NA | https://www.caiso.com/documents/board-approved_2016-2017transmissionplan.pdf | FALSE | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 1 | 2023-10-09 | 2021-06-30 | 2023-11-16 | Construction Delays | NA | FALSE | 64500 | NA ¦ NA | 100.3155 | 100.3155 | 0 | 0 | 114.3867 | -14.1814 | 0.1102 | 0 | 0 | 0 | 0 | 0 | 100.3155 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 112.4074 | -13.9304 | 0.10824 | 0 | 0% | 60% ¦ $100 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1961 | WRO Generator Network Upgrades |  |  |  | The project proposes to interconnect a 46.2 megawatt (MW) (net output) wind power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) owned Vasco – Herdlyn 60 kV Line at the junction of the PG&E-owned US Windpower #1 60 kV tap line, also known as the Windpower Junction, in Alameda County, California. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.81884 | NA | 60 kV | 3 | 6. Customer commitments | NA | NA | NA | 5772230 | T.0002228 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2020 | 2016 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-01 | 2018-02-01 | 2021-06-08 | Prioritization | NA | FALSE | 620 | NA ¦ NA | 512.7177 | 512.7177 | 157.8693 | 9.7611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512.7177 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 502.8796 | 9.7625 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $513 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1962 | WRO Generator Network Upgrades |  |  |  | The project proposes to interconnect a 46.2 megawatt (MW) (net output) wind power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) owned Vasco – Herdlyn 60 kV Line at the junction of the PG&E-owned US Windpower #1 60 kV tap line, also known as the Windpower Junction, in Alameda County, California. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-04-02 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.2184 | NA | 60 kV | 3 | 6. Customer commitments | NA | NA | NA | 5772231 | T.0002228 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2018 | Project Management Governance Standard | 2020 | 2016 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-01 | 2018-02-01 | 2021-06-08 | Prioritization | NA | FALSE | 620 | NA ¦ NA | 330.5706 | 330.5706 | 95.7323 | 35.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330.5706 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 295.3473 | 35.0545 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $331 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1963 | WRO Generator Network Upgrades |  |  |  | The project proposes to interconnect a 20-megawatt (MW) & a 100 (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) existing Mendota 115 kV Breaker-and-a-half (BAAH) Substation, in Fresno County, California. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.0936 | NA | 115 kV | 3 | 6. Customer commitments | NA | NA | Non-IGP | 5774923 | T.0003005 | WRO Generator Network Upgrades | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2020 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-02-01 | 2020-04-30 | 2020-08-03 | NA | NA | FALSE | 4620 | NA ¦ NA | 1607.7461 | 1607.7461 | -88.0652 | 0 | 0 | 0 | 2514.006 | 0 | 0 | 0 | 0 | 0 | 1607.7461 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2025 ¦ 2026 | -88.0661 | 0 | 0 | 0 | 2514.006 | 0 | 0% | 100% ¦ $1,608 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1964 | QC8RAS-08 Gates 500/230 kV Transformer B |  |  | Fresno | The Gates 500kv Bank 11/12 QRAS project will install a relay scheme at Gates substation and the Castanea customer site that will provide overload protection in the event of an outage on Gates 500kv Bank 11 or 12 | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Deferral | $2 Mil - $3 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 77.6619 | NA | 500 ¦ 230 kV | NA | 6. Customer commitments | NA | 5.3 | Non-IGP | 5774961 | T.0003009 | QC8RAS-08 Gates 500/230 kV Transformer B | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2019 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-06-13 | 2021-01-01 | 2024-10-16 | Material | NA | FALSE | 2712 | NA ¦ NA | 2138.5455 | 2138.5455 | 139.8447 | 744.1364 | 463.8683 | 667.3469 | 0.9618 | -29.3796 | 0 | 0 | 0 | 0 | 2167.9251 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 2166.827 | 0.96184 | -29.3796 | 0% | 100% ¦ $2,139 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1965 | Los Banos: Upgrade Terminal Equipt. |  |  | Merced | Reconductor 4.5 miles of the Los Banos - Padre Flat Switching Station 230 kV Line No. 1 with 1113 ACSS conductor. Upgrade associated equipment to 1,900 Amps to match the new conductor rating, as needed. Replace structures, as needed | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | 70 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 53.2803 | NA | 230 kV | 3 | NA | NA | NA | NA | 5794848 | T.0003016 | Los Banos - Padre Flat SS 20266: Recon. | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2019 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6527-E | 2022-03-11 | Approved | 2022 | Operational | 1 | 2022-10-31 | 2021-09-30 | 2022-12-24 | Material | NA | FALSE | 14300 | NA ¦ NA | 1370.3891 | 1370.3891 | 138.8551 | 1061.3064 | 124.7371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1370.3891 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 138.8551 | 1010.868 | 119.6862 | 0 | 0 | 0 | 0% | 100% ¦ $1,370 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1966 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | T.0009188 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 26.1945 | NA | 230 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5775142 | T.0003035 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-06-07 | 2020-06-01 | 2027-08-11 | Customer Action | NA | TRUE | 31980 | NA ¦ NA | 238.6633 | 512.0548 | 75.248 | 36.5949 | 15.5666 | 11.349 | 17.0443 | 30.0933 | 246.2912 | 0 | 0 | 0 | 235.6703 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $512 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1967 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Substation - Line Termination | New | NA | T.0009188 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-04 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.7679 | NA | 230 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5775141 | T.0003035 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2018 | 2017 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2029-02-02 | 2020-06-01 | 2029-06-12 | Customer Action | NA | FALSE | 31980 | NA ¦ NA | 40.0546 | 1237.4049 | 18.4283 | 15.1257 | 2.6338 | 1.3732 | 0 | 84.1714 | 180.5265 | 366.605 | 325.9611 | 226.0611 | 40.0546 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,237 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1968 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | T.0009188 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 26.1945 | NA | 230 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5775144 | T.0003035 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2029-07-09 | 2020-06-01 | 2029-12-18 | Customer Action | NA | FALSE | 31980 | NA ¦ NA | 54.3354 | 8932.9063 | 15.9535 | 31.0664 | 2.9591 | 1.8628 | 0 | 37.31 | 86.64 | 74.8006 | 1956.9523 | 2654.6303 | 54.3354 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $8,933 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1969 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Substation - Line Termination | New | NA | T.0009188 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 26.1945 | NA | 230 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5775140 | T.0003035 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2018 | 2017 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2030-07-11 | 2020-06-01 | 2030-12-23 | Customer Action | NA | FALSE | 31980 | NA ¦ NA | 136.6418 | 2162.1711 | 57.2779 | 72.2547 | 1.4401 | 4.6845 | 0 | 84.3437 | 1051.6715 | 154.5487 | 144.8922 | 576.3868 | 136.6418 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,162 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
1970 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 400 megawatt (MW) (net output) solar power-based generation facility to the PG&E-owned 230 kV Tranquillity Switching Station in Fresno County, California. | Substation - Bus Arrangement | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-10 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 6.7555 | NA | 230 kV | 3 | 6. Customer commitments | NA | NA | NA | 5778461 | T.0003742 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-19 | 2020-12-31 | 2023-02-28 | Construction Delays | NA | FALSE | 6980 | NA ¦ NA | 6988.9579 | 6988.9579 | 212.4329 | 5707.6534 | 881.5375 | -38.6913 | -34.1499 | 0 | 0 | 0 | 0 | 0 | 6988.9579 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 7061.3135 | -38.6913 | -34.1499 | 0 | 0% | 100% ¦ $6,989 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1971 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a gross output of 10.21-megawatt (MW) (net output), with auxiliary load of 0.14 MW and an estimated line loss of 0.07 MW, results in a maximum net output of 10 MW Energy Storage facility into Pacific Gas and Electric Company’s (PG&E’s) Olive Switching Station (SS) which is tapped onto the Corcoran – Olive SS 115 kV Line in Tulare County, California. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.8529 | NA | 115 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5778903 | T.0003744 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2024 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2022-09-01 | 2019-11-01 | 2026-03-30 | Prioritization | NA | TRUE | 980 | NA ¦ NA | 276.4404 | 277.2697 | 52.1244 | 70.099 | 57.9675 | 47.4109 | 37.1346 | 3.298 | 0 | 0 | 0 | 0 | 273.9717 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 273.9793 | 2.4687 | 0% | 100% ¦ $277 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1972 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a gross output of 10.21-megawatt (MW) (net output), with auxiliary load of 0.14 MW and an estimated line loss of 0.07 MW, results in a maximum net output of 10 MW Energy Storage facility into Pacific Gas and Electric Company’s (PG&E’s) Olive Switching Station (SS) which is tapped onto the Corcoran – Olive SS 115 kV Line in Tulare County, California. | Substation - Other Equipment | New | NA | 5794018 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.2701 | NA | 115 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5778904 | T.0003744 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2024 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-01 | 2019-11-01 | 2026-03-02 | Prioritization | NA | TRUE | 980 | NA ¦ NA | 400.5341 | 401.7357 | 43.097 | 154.0225 | 79.6625 | 54.3355 | 54.944 | 3.9789 | 0 | 0 | 0 | 0 | 397.7568 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 397.7722 | 2.7773 | 0% | 100% ¦ $402 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1973 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a gross output of 10.21-megawatt (MW) (net output), with auxiliary load of 0.14 MW and an estimated line loss of 0.07 MW, results in a maximum net output of 10 MW Energy Storage facility into Pacific Gas and Electric Company’s (PG&E’s) Olive Switching Station (SS) which is tapped onto the Corcoran – Olive SS 115 kV Line in Tulare County, California. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5798800 | T.0003744 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2024 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-01 | 2019-11-01 | 2026-03-02 | Prioritization | NA | TRUE | 980 | NA ¦ NA | 169.5126 | 188.8668 | 7.9416 | 51.8635 | 43.9983 | 36.4723 | 23.9801 | 24.611 | 0 | 0 | 0 | 0 | 164.2558 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 164.2575 | 5.2568 | 0% | 100% ¦ $189 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1974 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a gross output of 10.21-megawatt (MW) (net output), with auxiliary load of 0.14 MW and an estimated line loss of 0.07 MW, results in a maximum net output of 10 MW Energy Storage facility into Pacific Gas and Electric Company’s (PG&E’s) Olive Switching Station (SS) which is tapped onto the Corcoran – Olive SS 115 kV Line in Tulare County, California. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3608 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5798801 | T.0003744 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2024 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-01 | 2019-11-01 | 2026-03-02 | Prioritization | NA | TRUE | 980 | NA ¦ NA | 167.4565 | 167.9589 | 8.0534 | 53.2267 | 39.9506 | 35.4859 | 27.9627 | 3.2797 | 0 | 0 | 0 | 0 | 164.6792 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 164.6809 | 2.7773 | 0% | 100% ¦ $168 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1975 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 200 megawatt (MW) (net output) energy-storage generation facility to the Pacific Gas and Electric Company’s (PG&E’s) Pittsburg 230kV Substation. | Substation - Switch | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.72358 | NA | 230 kV | 3 | 6. Customer commitments | NA | NA | NA | 5779009 | T.0003747 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-12-01 | 2021-03-01 | 2021-06-15 | NA | NA | FALSE | 2860 | NA ¦ NA | 3284.5004 | 3284.5004 | 2435.1748 | 1.7329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3284.5004 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 3056.6184 | 1.6139 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,285 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1976 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 250 megawatt (MW) (net output) solar power-based generation facility to the PG&E-owned Gates 230 kV Substation in Fresno County, California. | Substation - Bus Arrangement | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | 3 | 6. Customer commitments | NA | NA | NA | 5779030 | T.0003750 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-04-06 | 2020-09-28 | 2021-03-22 | NA | NA | FALSE | 5600 | NA ¦ NA | 4992.8242 | 4992.8242 | 2010.3877 | -4.2589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4992.8242 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | 4955.2889 | -4.2221 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,993 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1977 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 300 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) new Switching Station looped into the Quinto Switching Station - Westley 230 kV Line, in Stanislaus County, California. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 230 kV | NA | NA | NA | NA | Non-IGP | 5779104 | T.0003770 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6529-E | 2022-03-16 | Approved | 2022 | Operational | 1 | 2022-06-29 | 2020-01-10 | 2023-11-02 | Prioritization | NA | FALSE | 25500 | NA ¦ NA | 2114.6167 | 2114.6167 | 528.724 | 229.0131 | 1241.1168 | 107.1719 | 0 | 0 | 0 | 0 | 0 | 0 | 2114.6167 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 1999.6579 | 106.7249 | 0 | 0 | 0% | 100% ¦ $2,115 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1978 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 300 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) new Switching Station looped into the Quinto Switching Station - Westley 230 kV Line, in Stanislaus County, California. | Substation - Multiple | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 230 kV | NA | NA | NA | NA | NA | 5779105 | T.0003770 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2020 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6529-E | 2022-03-16 | Approved | 2022 | Operational | 1 | 2022-08-16 | 2020-01-10 | 2023-11-02 | Prioritization | NA | FALSE | 25500 | NA ¦ NA | 536.2586 | 536.2586 | 132.6052 | 68.0976 | 275.7174 | 57.3422 | 0 | 0 | 0 | 0 | 0 | 0 | 536.2586 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 478.9162 | 57.3422 | 0 | 0 | 0% | 100% ¦ $536 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1979 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 300 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) new Switching Station looped into the Quinto Switching Station - Westley 230 kV Line, in Stanislaus County, California. | Substation - Multiple | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 230 kV | NA | NA | NA | NA | NA | 5545722 | T.0003770 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2023 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6529-E | 2022-03-16 | Approved | 2022 | Operational | 1 | NA | 2020-01-10 | 2023-12-01 | Prioritization | NA | FALSE | 25500 | NA ¦ NA | 306.0598 | 306.0598 | 0 | 0 | 301.4887 | 5.1 | -0.5289 | 0 | 0 | 0 | 0 | 0 | 306.0598 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 301.4887 | 5.1 | -0.52891 | 0 | 0% | 100% ¦ $306 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1980 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 300 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) new Switching Station looped into the Quinto Switching Station - Westley 230 kV Line, in Stanislaus County, California. | Substation - Multiple | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.67641 | NA | 230 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5779140 | T.0003770 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6529-E | 2022-03-16 | Approved | 2022 | Operational | 1 | 2023-06-02 | 2020-01-10 | 2024-03-06 | Prioritization | NA | FALSE | 25500 | NA ¦ NA | 22417.7455 | 22417.7455 | 2705.6196 | 3803.3395 | 14338.5676 | 1470.3133 | 2.522 | 0 | 0 | 0 | 0 | 0 | 22417.7455 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 22415.3016 | 2.522 | 0 | 0% | 100% ¦ $22,418 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1981 | Los Banos: Upgrade Terminal Equipt. |  |  | Merced | Reconductor 6.11 miles of the Los Banos - Quinto Switching Station 230 kV Line with super bundled 795 ACSS conductor. Upgrade associated terminal equipment at Los Banos and Quinto Switching Station to match the new conductor rating as needed. Replace structures as needed | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | 60 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 53.2803 | NA | 230 kV | NA | NA | NA | NA | NA | 5794846 | T.0003789 | Los Banos - Quinto SS 20244: EGI Recon. | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2019 | 2018 | FALSE | NA | NA | NA | TRUE | Final Certified | 2012-11-06 | EIR | NA | Merced County | NA | NOC: AL 4180-E | 2013-01-17 | Approved | 2013 | Operational | 1 | 2023-03-06 | 2020-04-30 | 2023-05-08 | Material | NA | FALSE | 12430 | NA ¦ NA | 482.5367 | 482.5367 | 79.7904 | 26.6773 | 324.4721 | 2.453 | 0 | 0 | 0 | 0 | 0 | 0 | 482.5367 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 76.55 | 26.0082 | 316.3178 | 2.3914 | 0 | 0 | 0% | 100% ¦ $483 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1982 | Panoche: Upgrade Terminal Equipt. |  |  | Fresno | Reconductor 32.59 miles of the Padre Flat Switching Station - Panoche 230 kV Line No. 1 with 795 ACSS conductor. Upgrade associated equipment and structures to match the new conductor rating, as needed. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | 71 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | 3 | NA | NA | 5.3 | Non-IGP | 5794847 | T.0003792 | Padre Flat SS - Panoche #1 20267: Recon. | 4 | 82 | NA ¦ 5534921 ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2020 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-01-22 | 2021-09-30 | 2024-05-10 | Material | NA | FALSE | 49490 | NA ¦ NA | 1382.4259 | 1382.4259 | 72.1323 | 162.7113 | 172.9817 | 888.6397 | 10.8 | 0 | 0 | 0 | 0 | 0 | 1382.4259 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 72.1323 | 162.7132 | 144.2681 | 835.8098 | 10.1579 | 0 | 0% | 100% ¦ $1,382 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1983 | PANOCHE: UPGD EQUIP TO 1517AûEGI DOS AMI |  |  | Fresno | The Project proposes to reconductor 23.63 miles of the Pacific Gas and Electric Company’s (PG&E’s) Dos Amigos - Panoche 230 kV Line No. 3 with a higher capacity conductor, in Merced and Fresno Counties, California. During the Cluster 9 Phase I Fresno Area Interconnection Study, the Dos Amigos - Panoche 230 kV Line No. 3 was found to be overloaded by roughly 84%. To eliminate this deliverability constraint, the CAISO requires reconductoring the overloaded line and the costs are allocated among multiple full capacity generation projects identified by the CAISO. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | 78 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5805074 | T.0004255 | Dos Amigos PP-Panoche #3 230 kV Recondu. | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7392-E | 2024-10-02 | Approved | 2024 | Construction (50%-75%) | 2 | 2025-11-17 | 2021-09-30 | 2026-06-16 | Land Rights | NA | TRUE | 66420 | NA ¦ NA | 1180.4219 | 1563.8002 | 81.1738 | 103.9315 | 114.6554 | 179.8092 | 284.3457 | 738.719 | 0 | 0 | 0 | 0 | 825.0812 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 81.1738 | 103.9379 | -246.4102 | 0 | 0 | 0 | 0% | 100% ¦ $1,564 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1984 | WRO Generator Network Upgrades |  |  |  | Install one 230 kV BAAH bay with two CBS, gen-tie line deadend, line switches, CCVT’s, and protective relays at Tesla Sub. The project is to accommodate installment of the Wind project, a small generating facility comprised of 11 wind turbines, each rated at 2 MW. The Small Generating Facility and the associated Interconnection Facilities plan to connect to Tesla 230 kV Substation in Alameda, CA. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 69.382 | NA | 230 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5782662 | T.0004354 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2024-06-25 | 2021-01-14 | 2026-05-04 | Customer Action | NA | TRUE | 5467 | NA ¦ NA | 7003.4567 | 7753.3517 | 1154.22 | 127.6629 | 354.5138 | 3609.0813 | 1124.0937 | 862.6002 | 43.2531 | 0 | 0 | 0 | 6847.4984 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $7,753 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1985 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 76.35 wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Los Banos Substation in Merced, California | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 53.2803 | NA | 70 kV | NA | NA | NA | 3.002 | Non-IGP | 5815282 | T.0004423 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2025 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-01-21 | 2023-07-01 | 2026-04-30 | Customer Action | NA | TRUE | 6060 | NA ¦ NA | 760.4205 | 4102.4089 | 0 | 0 | 0 | 0 | 598.8434 | 3503.5655 | 0 | 0 | 0 | 0 | 598.8434 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,102 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1986 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 76.35 wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Los Banos Substation in Merced, California | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 70 kV | 3 | NA | NA | 3.002 | Non-IGP | 5783302 | T.0004423 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2019 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-07-03 | 2023-07-01 | 2025-01-17 | Customer Action | NA | TRUE | 6060 | NA ¦ NA | 16846.5446 | 16846.6715 | 294.2066 | 684.2893 | 6746.6052 | 5799.949 | 3184.3208 | 56.1329 | 0 | 0 | 0 | 0 | 16790.5386 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 16051.1648 | 53.368 | 0% | 100% ¦ $16,847 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1987 | WRO Generator Network Upgrades |  |  |  | The project is to accommodate the Energy Storage Project, which proposes to install 13 inverters rated at 1.9385 MW each with a maximum gross output of 25.2 MW. Auxiliary load of 0 MW and estimated losses of 0.2 MW. The net output is 25 MW to the CAISO Controlled Grid. This Generating Facility and the associated Interconnection Facilities plan to connect to Weber 60 kV Substation in San Joaquin County. Reconductor 0.9 mi of Stockton A0Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | 70 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 6.1366 | NA | 60 kV | NA | NA | NA | NA | Non-IGP | 5794597 | T.0004561 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2021 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 5770-E | 2020-02-25 | Approved | 2020 | Operational | 1 | 2022-02-15 | 2021-11-01 | 2023-05-31 | Customer Action | NA | FALSE | 8650 | NA ¦ NA | 773.403 | 773.403 | 201.233 | 393.7393 | 162.7217 | 15.578 | 0 | 0 | 0 | 0 | 0 | 0 | 773.403 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 757.825 | 15.578 | 0 | 0 | 0% | 100% ¦ $773 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1988 | WRO Generator Network Upgrades |  |  |  | The project is to accommodate the Energy Storage Project, which proposes to install 13 inverters rated at 1.9385 MW each with a maximum gross output of 25.2 MW. Auxiliary load of 0 MW and estimated losses of 0.2 MW. The net output is 25 MW to the CAISO Controlled Grid. This Generating Facility and the associated Interconnection Facilities plan to connect to Weber 60 kV Substation in San Joaquin County. Reconductor 0.9 mi of Stockton A0Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 6.1366 | NA | 60 kV | 3 | NA | NA | 3.002 | Non-IGP | 5783873 | T.0004561 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-02-01 | 2021-11-01 | 2023-05-31 | Customer Action | NA | FALSE | 8650 | NA ¦ NA | 3560.8596 | 3560.8596 | 867.2984 | 2209.916 | 395.2348 | 16.5438 | 0 | 0 | 0 | 0 | 0 | 0 | 3560.8596 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 3429.1952 | 15.9615 | 0 | 0 | 0% | 100% ¦ $3,561 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1989 | WRO Generator Network Upgrades |  |  |  | The project proposes to install 200 inverters rated at 2.09 MW each at 95% power factor with a maximum gross output of 418 MW. Auxiliary load of 4 MW and estimated losses of 4.54 MW. The net output is 400 MW to the CAISO Controlled Grid, interconnected to PG&E's Telsa 230 kV substation. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 69.382 | NA | 115 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5783904 | T.0004563 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2020 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-08-19 | 2023-01-10 | 2025-07-12 | Workforce | NA | TRUE | 6630 | NA ¦ NA | 3418.0098 | 3740.1228 | 38.8384 | 23.0333 | 202.4183 | 1417.7535 | 1681.2738 | 336.2339 | 0 | 0 | 0 | 0 | 3403.889 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 3403.9524 | 14.1208 | 0% | 100% ¦ $3,740 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1990 | WRO Generator Network Upgrades |  |  |  | The project proposes to install a battery generation plant with a total rated output of 400 megawatt (MW) (net output) to Pacific Gas and Electric Company’s (PG&E’s) Moss Landing Substation 500 kV in Moss Landing, Monterey, CA. The Project was modeled with a total installed capacity of 434.5 megawatt (MW) (gross output) and will have a net output of 400 megawatt (MW) (net output) to the California Independent System Operator (CAISO)Controlled Grid. The interconnection agreement for Q1472 was executed on March 17, 2020. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-10 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 41.3213 | NA | 500 kV | 3 | 6. Customer commitments | NA | NA | NA | 5784784 | T.0004662 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-07-15 | 2020-08-01 | 2020-11-23 | NA | NA | FALSE | 6352 | NA ¦ NA | 10903.4817 | 10903.4817 | -201.0826 | 14.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10903.4817 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 | -201.0826 | 14.9229 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $10,903 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1991 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 75 megawatt (MW) (net output) energy storage generation facility to the Pacific Gas and Electric Company’s (PG&E’s) Metcalf 115 kV Substation, in Santa Clara County, California. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 115 kV | 3 | 6. Customer commitments | NA | 5.4 | Non-IGP | 5784846 | T.0004676 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-21 | 2020-08-01 | 2023-10-13 | Customer Action | NA | TRUE | 9053 | NA ¦ NA | 4573.8529 | 4584.6958 | 299.182 | 2544.0623 | 1142.7379 | 0.5719 | 1.5523 | 10.8429 | 0 | 0 | 0 | 0 | 4573.8529 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 4571.7136 | 0.57195 | 1.5523 | 0 | 0% | 100% ¦ $4,585 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1992 | ROCK CREEK PH Remote Ends |  |  | Plumas | The Caibou-Palermo 115 kV line, which connected the Powerhouse to the transmission grid, has been taken out of service for an extended timeframe in the aftermath of the November 2018 Camp Fire. This outage has disabled the Powerhouse’s ability to transmit power to SVP. The Powerhouse is currently generating a small amount to only provide station service. PG&E is obligated under the Agreement to transmit the power generated by the Powerhouse to SVP. The Agreement states that in the event of a transmission line outage, PG&E must work diligently to restore service on the same value-based schedule and priority as if it were a PG&E-owned facility. This project will provide an alternative interconnection for the Powerhouse. This project will connect the Powerhouse to the Bucks Creek-Rock Creek-Cresta 230 kV Line and install a 230/115kV step-up transformer at Bucks Creek Switchyard to facilitate the interconnection to the 230kV grid. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-13 | NA | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 1.0255 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5790519 | T.0004715 | Bucks Creek PH-Grizzly PH Reconnection | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 2 | 2025-11-25 | 2021-12-31 | 2027-05-10 | Project Design | NA | TRUE | 19981 | NA ¦ NA | 2382.9121 | 7891.0861 | 172.8791 | 671.8764 | 516.9503 | 293.505 | 645.5358 | 1669.4967 | 3890.134 | 0 | 0 | 0 | 2331.4554 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $7,891 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1993 | CRESTA PH Remote Ends |  |  | Butte | The Caibou-Palermo 115 kV line, which connected the Powerhouse to the transmission grid, has been taken out of service for an extended timeframe in the aftermath of the November 2018 Camp Fire. This outage has disabled the Powerhouse’s ability to transmit power to SVP. The Powerhouse is currently generating a small amount to only provide station service. PG&E is obligated under the Agreement to transmit the power generated by the Powerhouse to SVP. The Agreement states that in the event of a transmission line outage, PG&E must work diligently to restore service on the same value-based schedule and priority as if it were a PG&E-owned facility. This project will provide an alternative interconnection for the Powerhouse. This project will connect the Powerhouse to the Bucks Creek-Rock Creek-Cresta 230 kV Line and install a 230/115kV step-up transformer at Bucks Creek Switchyard to facilitate the interconnection to the 230kV grid. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-02-10 | NA | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.4913 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5790518 | T.0004715 | Bucks Creek PH-Grizzly PH Reconnection | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-01-20 | 2021-12-31 | 2027-03-03 | Project Design | NA | TRUE | 19981 | NA ¦ NA | 1230.5211 | 3660.7378 | 179.8266 | 367.1815 | 270.4477 | 165.7002 | 198.6821 | 1041.1149 | 1411.5491 | 0 | 0 | 0 | 1208.0739 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,661 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1994 | BUCKS CREEK PH RECONNECTION SUB NU WORK |  |  | Plumas | The Caibou-Palermo 115 kV line, which connected the Powerhouse to the transmission grid, has been taken out of service for an extended timeframe in the aftermath of the November 2018 Camp Fire. This outage has disabled the Powerhouse’s ability to transmit power to SVP. The Powerhouse is currently generating a small amount to only provide station service. PG&E is obligated under the Agreement to transmit the power generated by the Powerhouse to SVP. The Agreement states that in the event of a transmission line outage, PG&E must work diligently to restore service on the same value-based schedule and priority as if it were a PG&E-owned facility. This project will provide an alternative interconnection for the Powerhouse. This project will connect the Powerhouse to the Bucks Creek-Rock Creek-Cresta 230 kV Line and install a 230/115kV step-up transformer at Bucks Creek Switchyard to facilitate the interconnection to the 230kV grid. | Substation - Transformer | New | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-02 | NA | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 0.31219 | NA | 230 ¦ 115 kV | NA | 6. Customer commitments | NA | NA | Non-IGP | 5785299 | T.0004715 | Bucks Creek PH-Grizzly PH Reconnection | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-25 | 2021-12-31 | 2023-12-19 | Weather | NA | TRUE | 19981 | NA ¦ NA | 40541.7297 | 40901.2718 | 3098.4621 | 18297.9835 | 11013.2824 | 1704.2328 | 2745.0697 | 332.7214 | 1.4529 | 0 | 0 | 0 | 40567.0975 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 35784.2186 | 1686.8669 | 2717.0979 | -25.1093 | 0% | 100% ¦ $40,901 | NA | NA ¦ NA | NA | 35.18% | 64.82% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1995 | Replace Panoche 115 kV CB 112 with 50 kA |  |  | Fresno | Replace 115kV CB 112 at Panoche Substation 2000A 40 kA breaker with a 3000A 50 kA breaker equipped with 3000/5 CT to relieve breaker from being overstressed as a result of a 3rd party generation interconnection. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | 16 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 115 kV | 3 | 6. Customer commitments | NA | NA | NA | 5782068 | T.0004760 | Panoche CB 112 Overstress | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2012 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2020-10-26 | 2020-09-01 | 2021-03-05 | Construction Delays | NA | FALSE | 1655 | NA ¦ NA | 1917.0744 | 1917.0744 | 1022.2385 | 0 | 0.3822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1917.0744 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2023 ¦ 2026 | 1759.4464 | 0 | 0.35012 | 0 | 0 | 0 | 0% | 100% ¦ $1,917 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1996 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install an energy storage project, which is comprised of 123 batteries rated at 1.25 MW with a maximum gross output of 151.90 MW, limited to 150 MW net to CAISO grid at Point of Interconnection (POI). | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-14 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 14.7513 | NA | 115 kV | 3 | NA | NA | NA | NA | 5785810 | T.0004818 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 6581-E | 2022-05-04 | Approved | 2022 | Operational | 1 | 2023-03-01 | 2022-01-15 | 2023-11-01 | Customer Action | NA | FALSE | 5750 | NA ¦ NA | 3965.7854 | 3965.7854 | 319.7742 | 1919.9 | 1499.0786 | 23.1261 | 0 | 0 | 0 | 0 | 0 | 0 | 3965.7854 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 3492.8908 | 20.2631 | 0 | 0 | 0% | 100% ¦ $3,966 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
1997 | WRO Generator Network Upgrades |  |  |  | Interconnection to the Pacific Gas and Electric Company (PG&E)’s distribution system for a 2,344 kW Synchronous generating facility. Scope: 1. Install a new 19" Rack. Install DTT Transmitter to A G Wishon PH. 2. Wire the DTT Transmitter by CB 12 Line Relays, CB 22 Line Relays, CB 32 b Seals and Bank 1 Relays. 3. Install SCADA Controller Selector Switch between CB 12, 22 and 32 Trips to DTT. 4. Install Local Remote and SCADA DTT Cut in / Cut out Switch. 6. Provide DC Power to the DTT Rack. 7. Install MVAJ Relay for Bank 1 DTT Trip. Drawing 4159442 provides the DTT Scheme and its triggers. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-13 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.4893 | NA | 70 kV | NA | 6. Customer commitments | NA | 5.4 | Non-IGP | 5785811 | T.0004899 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2022-01-31 | NA | 2026-10-26 | NA | NA | TRUE | NA | NA ¦ NA | 479.7219 | 608.5921 | 101.5171 | 34.7047 | 87.1871 | 125.7095 | 48.7448 | 113.3982 | 21.6058 | 0 | 0 | 0 | 473.588 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $609 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1998 | WRO Generator Network Upgrades |  |  |  | Interconnection to the Pacific Gas and Electric Company (PG&E)’s distribution system for a 2,344 kW Synchronous generating facility. Scope: 1. Install a new 19" Rack. Install DTT Transmitter to A G Wishon PH. 2. Wire the DTT Transmitter by CB 12 Line Relays, CB 22 Line Relays, CB 32 b Seals and Bank 1 Relays. 3. Install SCADA Controller Selector Switch between CB 12, 22 and 32 Trips to DTT. 4. Install Local Remote and SCADA DTT Cut in / Cut out Switch. 6. Provide DC Power to the DTT Rack. 7. Install MVAJ Relay for Bank 1 DTT Trip. Drawing 4159442 provides the DTT Scheme and its triggers. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-13 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.4893 | NA | 70 kV | NA | 6. Customer commitments | NA | 5.4 | Non-IGP | 5785812 | T.0004899 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2021-10-01 | NA | 2026-10-26 | NA | NA | TRUE | NA | NA ¦ NA | 501.2047 | 867.7648 | 83.8418 | 131.6611 | 140.939 | 43.8848 | 51.5368 | 351.8511 | 21.6058 | 0 | 0 | 0 | 494.3079 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $868 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
1999 | WRO Generator Network Upgrades |  |  |  | Interconnection to the Pacific Gas and Electric Company (PG&E)’s distribution system for a 2,344 kW Synchronous generating facility. Scope: 1. Install a new 19" Rack. Install DTT Transmitter to A G Wishon PH. 2. Wire the DTT Transmitter by CB 12 Line Relays, CB 22 Line Relays, CB 32 b Seals and Bank 1 Relays. 3. Install SCADA Controller Selector Switch between CB 12, 22 and 32 Trips to DTT. 4. Install Local Remote and SCADA DTT Cut in / Cut out Switch. 6. Provide DC Power to the DTT Rack. 7. Install MVAJ Relay for Bank 1 DTT Trip. Drawing 4159442 provides the DTT Scheme and its triggers. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-16 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 7.1874 | NA | 70 kV | NA | 6. Customer commitments | NA | 5.4 | Non-IGP | 5785813 | T.0004899 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2021-10-29 | NA | 2026-10-26 | NA | NA | TRUE | NA | NA ¦ NA | 356.5112 | 512.3131 | 66.052 | 29.7661 | 92.4053 | 28.1541 | 27.1565 | 138.7889 | 21.6245 | 0 | 0 | 0 | 351.8997 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $512 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2000 | WRO Generator Network Upgrades |  |  |  | Interconnection to the Pacific Gas and Electric Company (PG&E)’s distribution system for a 2,344 kW Synchronous generating facility. Scope: 1. Install a new 19" Rack. Install DTT Transmitter to A G Wishon PH. 2. Wire the DTT Transmitter by CB 12 Line Relays, CB 22 Line Relays, CB 32 b Seals and Bank 1 Relays. 3. Install SCADA Controller Selector Switch between CB 12, 22 and 32 Trips to DTT. 4. Install Local Remote and SCADA DTT Cut in / Cut out Switch. 6. Provide DC Power to the DTT Rack. 7. Install MVAJ Relay for Bank 1 DTT Trip. Drawing 4159442 provides the DTT Scheme and its triggers. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.0827 | NA | 70 kV | NA | 6. Customer commitments | NA | 5.4 | Non-IGP | 5785891 | T.0004899 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2021-11-22 | 2022-08-30 | 2026-10-26 | Prioritization | NA | TRUE | 490 | NA ¦ NA | 3110.5192 | 3531.3373 | 105.7196 | 49.193 | 1476.0176 | 247.5498 | 1073.5676 | 439.1375 | 21.6058 | 0 | 0 | 0 | 3070.594 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,531 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2001 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 200 MW. This Generating Facility and the associated Interconnection Facilities plan to connect to the 230 kV Bus at Wheeler Ridge Substation in Kern County. Wheeler Ridge Substation - Install (1) New 230 kV Bay, DTT Rx, & (2) 230 kV CB’s | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | 3 | 6. Customer commitments | NA | 5.4 | Non-IGP | 5787421 | T.0004974 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-03 | 2022-08-15 | 2024-02-07 | Prioritization | NA | FALSE | 5684 | NA ¦ NA | 3097.8994 | 3097.8994 | 270.3739 | 1522.336 | 1113.1009 | 164.3565 | 10.1454 | 0 | 0 | 0 | 0 | 0 | 3097.8994 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 3087.7901 | 10.1454 | 0 | 0% | 100% ¦ $3,098 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2002 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 200 MW. This Generating Facility and the associated Interconnection Facilities plan to connect to the 230 kV Bus at Wheeler Ridge Substation in Kern County. Wheeler Ridge Substation - Install (1) New 230 kV Bay, DTT Rx, & (2) 230 kV CB’s | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | NA | 6. Customer commitments | NA | 5.4 | NA | 5787422 | T.0004974 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-11-01 | 2022-08-15 | 2024-02-07 | Prioritization | NA | FALSE | 5684 | NA ¦ NA | 486.8879 | 486.8879 | 97.3927 | 157.8159 | 170.4357 | 47.9588 | 0 | 0 | 0 | 0 | 0 | 0 | 486.8879 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2026 | 0 | 0 | 0 | 479.7038 | 0 | 0 | 0% | 100% ¦ $487 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2003 | WRO Generator Network Upgrades |  |  |  | Interconnect a 21.3 megawatt (MW) (net output) wind power-based generation facility to Pacific Gas and Electric Company’s (Pacific Gas and Electric) owned Las Positas – Vasco 60 kV Line in Alameda County, California. The project scope includes the following: Network Upgrades: Herdlyn Substation: 1. Install (1) GARD 8000 DTT transmitter at Herdlyn to communicate to the new Forebay site and new Santa Clara site (Previously named ZOND). Initiate from Herdlyn CB 62 line relays. i. Install one (1) DTT Transmitter (RFL Gard 8000) ii. An auxiliary tripping relay is required to interface the RFL with the line relays. The auxiliary relay will be installed on the new DTT panel. iii. Install SCADA Operable Cut-In/Cut-Out Switch. iv. Install DTT Local/Remote Switch. v. Included in the installation are new status and alarm points wire to SCADA and/or the station annunciator. These points may include: i. DTT Communication Channel Failure. ii. DTT Hardware Problem. iii. DTT Receipt Status. iv. DTT Cutout Status. v. Local/Remote Status. vi. Cut-In/Cut-Out Status. 2. Update protection relay settings on existing line a breaker relaying Las Positas Substation: 1. Update existing DTT equipment: i. Remove existing RFL GARD 6745 transmitter from Las Positas CB 12 & CB 32 to ZOND/SEAWEST (new Forebay site and new Santa Clara site). ii. Install and test one (1) RFL GARD 8000 transmitter from Las Positas CB 12 & CB 32 to new Forebay site and new Santa Clara site (Previously named ZOND). 2. Update protection relay settings on existing line a breaker relaying Interconnection Facilities: Santa Clara Wind Repower Generation Site 1. The Project will export power through a 24/32/40 MVA power transformer, which shall be connected wye grounded on the PG&E side per Generation Interconnection Handbook G2.5.4.1 and G2.5.4.2. This transformer will be shared with the Forebay Wind Repower project and it is the responsibility of the Interconnection customer to provide the protective schemes and coordination between the two sites. Basic protective devices of the substation should be referenced to Table G2-1a and G2-1b of the Interconnection Handbook as required. All relays must be utility grade, fully redundant, and PG&E approved. 2. The Interconnection Customer is required to comply with all the applicable requirements in the PG&E Interconnection Handbook, plus specific requirements established for this project. 3. PG&E will provide engineering review of the Santa Clara Wind Generation Site modifications. These reviews typically include three separate drawing submittals throughout the design phases. The PG&E Protection Engineer will also review the final relay settings and test report data. 4. All metering and associated telemetry equipment will be located at Santa Clara Wind Generation Site. PG&E will review the Customer’s revenue metering design and will install PG&E revenue meter inside a Customer provided metering enclosure. 5. The IC to provide space for space for two (2) 19-inch racks for installation of the PG&E RTU and DTT equipment. 6. The Customer is required to obtain and provide all the required leased circuits and phone lines in accordance with PG&E’s Interconnection Handbook for EMS, telemetry, and SCADA. 7. PG&E will provide pre-parallel inspection and witness testing at the Customer’s facility. 8. PG&E IT will install one (1) channel bank to support the leased T1 circuits transporting the EMS telemetry and SCADA to the nearest PG&E control center. 9. PG&E IT will support the IC during the installation and testing of the RTU. 10. The PG&E Protection Engineer has required Direct Transfer Trip (DTT) schemes at the Customer’s new 60kV main circuit breaker (for both new Forebay site and Santa Clara site). i. PG&E will provide and install two (2) RFL Guard 8000 receivers to receive DTT from Herdlyn CB 62 and Las Positas CB 12 & CB 32 line relays. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-04-02 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Heat Wave |  | NA | 4.2184 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5787846 | T.0005176 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2024 | 2018 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-09-09 | 2021-12-01 | 2027-02-01 | Prioritization | NA | TRUE | 1000 | NA ¦ NA | 167.4053 | 410.9408 | 0 | 0 | 34.5951 | 111.3615 | 19.3493 | 188.636 | 38.9575 | 18.0413 | 0 | 0 | 165.3059 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $411 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2004 | WRO Generator Network Upgrades |  |  |  | Interconnect a 21.3 megawatt (MW) (net output) wind power-based generation facility to Pacific Gas and Electric Company’s (Pacific Gas and Electric) owned Las Positas – Vasco 60 kV Line in Alameda County, California. The project scope includes the following: Network Upgrades: Herdlyn Substation: 1. Install (1) GARD 8000 DTT transmitter at Herdlyn to communicate to the new Forebay site and new Santa Clara site (Previously named ZOND). Initiate from Herdlyn CB 62 line relays. i. Install one (1) DTT Transmitter (RFL Gard 8000) ii. An auxiliary tripping relay is required to interface the RFL with the line relays. The auxiliary relay will be installed on the new DTT panel. iii. Install SCADA Operable Cut-In/Cut-Out Switch. iv. Install DTT Local/Remote Switch. v. Included in the installation are new status and alarm points wire to SCADA and/or the station annunciator. These points may include: i. DTT Communication Channel Failure. ii. DTT Hardware Problem. iii. DTT Receipt Status. iv. DTT Cutout Status. v. Local/Remote Status. vi. Cut-In/Cut-Out Status. 2. Update protection relay settings on existing line a breaker relaying Las Positas Substation: 1. Update existing DTT equipment: i. Remove existing RFL GARD 6745 transmitter from Las Positas CB 12 & CB 32 to ZOND/SEAWEST (new Forebay site and new Santa Clara site). ii. Install and test one (1) RFL GARD 8000 transmitter from Las Positas CB 12 & CB 32 to new Forebay site and new Santa Clara site (Previously named ZOND). 2. Update protection relay settings on existing line a breaker relaying Interconnection Facilities: Santa Clara Wind Repower Generation Site 1. The Project will export power through a 24/32/40 MVA power transformer, which shall be connected wye grounded on the PG&E side per Generation Interconnection Handbook G2.5.4.1 and G2.5.4.2. This transformer will be shared with the Forebay Wind Repower project and it is the responsibility of the Interconnection customer to provide the protective schemes and coordination between the two sites. Basic protective devices of the substation should be referenced to Table G2-1a and G2-1b of the Interconnection Handbook as required. All relays must be utility grade, fully redundant, and PG&E approved. 2. The Interconnection Customer is required to comply with all the applicable requirements in the PG&E Interconnection Handbook, plus specific requirements established for this project. 3. PG&E will provide engineering review of the Santa Clara Wind Generation Site modifications. These reviews typically include three separate drawing submittals throughout the design phases. The PG&E Protection Engineer will also review the final relay settings and test report data. 4. All metering and associated telemetry equipment will be located at Santa Clara Wind Generation Site. PG&E will review the Customer’s revenue metering design and will install PG&E revenue meter inside a Customer provided metering enclosure. 5. The IC to provide space for space for two (2) 19-inch racks for installation of the PG&E RTU and DTT equipment. 6. The Customer is required to obtain and provide all the required leased circuits and phone lines in accordance with PG&E’s Interconnection Handbook for EMS, telemetry, and SCADA. 7. PG&E will provide pre-parallel inspection and witness testing at the Customer’s facility. 8. PG&E IT will install one (1) channel bank to support the leased T1 circuits transporting the EMS telemetry and SCADA to the nearest PG&E control center. 9. PG&E IT will support the IC during the installation and testing of the RTU. 10. The PG&E Protection Engineer has required Direct Transfer Trip (DTT) schemes at the Customer’s new 60kV main circuit breaker (for both new Forebay site and Santa Clara site). i. PG&E will provide and install two (2) RFL Guard 8000 receivers to receive DTT from Herdlyn CB 62 and Las Positas CB 12 & CB 32 line relays. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 0.81884 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5787845 | T.0005176 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2019 | Project Management Governance Standard | 2024 | 2018 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-05-08 | 2021-12-01 | 2028-09-19 | Prioritization | NA | TRUE | 1000 | NA ¦ NA | 286.2021 | 419.358 | 0 | 0 | 35.2962 | 222.7357 | 24.5811 | 68.5773 | 31.8486 | 30.6377 | 4.7531 | 0.9285 | 282.6129 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $419 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2005 | NU GABILAN - INSTALL CTRL BLDG, ETC |  |  | Monterey | Install a new control enclosure, 60kV PT, 60kV Over voltage relay package, SMP cabinets for FDRs 1101 & 1102 and 12kV line PT for FDR 1101 to support the Rule 21 EGI project as requested by the Interconnection Customer. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 0.28891 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5814024 | T.0005677 | Gabilan: Install Ctrl Bldg and OV Relays | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-05-12 | 2025-12-31 | 2026-03-10 | NA | NA | TRUE | 9430 | NA ¦ NA | 4123.3168 | 4677.3395 | 264.7892 | 163.5248 | 312.2881 | 389.3436 | 2699.1262 | 795.4323 | 0 | 0 | 0 | 0 | 3881.9071 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 270.0727 | 164.5543 | 312.2881 | 389.3436 | 2605.6221 | 235.5949 | 0% | 100% ¦ $4,677 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2006 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-02 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.373 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5789331 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2021 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2026-01-14 | 2023-04-14 | 2026-05-01 | Prioritization | NA | TRUE | 7940 | NA ¦ NA | 1167.5303 | 1536.496 | 56.3671 | 106.6652 | 181.0794 | 58.6783 | 296.2894 | 805.6213 | 0 | 0 | 0 | 0 | 730.8747 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,536 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2007 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.1779 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5792479 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2021 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-01-24 | 2023-04-14 | 2026-04-30 | Prioritization | NA | TRUE | 7940 | NA ¦ NA | 434.6178 | 486.3887 | 61.2689 | 118.1911 | 63.2178 | 56.2251 | 104.8858 | 68.7944 | 0 | 0 | 0 | 0 | 417.5943 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $486 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2008 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-04-01 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 0.26068 | NA | 230 kV | 3 | NA | NA | 3.002 | Non-IGP | 5789329 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2021 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-11-18 | 2023-04-14 | 2026-01-14 | Prioritization | NA | TRUE | 7940 | NA ¦ NA | 15128.8499 | 15560.1894 | 108.1569 | 385.5924 | 1218.0585 | 6815.5277 | 6174.8597 | 829.6851 | 0 | 0 | 0 | 0 | 14730.5043 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 14801.2208 | 0% | 100% ¦ $15,560 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2009 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3791 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5792514 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2021 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-18 | 2023-04-14 | 2026-01-14 | Prioritization | NA | TRUE | 7940 | NA ¦ NA | 1867.5149 | 1880.2995 | 37.915 | 107.5189 | 323.1324 | 702.6132 | 585.0989 | 106.7411 | 0 | 0 | 0 | 0 | 1773.5584 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 1798.611 | 0% | 100% ¦ $1,880 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2010 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-04-01 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.26068 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5795098 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-07-30 | 2023-04-14 | 2026-01-14 | Prioritization | NA | TRUE | 7940 | NA ¦ NA | 1125.0579 | 1140.7187 | 30.4639 | 85.9446 | 152.8874 | 132.3467 | 604.0835 | 134.9926 | 0 | 0 | 0 | 0 | 1005.7262 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 1089.6431 | 0% | 100% ¦ $1,141 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2011 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 27.7611 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5792480 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2021 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2026-01-05 | 2023-04-14 | 2026-03-07 | Prioritization | NA | TRUE | 7940 | NA ¦ NA | 429.0971 | 436.1121 | 22.6157 | 127.1617 | 96.0931 | 36.8325 | 94.5567 | 44.301 | 0 | 0 | 0 | 0 | 391.8111 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $436 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2012 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-04 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.9102 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5792515 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2021 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-09-04 | 2023-04-14 | 2026-03-07 | Prioritization | NA | TRUE | 7940 | NA ¦ NA | 433.4393 | 450.3528 | 35.233 | 113.5082 | 76.8191 | 35.9847 | 137.6013 | 35.5052 | 0 | 0 | 0 | 0 | 414.8476 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $450 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2013 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 70.9 MW. This Generating Facility and the associated Interconnection Facilities plan connect to PG&E’s Lakeview Substation in Bakersfield, in Kern County. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.94829 | NA | 70 kV | NA | NA | NA | 3.002 | Non-IGP | 5791722 | T.0006097 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | Final Certified | 2024-04-08 | EIR | NA | Kern County | NA | NOC: AL 7247-E | 2024-04-26 | Approved | 2024 | Construction (50%-75%) | 2 | 2025-09-02 | 2024-07-07 | 2026-05-27 | Prioritization | NA | TRUE | 10000 | NA ¦ NA | 173.9767 | 264.0424 | 1.4802 | 17.2352 | 36.5277 | 3.8477 | 96.0824 | 93.5823 | 15.2868 | 0 | 0 | 0 | 155.1733 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $264 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2014 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 70.9 MW. This Generating Facility and the associated Interconnection Facilities plan connect to PG&E’s Lakeview Substation in Bakersfield, in Kern County. | Transmission Line - Conductor | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3475 | NA | 70 kV | 3 | NA | NA | 3.002 | Non-IGP | 5791721 | T.0006097 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | Final Certified | 2024-04-08 | EIR | NA | Kern County | NA | NOC: AL 7247-E | 2024-04-26 | Approved | 2024 | Construction (50%-75%) | 2 | 2025-03-31 | 2024-07-07 | 2026-07-28 | Prioritization | NA | TRUE | 10000 | NA ¦ NA | 10612.604 | 12341.1007 | 183.8598 | 863.0174 | 495.8573 | 811.7251 | 7380.5765 | 2592.5272 | 13.5373 | 0 | 0 | 0 | 9735.0362 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $12,341 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2015 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 70.9 MW. This Generating Facility and the associated Interconnection Facilities plan connect to PG&E’s Lakeview Substation in Bakersfield, in Kern County. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3755 | NA | 70 kV | NA | NA | NA | 3.002 | Non-IGP | 5791723 | T.0006097 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2022 | 2020 | FALSE | NA | NA | NA | TRUE | Final Certified | 2024-04-08 | EIR | NA | Kern County | NA | NOC: AL 7247-E | 2024-04-26 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-05-04 | 2024-07-07 | 2026-06-15 | Prioritization | NA | TRUE | 10000 | NA ¦ NA | 134.6433 | 218.9966 | 0 | 17.1127 | 37.7779 | 3.8309 | 23.8516 | 120.9712 | 15.4524 | 0 | 0 | 0 | 82.573 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $219 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2016 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 70.9 MW. This Generating Facility and the associated Interconnection Facilities plan connect to PG&E’s Lakeview Substation in Bakersfield, in Kern County. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 70 kV | NA | NA | NA | 3.002 | Non-IGP | 5791724 | T.0006097 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2020 | FALSE | NA | NA | NA | TRUE | Final Certified | 2024-04-08 | EIR | NA | Kern County | NA | NOC: AL 7247-E | 2024-04-26 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-05-28 | 2024-07-07 | 2026-07-29 | Prioritization | NA | TRUE | 10000 | NA ¦ NA | 240.4129 | 351.6897 | 1.1494 | 16.7062 | 45.1075 | 8.0863 | 94.2983 | 167.0016 | 17.3449 | 0 | 0 | 0 | 167.3432 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $352 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2017 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 70.9 MW. This Generating Facility and the associated Interconnection Facilities plan connect to PG&E’s Lakeview Substation in Bakersfield, in Kern County. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3475 | NA | 70 kV | NA | NA | NA | NA | NA | 5549795 | T.0006097 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2023 | 2020 | FALSE | NA | NA | NA | TRUE | Final Certified | 2024-04-08 | EIR | NA | Kern County | NA | NOC: AL 7247-E | 2024-04-26 | Approved | 2024 | Operational | 1 | NA | 2024-07-07 | 2023-06-29 | NA | NA | FALSE | 10000 | NA ¦ NA | 16 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 16 | 0 | 0 | 0 | 0% | 100% ¦ $16 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2018 | WRO Generator Network Upgrades |  |  |  | Interconnect a 60 megawatt (MW) (net output) solar power-based generation and battery storage facility to Pacific Gas and Electric Company’s (PG&E’s) Arco 70 kV Substation. Arco Sub:  Install new partial Double Bus bay  Install one (1) 70kV CB, with breaker control relays  Install Four TSP's, Conductor, Relocate Arco-Tulare Lake 70kV line  Raise 230kV Arco-Gates and Arco-Midway double-circuit | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 70 kV | NA | NA | NA | 5.3 | NA | 5545947 | T.0006119 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-03-01 | 2024-12-07 | 2024-03-20 | NA | NA | FALSE | 3640 | NA ¦ NA | 101.6877 | 101.6877 | 6.0618 | 48.844 | 19.5347 | 27.2472 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6877 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 54.9058 | -54.9058 | 0 | 0 | 0 | 0% | 100% ¦ $102 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2019 | WRO Generator Network Upgrades |  |  |  | Interconnect a 60 megawatt (MW) (net output) solar power-based generation and battery storage facility to Pacific Gas and Electric Company’s (PG&E’s) Arco 70 kV Substation. Arco Sub:  Install new partial Double Bus bay  Install one (1) 70kV CB, with breaker control relays  Install Four TSP's, Conductor, Relocate Arco-Tulare Lake 70kV line  Raise 230kV Arco-Gates and Arco-Midway double-circuit | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.5471 | NA | 70 kV | NA | NA | NA | 3.002 | Non-IGP | 5545945 | T.0006119 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-11-15 | 2024-12-07 | 2024-06-06 | NA | NA | TRUE | 3640 | NA ¦ NA | 2814.0346 | 2822.8086 | 28.4007 | 447.8661 | 1632.7498 | 735.2678 | -31.2948 | 9.8191 | 0 | 0 | 0 | 0 | 2812.9895 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 476.2859 | 1609.0185 | 726.9941 | -30.9426 | 1.0333 | 0% | 100% ¦ $2,823 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2020 | Manteca Sub Install PTs & Cntrl Bldng |  |  | Manteca, San Joaquin | Install a new protection scheme for the incoming EGI connection. The new protection scheme will require the installation of three new CCVTs and expanding the control building. A new DC panel will be installed to provide the DC power supply the new relays. | Substation - Protection Relay | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-14 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.8539 | NA | 115 kV | NA | NA | NA | 5.4 | Non-IGP | 5792365 | T.0006364 | Manteca: Install PTs & Cntrl Room | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2021 | 2018 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-04-01 | 2022-07-01 | 2022-12-28 | NA | NA | FALSE | 2831 | NA ¦ NA | 3610.5107 | 3610.5107 | 469.1321 | 2389.8109 | 497.2818 | 263.7572 | -13.7079 | 0 | 0 | 0 | 0 | 0 | 3610.5107 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 2860.5789 | 496.788 | 263.4953 | -13.6943 | 0 | 0% | 100% ¦ $3,611 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2021 | Q1391 Gates Bus Section E PACIRAS - SFGO |  |  | San Francisco, San Francisco | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | NA | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.2173 | NA | 230 kV | NA | NA | NA | NA | NA | 5538721 | T.0006452 | GATES BUS SECTION "E" | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-19 | 2023-08-15 | 2023-04-17 | NA | NA | FALSE | 20060 | NA ¦ NA | 302.4429 | 302.4429 | 139.87 | 62.395 | 95.4415 | -1.729 | 0 | 0 | 0 | 0 | 0 | 0 | 302.4429 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 146.3318 | 54.9991 | 92.0516 | -1.6676 | 2e-05 | 0 | 0% | 100% ¦ $302 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2022 | Q1391 Gates Bus Section E PACIRAS - VGCC |  |  | Solano | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | NA | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 230 kV | NA | NA | NA | NA | NA | 5538722 | T.0006452 | GATES BUS SECTION "E" | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2021 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-09-09 | 2023-08-15 | 2023-04-17 | NA | NA | FALSE | 20060 | NA ¦ NA | 324.1219 | 324.1219 | 115.3283 | 135.4477 | 72.9603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.1219 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 115.7117 | 126.4657 | 70.3468 | 0 | 0 | 0 | 0% | 100% ¦ $324 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2023 | Q1391 Gates Sub Bus Section E(RNU) |  |  | Fresno | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Substation - Bus Arrangement | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | 63 | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | NA | NA | NA | NA | NA | 5787158 | T.0006452 | GATES BUS SECTION "E" | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2021-09-23 | 2023-08-15 | 2023-04-17 | NA | NA | FALSE | 20060 | NA ¦ NA | 37465.119 | 37465.119 | 14702.0445 | 15120.0677 | 7203.1832 | 73.5207 | 0.745 | 0 | 0 | 0 | 0 | 0 | 37465.119 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 36455.5986 | 71.5454 | 0.72498 | 0 | 0% | 100% ¦ $37,465 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2024 | Q1391 PANOCHE 230 KV BUS (RNU) |  |  | Fresno | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | NA | NA | NA | NA | NA | 5792517 | T.0006452 | GATES BUS SECTION "E" | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2021 | Project Management Governance Standard | 2020 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-07-15 | 2023-08-15 | 2023-04-17 | NA | NA | FALSE | 20060 | NA ¦ NA | 466.929 | 466.929 | 125.4062 | 98.5241 | 235.8268 | 6.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 466.929 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 434.4659 | 5.9106 | 0 | 0 | 0% | 100% ¦ $467 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2025 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install generation interconnection project, which is comprised of photovoltaic solar panels, 13 PV Inverters, each rated at 3.3725 MW, with a maximum gross output of 41.05 MW. Auxiliary load of 0.411 MW and estimated losses of [0.639] MW, results in a net output of 40 MW to the CAISO Controlled Grid,, a 20 MW Battery Energy Storage System (“BESS”) using DC coupling is added to the PV system. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3608 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5794020 | T.0006847 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2022-09-02 | 2023-02-07 | 2026-04-20 | Prioritization | NA | TRUE | 3980 | NA ¦ NA | 329.8322 | 415.0832 | 52.1825 | 86.8614 | 48.1663 | 40.8216 | 90.9678 | 96.0838 | 0 | 0 | 0 | 0 | 318.9995 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $415 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2026 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install generation interconnection project, which is comprised of photovoltaic solar panels, 13 PV Inverters, each rated at 3.3725 MW, with a maximum gross output of 41.05 MW. Auxiliary load of 0.411 MW and estimated losses of [0.639] MW, results in a net output of 40 MW to the CAISO Controlled Grid,, a 20 MW Battery Energy Storage System (“BESS”) using DC coupling is added to the PV system. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.8529 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5794021 | T.0006847 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2022-09-02 | 2023-02-07 | 2026-06-17 | Prioritization | NA | TRUE | 3980 | NA ¦ NA | 361.1883 | 454.3105 | 45.7621 | 138.0046 | 67.3722 | 44.5178 | 57.8165 | 97.8254 | 3.0121 | 0 | 0 | 0 | 353.473 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $454 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2027 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install generation interconnection project, which is comprised of photovoltaic solar panels, 13 PV Inverters, each rated at 3.3725 MW, with a maximum gross output of 41.05 MW. Auxiliary load of 0.411 MW and estimated losses of [0.639] MW, results in a net output of 40 MW to the CAISO Controlled Grid,, a 20 MW Battery Energy Storage System (“BESS”) using DC coupling is added to the PV system. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5794019 | T.0006847 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2022-09-02 | 2023-02-07 | 2026-11-13 | Prioritization | NA | TRUE | 3980 | NA ¦ NA | 383.7458 | 542.3468 | 68.9749 | 96.2852 | 79.8256 | 46.5568 | 82.2612 | 142.9275 | 25.5157 | 0 | 0 | 0 | 373.9036 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $542 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2028 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install generation interconnection project, which is comprised of photovoltaic solar panels, 13 PV Inverters, each rated at 3.3725 MW, with a maximum gross output of 41.05 MW. Auxiliary load of 0.411 MW and estimated losses of [0.639] MW, results in a net output of 40 MW to the CAISO Controlled Grid,, a 20 MW Battery Energy Storage System (“BESS”) using DC coupling is added to the PV system. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-10 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.0905 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5794018 | T.0006847 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-05-13 | 2023-02-07 | 2023-10-13 | Prioritization | NA | TRUE | 3980 | NA ¦ NA | 2062.9551 | 2179.9336 | 185.8287 | 918.2658 | 632.2351 | 19.3498 | 277.7233 | 136.8214 | 9.7094 | 0 | 0 | 0 | 2033.4029 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 1736.6445 | 19.3498 | 277.7233 | 29.5522 | 0% | 100% ¦ $2,180 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2029 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC) has requested PG&E to serve the proposed data center. The project scope of work includes following: SUBSTATION • Relocate Bank #2 230 kV line to make room for the double circuit IC lines o Install two TSP’s and remove one TSP o Install three spans of conductor to reconnect the bank #2 • Install 230 kV complete BAAH Bay #5 o Three 230 kV breakers o Six 230 kV disconnects o Two 230 kV line disconnect switches o Wave-trap with 3 CCVT’s, with line tuner accessories o With an additional dead-end on the West side terminal for the IC • Install all line relays and controls for Bay #5 o Install additional conduits as needed o Install control wiring to all BAAH Bay #5 elements • Install 230 kV Dead-end East of bay #5 for the line disconnect switch and CCVT’s location for IC #2 line • Remove Line Trap and CCVT’s from Bay #4 • Install conduit extensions for fiber optic communications (protection) between PG&E and IC T-LINE • Two 230 kV Overhead (OH) Transmission lines made of 715.5 AAC conductor will be built to interconnect IC’s 230 kV substation to Eastshore 230 kV bus. The project will consist of 9 new Tubular Steel Poles (TSP) on drilled pier foundations, and about 0.5 double circuit miles of 230 kV transmission lines. TELEMETRY • Add telemetry from IC’s substation to PG&E system | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Work Requested by Others | Load Interconnection | NA | NA | 2026-03-04 | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 9.9849 | NA | 230 kV | NA | NA | NA | 5.3 | NA | 5800983 | T.0006960 | Private Load Interconnection Project | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6570-E | 2022-04-22 | Approved | 2022 | Operational | 1 | 2023-12-29 | 2023-06-30 | 2024-01-25 | Workforce | NA | FALSE | 26700 | NA ¦ NA | 9.9361 | 9.9361 | 0 | 43.1047 | -415.7112 | 382.3767 | 0.1659 | 0 | 0 | 0 | 0 | 0 | 9.9361 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 9.5382 | 0.16136 | 0 | 0% | 0% ¦ $0 | Type 3 | NA ¦ NA | NA | 0% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - New Substation Alternative [Alternative Solutions and Costs - Costs] $15 Mil - $20 Mil ¦ $20 Mil - $30 Mil
2030 | Borden: Upgrade Terminal Equipt. |  |  | Madera | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-16 | 95 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 7.1874 | NA | 230 kV | NA | 6. Customer commitments | NA | 3.002 | Non-IGP | 5534923 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7393-E | 2024-10-02 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-01-13 | 2020-09-30 | 2027-05-06 | Land Rights | NA | TRUE | 41660 | NA ¦ NA | 314.7351 | 1921.223 | 15.3787 | 7.1589 | 4.0165 | 44.6448 | 163.7944 | 244.4433 | 1383.2562 | 0 | 0 | 0 | 293.5235 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 15.3787 | 7.1594 | 4.0165 | 44.6448 | 163.7944 | 21.2116 | 0% | 100% ¦ $1,921 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2031 | Gregg: Upgrade Terminal Equipt. |  |  | Madera | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Substation - Line Termination | Upgrade/Retrofit | NA | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-10 | 95 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.266 | NA | 230 kV | NA | 6. Customer commitments | NA | 3.002 | Non-IGP | 5534924 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2019 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7393-E | 2024-10-02 | Approved | 2024 | Engineering more than 50% complete | 3 | 2027-01-14 | 2020-09-30 | 2027-05-07 | Land Rights | NA | TRUE | 41660 | NA ¦ NA | 101.4066 | 245.3864 | 25.4831 | 4.3392 | 2.3113 | 9.2132 | 45.6962 | 18.4895 | 131.2442 | 0 | 0 | 0 | 95.6526 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 25.4831 | 4.3397 | 2.3113 | 9.2132 | 45.6962 | 5.754 | 0% | 100% ¦ $245 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2032 | BORDEN - GREGG#1: OPGW EGI |  |  | Madera | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Transmission Line - Other Equipment | New | NA | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-23 | 95 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.25 | NA | NA | NA | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5787080 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2020 | Project Management Governance Standard | 2020 | 2019 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7393-E | 2024-10-02 | Approved | 2024 | Engineering more than 50% complete | 3 | 2026-12-02 | 2020-09-30 | 2027-05-12 | Land Rights | NA | TRUE | 41660 | NA ¦ NA | 1.2829 | 5.6853 | 10.982 | 7.0505 | 1.7733 | 10.2861 | -35.1001 | 2.6292 | 1.7894 | 0 | 0 | 0 | 1.2668 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $6 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2033 | WRO Generator Network Upgrades |  |  |  | Interconnect Solar Photovoltaic panels with 11 inverters, each rated at 2.08 MW and a 15 MW of Battery Energy Storage Systems to PG&Es Crow Creek 60 kV Sw Sta. Crow Creek Sub: Install new partial BAAH 60 kV bay, 2 CB | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-02 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.036 | NA | 60 kV | NA | NA | NA | NA | NA | 5795664 | T.0007108 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-01-02 | 2023-02-01 | 2023-03-14 | NA | NA | FALSE | 2570 | NA ¦ NA | 1895.0038 | 1895.0038 | 32.7382 | 922.6989 | 933.2971 | 6.2694 | 0 | 0 | 0 | 0 | 0 | 0 | 1895.0038 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 1799.1463 | 5.9644 | -0.0001 | 0 | 0% | 100% ¦ $1,895 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2034 | WRO Generator Network Upgrades |  |  |  | Install the generation and energy storage project, which is comprised of photovoltaic solar panels, 37 Inverters, each rated at 1.8 MW, and a Battery Energy Storage System (“BESS”) comprised of 14 inverters each rated at 1.8 MW, with a maximum gross output of 66.6 MW. Auxiliary load of 1 MW and estimated losses of 0.7 MW, results in a net output of 64.9 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Arco 230 kV Substation in Kern County, California. Install one new 230 kV BAAH bay w/ three (3) CB, SW’s, new relays for Bank #2 at Arco Sub. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.5471 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5796088 | T.0007165 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-07-24 | 2024-05-30 | 2024-05-22 | NA | NA | TRUE | 8211 | NA ¦ NA | 8256.1814 | 8350.3074 | 30.2925 | 440.4212 | 4789.7095 | 2206.3888 | 797.3347 | 84.1525 | 2.0083 | 0 | 0 | 0 | 8264.1466 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 7385.3981 | 788.2154 | -7.8741 | 0% | 100% ¦ $8,350 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2035 | WRO Generator Network Upgrades |  |  |  | Construct the Energy Storage Project, which is comprised of 59 Inverters, each rated at 1.8 MW with a maximum gross output of 106.16 MW. Auxiliary load of 5.3 MW and estimated losses of 1.16 MW, results in a net output of 99.7 MW to the CAISO Controlled Grid. | Substation - Bus Arrangement | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-09 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 10.5414 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5796082 | T.0007181 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-06-01 | 2023-10-01 | 2024-01-19 | NA | NA | FALSE | 4090 | NA ¦ NA | 2219.1013 | 2219.1013 | 42.5029 | 459.7308 | 1223.9427 | 456.7495 | 36.1754 | 0 | 0 | 0 | 0 | 0 | 2219.1013 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 2147.2598 | 35.5598 | 0 | 0% | 100% ¦ $2,219 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2036 | WRO Generator Network Upgrades |  |  |  | Construct the Energy Storage Project, which is comprised of 59 Inverters, each rated at 1.8 MW with a maximum gross output of 106.16 MW. Auxiliary load of 5.3 MW and estimated losses of 1.16 MW, results in a net output of 99.7 MW to the CAISO Controlled Grid. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 35.6227 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5796083 | T.0007181 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-07-29 | 2023-10-01 | 2024-10-09 | Customer Action | NA | FALSE | 4090 | NA ¦ NA | 898.757 | 898.757 | 31.0424 | 142.4362 | 330.7758 | 385.5592 | 8.9434 | 0 | 0 | 0 | 0 | 0 | 898.757 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 889.8241 | 8.9434 | 0 | 0% | 100% ¦ $899 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2037 | WRO Generator Network Upgrades |  |  |  | Construct the Energy Storage Project, which is comprised of 59 Inverters, each rated at 1.8 MW with a maximum gross output of 106.16 MW. Auxiliary load of 5.3 MW and estimated losses of 1.16 MW, results in a net output of 99.7 MW to the CAISO Controlled Grid. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-02 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.6079 | NA | 230 kV | NA | NA | NA | 5.3 | Non-IGP | 5796084 | T.0007181 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-12-01 | 2023-10-01 | 2024-10-09 | Customer Action | NA | FALSE | 4090 | NA ¦ NA | 601.8357 | 601.8357 | 16.2019 | 202.7864 | 222.2034 | 151.3838 | 9.2602 | 0 | 0 | 0 | 0 | 0 | 601.8357 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 592.5861 | 9.2602 | 0 | 0% | 100% ¦ $602 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2038 | WRO Generator Network Upgrades |  |  |  | Interconnect 300 MW battery storage generating facility to PG&E's Vaca Dixon 230 kV Sub. Vaca-Dixon Sub: Install one new 230 kV double bus bay w/ 1 CB, SWs | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-25 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5796191 | T.0007195 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2023 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-07-01 | 2024-02-01 | 2026-09-18 | Customer Action | NA | TRUE | 6410 | NA ¦ NA | 4016.153 | 4627.0717 | 2.7157 | 92.7603 | 664.9602 | 1943.8787 | 1238.5987 | 399.6993 | 284.4587 | 0 | 0 | 0 | 3942.9136 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,627 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2039 | WRO Generator Network Upgrades |  |  |  | Install the generation project, which is comprised of photovoltaic solar panels, 43 x 2.4225 MW inverters, with a maximum gross output of 102.5 MW and Auxiliary load of 1.08 MW results in a net output of 100 MW to the CAISO Controlled Grid. Install a new BAAH bay with two (2) new 230kV circuit breaker with breaker failure relays to The Los Banos 230kV BAAH substation, and (2) Bus Sectionalized CB's, Bus Extension, Site Grading, &New Ctrl Bldg | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5796583 | T.0007250 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-08-08 | 2025-03-30 | 2027-01-28 | Prioritization | NA | TRUE | 13630 | NA ¦ NA | 20719.6968 | 33582.679 | 8.419 | 689.3535 | 3250.2481 | 5990.6811 | 9793.0664 | 8119.0304 | 5731.8806 | 0 | 0 | 0 | 19731.768 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $33,583 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2040 | TESLA 500KV REPLACE CB 612 |  |  | Alameda | Replace overstressed breakers 542, 612, & 642 at Tesla 500 kV sub to address a normal deficiency projected for 2021 and beyond. | Substation - Circuit Breaker | Replace | NA | T.0007195 ¦ T.0004563 ¦ T.0004354 ¦ T.0007467 ¦ T.0007981 ¦ T.0008098 ¦ T.0008918 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | 37 | Interconnection System Impact/Facilities Studies | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5797750 | T.0007288 | Tesla: Replace CB 542_CB 642_CB 612 | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-10-23 | 2024-09-30 | 2026-06-04 | Prioritization | NA | TRUE | 14700 | NA ¦ NA | 5835.6299 | 7255.5139 | 10.6595 | 109.7511 | 206.0561 | 1219.0424 | 2694.0374 | 2996.0604 | 19.907 | 0 | 0 | 0 | 4239.5464 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $7,256 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2041 | TESLA 500KV REPLACE CB 542 AND CB 642 |  |  | Alameda | Replace overstressed breakers 542, 612, & 642 at Tesla 500 kV sub to address a normal deficiency projected for 2021 and beyond. | Substation - Circuit Breaker | Replace | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | 35 | Interconnection System Impact/Facilities Studies | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 69.382 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5796865 | T.0007288 | Tesla: Replace CB 542_CB 642_CB 612 | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-09-16 | 2024-09-30 | 2025-03-27 | NA | NA | TRUE | 14700 | NA ¦ NA | 12983.3023 | 12988.3502 | 57.5615 | 381.631 | 2583.0326 | 7009.5803 | 2876.1855 | 80.3592 | 0 | 0 | 0 | 0 | 12907.9909 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 12167.8151 | 70.785 | 0% | 100% ¦ $12,988 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2042 | Gates: Replace CBs 352, 362, 372 |  |  | Fresno | Replace 230 kV Cap Bank Breakers: CB352, CB362, CB372 at Gates Substation as part of several generation interconnections required network upgrades. CAISO-approved Projects are directly impacting the overstressed level on breakers. Short circuit study in CAISO Generator Interconnection 2020 Annual Reassessment Study revealed that the Gates Cap Bank Breakers have become overstressed and that the overstress is caused by CAISO generation interconnection studies from cluster 10 through 12 for Electric Generation Interconnection projects. PG&E evaluated the short-circuit duty contributions to determine the projects triggering the circuit breaker overstressed and proposes to replace these breakers as part of Network Upgrade. | Substation - Circuit Breaker | Replace | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | 20 | Interconnection System Impact/Facilities Studies | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | NA | NA | NA | NA | NA | 5796864 | T.0007289 | Gates: Replace CBs 352, 362, 372 | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2022-10-24 | 2023-03-31 | 2023-07-12 | NA | NA | FALSE | 4850 | NA ¦ NA | 4130.7178 | 4130.7178 | 63.9816 | 2346.9876 | 1742.0386 | -22.2899 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.7178 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 3797.6746 | -20.3163 | 0 | 0 | 0% | 100% ¦ $4,131 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2043 | Metcalf: Replace Overstressed CBs |  |  | Santa Clara | Replace overstressed CB 492, CB 502, & CB 632 at Metcalf 115 kV substation. | Substation - Circuit Breaker | Replace | NA | T.0007467 ¦ T.0007032 ¦ T.0007981 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-05 | 23 | Interconnection System Impact/Facilities Studies | Other - Deferral | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5796866 | T.0007291 | Metcalf: Replace Overstressed CBs | 3 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2021 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-12-22 | 2028-01-28 | 2027-04-22 | NA | NA | TRUE | 9958 | NA ¦ NA | 4738.3472 | 13222.386 | 67.0516 | 64.1256 | 138.6982 | 306.1071 | 4108.9898 | 6587.0742 | 1938.5604 | 11.7792 | 0 | 0 | 4684.9722 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $13,222 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2044 | WRO Generator Network Upgrades |  |  |  | Interconnect 99 MW battery energy storage project at the Ripon 115 kV substation by completing Ring Bus with 2 CBs at Ripon Sub. Reconductor Ripon-Manteca 115 kV Line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total). Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line 25.23 mi section of various conductors from 018/115-043/277. Reconductor Bellota-Riverbank-Melones Sw Sta 115 kV Line (Tulloch Tap) section of 17 miles. Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/0 | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0004515 ¦ T.0007979 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.0603 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5797829 | T.0007445 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-02-11 | 2025-01-10 | 2026-10-26 | Construction Delays | Customer Action | TRUE | 12160 | NA ¦ NA | 301.0965 | 346.1608 | 1.6076 | 96.1893 | 58.2352 | 18.5441 | 122.7443 | 44.7325 | 4.1078 | 0 | 0 | 0 | 297.3205 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $346 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2045 | WRO Generator Network Upgrades |  |  |  | Interconnect 99 MW battery energy storage project at the Ripon 115 kV substation by completing Ring Bus with 2 CBs at Ripon Sub. Reconductor Ripon-Manteca 115 kV Line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total). Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line 25.23 mi section of various conductors from 018/115-043/277. Reconductor Bellota-Riverbank-Melones Sw Sta 115 kV Line (Tulloch Tap) section of 17 miles. Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/0 | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0004515 ¦ T.0007979 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.0603 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5797830 | T.0007445 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-02-05 | 2025-01-10 | 2026-10-26 | Construction Delays | Customer Action | TRUE | 12160 | NA ¦ NA | 294.4813 | 327.9376 | 1.1038 | 81.6032 | 54.0232 | 87.5414 | 65.6245 | 35.8044 | 2.2371 | 0 | 0 | 0 | 289.8961 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $328 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2046 | WRO Generator Network Upgrades |  |  |  | Interconnect 99 MW battery energy storage project at the Ripon 115 kV substation by completing Ring Bus with 2 CBs at Ripon Sub. Reconductor Ripon-Manteca 115 kV Line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total). Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line 25.23 mi section of various conductors from 018/115-043/277. Reconductor Bellota-Riverbank-Melones Sw Sta 115 kV Line (Tulloch Tap) section of 17 miles. Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/0 | Other - Operations Tech | New | NA | T.0004515 ¦ T.0007979 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-10 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.3123 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5797831 | T.0007445 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-05-23 | 2025-01-10 | 2026-10-26 | Construction Delays | Customer Action | TRUE | 12160 | NA ¦ NA | 1656.3782 | 1770.9358 | 2.1114 | 104.8051 | 137.2106 | 1220.938 | 170.3221 | 131.4407 | 4.1078 | 0 | 0 | 0 | 1635.3873 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,771 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2047 | WRO Generator Network Upgrades |  |  |  | Interconnect 99 MW battery energy storage project at the Ripon 115 kV substation by completing Ring Bus with 2 CBs at Ripon Sub. Reconductor Ripon-Manteca 115 kV Line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total). Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line 25.23 mi section of various conductors from 018/115-043/277. Reconductor Bellota-Riverbank-Melones Sw Sta 115 kV Line (Tulloch Tap) section of 17 miles. Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/0 | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0004515 ¦ T.0007979 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.0603 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5797832 | T.0007445 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2021 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2025-02-05 | 2025-01-10 | 2026-10-26 | Construction Delays | Customer Action | TRUE | 12160 | NA ¦ NA | 376.2504 | 450.8608 | 1.776 | 76.9491 | 128.7432 | 92.4272 | 67.5061 | 79.3514 | 4.1078 | 0 | 0 | 0 | 367.4016 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $451 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2048 | WRO Generator Network Upgrades |  |  |  | Interconnect 99 MW battery energy storage project at the Ripon 115 kV substation by completing Ring Bus with 2 CBs at Ripon Sub. Reconductor Ripon-Manteca 115 kV Line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total). Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line 25.23 mi section of various conductors from 018/115-043/277. Reconductor Bellota-Riverbank-Melones Sw Sta 115 kV Line (Tulloch Tap) section of 17 miles. Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/0 | Substation - Circuit Breaker | New | NA | T.0004515 ¦ T.0007979 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.0603 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5797828 | T.0007445 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2024-02-12 | 2025-01-10 | 2026-10-26 | Construction Delays | Customer Action | TRUE | 12160 | NA ¦ NA | 1739.9079 | 1933.4351 | 13.8209 | 48.7145 | 584.154 | 498.2674 | 555.8113 | 224.9179 | 7.7491 | 0 | 0 | 0 | 1700.7681 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,933 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2049 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Energy Storage Project, which is comprised of three hundred and ninety six (396) Parker 890GT-B inverters rated at 1.976 MW each with auxiliary load and associated losses of 26.3 MW that result in a maximum net output of 750 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities (the “Project”) connect to the Participating TO (Pacific Gas and Electric Company (“PG&E”) – owned 500 kV Moss Landing PP Substation in Monterey County California. | Substation - Circuit Breaker | New | NA | T.0007291 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-10 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 41.3213 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5797901 | T.0007467 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2029-02-06 | 2025-08-30 | 2030-05-31 | Material | NA | FALSE | 9120 | NA ¦ NA | 1250.0846 | 24534.4929 | 0 | 13.6239 | 61.2168 | 454.4057 | 629.9138 | 551.1638 | 10343.9703 | 2435.647 | 4136.5215 | 5908.0302 | 1159.1602 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $24,534 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2050 | WRO Generator Network Upgrades |  |  |  | Install a storage generation plant with a net output of 24.5 MW PG&Es 60 kV Tulucay Substation in Napa County, California. Tulucay Substation: • Extend maiNAux bus with DBSB, install aux switch, fence and grading • Install 2 DTT Receivers with new DTT panel Vaca-Dixon Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit Lakeville Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-25 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 42.1076 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5798549 | T.0007591 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | CEQA Final Published | 2024-04-08 | IS/MND | NA | County of Napa | NA | NOC: AL 7472-E | 2025-01-02 | Approved | 2025 | Construction (50%-75%) | 2 | 2025-03-21 | 2025-10-10 | 2027-01-22 | Customer Action | NA | TRUE | 5750 | NA ¦ NA | 183.5458 | 280.0722 | 0 | 32.8052 | 81.079 | 38.107 | 28.7943 | 68.9512 | 30.3354 | 0 | 0 | 0 | 180.7855 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $280 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2051 | WRO Generator Network Upgrades |  |  |  | Install a storage generation plant with a net output of 24.5 MW PG&Es 60 kV Tulucay Substation in Napa County, California. Tulucay Substation: • Extend maiNAux bus with DBSB, install aux switch, fence and grading • Install 2 DTT Receivers with new DTT panel Vaca-Dixon Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit Lakeville Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-13 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 14.7021 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5798550 | T.0007591 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | CEQA Final Published | 2024-04-08 | IS/MND | NA | County of Napa | NA | NOC: AL 7472-E | 2025-01-02 | Approved | 2025 | Construction (50%-75%) | 2 | 2025-03-21 | 2025-10-10 | 2027-02-08 | Customer Action | NA | TRUE | 5750 | NA ¦ NA | 209.0592 | 297.1917 | 0 | 22.292 | 77.1313 | 70.7063 | 35.4325 | 22.9826 | 68.647 | 0 | 0 | 0 | 205.5621 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $297 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2052 | WRO Generator Network Upgrades |  |  |  | Install a storage generation plant with a net output of 24.5 MW PG&Es 60 kV Tulucay Substation in Napa County, California. Tulucay Substation: • Extend maiNAux bus with DBSB, install aux switch, fence and grading • Install 2 DTT Receivers with new DTT panel Vaca-Dixon Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit Lakeville Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-04 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 4.1869 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5798548 | T.0007591 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | CEQA Final Published | 2024-04-08 | IS/MND | NA | County of Napa | NA | NOC: AL 7472-E | 2025-01-02 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-08-27 | 2025-10-10 | 2027-05-24 | Customer Action | NA | TRUE | 5750 | NA ¦ NA | 3950.6052 | 10702.3211 | 0 | 100.855 | 521.4118 | 880.9808 | 2406.0417 | 5303.7488 | 1489.2829 | 0 | 0 | 0 | 3909.2894 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $10,702 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2053 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Storage generation plant with a net output of 300.1 MW to Pacific Gas and Electric Company’s (PG&E’s) Gates Substation 500 kV bus in Huron, Fresno County, CA. The project scope of work includes following: Interconnection Facility: Gates Substation:  Install Gen. Tie BAAH Line Terminal Equipment  Install Fiber termination Generation Site:  PG&E pre-parallel inspection, Engineering Review  PG&E Install RTU, EMS Telemetry, SCADA Transmission Line:  Construct Gen-Tie conductors, 1 TSP single circuit, and PG&E review Reliability Network Upgrade: Gates Substation:  Install a new 500kV BAAH Bay with (2) 500kV breakers  Building and site expansion with security wall Midway Substation:  Replace 500kV breaker CB 722 (due to overstress) including relays  Replace CB 722 disconnects | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5799148 | T.0007722 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2024-06-18 | 2025-08-01 | 2026-05-20 | Material | NA | TRUE | 22660 | NA ¦ NA | 31918.2219 | 35029.0841 | 0 | 136.2726 | 2691.5593 | 12735.019 | 15272.9325 | 4193.3009 | 0 | 0 | 0 | 0 | 30835.7833 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $35,029 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2054 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Storage generation plant with a net output of 300.1 MW to Pacific Gas and Electric Company’s (PG&E’s) Gates Substation 500 kV bus in Huron, Fresno County, CA. The project scope of work includes following: Interconnection Facility: Gates Substation:  Install Gen. Tie BAAH Line Terminal Equipment  Install Fiber termination Generation Site:  PG&E pre-parallel inspection, Engineering Review  PG&E Install RTU, EMS Telemetry, SCADA Transmission Line:  Construct Gen-Tie conductors, 1 TSP single circuit, and PG&E review Reliability Network Upgrade: Gates Substation:  Install a new 500kV BAAH Bay with (2) 500kV breakers  Building and site expansion with security wall Midway Substation:  Replace 500kV breaker CB 722 (due to overstress) including relays  Replace CB 722 disconnects | Substation - Circuit Breaker | Replace | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | 31 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5799149 | T.0007722 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-07 | 2025-08-01 | 2024-11-22 | NA | NA | TRUE | 22660 | NA ¦ NA | 2658.7743 | 2658.7743 | 0 | 71.2465 | 696.8936 | 1352.015 | 532.5182 | 6.101 | 0 | 0 | 0 | 0 | 2652.6733 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 1917.6287 | 479.0165 | 5.488 | 0% | 100% ¦ $2,659 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2055 | Live Oak Transmission |  |  | Live Oak, Sutter | Replace Transformer #1 High Side protection, remove fuse and install 60 kV circuit switcher. | Substation - Switch | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-11 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 0.39793 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5804585 | T.0007727 | Live Oak Sub DTT, LTC & Hardwire | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-07-02 | 2026-03-31 | 2026-10-28 | Material | NA | TRUE | 2500 | NA ¦ NA | 1890.6573 | 3282.4624 | 0 | 0 | 404.8527 | 138.9701 | 661.1242 | 2072.4895 | 5.0258 | 0 | 0 | 0 | 1204.9471 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,282 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2056 | WRO Generator Network Upgrades |  |  |  | The project is a solar generation plant with a net output of 800 MW to Pacific Gas and Electric Company’s (PG&E’s) Midway Substation in Kern County. The project scope of work includes following: Interconnection Facility (From LGIA Table A-1): Midway Substation: • The Point of Interconnection of the Project is Midway Substation, at Bay 5 between CBs 852 and 952 on the 500 kV bus in a breaker-and-a-half (“BAAH”) configuration. • Install fiber terminations near the fence for LCD communications. Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E Install RTU, EMS Telemetry, SCADA Transmission Line: • Gen-Tie: Install 2 conductors, 1 TSP single circuit, and PG&E review Reliability Network Upgrade (From LGIA Table G-1): Midway Substation: • Complete BAAH Bay, CB, Sw, • Install Dead-end structure, Bkr, Control Relays • Replace CB 712 with new breaker with 63kA interrupting capacity Gates Substation: • Install series bus reactors between Gates Substation 230kV bus sections E and F | Substation - Circuit Breaker | New | NA | T.0008543 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5799285 | T.0007731 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 2 | 2025-06-03 | 2025-05-01 | 2028-03-01 | Prioritization | NA | FALSE | 20300 | NA ¦ NA | 13622.8928 | 24486.4534 | 0 | 85.6381 | 668.1337 | 4305.4053 | 8090.7919 | 5625.6502 | 3376.782 | 2334.0523 | 0 | 0 | 13149.9689 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $24,486 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2057 | WRO Generator Network Upgrades |  |  |  | The project is a solar generation plant with a net output of 800 MW to Pacific Gas and Electric Company’s (PG&E’s) Midway Substation in Kern County. The project scope of work includes following: Interconnection Facility (From LGIA Table A-1): Midway Substation: • The Point of Interconnection of the Project is Midway Substation, at Bay 5 between CBs 852 and 952 on the 500 kV bus in a breaker-and-a-half (“BAAH”) configuration. • Install fiber terminations near the fence for LCD communications. Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E Install RTU, EMS Telemetry, SCADA Transmission Line: • Gen-Tie: Install 2 conductors, 1 TSP single circuit, and PG&E review Reliability Network Upgrade (From LGIA Table G-1): Midway Substation: • Complete BAAH Bay, CB, Sw, • Install Dead-end structure, Bkr, Control Relays • Replace CB 712 with new breaker with 63kA interrupting capacity Gates Substation: • Install series bus reactors between Gates Substation 230kV bus sections E and F | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0008543 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5553765 | T.0007731 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2023 | Project Management Governance Standard | 2023 | 2021 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-06-10 | 2025-05-01 | 2028-03-28 | Prioritization | NA | TRUE | 20300 | NA ¦ NA | 289.5039 | 803.6707 | 0 | 0 | 3.2414 | 56.7307 | 206.4105 | 91.8979 | 296.5744 | 148.8157 | 0 | 0 | 266.3826 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2028 | 0 | 0 | 0 | 59.9721 | 206.4105 | 23.1213 | 0% | 100% ¦ $804 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2058 | WRO Generator Network Upgrades |  |  |  | The project proposes to reconductor 45 miles of 115kV Line upgrades with a higher capacity conductor and is a Local Delivery Network Upgrade (LDNU) project tied to the Q1557 electric generation interconnection project. The project scope of work includes the following: • Ripon-Manteca 115 kV Line Reconductor: Reconductor Ripon-Manteca 115 kV Line 2/0 CU and 4/0 ACSR sections with 715.5 AAC, 126/148 MVA • Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line Reconductor: Reconductor Ripon -Manteca 115 kV Line 2/0 CU and 4/0 ACSR sections with 715.5 AAC, 126/148 MVA • Bellota-Riverbank-Melones Sw Sta 115 kV Line 115 kV Line Reconductor: Reconductor 17 miles of Bellota-Riverbank-Melones Sw Sta 115 kV Line (Riverbank Tap to Tulloch Tap) with 477 ACSS 224/224/245/245 MVA. • Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line Reconductor: Reconductor 7.49 miles of Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line from :000/001 to :007/043 with 715 AAC, 126/148 MVA. | Substation - Line Termination | New | NA | T.0007445 ¦ T.0004515 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-14 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 9.8539 | NA | 115 kV | NA | NA | NA | 5.211 | Non-IGP | 5812826 | T.0007979 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2021 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-07-22 | 2025-01-10 | 2027-08-11 | Prioritization | NA | TRUE | 136800 | NA ¦ NA | 44.9126 | 580.6942 | 0 | 0 | 0 | 0 | 34.7321 | 383.5457 | 152.1825 | 10.234 | 0 | 0 | 34.732 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $581 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2059 | WRO Generator Network Upgrades |  |  |  | The Project is a Storage generation plant with a net output of 200.0 MW to Pacific Gas and Electric Company’s (PG&E’s) Los Esteros Substation San Jose CA. | Substation - Circuit Breaker | New | NA | T.0007287 ¦ T.0007291 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-09 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5799786 | T.0007981 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-05-03 | 2025-01-01 | 2027-09-27 | Material | Land Rights | TRUE | 6420 | NA ¦ NA | 1378.3804 | 8816.5697 | 0 | 11.2157 | 527.9499 | 320.3202 | 465.0647 | 2077.7282 | 4874.919 | 207.3811 | 171.2083 | 160.7826 | 1324.5505 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $8,817 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2060 | NU upgrade Los Gatos Sub Install PTs |  |  | Los Gatos, Santa Clara | This project proposes to connect 160kW Photovoltaic generating facility to PG&E’s Los Gatos 1101 distribution circuit. MWC 82 • Replace existing C-phase PT with three new PTs and associated support structures | Substation - Protection Relay | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.7484 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5548348 | T.0008054 | NU upgrade Los Gatos Sub Install PTs | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-11-03 | 2027-05-28 | 2026-02-02 | NA | NA | TRUE | 6900 | NA ¦ NA | 413.5284 | 461.9279 | 0 | 27.9633 | 75.175 | 117.2802 | 191.0912 | 35.9216 | 14.4967 | 0 | 0 | 0 | 411.5097 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 27.9633 | 75.1751 | 117.2802 | 191.0912 | 2.0187 | 0% | 100% ¦ $462 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2061 | WRO Generator Network Upgrades |  |  |  | The IC plans to install a Battery Energy Storage and Photovoltaic Solar System, 244 BESS Inverters, each rated at 2.09 MW and 235 PV inverters, each rated at 2.185 MW, with a maximum gross output of 511.9 MW. Auxiliary load of 5.1 MW and estimated losses of 11.9 MW, results in a net output of 500 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Delevan Substation in Colusa County, California (the “Project”). The project scope of work includes following: Interconnection Facility: Substation scope: Delevan Substation: • Install line relay package, voltage transformers, dead-end, and line switch • Install fiber terminations near the fence for LCD communications at Delevan Substation Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E RTU, EMS Telemetry, SCADA Transmission Line: • Install 2 spans of conductor, 1 TSP single circuit, and a Gen-Tie review by PG&E Reliability Network Upgrade: Substation scope: Delevan Substation (IRNU): • Install new CB to complete BAAH bay, with breaker control relays Cottonwood Substation (GRNU): • Replace 230 kV circuit breakers 232, 242 and associated switches/relays | Substation - Circuit Breaker | New | NA | T.0009188¦ T.0001609 ¦ T.0008063 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 26.1945 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5799987 | T.0008063 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-05-15 | 2025-03-21 | 2026-08-13 | Construction Delays | Material | TRUE | 7480 | NA ¦ NA | 1830.9435 | 4153.0976 | 0 | 20.1054 | 139.1965 | 205.4974 | 477.6329 | 3107.1788 | 203.4867 | 0 | 0 | 0 | 842.4321 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,153 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2062 | WRO Generator Network Upgrades |  |  |  | The IC plans to install a Battery Energy Storage and Photovoltaic Solar System, 244 BESS Inverters, each rated at 2.09 MW and 235 PV inverters, each rated at 2.185 MW, with a maximum gross output of 511.9 MW. Auxiliary load of 5.1 MW and estimated losses of 11.9 MW, results in a net output of 500 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Delevan Substation in Colusa County, California (the “Project”). The project scope of work includes following: Interconnection Facility: Substation scope: Delevan Substation: • Install line relay package, voltage transformers, dead-end, and line switch • Install fiber terminations near the fence for LCD communications at Delevan Substation Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E RTU, EMS Telemetry, SCADA Transmission Line: • Install 2 spans of conductor, 1 TSP single circuit, and a Gen-Tie review by PG&E Reliability Network Upgrade: Substation scope: Delevan Substation (IRNU): • Install new CB to complete BAAH bay, with breaker control relays Cottonwood Substation (GRNU): • Replace 230 kV circuit breakers 232, 242 and associated switches/relays | Substation - Circuit Breaker | New | NA | T.0009188¦ T.0001609 ¦ T.0008063 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 26.1945 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5812423 | T.0008063 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2021 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-09-15 | 2025-03-21 | 2026-10-15 | Construction Delays | Material | TRUE | 7480 | NA ¦ NA | 552.4061 | 2394.7775 | 0 | 0 | 0 | 1.0649 | 200.142 | 2191.8737 | 1.6968 | 0 | 0 | 0 | 201.2069 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,395 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2063 | WRO Generator Network Upgrades |  |  |  | The IC plans to install a Battery Energy Storage and Photovoltaic Solar System, 244 BESS Inverters, each rated at 2.09 MW and 235 PV inverters, each rated at 2.185 MW, with a maximum gross output of 511.9 MW. Auxiliary load of 5.1 MW and estimated losses of 11.9 MW, results in a net output of 500 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Delevan Substation in Colusa County, California (the “Project”). The project scope of work includes following: Interconnection Facility: Substation scope: Delevan Substation: • Install line relay package, voltage transformers, dead-end, and line switch • Install fiber terminations near the fence for LCD communications at Delevan Substation Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E RTU, EMS Telemetry, SCADA Transmission Line: • Install 2 spans of conductor, 1 TSP single circuit, and a Gen-Tie review by PG&E Reliability Network Upgrade: Substation scope: Delevan Substation (IRNU): • Install new CB to complete BAAH bay, with breaker control relays Cottonwood Substation (GRNU): • Replace 230 kV circuit breakers 232, 242 and associated switches/relays | Substation - Circuit Breaker | New | NA | T.0009188¦ T.0001609 ¦ T.0008063 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 26.1945 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5812424 | T.0008063 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2021 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-08-27 | 2025-03-21 | 2026-10-28 | Construction Delays | Material | TRUE | 7480 | NA ¦ NA | 637.1169 | 2791.3304 | 0 | 0 | 0 | 1.3223 | 266.2 | 2515.9196 | 7.8885 | 0 | 0 | 0 | 267.5223 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,791 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2064 | WRO Generator Network Upgrades |  |  |  | The IC plans to install a Battery Energy Storage and Photovoltaic Solar System, 244 BESS Inverters, each rated at 2.09 MW and 235 PV inverters, each rated at 2.185 MW, with a maximum gross output of 511.9 MW. Auxiliary load of 5.1 MW and estimated losses of 11.9 MW, results in a net output of 500 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Delevan Substation in Colusa County, California (the “Project”). The project scope of work includes following: Interconnection Facility: Substation scope: Delevan Substation: • Install line relay package, voltage transformers, dead-end, and line switch • Install fiber terminations near the fence for LCD communications at Delevan Substation Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E RTU, EMS Telemetry, SCADA Transmission Line: • Install 2 spans of conductor, 1 TSP single circuit, and a Gen-Tie review by PG&E Reliability Network Upgrade: Substation scope: Delevan Substation (IRNU): • Install new CB to complete BAAH bay, with breaker control relays Cottonwood Substation (GRNU): • Replace 230 kV circuit breakers 232, 242 and associated switches/relays | Substation - Circuit Breaker | New | NA | T.0009188¦ T.0001609 ¦ T.0008063 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.7615 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5799986 | T.0008063 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2033-07-28 | 2025-03-21 | 2033-12-16 | Construction Delays | Material | FALSE | 7480 | NA ¦ NA | 402.7421 | 4824.7485 | 0 | 41.9215 | 235.6682 | 67.4153 | 52.2278 | 29.9264 | 31.2659 | 33.5576 | 36.0173 | 38.6572 | 397.2328 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,825 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2065 | Arco 230kV Control Building NU |  |  | Kern | The project proposes to install a new control building to accommodate several new Generation Interconnection and Storage Projects already in the queue for the 230kV bus at Arco. The station control building was installed in 1973. It houses both 230 and 70 kV, but the main issue is that the existing control building is deficient in space and location to be used for the new interconnections. | Substation - Modular Protection and Automation Control Building | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | 51 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.5471 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5800064 | T.0008073 | Arco 230kV Control Building NU | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2023-08-21 | 2023-07-30 | 2024-05-22 | Project Design | NA | TRUE | 9200 | NA ¦ NA | 14103.3488 | 14120.281 | 0 | 660.4102 | 8829.0774 | 2851.5821 | 1547.3443 | 231.867 | 0 | 0 | 0 | 0 | 13888.4141 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 11936.2038 | 1493.914 | 207.5129 | 0% | 100% ¦ $14,120 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2066 | ARCO 230kV - MIDWAY LCD |  |  | Kern | The project proposes to install a new control building to accommodate several new Generation Interconnection and Storage Projects already in the queue for the 230kV bus at Arco. The station control building was installed in 1973. It houses both 230 and 70 kV, but the main issue is that the existing control building is deficient in space and location to be used for the new interconnections. | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.5471 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5803819 | T.0008073 | Arco 230kV Control Building NU | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2020 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-10-01 | 2023-07-30 | 2025-05-20 | Project Design | NA | TRUE | 9200 | NA ¦ NA | 473.4502 | 473.4502 | 0 | 3.2452 | 38.7304 | 228.1057 | 203.3689 | 0 | 0 | 0 | 0 | 0 | 473.4502 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 449.1894 | 0 | 0% | 100% ¦ $473 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2067 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Storage generation plant with a net output of 250MW to Pacific Gas and Electric Company’s (PG&E’s) SF H (Martin) Substation 115kV bus in San Francisco CA. | Substation - Circuit Breaker | New | NA | T.0007288 ¦ T.0007287 ¦ T.0001493 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Subsidence |  | NA | 18.2105 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5799981 | T.0008098 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2027-02-16 | 2024-12-15 | 2027-12-23 | Material | NA | TRUE | 2798 | NA ¦ NA | 327.2733 | 5799.4449 | 0 | 0 | 2.9845 | 13.2024 | 301.0643 | 2439.0456 | 2370.6553 | 672.4928 | 0 | 0 | 317.2512 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $5,799 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2068 | WRO Generator Network Upgrades |  |  |  | The Project is a PV and battery generation plant with a net output of 150 MW to Pacific Gas and Electric Company’s (PG&E’s) owned Cortina 115 kV Substation in Colusa County CA The high level project scope of work includes following: Interconnection Facility: Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E RTU, EMS Telemetry, SCADA Transmission Line: • Install 4 spans of conductor, 3 TSPs single circuit, and gen-tie review by PG&E Interconnection Facilities: • Cortina Substation: Install line relay package, voltage transformers, dead-end, and line switch; IT: Install fiber terminations near the fence for LCD communications Reliability Network Upgrade: Substation scope: • Cortina Substation: Install new BAAH bay, 3 CBs, with breaker control relays Deliverability Network Upgrade: • See separate Authorization for T.0007629 order 74043720 routed in Unifier. o Re-conductor Fulton – Hopland 60 kV Line (Fitch Mountain Tap 009/005A – Geysers Jct 016/004) ~7 mi total length with 715 AAC | Substation - Circuit Breaker | New | NA | T.0001609 ¦ T.0007629 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.7436 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5800367 | T.0008218 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2022 | 2022 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | CEC | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-10-30 | 2025-04-28 | 2027-06-09 | Permitting | Customer Action | TRUE | 5612 | NA ¦ NA | 2762.3726 | 7023.1183 | 0 | 63.9599 | 271.3132 | 472.9591 | 1906.5687 | 2138.3977 | 2169.9197 | 0 | 0 | 0 | 2714.8009 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $7,023 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2069 | WRO Generator Network Upgrades |  |  |  | Install series bus reactors between Gates Substation 230 kV bus sections E and F (18 ohms in parallel, 9 ohms equivalent/net) (Count: 6 Reactors) which will remove the overstress condition on the Gates Substation 230 kV Bus. This project will support California’s policy to increase renewable energy production and reduce greenhouse gas emission. Completion of the project will enable PG&E to purchase renewable energy from Generation Owners, under a California Public Utilities Commission (CPUC) approved power purchase agreement as part of PG&E’s effort to achieve its renewable portfolio standards (RPS) | Substation - Reactive Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5799287 | T.0008543 | WRO Generator Network Upgrades | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2022 | Project Management Governance Standard | 2022 | 2021 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2024-11-06 | 2025-05-01 | 2025-09-04 | Customer Action | NA | TRUE | 20300 | NA ¦ NA | 11074.3784 | 11508.8288 | 0 | 149.8517 | 884.7763 | 7674.1023 | 2332.2251 | 454.4257 | 13.4477 | 0 | 0 | 0 | 11040.9553 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 10896.6008 | 32.9432 | 0% | 100% ¦ $11,509 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2070 | WRO Generator Network Upgrades |  |  |  | The Project is a combined photovoltaic solar and battery energy storage technology-based generation facility with a net output of 500.0 MW to the CAISO controlled grid. The Large Generating Facility and associated Interconnection Facilities connects to the new 230kV switching station (or the new “Q1593 Switching Station”) along PG&E’s Gates-Midway 230kV transmission line in Kettleman City, Kings County, California (the “Project”). | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0008543 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5803141 | T.0008735 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | NA | NA | NA | TRUE | Final Certified | 2023-12-01 | EIR | NA | Kern County | NA | NOC: AL 7236-E | 2024-04-05 | Approved | 2024 | Construction (over 75%) | 2 | 2026-02-03 | 2026-09-22 | 2026-03-13 | NA | NA | TRUE | 30284 | NA ¦ NA | 241.0512 | 380.9109 | 0 | 0 | 67.4614 | 72.3828 | 56.7937 | 184.273 | 0 | 0 | 0 | 0 | 196.6379 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $381 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2071 | WRO Generator Network Upgrades |  |  |  | The Project is a combined photovoltaic solar and battery energy storage technology-based generation facility with a net output of 500.0 MW to the CAISO controlled grid. The Large Generating Facility and associated Interconnection Facilities connects to the new 230kV switching station (or the new “Q1593 Switching Station”) along PG&E’s Gates-Midway 230kV transmission line in Kettleman City, Kings County, California (the “Project”). | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0008543 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5803142 | T.0008735 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | NA | NA | NA | TRUE | Final Certified | 2023-12-01 | EIR | NA | Kern County | NA | NOC: AL 7236-E | 2024-04-05 | Approved | 2024 | Construction (over 75%) | 2 | 2026-02-03 | 2026-09-22 | 2026-03-13 | NA | NA | TRUE | 30284 | NA ¦ NA | 202.3425 | 392.296 | 0 | 0 | 72.5372 | 39.7289 | 48.4832 | 231.5466 | 0 | 0 | 0 | 0 | 160.7494 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $392 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2072 | WRO Generator Network Upgrades |  |  |  | The Project is a combined photovoltaic solar and battery energy storage technology-based generation facility with a net output of 500.0 MW to the CAISO controlled grid. The Large Generating Facility and associated Interconnection Facilities connects to the new 230kV switching station (or the new “Q1593 Switching Station”) along PG&E’s Gates-Midway 230kV transmission line in Kettleman City, Kings County, California (the “Project”). | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0008543 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.5471 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5803143 | T.0008735 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | NA | NA | NA | TRUE | Final Certified | 2023-12-01 | EIR | NA | Kern County | NA | NOC: AL 7236-E | 2024-04-05 | Approved | 2024 | Construction (over 75%) | 2 | 2025-11-14 | 2026-09-22 | 2026-03-13 | NA | NA | TRUE | 30284 | NA ¦ NA | 81.5195 | 81.7641 | 0 | 0 | 24.8984 | 27.7331 | 23.5846 | 5.548 | 0 | 0 | 0 | 0 | 76.2161 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $82 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2073 | WRO Generator Network Upgrades |  |  |  | The Project is a combined photovoltaic solar and battery energy storage technology-based generation facility with a net output of 500.0 MW to the CAISO controlled grid. The Large Generating Facility and associated Interconnection Facilities connects to the new 230kV switching station (or the new “Q1593 Switching Station”) along PG&E’s Gates-Midway 230kV transmission line in Kettleman City, Kings County, California (the “Project”). | Substation - Multiple | New | NA | T.0008543 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5803145 | T.0008735 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | NA | NA | NA | TRUE | Final Certified | 2023-12-01 | EIR | NA | Kern County | NA | NOC: AL 7236-E | 2024-04-05 | Approved | 2024 | Construction (over 75%) | 2 | 2024-12-16 | 2026-09-22 | 2026-03-15 | NA | NA | TRUE | 30284 | NA ¦ NA | 3644.6095 | 4125.9879 | 0 | 0 | 169.2074 | 341.6148 | 2238.3597 | 1376.806 | 0 | 0 | 0 | 0 | 2749.1819 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,126 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2074 | WRO Generator Network Upgrades |  |  |  | The Project is a combined photovoltaic solar and battery energy storage technology-based generation facility with a net output of 500.0 MW to the CAISO controlled grid. The Large Generating Facility and associated Interconnection Facilities connects to the new 230kV switching station (or the new “Q1593 Switching Station”) along PG&E’s Gates-Midway 230kV transmission line in Kettleman City, Kings County, California (the “Project”). | Substation - Multiple | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 4.5471 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5556900 | T.0008735 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ 5803146 ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2022 | FALSE | NA | NA | NA | TRUE | Final Certified | 2023-12-01 | EIR | NA | Kern County | NA | NOC: AL 7236-E | 2024-04-05 | Approved | 2024 | Engineering less than 50% complete | 4 | NA | 2026-09-22 | 2026-03-15 | NA | NA | TRUE | 30284 | NA ¦ NA | 37.1575 | 23402.0335 | 0 | 0 | 1.3599 | 7.6243 | 17.1197 | 23375.9296 | 0 | 0 | 0 | 0 | 26.1039 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 26.1039 | 11.0536 | 0% | 100% ¦ $23,402 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2075 | AVENA SUB Install 3 CCVTs - Reg. Upgrade |  |  | San Joaquin | Lagorio Properties LP North, an Interconnection Customer (IC), has requested a Generating Facility (GF)interconnection for Lagorio Properties LP (Project) to the Pacific Gas and Electric Company (PG&E)'sdistribution system for a 576 kW Photovoltaic generating facility to be located at GPS: 37.921169, -121.038304, Stockton, CA 95320. The Generating Facility will be connected to PG&E's Avena1702 distribution circuit. Interconnection will be in accordance with CPUC's Generating Facility Interconnections, Electric Rule 21. Transmission Scope: 1. Avena Substation Install 115kV CCVTs - Overvoltage Protection scheme for Bank #1 | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-02 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 1.1347 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5808018 | T.0008759 | Avena Sub_DC panel, Relay Cab, OV relays | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-02-01 | NA | 2027-11-08 | NA | NA | TRUE | 1708 | NA ¦ NA | 131.734 | 1215.9791 | 0 | 0 | 15.3847 | 25.9752 | 58.002 | 293.7733 | 649.6065 | 173.2374 | 0 | 0 | 99.3619 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,216 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2076 | WRO Generator Network Upgrades |  |  |  | The Project is a Solar-PV, Wind, and Battery Storage generation plant with a net output of 400MW connects to Pacific Gas and Electric Company’s (PG&E’s) Tesla Substation in Tracy, San Joaquin County, CA. Tesla Substation 500 kV:  Expand 500 kV BAAH Bay expansion with (1) 500 kV CB. | Substation - Circuit Breaker | New | NA | T.0001609 ¦ T.0007291 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | 69.382 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5803784 | T.0008918 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2022 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-02-02 | 2028-03-20 | 2027-03-23 | NA | NA | TRUE | 13566 | NA ¦ NA | 1955.252 | 9868.3434 | 0 | 0 | 66.6191 | 134.3799 | 409.7104 | 6168.8622 | 3031.3983 | 57.3736 | 0 | 0 | 610.7093 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $9,868 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2077 | WRO Generator Network Upgrades |  |  |  | The Project is a Wind generation plant with a net output of 1000MW connects to Pacific Gas and Electric Company’s (PG&E’s) Diablo Canyon Switching Station 500 kV in Avila Beach San Luis County, CA | Substation - Circuit Breaker | New | NA | T.0003009 ¦ T.0008543 ¦ T.0007722 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 35.6227 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5804097 | T.0008967 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2023 | 2022 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2033-12-05 | 2028-04-12 | 2035-01-02 | Permitting | Customer Action | FALSE | 18553 | NA ¦ NA | 408.6912 | 6283.6543 | 0 | 0 | 54.8057 | 317.6769 | 33.6299 | 27.8112 | 32.2247 | 34.5877 | 90.9962 | 999.0422 | 406.1124 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $6,284 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
2078 | New SS for Los Banos-Panoche 230kV |  |  | Merced | The high level project scope of work includes following: • Build a new 3-bay BAAH, 230 kV Switching Station (SS) near the existing Dos Amigos Pumping Plant (PP). The ultimate bus arrangement should be 6-bay BAAH. • Build the Switching Station with enough room for future installation of two 230/70 kV transformers, a 70 kV bus and line terminations for future connection to the Mercy Springs Switching Station (this is a separate project submitted by PG&E to CAISO through the TPP process). • Disconnect the Los Banos-Dos Amigos PP 230 kV and the Dos Amigos PP-Panoche 230 kV line terminals at Dos Amigos PP. • Build two 230 kV lines (less than 2 miles each) to loop the Los Banos-Dos Amigos PP and the Dos Amigos PP-Panoche 230 kV Lines into the new Switching Station • Build two 230 kV lines from the new Switching Station to Dos Amigos PP. • Upgrade associated equipment at Los Banos and Panoche substations to meet the required ampacity of the lines. • Acquire land for the new Switching Station | Substation - Multiple | New | NA | T.0009550 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.17 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5804622 | T.0009177 | New SS for Los Banos-Panoche 230kV | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2023 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-12-20 | 2028-05-01 | 2029-06-27 | Scope Change | NA | FALSE | $50,000 ¦ $100,000 | NA ¦ NA | 317.9166 | 2621.2653 | 0 | 0 | 0 | 74.3835 | 187.5916 | 957.5029 | 304.3859 | 355.3724 | 742.029 | 0 | 261.9751 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,621 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2079 | SS Los Banos-Panoche Perm Land Acq |  |  | Merced | The high level project scope of work includes following: • Build a new 3-bay BAAH, 230 kV Switching Station (SS) near the existing Dos Amigos Pumping Plant (PP). The ultimate bus arrangement should be 6-bay BAAH. • Build the Switching Station with enough room for future installation of two 230/70 kV transformers, a 70 kV bus and line terminations for future connection to the Mercy Springs Switching Station (this is a separate project submitted by PG&E to CAISO through the TPP process). • Disconnect the Los Banos-Dos Amigos PP 230 kV and the Dos Amigos PP-Panoche 230 kV line terminals at Dos Amigos PP. • Build two 230 kV lines (less than 2 miles each) to loop the Los Banos-Dos Amigos PP and the Dos Amigos PP-Panoche 230 kV Lines into the new Switching Station • Build two 230 kV lines from the new Switching Station to Dos Amigos PP. • Upgrade associated equipment at Los Banos and Panoche substations to meet the required ampacity of the lines. • Acquire land for the new Switching Station | Other | New | NA | T.0009550 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.17 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5552372 | T.0009177 | New SS for Los Banos-Panoche 230kV | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2023 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | NA | 2028-05-01 | 2029-09-07 | Scope Change | NA | FALSE | $50,000 ¦ $100,000 | NA ¦ NA | 0 | 4511.7165 | 0 | 0 | 0 | 0 | 0 | 88.6435 | 43.4202 | 122.3993 | 4257.2536 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,512 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2080 | WRO Generator Network Upgrades |  |  |  | Replace overstressed 230kV CB's 522 & 542 with 63kA CB's for an interconnection of a Wind Cottonwood 230KV Project. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 26.1945 | NA | 230 kV | 3 | 6. Customer commitments | NA | 3.002 | Non-IGP | 5775145 | T.0009188 | WRO Generator Network Upgrades | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2019 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-06-27 | 2020-06-01 | 2025-09-29 | Permitting | Customer Action | TRUE | 31980 | NA ¦ NA | 2052.443 | 2099.3257 | 25.7448 | 106.8242 | 109.575 | 647.1878 | 1085.7922 | 114.0844 | 0 | 0 | 0 | 0 | 1985.2413 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 1687.7555 | 56.5131 | 0% | 100% ¦ $2,099 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2081 | WRO Generator Network Upgrades |  |  |  | Replace overstressed 230kV CB's 522 & 542 with 63kA CB's for an interconnection of a Wind Cottonwood 230KV Project. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | 62 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 26.1945 | NA | 230 kV | NA | NA | NA | 5.211 | Non-IGP | 5816658 | T.0009188 | WRO Generator Network Upgrades | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2024 | Project Management Governance Standard | 2025 | 2017 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-10-06 | 2020-06-01 | 2025-11-13 | Permitting | Customer Action | TRUE | 31980 | NA ¦ NA | 152.3282 | 206.4287 | 0 | 0 | 0 | 0 | 151.6871 | 54.7416 | 0 | 0 | 0 | 0 | 151.6871 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 151.6871 | 0.64111 | 0% | 100% ¦ $206 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2082 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer, IC, plans to install the project, with a net output of 100 MW to PG&E owned Arco Substation in Lost Hills, Kern County. The IC will connected to the 230kv BAAH bus. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5804794 | T.0009193 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2022 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-11-10 | 2025-12-15 | 2028-02-16 | Permitting | Customer Action | FALSE | 5350 | NA ¦ NA | 13.062 | 1097.9282 | 0 | 0 | 0 | 0.8812 | 11.0897 | 153.7727 | 745.9161 | 186.2685 | 0 | 0 | 11.9709 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,098 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2083 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer, IC, plans to install the project, with a net output of 100 MW to PG&E owned Arco Substation in Lost Hills, Kern County. The IC will connected to the 230kv BAAH bus. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5804795 | T.0009193 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2022 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-08-25 | 2025-12-15 | 2028-02-25 | Permitting | Customer Action | FALSE | 5350 | NA ¦ NA | 2.3859 | 1103.8323 | 0 | 0 | 0 | 0.6191 | 1.1654 | 165.9965 | 801.3131 | 134.7382 | 0 | 0 | 1.7845 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,104 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2084 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer, IC, plans to install the project, with a net output of 100 MW to PG&E owned Arco Substation in Lost Hills, Kern County. The IC will connected to the 230kv BAAH bus. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.5471 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5804793 | T.0009193 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2022 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-03-16 | 2025-12-15 | 2028-06-22 | Permitting | Customer Action | FALSE | 5350 | NA ¦ NA | 50.5254 | 1205.2197 | 0 | 0 | 0 | 1.1531 | 37.9881 | 149.4178 | 217.0417 | 763.7874 | 35.8317 | 0 | 39.1412 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,205 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2085 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Substation - Other Equipment | Upgrade/Retrofit | NA | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5805802 | T.0009383 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2023 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7656-E | 2025-07-30 | Approved | 2025 | Construction (under 10%) | 2 | 2026-02-02 | 2028-08-01 | 2029-12-12 | Customer Action | Scope Change | FALSE | 94899 | NA ¦ NA | 1225.1549 | 8846.4924 | 0 | 0 | 12.4086 | 299.4871 | 644.1981 | 3809.8366 | 1340.6862 | 421.8977 | 2317.9781 | 0 | 956.0938 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $8,846 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2086 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Substation - Multiple | New | NA | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5805805 | T.0009383 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2023 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7656-E | 2025-07-30 | Approved | 2025 | Engineering more than 50% complete | 3 | 2026-07-06 | 2028-08-01 | 2027-05-12 | NA | NA | TRUE | 94899 | NA ¦ NA | 240.2994 | 1020.7829 | 0 | 0 | 0 | 14.0959 | 204.5811 | 325.7293 | 419.9817 | 56.3949 | 0 | 0 | 218.677 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,021 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2087 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Substation - Multiple | New | NA | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5805804 | T.0009383 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2023 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7656-E | 2025-07-30 | Approved | 2025 | Engineering more than 50% complete | 3 | 2028-03-01 | 2028-08-01 | 2028-05-12 | NA | NA | FALSE | 94899 | NA ¦ NA | 417.0381 | 30654.367 | 0 | 0 | 0 | 16.9168 | 311.5917 | 1954.5675 | 18905.4884 | 4257.703 | 5208.0995 | 0 | 328.5085 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $30,654 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2088 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Substation - Multiple | New | NA | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5554012 | T.0009383 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2023 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7656-E | 2025-07-30 | Approved | 2025 | Engineering more than 50% complete | 3 | NA | 2028-08-01 | 2029-12-12 | Customer Action | Scope Change | FALSE | 94899 | NA ¦ NA | 0 | 98200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98200 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $98,200 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2089 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Substation - Multiple | New | NA | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5805806 | T.0009383 | WRO Generator Network Upgrades | 9 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2023 | 2023 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NOC: AL 7656-E | 2025-07-30 | Approved | 2025 | Engineering more than 50% complete | 3 | 2029-08-02 | 2028-08-01 | 2029-12-12 | Customer Action | Scope Change | FALSE | 94899 | NA ¦ NA | 113.3766 | 37065.9712 | 0 | 0 | 0 | 6.7844 | 91.1128 | 183.6661 | 2375.9986 | 314.9608 | 33848.3493 | 245.0992 | 97.8972 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $37,066 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2090 | RALSTON: EGI: INSTALL 3 -1PH PTS |  |  | Highlands CDP, San Mateo | Install 3 PTs on the high side of Bank 1. Install 3 Pts on the high side of Bank 2. Install PTs on new structure. Connect drops from the Overheads conductors to the Pts. Wire PTs secondaries to OV relays. Run Conduit from the PTs to the stand- alone relay cabinet. Install grounding conductors and associate hardware for a complete grounding system. Underground conduits and junction boxes. Civil foundations and site surfacing, grading, drainage. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.62031 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5553556 | T.0009411 | RALSTON: EGI (PT and OV RELAY) | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-07-30 | 2025-10-31 | 2025-11-17 | NA | NA | TRUE | 1623 | NA ¦ NA | 1207.2758 | 1210.5958 | 0 | 0 | 18.7137 | 200.2827 | 956.7639 | 34.8355 | 0 | 0 | 0 | 0 | 1175.7603 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 18.7137 | 178.383 | 861.0872 | 28.3639 | 0% | 100% ¦ $1,211 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2091 | Gustine:Instl crcit swchr,rcls prt,ph PT |  |  | Merced | Silva Dairy Farms, an Interconnection Customer (IC), has requested a Generating Facility (GF) interconnection for Silva Dairy Farms (Project) to the Pacific Gas and Electric Company (PG&E)’s distribution system for a 501.020 kW Photovoltaic generating facility to be located at SE SE NW 20 7 10, Stevinson, CA, 95374. The Generating Facility will be connected to PG&E’s Gustine 1101 distribution circuit. Install high side Bank 1 60 kV circuit switcher and reclosing protection scheme at Gustine sub. Install C phase PT for Reclosing Protection Scheme. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-04 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.6366 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5554359 | T.0009606 | Gustine Projects | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-10-05 | NA | 2027-04-23 | NA | NA | TRUE | NA | NA ¦ NA | 515.5477 | 3857.601 | 0 | 0 | 0 | 29.8563 | 348.0968 | 2470.5963 | 1002.8189 | 6.2326 | 0 | 0 | 377.9531 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 340.1575 | 123.8351 | 0% | 100% ¦ $3,858 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2092 | WRO Generator Network Upgrades |  |  |  | The high-level project scope of work includes following: Interconnection Facility Upgrade (Direct Assigned- DA): Generation Site: • Engineering Reviews, Project Management, Pre-Parallel Inspection, and Metering Installation • Install RTU, DTT receiver, and provide IC Support with telecom circuits. Generation Tie-Line: • The Zeta interconnection will require a 70kV transmission line that is constructed, designed, and maintained by the Interconnection Customer. This proposed Gen-Tie line to be constructed will tie to the Interconnection Customer’s facility. • The Gen-Tie line will be designed and installed by the Interconnection Customer. The customer will own and maintain the line from their facility up to the property line of the PG&E owned substation. PG&E will install and maintain a span of line from the substation Dead-End structure up to the customer provided Tubular Steel Pole, at the PG&E station property line. POI: Mercy Springs 70kV Switching Station • Install and maintain a span of line from the substation Dead-End structure up to the customer provided Tubular Steel Pole, at the PG&E station property line. • Install the following related to the new Gen-Tie line: o Install three (3) single phase line PTs for the new Gen-Tie line protection. o Install one (1) line dead-end structure and line disconnect switches. o Civil foundations and ground connections. o Install Line Current Differential relay scheme on the Mercy Springs SS – Zeta 70kV line. o Install a Direct Transfer Trip (DTT) scheme between Mercy Springs Switching Station and the Customer substation. o Install fiber termination at the Mercy Springs Switching Station Substation. Reliability Network Upgrade (RNU): POI: Mercy Springs 70kV Switching Station • Install a 70kV circuit breaker to existing ring bus in “Bay 1” of existing 70kV Ring Bus and associated relays. Precursor Dependencies: • QC8RAS-08 Gates 500/230 kV Transformer Banks 11 and 12 o MWC 82, T.0003009, under separate authorization o Planned ISD: May 2024 • Oro Loma 70 kV Reinforcement o TPP, T.0000157, under separate authorizations o Planned ISD: Nov 2026 o Note: Some requirements for this project have been split up into more than one project. | Substation - Circuit Breaker | New | NA | T.0003009 ¦ T.0000157 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.8847 | NA | 70 kV | NA | NA | NA | 3.002 | Non-IGP | 5807928 | T.0009846 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2024 | 2023 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2026-03-02 | 2027-03-09 | 2027-01-29 | NA | NA | TRUE | 3300 | NA ¦ NA | 1153.3785 | 3829.5043 | 0 | 0 | 0 | 189.0117 | 717.7528 | 1100.7796 | 1229.2696 | 592.6906 | 0 | 0 | 906.7645 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,830 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2093 | WRO Generator Network Upgrades |  |  |  | The project proposes to install new transmission line from generation site to the Mustang 230kV switching station. Scope details listed below. Transmission line: Install 5 spans of transmission line conductor. Install 4 double-circuit TSps. At Mustang Switching station: Install 1 BAAH new bay. 2 new breakers. Install breaker control relay package. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5808278 | T.0009863 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2022 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-09-07 | 2027-11-19 | 2028-09-20 | Customer action | NA | FALSE | 7280 | NA ¦ NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -274.49 | -312.1671 | -144.302 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ -$1,141 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2094 | WRO Generator Network Upgrades |  |  |  | The project proposes to install new transmission line from generation site to the Mustang 230kV switching station. Scope details listed below. Transmission line: Install 5 spans of transmission line conductor. Install 4 double-circuit TSps. At Mustang Switching station: Install 1 BAAH new bay. 2 new breakers. Install breaker control relay package. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-12 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5808247 | T.0009863 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2022 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2028-01-31 | 2027-11-19 | 2028-09-20 | Customer action | NA | FALSE | 7280 | NA ¦ NA | 191.1871 | 7087.5159 | 0 | 0 | 0 | 22.8465 | 152.4066 | 907.6532 | 4688.5405 | 998.9857 | 317.0833 | 0 | 175.2532 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $7,088 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2095 | WRO Generator Network Upgrades |  |  |  | Project proposes to connect 150MW of solar generation to the Tranquility switching station. -Install New Bay 6 with 2 circuit breakers. -Install 5 230kV disconnects switches. -Install 2 dead-end/pull off structures. -Install SMP breakers control relays. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5809203 | T.0009923 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2023 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-04-22 | 2028-04-30 | 2027-10-25 | NA | NA | TRUE | 5936 | NA ¦ NA | 129.1279 | 4219.0358 | 0 | 0 | 0 | 63.4186 | 60.4217 | 960.0602 | 2682.6603 | 452.4749 | 0 | 0 | 123.8404 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,219 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2096 | WRO Generator Network Upgrades |  |  |  | The Project is a Solar generation plant with a net output of 100MW connects to Pacific Gas and Electric Company’s (PG&E’s) Lamont 115kV Substation in Kern County, CA. Reliability Network Upgrade: Point of Interconnection: Lamont 115kV Substation Network Upgrades Indoor/Outdoor Work  Install (1) 115kV breaker to complete existing BAAH bay  Install SMP relay package | Substation - Circuit Breaker | New | NA | T.0010031 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-10 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 8.1615 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5809025 | T.0010025 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-04-29 | 2030-10-12 | 2030-04-11 | NA | NA | FALSE | 1141 | NA ¦ NA | 76.0782 | 6113.6289 | 0 | 0 | 0 | 0 | 49.2432 | 123.1483 | 3110.5745 | 353.5753 | 1461.8157 | 784.7535 | 49.2433 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $6,114 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2097 | Midway 500 kV RAS C13P1-KGR01 NU |  |  | Buttonwillow CDP, Kern | The project proposes to Modify existing Midway 500/230kV transformer overload SPS RAS to facilitate the interconnection of solar generation projects affecting the Midway 500/230kV transformers. This project is a shared network upgrade project resulting from CAISO interconnection System Cluster 13 Phase 2 study. Midway Substation • Modify existing Midway 500/230kV transformer overload SPS to include transformer outage detection and transformer overload detection for Bank 11, 12, and 13. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | 16 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5809123 | T.0010031 | Midway 500 kV RAS C13P1-KGR01 NU | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2024 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-02-01 | 2027-03-31 | 2027-05-17 | NA | NA | TRUE | 4029 | NA ¦ NA | 10.3212 | 1842.9279 | 0 | 0 | 0 | 0.5705 | 8.2197 | 557.9176 | 1232.6563 | 43.5638 | 0 | 0 | 8.7902 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,843 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2098 | WRO Generator Network Upgrades |  |  |  | The Project is a Solar and battery storage generation plant with a net output of 35MW connects to TRN’s Cresent switching station in Fresno County, CA. Install one (1) 70kV BAAH bay at PG&E’s Crescent Switching Station, which will serve as the Point of Interconnection (POI) for the 35MW Generating Facility. | Substation - Circuit Breaker | New | NA | T.0010934 ¦ T.0006452 ¦ T.0000043 ¦ T.0003016 ¦ T.0004255 ¦ T.0007056 ¦ T.0003009 ¦ T.0009194 ¦ T.0009177 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 0.84207 | NA | 70 kV | NA | NA | NA | 3.002 | Non-IGP | 5811150 | T.0010467 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-07-01 | 2027-12-03 | 2027-07-19 | NA | NA | TRUE | 3600 | NA ¦ NA | 486.4711 | 9176.9739 | 0 | 0 | 0 | 0 | 436.9512 | 4675.5222 | 3278.622 | 785.8785 | 0 | 0 | 436.9512 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $9,177 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2099 | WRO Generator Network Upgrades |  |  |  | The Project is a solar PV generation facility with a net output of 100MW connecting to Pacific Gas and Electric Company’s (PG&E’s) Bitterwater switching station in Kern County, CA. Reliability Network Upgrade: Point of Interconnection: Bitterwater Switching Station 230kV Bus Network Upgrades Indoor/Outdoor Work  Install (1) 230kV, 3000A, 63kA with two or three CT’s  Install breaker failure and reclosing relays for the breakers associated with the following lines: o Bitterwater switching station – Kyan Solar 230kV line in new panel  Install (1) 230kVdisconnect switches | Substation - Circuit Breaker | New | NA | T.0001353 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5811845 | T.0010617 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2026-07-01 | 2027-07-03 | 2026-12-21 | NA | NA | TRUE | 1350 | NA ¦ NA | 319.531 | 1259.5232 | 0 | 0 | 0 | 0 | 228.0082 | 166.5327 | 659.708 | 76.0603 | 21.783 | 1.0783 | 228.0082 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,260 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2100 | Beresford, Install, 3 Single Phase PT's |  |  | San Mateo, San Mateo | IC has requested a Generating Facility (GF) interconnection to the Pacific Gas and Electric Company (PG&E)’s distribution system for a 23.0 kW Photovoltaic and 20.0 kW Advance Energy Storage generating facility to be located in San Mateo County, CA. The Generating Facility will be connected to PG&E’s Beresford 0403 distribution circuit. Interconnection will be in accordance with CPUC’s Generating Facility Interconnections, Electric Rule 21 | Substation - Other Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-10 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.29412 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5555324 | T.0010698 | BERESFORD: INSTALL 3 SINGLE PHASE PT's | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2026-09-02 | NA | 2027-01-07 | NA | NA | TRUE | NA | NA ¦ NA | 137.3074 | 3195.1195 | 0 | 0 | 0 | 0 | 103.4763 | 3049.2685 | 42.3746 | 0 | 0 | 0 | 103.4764 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 93.129 | 30.448 | 0% | 100% ¦ $3,195 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2101 | LOS BANOS 500KV UPRATE CB 822, 832 |  |  | Merced | The Los Banos 500kV Circuit Breakers (CB) 822 and 832 will be uprated to a higher interrupting current (IC) ratings. The Los Banos 500kV CB 822 and 832 were identified as overstressed by the Cluster 14 Phase 2 study report dated January 31, 2024. Overstressed breakers can lead to: outages impacting significant numbers of customers, preventing generators from interconnecting, a safety hazard, and NERC violations. The State of California has mandates to interconnect new generation to support forecasted energy shortages in the next 2-5 years. PG&E has started to see escalations from Generation Interconnection customers that are being financially affected, as well as the additional pressure from CAISO to address timely replacement of these overstressed breakers. Therefore, it is recommended to uprate these circuit breakers prior to the In-Service Date of generation interconnection customers. Therefore, it is recommended to uprate these circuit breakers prior to the In-Service Date of generation interconnection customers. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | 31 | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 500 kV | NA | NA | NA | 5.211 | Non-IGP | 5812665 | T.0010787 | Los Banos 500kV Uprate CB 822, 832 | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 2 | 2025-10-05 | 2027-02-28 | 2026-08-03 | NA | NA | TRUE | 2500 | NA ¦ NA | 1132.4648 | 1513.877 | 0 | 0 | 0 | 0 | 1101.5062 | 412.3707 | 0 | 0 | 0 | 0 | 1101.5062 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,514 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2102 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Energy Storage System (BESS) Large Generating Facility with a net output of 500MW connecting to Pacific Gas and Electric Company’s (PG&E’s) Tesla Substation in Tracy, San Joaquin County, CA. | Substation - Circuit Breaker | New | NA | T.0010881 ¦ T.0010880 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.2961 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5813445 | T.0010805 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-04-11 | 2031-04-21 | 2029-07-24 | NA | NA | FALSE | 22977 | NA ¦ NA | 11.3584 | 15910.5979 | 0 | 0 | 0 | 0 | 5.9573 | 138.3468 | 191.3223 | 327.6946 | 14909.4678 | 253.5203 | 5.9573 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $15,911 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2103 | WRO Generator Network Upgrades |  |  |  | The Project is a 200 MW Battery Energy Storage System (BESS) Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) Wilson Substation in Merced, Merced County, CA. | Substation - Circuit Breaker | New | NA | T.0009194 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-08-25 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5813606 | T.0010816 | WRO Generator Network Upgrades | 4 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-02-01 | 2029-04-19 | 2029-04-19 | NA | NA | FALSE | 6113 | NA ¦ NA | 45.0859 | 5923.0132 | 0 | 0 | 0 | 0 | 35.8184 | 319.4226 | 149.1152 | 3895.8934 | 1521.7281 | 1.0355 | 35.8184 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $5,923 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2104 | WRO Generator Network Upgrades |  |  |  | The Project is a 100MW Battery Energy Storage System (BESS) Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) Vierra Substation in Lathrop, San Joaquin County, CA. Reliability Network Upgrades (RNU): Vierra Substation: • Install partial Breaker and a Half (BAAH) Bay #5 at the existing 115kV Vierra Substation which consists of: o Two (2) 115kV circuit breaker and associated disconnect switches, bus support structures, foundation, grounding system, etc. o Install Breaker Failure and Reclosing Relays for breakers associated with the Vierra- Denali Energy Storage 115kV line. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 1.355 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5813682 | T.0010818 | WRO Generator Network Upgrades | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-09-13 | 2028-07-30 | 2028-07-28 | NA | NA | FALSE | 1112 | NA ¦ NA | 25.9499 | 627.4749 | 0 | 0 | 0 | 0 | 7.0762 | 264.1171 | 302.7442 | 50.7076 | 2.8297 | 0 | 7.0763 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $627 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2105 | Los Banos 500 KV CB 842 Replacement |  |  | Merced | The project scope of work includes following: General Reliability Network Upgrades (GRNU): Los Banos Substation: • Replace existing 500kV CB 842 with associated equipment. (Breaker already ordered under OBS # 9753642) • Replace relays as needed. The Los Banos 500kV CB 842 was identified as overstressed by the Cluster 14 Phase 2 study report dated January 31, 2024. Overstressed breakers can lead to: outages impacting significant numbers of customers, preventing generators from interconnecting, a safety hazard, and NERC violations. The State of California has mandates to interconnect new generation to support forecasted energy shortages in the next 2-5 years. PG&E has started to see escalations from Generation Interconnection customers that are being financially affected, as well as the additional pressure from CAISO to address timely replacement of these overstressed breakers. Therefore, it is recommended to uprate these circuit breakers prior to the In-Service Date of generation interconnection customers. Therefore, it is recommended to replace this circuit breaker prior to the In-Service Date of generation interconnection customers. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | 37 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5813650 | T.0010835 | Los Banos 500 KV CB 842 Replacement | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | 2027-04-08 | 2031-02-28 | 2027-09-16 | NA | NA | TRUE | 7652 | NA ¦ NA | 70.4467 | 5605.4523 | 0 | 0 | 0 | 0 | 60.8892 | 939.5315 | 4593.0346 | 11.997 | 0 | 0 | 60.8892 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $5,605 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2106 | Midway500kV Uprate CB 742, 822, 912, 942 |  |  | Buttonwillow CDP, Kern | Cluster 14 Phase 2 study reports, dated January 31, 2024, identified a shared network upgrade for the Midway 500kV circuit breakers 742, 822, 912, and 942. The Midway 500kV Uprate CB 742, 822, 912, 942 project, will modify the breakers to increase their IC capability from 50kA to 63kA. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | NA | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 94.5324 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5813651 | T.0010836 | Midway500kV Uprate CB 742, 822, 912, 942 | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 1 | 2025-07-21 | 2025-12-31 | 2025-10-09 | NA | NA | TRUE | 5000 | NA ¦ NA | 2692.4041 | 2700.5545 | 0 | 0 | 0 | 0 | 2693.4606 | 7.0938 | 0 | 0 | 0 | 0 | 2693.4607 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 2425.9426 | -0.95095 | 0% | 100% ¦ $2,701 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
2107 | WRO Generator Network Upgrades |  |  |  | The Project is a combination of solar and Battery Energy Storage System (BESS) 250 MW Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) new 230kV Switching Station in Linden, San Joaquin County, CA. Below is the high-level project scope to loop in a new 230kV switching station on existing 230kV Racho Seco PP - Bellota #1 line and associated work to interconnect a 350MW generation. Reliability Network Upgrades (RNU): New 230kV Switching Station: • Two (2) 230kV Breaker-and-a-half (BAAH) bays with ultimate arrangement of five (5) bays. o Install five (5) 230kV circuit breakers (CB) with breaker and line disconnects. o Install four (4) dead-end structures, bus support structures, foundation, grounding system. • Install one (1) 98” Modular Protection Automation and Control (MPAC) building with line, breaker and bus differential relay panels. • Install One (1) stand-alone 34’ battery building including all necessary concrete foundations, rebar and anchor bolts. • Clear, Grade, and improve approximately 1 mile of roadway for access road to the switching station. • Install redundant communication paths between the switching stations and remote ends as necessary including the microwave tower. Rancho-Seco PP Substation: • Install Direct Transfer Trip (DTT) scheme between from Switching Station and Rancho-Seco PP Substation including new IT T1 infrastructure for the communication circuits. Bellota Substation: • Replace the existing line and breaker relays for the 230kV Switching Station - Bellota line. • Install redundant communication paths between the Switching Station and any remote ends as necessary including the microwave tower. • Install a DTT scheme between Switching Station and Bellota Substation including new IT T1 infrastructure for the communication circuits. T-Line work: • PG&E T-Line to install six (6) TSPs and conductor to route the following two (2) 230 kV lines into Switching Station: o Switching Station - Bellota Substation 230 kV. o Switching Station - Rancho-Seco PP Substation 230 kV. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-14 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5813716 | T.0010853 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-12-22 | 2030-11-04 | 2030-10-03 | NA | NA | FALSE | 1914 | NA ¦ NA | 15.6739 | 1014.3876 | 0 | 0 | 0 | 0 | 12.5579 | 133.163 | 388.4408 | 132.528 | 196.6417 | 151.0561 | 12.558 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,014 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2108 | WRO Generator Network Upgrades |  |  |  | The Project is a combination of solar and Battery Energy Storage System (BESS) 250 MW Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) new 230kV Switching Station in Linden, San Joaquin County, CA. Below is the high-level project scope to loop in a new 230kV switching station on existing 230kV Racho Seco PP - Bellota #1 line and associated work to interconnect a 350MW generation. Reliability Network Upgrades (RNU): New 230kV Switching Station: • Two (2) 230kV Breaker-and-a-half (BAAH) bays with ultimate arrangement of five (5) bays. o Install five (5) 230kV circuit breakers (CB) with breaker and line disconnects. o Install four (4) dead-end structures, bus support structures, foundation, grounding system. • Install one (1) 98” Modular Protection Automation and Control (MPAC) building with line, breaker and bus differential relay panels. • Install One (1) stand-alone 34’ battery building including all necessary concrete foundations, rebar and anchor bolts. • Clear, Grade, and improve approximately 1 mile of roadway for access road to the switching station. • Install redundant communication paths between the switching stations and remote ends as necessary including the microwave tower. Rancho-Seco PP Substation: • Install Direct Transfer Trip (DTT) scheme between from Switching Station and Rancho-Seco PP Substation including new IT T1 infrastructure for the communication circuits. Bellota Substation: • Replace the existing line and breaker relays for the 230kV Switching Station - Bellota line. • Install redundant communication paths between the Switching Station and any remote ends as necessary including the microwave tower. • Install a DTT scheme between Switching Station and Bellota Substation including new IT T1 infrastructure for the communication circuits. T-Line work: • PG&E T-Line to install six (6) TSPs and conductor to route the following two (2) 230 kV lines into Switching Station: o Switching Station - Bellota Substation 230 kV. o Switching Station - Rancho-Seco PP Substation 230 kV. | Substation - Protection Relay | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-14 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5813717 | T.0010853 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-04-25 | 2030-11-04 | 2031-02-07 | NA | NA | FALSE | 1914 | NA ¦ NA | 19.4867 | 3687.0539 | 0 | 0 | 0 | 0 | 12.7084 | 265.9085 | 878.6631 | 572.0714 | 745.9004 | 1091.4162 | 12.7084 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,687 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2109 | WRO Generator Network Upgrades |  |  |  | The Project is a combination of solar and Battery Energy Storage System (BESS) 250 MW Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) new 230kV Switching Station in Linden, San Joaquin County, CA. Below is the high-level project scope to loop in a new 230kV switching station on existing 230kV Racho Seco PP - Bellota #1 line and associated work to interconnect a 350MW generation. Reliability Network Upgrades (RNU): New 230kV Switching Station: • Two (2) 230kV Breaker-and-a-half (BAAH) bays with ultimate arrangement of five (5) bays. o Install five (5) 230kV circuit breakers (CB) with breaker and line disconnects. o Install four (4) dead-end structures, bus support structures, foundation, grounding system. • Install one (1) 98” Modular Protection Automation and Control (MPAC) building with line, breaker and bus differential relay panels. • Install One (1) stand-alone 34’ battery building including all necessary concrete foundations, rebar and anchor bolts. • Clear, Grade, and improve approximately 1 mile of roadway for access road to the switching station. • Install redundant communication paths between the switching stations and remote ends as necessary including the microwave tower. Rancho-Seco PP Substation: • Install Direct Transfer Trip (DTT) scheme between from Switching Station and Rancho-Seco PP Substation including new IT T1 infrastructure for the communication circuits. Bellota Substation: • Replace the existing line and breaker relays for the 230kV Switching Station - Bellota line. • Install redundant communication paths between the Switching Station and any remote ends as necessary including the microwave tower. • Install a DTT scheme between Switching Station and Bellota Substation including new IT T1 infrastructure for the communication circuits. T-Line work: • PG&E T-Line to install six (6) TSPs and conductor to route the following two (2) 230 kV lines into Switching Station: o Switching Station - Bellota Substation 230 kV. o Switching Station - Rancho-Seco PP Substation 230 kV. | Substation - Multiple | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-14 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 14.7513 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5813715 | T.0010853 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-10-12 | 2030-11-04 | 2031-11-13 | Customer action | NA | FALSE | 1914 | NA ¦ NA | 93.6292 | 34596.5465 | 0 | 0 | 0 | 0 | 49.2062 | 631.3516 | 1278.1644 | 9077.9485 | 11376.8291 | 6325.7912 | 49.2062 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $34,597 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2110 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Energy Storage System (BESS) Large Generating Facility with a net output of 300MW connecting to Pacific Gas and Electric Company’s (PG&E’s) Templeton-Gates 230kV line looped into a new Switching Station, Fresno County, CA. | Substation - Other Equipment | New | NA | T.0010031 ¦ T.0001650 ¦ T.0007722 ¦ T.0010879 ¦ T.0000154 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5813939 | T.0010878 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-05-31 | 2030-08-18 | 2030-09-12 | NA | NA | FALSE | 34420 | NA ¦ NA | 1.0561 | 243.9726 | 0 | 0 | 0 | 0 | 0.0669 | 135.6166 | 68.4464 | 13.8388 | 14.8195 | 11.1845 | 0.0669 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $244 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2111 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Energy Storage System (BESS) Large Generating Facility with a net output of 300MW connecting to Pacific Gas and Electric Company’s (PG&E’s) Templeton-Gates 230kV line looped into a new Switching Station, Fresno County, CA. | Substation - Other Equipment | New | NA | T.0010031 ¦ T.0001650 ¦ T.0007722 ¦ T.0010879 ¦ T.0000154 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5813938 | T.0010878 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-06-07 | 2030-08-18 | 2030-09-19 | NA | NA | FALSE | 34420 | NA ¦ NA | 1.0784 | 244.0152 | 0 | 0 | 0 | 0 | 0.0889 | 136.7751 | 67.3062 | 13.8191 | 14.8319 | 11.194 | 0.0889 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $244 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2112 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Energy Storage System (BESS) Large Generating Facility with a net output of 300MW connecting to Pacific Gas and Electric Company’s (PG&E’s) Templeton-Gates 230kV line looped into a new Switching Station, Fresno County, CA. | Substation - Other Equipment | New | NA | T.0010031 ¦ T.0001650 ¦ T.0007722 ¦ T.0010879 ¦ T.0000154 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5813940 | T.0010878 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-06-07 | 2030-08-18 | 2030-09-19 | NA | NA | FALSE | 34420 | NA ¦ NA | 1.0561 | 123.4419 | 0 | 0 | 0 | 0 | 0.0669 | 75.3693 | 18.9968 | 15.8072 | 7.5419 | 5.6599 | 0.0669 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $123 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2113 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Energy Storage System (BESS) Large Generating Facility with a net output of 300MW connecting to Pacific Gas and Electric Company’s (PG&E’s) Templeton-Gates 230kV line looped into a new Switching Station, Fresno County, CA. | Substation - Multiple | New | NA | T.0010031 ¦ T.0001650 ¦ T.0007722 ¦ T.0010879 ¦ T.0000154 | Generator Interconnection | Generation Interconnection | NA | NA | 2025-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5813941 | T.0010878 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-06-07 | 2030-08-18 | 2030-09-19 | NA | NA | FALSE | 34420 | NA ¦ NA | 8.8199 | 26291.0721 | 0 | 0 | 0 | 0 | 0.2642 | 94.4227 | 2789.3911 | 2981.7687 | 10120.4543 | 10304.7711 | 0.2642 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $26,291 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2114 | MIDWAY 500/230 KV REACTORS NU |  |  | Buttonwillow CDP, Kern | General Reliability Network Upgrades (GRNU): Midway Substation: Outdoor work: • Replace existing 9ohm Midway 500/230kV reactors with 13ohm reactors on Banks 11, 12, and 13. o 3-1 phase per transformer 9ohm 4000A, replace with 13ohm 4000A. The Midway 230kV Bus was identified as overstressed in Cluster 14 Study Report due to the interconnection projects Q1831, Q1959, Q1968, Q1980, Q1983, Q1992, Q1994, Q1995, Q2001, Q2004, Q2006, Q2010, Q2012, Q2013, Q2015, Q2017 in Cluster 14. Overstressed bus can lead to: outages impacting significant numbers of customers, preventing generators from interconnecting, a safety hazard, and NERC violations. The State of California has mandates to interconnect new generation to support forecasted energy shortages in the next 2-5 years. PG&E has started to see escalations from Generation Interconnection customers that are being financially affected, as well as the additional pressure from CAISO to address timely resolve the bus overstress issue. Therefore, it is recommended to replace Midway 500/230kV 9ohm series reactors with 13ohm reactors for Bank 11,12, and 13 prior to the In-Service Date of generation interconnection customers. | Substation - Reactive Equipment | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-03 | 10 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 500 ¦ 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5813947 | T.0010879 | Midway 500/230 kV Reactors NU | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-01-09 | 2029-03-31 | 2029-03-30 | NA | NA | FALSE | 21000 | NA ¦ NA | 31.3969 | 6302.1418 | 0 | 0 | 0 | 0 | 18.4749 | 129.76 | 133.6994 | 4599.9899 | 1390.5374 | 29.6803 | 18.4749 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $6,302 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2115 | Pittsburg 230kV Bus Overstress |  |  | Pittsburg, Contra Costa | Install 230kV Bus Reactors between bus sections D & E to reduce the fault duty/overstress at Pittsburg substation | Substation - Circuit Breaker | New | NA | EX139157 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.72358 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5813980 | T.0010880 | Pittsburg 230kV Bus Overstress | 1 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2028-01-14 | 2030-03-31 | 2028-07-20 | NA | NA | FALSE | 26800 | NA ¦ NA | 30.2378 | 3603.1032 | 0 | 0 | 0 | 0 | 26.5176 | 157.6637 | 808.2194 | 2600.3217 | 10.3809 | 0 | 26.5176 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,603 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2116 | TESLA 230KV BAAH BUS F EXTENSION RNU |  |  | Alameda | The project scope of work includes following: General Reliability Network Upgrades (GRNU): Tesla Substation: • Relocate a Tesla – Tracy #2 230kV line to Bus Section C into BAAH Bay position where Tesla- Newark #2 line resides today and shift Tesla - Newark #2 line to a new BAAH bay. • Install nine (9) 230kV T-line structures (4000 feet of new line). • Install two (2) circuit breakers and associated equipment in the new BAAH bay. • Install new relays and revise existing relay schemes as needed. | Substation - Circuit Breaker | New | NA | T.0011168 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-19 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 69.382 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5813979 | T.0010881 | Tesla 230kV & 500kV Mitigation | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-03-16 | 2031-04-18 | 2031-04-18 | NA | NA | FALSE | 30878 | NA ¦ NA | 174.7305 | 9849.7181 | 0 | 0 | 0 | 0 | 94.8996 | 1660.0648 | 1429.6655 | 715.6452 | 4086.3891 | 1371.9103 | 94.8996 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $9,850 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2117 | Tesla Yard Expansion Land |  |  | San Joaquin | The project scope of work includes following: General Reliability Network Upgrades (GRNU): Tesla Substation: • Relocate a Tesla – Tracy #2 230kV line to Bus Section C into BAAH Bay position where Tesla- Newark #2 line resides today and shift Tesla - Newark #2 line to a new BAAH bay. • Install nine (9) 230kV T-line structures (4000 feet of new line). • Install two (2) circuit breakers and associated equipment in the new BAAH bay. • Install new relays and revise existing relay schemes as needed. | Other | Upgrade/Retrofit | NA | T.0011168 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.2961 | NA | 500 ¦ 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5562722 | T.0010881 | Tesla 230kV & 500kV Mitigation | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-03-16 | 2031-04-18 | 2031-04-18 | NA | NA | FALSE | 30878 | NA ¦ NA | 12.8513 | 5619.108 | 0 | 0 | 0 | 0 | 0.6204 | 317.0715 | 399.3512 | 487.1331 | 3552.1365 | 621.8661 | 0.6204 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $5,619 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2118 | Vaca Dixon-Tesla 500kV Line Loop-in RNU |  |  | San Joaquin | The project scope of work includes following: General Reliability Network Upgrades (GRNU): Tesla Substation: • Relocate a Tesla – Tracy #2 230kV line to Bus Section C into BAAH Bay position where Tesla- Newark #2 line resides today and shift Tesla - Newark #2 line to a new BAAH bay. • Install nine (9) 230kV T-line structures (4000 feet of new line). • Install two (2) circuit breakers and associated equipment in the new BAAH bay. • Install new relays and revise existing relay schemes as needed. | Substation - Multiple | Relocate | NA | T.0011168 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.2961 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5816102 | T.0010881 | Tesla 230kV & 500kV Mitigation | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-10-12 | 2031-04-18 | 2031-04-18 | NA | NA | FALSE | 30878 | NA ¦ NA | 18.2236 | 6433.6758 | 0 | 0 | 0 | 0 | 2.679 | 270.19 | 428.7762 | 569.1135 | 3755.8747 | 1018.1552 | 2.679 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $6,434 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2119 | Tesla 500kV BAAH Bus E Extension RNU |  |  | San Joaquin | The project scope of work includes following: General Reliability Network Upgrades (GRNU): Tesla Substation: • Relocate a Tesla – Tracy #2 230kV line to Bus Section C into BAAH Bay position where Tesla- Newark #2 line resides today and shift Tesla - Newark #2 line to a new BAAH bay. • Install nine (9) 230kV T-line structures (4000 feet of new line). • Install two (2) circuit breakers and associated equipment in the new BAAH bay. • Install new relays and revise existing relay schemes as needed. | Substation - Multiple | New | NA | T.0011168 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.2961 | NA | 500 kV | NA | NA | NA | 3.002 | Non-IGP | 5816118 | T.0010881 | Tesla 230kV & 500kV Mitigation | 5 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-03-16 | 2031-04-18 | 2031-04-18 | NA | NA | FALSE | 30878 | NA ¦ NA | 31.9201 | 6282.1716 | 0 | 0 | 0 | 0 | 12.0758 | 283.5027 | 413.6286 | 531.6164 | 3718.3204 | 978.4943 | 12.0757 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $6,282 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2120 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Rosemary project, which is a Solar PV and Storage generation plant, comprised of 12 Solar PV Inverters each rated at 3.465 MW and a Battery Energy Storage System (“BESS”) comprised of 12 Inverters each rated at 3.465 MW, with a maximum gross output of 37.464 MW. • This project will build out a 3rd BAAH bay (Bay 3) at Crescent SW Sta. This bay will include two breakers and one line. This bay will follow the existing PGE Electrical Design Standard drawing 4042040. • Reconductor 4.7 miles rated ampacity 1400amp • Gentie line design with two TSP • Replace CB 22 at Helm Sub to meet 1400amp rating | Substation - Circuit Breaker | Upgrade/Retrofit | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-16 | 60 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | Heat Wave |  | NA | 0.93622 | NA | 70 kV | NA | NA | NA | 5.211 | Non-IGP | 5814818 | T.0010934 | WRO Generator Network Upgrades | 2 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | 2025 | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 3 | 2025-12-10 | 2027-12-03 | 2025-12-31 | NA | NA | FALSE | 13963 | NA ¦ NA | 12.7755 | 12.7755 | 0 | 0 | 0 | 0 | 12.7755 | 0 | 0 | 0 | 0 | 0 | 12.7755 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $13 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2121 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Seahawk Storage project, which is a Battery Energy Storage System (“BESS”) resulting in an Interconnection Service Capacity of 200 MW to PG&E - owned Green Valley 115 kV Substation in Santa Cruz, Santa Cruz County, California. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-02 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5814169 | T.0010941 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-11-24 | 2029-06-30 | 2029-03-29 | NA | NA | FALSE | 3051 | NA ¦ NA | 10.7798 | 586.1956 | 0 | 0 | 0 | 0 | 6.0416 | 144.2736 | 101.5549 | 228.1957 | 106.1299 | 0 | 6.0416 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $586 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2122 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Seahawk Storage project, which is a Battery Energy Storage System (“BESS”) resulting in an Interconnection Service Capacity of 200 MW to PG&E - owned Green Valley 115 kV Substation in Santa Cruz, Santa Cruz County, California. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-02 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5814170 | T.0010941 | WRO Generator Network Upgrades | 6 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-11-24 | 2029-06-30 | 2029-05-16 | NA | NA | FALSE | 3051 | NA ¦ NA | 7.5293 | 557.9409 | 0 | 0 | 0 | 0 | 5.5969 | 130.5207 | 81.5913 | 196.0784 | 143.3422 | 0.8114 | 5.5969 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $558 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2123 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Tokay Energy Storage project, which is a Battery Energy Storage System (“BESS”) resulting in an Interconnection Service Capacity of 100 MW to Pacific Gas and Electric Company - owned Santa Teresa 115 kV Substation in San Jose, Santa Clara County, California. | Substation - Circuit Breaker | New | NA | T.0007291 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 2.3853 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5814255 | T.0010944 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-12-06 | 2029-12-18 | 2029-10-04 | NA | NA | FALSE | 3874 | NA ¦ NA | 10.687 | 517.5039 | 0 | 0 | 0 | 0 | 5.1818 | 133.5889 | 80.656 | 138.8849 | 154.77 | 4.4225 | 5.1817 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $518 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2124 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Tokay Energy Storage project, which is a Battery Energy Storage System (“BESS”) resulting in an Interconnection Service Capacity of 100 MW to Pacific Gas and Electric Company - owned Santa Teresa 115 kV Substation in San Jose, Santa Clara County, California. | Substation - Other Equipment | New | NA | T.0007291 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 2.3853 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5814256 | T.0010944 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-12-06 | 2029-12-18 | 2029-09-28 | NA | NA | FALSE | 3874 | NA ¦ NA | 5.8742 | 541.6989 | 0 | 0 | 0 | 0 | 3.2715 | 132.3836 | 87.3772 | 146.5939 | 162.4266 | 9.6462 | 3.2714 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $542 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2125 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Tokay Energy Storage project, which is a Battery Energy Storage System (“BESS”) resulting in an Interconnection Service Capacity of 100 MW to Pacific Gas and Electric Company - owned Santa Teresa 115 kV Substation in San Jose, Santa Clara County, California. | Substation - Other Equipment | New | NA | T.0007291 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 37.8815 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5814257 | T.0010944 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2024 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-12-06 | 2029-12-18 | 2029-10-29 | NA | NA | FALSE | 3874 | NA ¦ NA | 5.9352 | 541.2044 | 0 | 0 | 0 | 0 | 3.0259 | 130.2627 | 86.7863 | 145.8461 | 163.1591 | 12.1243 | 3.0259 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $541 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2126 | WRO Generator Network Upgrades |  |  |  | The Project is a 100 MW Battery Energy Storage System (BESS) Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) Valley Springs Substation in Valley Springs, San Joaquin County, CA. Below is the project high level scope of work required to interconnect the 100MW Battery Storage to Valley Springs Substation: Interconnection Reliability Network Upgrades (IRNU-A): Valley Springs Substation: • Install 60kV Circuit Breaker and associated equipment to complete Bay 4 which consists of: o One (1) 60kV CB with associated disconnect switch, foundation, and grounding system, etc. o Breaker Failure and Reclosing Relays for breakers associated with the Valley Springs – Double Springs Energy Storage 60kV line. • Install Direct Transfer Trip (DTT) scheme between Valley Springs Substation and Double Springs Energy Storage using existing IT T1 infrastructure for the communication circuits: o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Tiger Creek Powerhouse: • Install DTT scheme between Valley Springs Substation and Tiger Creek Powerhouse using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Electra Powerhouse: • Install DTT scheme between Valley Springs Substation and Electra Powerhouse using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Bellota Substation: • Install DTT scheme between Valley Springs Substation and Bellota Substation using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Interconnection Facilities (IF) Valley Springs Substation: • Install the following related to the new Gen-Tie line: o Install three (3) single phase line PTs for the new Gen-Tie line protection. o Install one (1) line dead-end structure and one (1) set of 60kV line disconnect switches. o Install civil foundations and ground connections. o Install Line Current Differential (LCD) relay scheme on the Valley Springs Substation – Double Energy Storage 60kV line. • Install fiber termination at the Valley Springs Substation o Each line current differential (LCD)scheme will require fully redundant fiber circuits. o IT to install, terminate and test new fiber cable from station property line to control building. • Install DTT scheme at Valley Springs to trip customer site to avoid islanding condition. o Install One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Gensite: • PG&E project management, metering, engineering and protection review, and pre-parallel inspection • PG&E IT to install RTU, DTT receiver and provide IC support with telecom circuits. T-Line work: • PG&E T-Line to install two (2) Tubular Steel Poles (TSP) and conductors on PG&E’s property to connect customer’s Gen-Tie Line to the line deadend. • PG&E T-line to raise the following lines to allow the Customer’s Gen-Tie line to cross underneath: o Valley Springs #1 60 kV with two (2) single circuit TSPs and conductors • PG&E T-Line Engineering will provide detailed requirements and review customers’ design of the Gen-Tie line and interconnecting TSP at Valley Springs Substation property line. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-10-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 8.8736 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5813991 | T.0010947 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-10-25 | 2028-04-18 | 2028-04-18 | NA | NA | FALSE | 4424 | NA ¦ NA | 4.2487 | 450.6094 | 0 | 0 | 0 | 0 | 3.057 | 21.6108 | 392.5952 | 33.3464 | 0 | 0 | 3.057 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $451 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2127 | WRO Generator Network Upgrades |  |  |  | The Project is a 100 MW Battery Energy Storage System (BESS) Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) Valley Springs Substation in Valley Springs, San Joaquin County, CA. Below is the project high level scope of work required to interconnect the 100MW Battery Storage to Valley Springs Substation: Interconnection Reliability Network Upgrades (IRNU-A): Valley Springs Substation: • Install 60kV Circuit Breaker and associated equipment to complete Bay 4 which consists of: o One (1) 60kV CB with associated disconnect switch, foundation, and grounding system, etc. o Breaker Failure and Reclosing Relays for breakers associated with the Valley Springs – Double Springs Energy Storage 60kV line. • Install Direct Transfer Trip (DTT) scheme between Valley Springs Substation and Double Springs Energy Storage using existing IT T1 infrastructure for the communication circuits: o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Tiger Creek Powerhouse: • Install DTT scheme between Valley Springs Substation and Tiger Creek Powerhouse using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Electra Powerhouse: • Install DTT scheme between Valley Springs Substation and Electra Powerhouse using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Bellota Substation: • Install DTT scheme between Valley Springs Substation and Bellota Substation using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Interconnection Facilities (IF) Valley Springs Substation: • Install the following related to the new Gen-Tie line: o Install three (3) single phase line PTs for the new Gen-Tie line protection. o Install one (1) line dead-end structure and one (1) set of 60kV line disconnect switches. o Install civil foundations and ground connections. o Install Line Current Differential (LCD) relay scheme on the Valley Springs Substation – Double Energy Storage 60kV line. • Install fiber termination at the Valley Springs Substation o Each line current differential (LCD)scheme will require fully redundant fiber circuits. o IT to install, terminate and test new fiber cable from station property line to control building. • Install DTT scheme at Valley Springs to trip customer site to avoid islanding condition. o Install One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Gensite: • PG&E project management, metering, engineering and protection review, and pre-parallel inspection • PG&E IT to install RTU, DTT receiver and provide IC support with telecom circuits. T-Line work: • PG&E T-Line to install two (2) Tubular Steel Poles (TSP) and conductors on PG&E’s property to connect customer’s Gen-Tie Line to the line deadend. • PG&E T-line to raise the following lines to allow the Customer’s Gen-Tie line to cross underneath: o Valley Springs #1 60 kV with two (2) single circuit TSPs and conductors • PG&E T-Line Engineering will provide detailed requirements and review customers’ design of the Gen-Tie line and interconnecting TSP at Valley Springs Substation property line. | Substation - Circuit Breaker | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-10-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 8.8736 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5813992 | T.0010947 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-10-25 | 2028-04-18 | 2028-04-18 | NA | NA | FALSE | 4424 | NA ¦ NA | 52.8004 | 2193.2834 | 0 | 0 | 0 | 0 | 47.1582 | 700.0618 | 933.0083 | 513.0551 | 0 | 0 | 47.1582 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,193 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2128 | WRO Generator Network Upgrades |  |  |  | The Project is a 100 MW Battery Energy Storage System (BESS) Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) Valley Springs Substation in Valley Springs, San Joaquin County, CA. Below is the project high level scope of work required to interconnect the 100MW Battery Storage to Valley Springs Substation: Interconnection Reliability Network Upgrades (IRNU-A): Valley Springs Substation: • Install 60kV Circuit Breaker and associated equipment to complete Bay 4 which consists of: o One (1) 60kV CB with associated disconnect switch, foundation, and grounding system, etc. o Breaker Failure and Reclosing Relays for breakers associated with the Valley Springs – Double Springs Energy Storage 60kV line. • Install Direct Transfer Trip (DTT) scheme between Valley Springs Substation and Double Springs Energy Storage using existing IT T1 infrastructure for the communication circuits: o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Tiger Creek Powerhouse: • Install DTT scheme between Valley Springs Substation and Tiger Creek Powerhouse using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Electra Powerhouse: • Install DTT scheme between Valley Springs Substation and Electra Powerhouse using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Bellota Substation: • Install DTT scheme between Valley Springs Substation and Bellota Substation using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Interconnection Facilities (IF) Valley Springs Substation: • Install the following related to the new Gen-Tie line: o Install three (3) single phase line PTs for the new Gen-Tie line protection. o Install one (1) line dead-end structure and one (1) set of 60kV line disconnect switches. o Install civil foundations and ground connections. o Install Line Current Differential (LCD) relay scheme on the Valley Springs Substation – Double Energy Storage 60kV line. • Install fiber termination at the Valley Springs Substation o Each line current differential (LCD)scheme will require fully redundant fiber circuits. o IT to install, terminate and test new fiber cable from station property line to control building. • Install DTT scheme at Valley Springs to trip customer site to avoid islanding condition. o Install One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Gensite: • PG&E project management, metering, engineering and protection review, and pre-parallel inspection • PG&E IT to install RTU, DTT receiver and provide IC support with telecom circuits. T-Line work: • PG&E T-Line to install two (2) Tubular Steel Poles (TSP) and conductors on PG&E’s property to connect customer’s Gen-Tie Line to the line deadend. • PG&E T-line to raise the following lines to allow the Customer’s Gen-Tie line to cross underneath: o Valley Springs #1 60 kV with two (2) single circuit TSPs and conductors • PG&E T-Line Engineering will provide detailed requirements and review customers’ design of the Gen-Tie line and interconnecting TSP at Valley Springs Substation property line. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-10-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 8.8736 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5814125 | T.0010947 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-10-25 | 2028-04-18 | 2028-04-18 | NA | NA | FALSE | 4424 | NA ¦ NA | 4.1983 | 692.9196 | 0 | 0 | 0 | 0 | 3.632 | 20.9824 | 629.975 | 38.3303 | 0 | 0 | 3.632 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $693 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2129 | WRO Generator Network Upgrades |  |  |  | The Project is a 100 MW Battery Energy Storage System (BESS) Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) Valley Springs Substation in Valley Springs, San Joaquin County, CA. Below is the project high level scope of work required to interconnect the 100MW Battery Storage to Valley Springs Substation: Interconnection Reliability Network Upgrades (IRNU-A): Valley Springs Substation: • Install 60kV Circuit Breaker and associated equipment to complete Bay 4 which consists of: o One (1) 60kV CB with associated disconnect switch, foundation, and grounding system, etc. o Breaker Failure and Reclosing Relays for breakers associated with the Valley Springs – Double Springs Energy Storage 60kV line. • Install Direct Transfer Trip (DTT) scheme between Valley Springs Substation and Double Springs Energy Storage using existing IT T1 infrastructure for the communication circuits: o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Tiger Creek Powerhouse: • Install DTT scheme between Valley Springs Substation and Tiger Creek Powerhouse using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Electra Powerhouse: • Install DTT scheme between Valley Springs Substation and Electra Powerhouse using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Bellota Substation: • Install DTT scheme between Valley Springs Substation and Bellota Substation using existing IT T1 infrastructure for the communication circuits. o One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Interconnection Facilities (IF) Valley Springs Substation: • Install the following related to the new Gen-Tie line: o Install three (3) single phase line PTs for the new Gen-Tie line protection. o Install one (1) line dead-end structure and one (1) set of 60kV line disconnect switches. o Install civil foundations and ground connections. o Install Line Current Differential (LCD) relay scheme on the Valley Springs Substation – Double Energy Storage 60kV line. • Install fiber termination at the Valley Springs Substation o Each line current differential (LCD)scheme will require fully redundant fiber circuits. o IT to install, terminate and test new fiber cable from station property line to control building. • Install DTT scheme at Valley Springs to trip customer site to avoid islanding condition. o Install One (1) SEL-2411 transmitter, cut out switch and auxiliary tripping relays. Gensite: • PG&E project management, metering, engineering and protection review, and pre-parallel inspection • PG&E IT to install RTU, DTT receiver and provide IC support with telecom circuits. T-Line work: • PG&E T-Line to install two (2) Tubular Steel Poles (TSP) and conductors on PG&E’s property to connect customer’s Gen-Tie Line to the line deadend. • PG&E T-line to raise the following lines to allow the Customer’s Gen-Tie line to cross underneath: o Valley Springs #1 60 kV with two (2) single circuit TSPs and conductors • PG&E T-Line Engineering will provide detailed requirements and review customers’ design of the Gen-Tie line and interconnecting TSP at Valley Springs Substation property line. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2025-10-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 8.8736 | NA | 60 kV | NA | NA | NA | 3.002 | Non-IGP | 5814126 | T.0010947 | WRO Generator Network Upgrades | 8 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-10-25 | 2028-04-18 | 2028-04-18 | NA | NA | FALSE | 4424 | NA ¦ NA | 5.1808 | 451.6929 | 0 | 0 | 0 | 0 | 5.1158 | 20.5407 | 392.6676 | 33.3687 | 0 | 0 | 5.1158 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $452 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2130 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Hybrid project, which is a Solar PV and Storage generation plant, with a net output of 110 MW to the CAISO Controlled Grid. The Large Generating Facility connects to PG&E's New 115kV Switching Station looped into Crazy Horse Canyon Sw Sta —Hollister 115 kV line in San Benito County, California. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.5641 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5814526 | T.0011010 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-06-25 | 2030-09-19 | 2030-10-04 | NA | NA | FALSE | 36997 | NA ¦ NA | 19.8932 | 576.2003 | 0 | 0 | 0 | 0 | 14.7455 | 6.3586 | 86.6757 | 92.7024 | 185.5117 | 190.2065 | 14.7454 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $576 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2131 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Hybrid project, which is a Solar PV and Storage generation plant, with a net output of 110 MW to the CAISO Controlled Grid. The Large Generating Facility connects to PG&E's New 115kV Switching Station looped into Crazy Horse Canyon Sw Sta —Hollister 115 kV line in San Benito County, California. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.5641 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5814527 | T.0011010 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-06-25 | 2030-09-19 | 2030-10-04 | NA | NA | FALSE | 36997 | NA ¦ NA | 20.9086 | 577.7023 | 0 | 0 | 0 | 0 | 15.7481 | 6.4331 | 87.1015 | 92.4878 | 185.9492 | 189.9827 | 15.7481 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $578 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2132 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Hybrid project, which is a Solar PV and Storage generation plant, with a net output of 110 MW to the CAISO Controlled Grid. The Large Generating Facility connects to PG&E's New 115kV Switching Station looped into Crazy Horse Canyon Sw Sta —Hollister 115 kV line in San Benito County, California. | Substation - Other Equipment | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.5641 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5814528 | T.0011010 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-06-25 | 2030-09-19 | 2030-10-04 | NA | NA | FALSE | 36997 | NA ¦ NA | 20.2317 | 8591.7393 | 0 | 0 | 0 | 0 | 15.0797 | 6.3834 | 1333.0087 | 1425.6107 | 2867.2698 | 2944.3871 | 15.0797 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $8,592 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2133 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Hybrid project, which is a Solar PV and Storage generation plant, with a net output of 110 MW to the CAISO Controlled Grid. The Large Generating Facility connects to PG&E's New 115kV Switching Station looped into Crazy Horse Canyon Sw Sta —Hollister 115 kV line in San Benito County, California. | Substation - Multiple | New | NA | NA | Generator Interconnection | Generation Interconnection | NA | NA | 2026-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.5641 | NA | 115 kV | NA | NA | NA | 3.002 | Non-IGP | 5814530 | T.0011010 | WRO Generator Network Upgrades | 10 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-06-25 | 2030-09-19 | 2030-10-04 | NA | NA | FALSE | 36997 | NA ¦ NA | 28.749 | 25330.7355 | 0 | 0 | 0 | 0 | 18.9512 | 11.5475 | 3957.2707 | 4186.4027 | 8479.053 | 8677.5103 | 18.9512 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $25,331 | NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2134 | WRO Generator Network Upgrades |  |  |  | The Project is a combination of solar and Battery Energy Storage System (BESS) 300 MW Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) Los Banos Substation 230kV in Merced County, CA. Below is the high-level project scope to build a new 230kV Breaker-and-a-half (BAAH) bay at Los Banos Substation to interconnect a 300MW generation. Interconnection Reliability Network Upgrades (IRNU): Los Banos Substation: • Install two (2) 230kV Circuit Breakers (CB) and associated switches for a new fifth BAAH Bay. o Expand the site grading inside the yard to allow for the additional bay o Install breakers, switches and associated structures, foundation, grounding system. o Install Breaker Failure and Reclosing relays for breakers associated with Los Banos - Australis 230 kV line in the new control building. Precursor Network Upgrade (PNU) Los Banos Substation • Q1382(T.0007250): Expand the yard within the existing property to accommodate a 6-bay BAAH ultimate bus section • C14P2-FGR04 (T.0010835): CB 842 Replacement Interconnection Facilities (IF) Los Banos Substation: • Install the following related to the new Gen-Tie line: o Install three (3) single phase line CCVTs for the new Gen-Tie line protection. o Install one (1) line dead-end structure and line disconnect switches. o Civil foundations and ground connections. o Install Line Current Differential (LCD) relay scheme on the Los Banos – Australis 230kV line. o Include Generation breakers into the bus differential scheme on the switching station bus. • Install fiber termination at the Los Banos Substation Generation Site: • PG&E project management, metering, engineering and protection review, and pre-parallel inspection • PG&E IT to install RTU and provide IC support with telecom circuits. T-Line work: • PG&E T-Line to install two (2) TSP and conductors on PG&E’s property to connect Customer’s Gen-Tie line to the line dead-end. • PG&E T-Line engineering will provide detailed requirements and review the design of the customer’s interconnecting tubular steel pole (TSP) at the PG&E Los Banos Substation property line. • PG&E T-Line to raise the following lines to allow the Customer’s Gen-Tie line to cross underneath: o Install two (2) double circuit TSPs and conductors for the Los Banos - Padre Flat SW Sta 230 kV and Los Banos - Mercy Springs Switching Station 70 kV. o Install one (1) double circuit TSP and conductors for the Los Banos - Panoche #2 230 kV and Los Banos - Dos Amigos 230 kV. | Substation - Circuit Breaker | New | NA | T.0007250 ¦ T.0010835 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 53.2803 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5814501 | T.0011060 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2030-03-26 | 2030-10-18 | 2030-10-17 | NA | NA | FALSE | 8065 | NA ¦ NA | 4.0126 | 429.5965 | 0 | 0 | 0 | 0 | 2.9454 | 24.0355 | 214.4931 | 46.1174 | 49.559 | 49.8302 | 2.9454 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $430 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
2135 | WRO Generator Network Upgrades |  |  |  | The Project is a combination of solar and Battery Energy Storage System (BESS) 300 MW Large Generating Facility connecting to Pacific Gas and Electric Company’s (PG&E’s) Los Banos Substation 230kV in Merced County, CA. Below is the high-level project scope to build a new 230kV Breaker-and-a-half (BAAH) bay at Los Banos Substation to interconnect a 300MW generation. Interconnection Reliability Network Upgrades (IRNU): Los Banos Substation: • Install two (2) 230kV Circuit Breakers (CB) and associated switches for a new fifth BAAH Bay. o Expand the site grading inside the yard to allow for the additional bay o Install breakers, switches and associated structures, foundation, grounding system. o Install Breaker Failure and Reclosing relays for breakers associated with Los Banos - Australis 230 kV line in the new control building. Precursor Network Upgrade (PNU) Los Banos Substation • Q1382(T.0007250): Expand the yard within the existing property to accommodate a 6-bay BAAH ultimate bus section • C14P2-FGR04 (T.0010835): CB 842 Replacement Interconnection Facilities (IF) Los Banos Substation: • Install the following related to the new Gen-Tie line: o Install three (3) single phase line CCVTs for the new Gen-Tie line protection. o Install one (1) line dead-end structure and line disconnect switches. o Civil foundations and ground connections. o Install Line Current Differential (LCD) relay scheme on the Los Banos – Australis 230kV line. o Include Generation breakers into the bus differential scheme on the switching station bus. • Install fiber termination at the Los Banos Substation Generation Site: • PG&E project management, metering, engineering and protection review, and pre-parallel inspection • PG&E IT to install RTU and provide IC support with telecom circuits. T-Line work: • PG&E T-Line to install two (2) TSP and conductors on PG&E’s property to connect Customer’s Gen-Tie line to the line dead-end. • PG&E T-Line engineering will provide detailed requirements and review the design of the customer’s interconnecting tubular steel pole (TSP) at the PG&E Los Banos Substation property line. • PG&E T-Line to raise the following lines to allow the Customer’s Gen-Tie line to cross underneath: o Install two (2) double circuit TSPs and conductors for the Los Banos - Padre Flat SW Sta 230 kV and Los Banos - Mercy Springs Switching Station 70 kV. o Install one (1) double circuit TSP and conductors for the Los Banos - Panoche #2 230 kV and Los Banos - Dos Amigos 230 kV. | Substation - Circuit Breaker | New | NA | T.0007250 ¦ T.0010835 | Generator Interconnection | Generation Interconnection | NA | NA | 2026-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ False | FALSE | NA |  | NA | 53.2803 | NA | 230 kV | NA | NA | NA | 3.002 | Non-IGP | 5814502 | T.0011060 | WRO Generator Network Upgrades | 7 | 82 | NA ¦ NA ¦ NA ¦ NA | FALSE | TBD | Project Management Governance Standard | 2025 | 2025 | FALSE | NA | NA | NA | TRUE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2027-08-13 | 2030-10-18 | 2030-10-18 | NA | NA | FALSE | 8065 | NA ¦ NA | 50.5152 | 11253.6491 | 0 | 0 | 0 | 0 | 26.4651 | 48.6252 | 347.0621 | 217.2841 | 4287.354 | 6322.5541 | 26.4651 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $11,254 | NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.