## CPUC TPR May 2024 Public
Date of Data Pull: | 2024-03-11
|  | Project Description | [35 empty] | Utility/CAISO Approval and FERC Rate Cases | [9 empty] | CPUC Permit Status | [9 empty] | Project Status | [6 empty] | Costs | [30 empty] | Notes
| 1 | 2 | 3a | 3b | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15a | 15b | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 |  |  |  |  | 26 | 27 |  |  | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40a | 40b | 41a | 41b | 42a | 42b | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 |  | 57 | 57 | 57 | 57 | 57 | 58 | 58 | 58 | 58 | 58 | 58 | 59 | 60 | 61 | 62 | 63 | 63 | 63 | 63 | 63 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70
| Row/Line No. | Project Name(s) | Latitude | Longitude | Location2 | Project Description | Project Description - What | Project Description - Action Taken | Project Dependencies | Primary Purpose | Secondary Purpose | NERC/WECC/CAISO Standard/Requirement/Contingency | Last Inspection | Age of Asset | Types of Analyses | Alternative Solutions and Costs - Solutions | Alternative Solutions and Costs - Costs | CPUC Fire Threat Zone/Rating | Wildfire Related | RAMP | Other Environmental Factors | Project Manager | Transmission Project Size (length in miles) | Substation Project Footprint (acres) | Transmission Voltage Level (kV) | Substation or Transformer Capacity (MVA and/or kV) | Utility Prioritization Ranking - RIBA | Utility Prioritization Ranking - Loading Order | Utility Prioritization Ranking - Circuit Based Plan Rank | Utility Prioritization Ranking - RBPPF | Utility Prioritization Ranking - Integrated Grid Planning | Utility Unique ID #1 (Most Specific) | Utility Unique ID #2 (Less Specific) - T.Dot | Utility Unique ID #2 (Less Specific) - T.Dot Name | Utility Unique ID #2 (Less Specific) - Planning Orders per T.Dot | Utility Unique ID #3 (Least Specific) | Changes in Unique IDs | Utility Approval (Year of AA) | Year of Internal Utility Approval (Year of BC) | Process(es) for Utility Approval | Long term Transmission Investment Plan Inclusion | CAISO Year | TPP Phase 3 | Year(s) when considered in CAISO TPP | Year when expected to be considered in CAISO TPP | Link to TPP where project has been considered, approved, and/or expected to be considered | GIDAP-Related | CEQA Status | CEQA Status - Date | CEQA Document Type | NEPA Document Type | CEQA Lead Agency | NEPA Lead Agency | CPUC Filing Type | CPUC Date Filed | CPUC Status | CPUC Status - Year | Project Status | AACE Class | Construction Start Date | Original Planned In-Service Date | Current Projected or Actual In-Service Date | Reason for Change in In-Service Date | In-Flight Projects | Original Projected Cost or Cost Range ($000) | Cost Cap ($000) | Inception to Date ($000) | Current Projected Total or Actual Final Cost ($000) | Actual Capital Expenditures 2019 ($000) | Actual Capital Expenditures 2020 ($000) | Actual Capital Expenditures 2021 ($000) | Actual Capital Expenditures 2022 ($000) | Actual Capital Expenditures 2023 ($000) | Actual and Forecast Capital Expenditures 2024 ($000) | Projected Capital Expenditures 2025 ($000) | Projected Capital Expenditures 2026 ($000) | Projected Capital Expenditures 2027 ($000) | Projected Capital Expenditures 2028 ($000) | Projected Capital Expenditures 2029 ($000) | Construction Work in Progress ($000) | Accrued Overhead ($000) | Accrued AFUDC ($000) | FERC: Year(s) | Dollars Put into FERC Rate Base 2019 ($000) | Dollars Put into FERC Rate Base 2020 ($000) | Dollars Put into FERC Rate Base 2021 ($000) | Dollars Put into FERC Rate Base 2022 ($000) | Dollars Put into FERC Rate Base 2023 ($000) | Dollars Put into FERC Rate Base 2024 ($000) | Percentage of Bid | Percentage and Value ($000) of Work Requested by Others Passed onto Ratepayers | Cost-Benefit Analysis | FERC Incentives | Percentage of Cost in High Voltage TAC | Percentage of Cost in Low Voltage TAC | Notes
| 1 | Trans Sub Constr Capital Tools |  |  | NA | Bucket for capital tools for Construction. | Other | New | NA | Other [See Notes] | Tools | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 31 | 9. Reliability (Low Safety Risk) | Not Available | Tier 1 | No | 5512939 | NA | NA | NA | 5 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 11688.2263 | 11688.2263 | 1618.4109 | 1066.0329 | 1266.1546 | 1758.3253 | 764.5146 | -8.1928 | 1457.3423 | 1457.3423 | 1457.3423 | 1457.3423 | 1487.084 | 11696.4191 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1648.4475 | 710.3104 | 1556.5436 | 1804.188 | 24.6751 | 751.1174 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 2 | Trans Sub Maint Capital Tools |  |  | NA | Bucket for capital tools for Maintenance work. | Other | New | NA | Other [See Notes] | Tools | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 247 | 9. Reliability (Low Safety Risk) | Not Available | Tier 1 | No | 5512940 | NA | NA | NA | 5 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 13342.7733 | 13342.7733 | 991.2637 | 894.8796 | 1607.6566 | 1300.7367 | 1106.4488 | -651.3929 | 1457.3423 | 1457.3423 | 1457.3423 | 1457.3423 | 1487.084 | 13994.1662 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1003.1676 | 604.8053 | 1719.5281 | 1426.5166 | 415.246 | 79.169 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 3 | Trans Sub Test Capital Tools |  |  | NA | Bucket for capital tools for testing. | Other | New | NA | Other [See Notes] | Tools | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 594 | 9. Reliability (Low Safety Risk) | Not Available | Tier 1 | No | 5512941 | NA | NA | NA | 5 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 15940.0209 | 15940.0209 | 1552.3417 | 1591.5351 | 1801.9134 | 1473.7188 | 1149.2063 | 0 | 1418.1423 | 1418.1423 | 1418.1423 | 1418.1423 | 1447.084 | 15940.0209 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1153.3648 | 1058.4261 | 2733.9993 | 1473.7188 | 1149.2063 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 4 | Purch Tools & Equip - TLINE |  |  | NA | Bucket for purchasing tools and equipment for T-Line. | Other | New | NA | Other [See Notes] | Tools | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 758 | 9. Reliability (Low Safety Risk) | Not Available | Tier 1 | No | 5501201 | NA | NA | NA | 5 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 42248.9116 | 42248.9116 | 774.2319 | 1403.3733 | 684.0502 | 656.3976 | 1029.9009 | 49.2912 | 1024.1588 | 1024.1588 | 1024.1588 | 1024.1588 | 1045.06 | 42199.6204 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 774.2319 | 1099.8809 | 836.9211 | 807.019 | 480.8762 | 597.4013 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 5 | ETrans - Treated Wood Transport&Disposal |  |  | NA | Bucket for costs associated with the transport and disposal of transmission wood poles after they have been removed from service and are being disposed. | Other - Environmental | Removal | NA | Other [See Notes] | Environmental | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5515081 | NA | NA | NA | 12 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 2440.0937 | 3643.118 | 219.6101 | 414.3962 | 363.4932 | 201.794 | 188.2452 | 415.5793 | 368 | 368 | 368 | 368 | 368 | 2392.5144 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 6 | Env Cap Improvements (Tran) |  |  | NA | Bucket for SPCC (Spill Prevention Containment Control) actions such as installation of concrete ponds and drainage to control the run-off of spills at Electric Transmission sites. | Other - Environmental | New | NA | Other [See Notes] | Environmental | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5515080 | NA | NA | NA | 12 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1687.8178 | 3939.1938 | 378.4829 | 420.1865 | 46.4235 | 1.9621 | 1.8272 | 515.3116 | 515 | 515 | 515 | 515 | 515 | 1687.5062 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 598.4697 | 122.5166 | 383.3207 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 7 | Misc. contracts |  |  | NA | Forecast placeholder for misc. contacts in support of ET capital work | Other | New | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5547779 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 801.2249 | 801.2249 | 801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2073 | 801.2249 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 | 0 | 0 | 0 | 100.1475 | 701.0774 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 8 | Transmission/Substation As-Built Process Improvement |  |  | NA | Forecast placeholder for substation As Build Process Improvement | Other | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 1 | No | Ex112889 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 9 | Transmission As-Build Process Improvement |  |  | NA | Forecast placeholder for t-line As Build Process Improvement | Other | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 1 | No | Ex112888 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 10 | 2021-2022 Replace Eureka T-line Trailer |  |  | Eureka, Humboldt | Procure a trailer in Eureka area due to a T-WRFR decision. | Other | New | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5546477 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-04-06 | NA | TRUE | NA | NA | 1315.4423 | 1315.4423 | 0 | 0 | 388.9056 | 464.7503 | 444.6448 | 17.1416 | 0 | 0 | 0 | 0 | 0 | 1298.3007 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 835.7013 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 11 | FIXED WING - CAMERAS |  |  | NA | Purchase and attach two MX-15 cameras to the aircraft. The addition of MX-15 cameras would enable the fixed wing fleet to support some Public Safety Power Shut-off -related patrol activities (that are traditionally performed by helicopters) in a much safer capacity and with improved asset inspection quality. Improved camera assets can provide support for external agencies (e.g., fire patrol, geological assessments) • Adds capability to perform circuit patrols at night, reducing customer outage time • Adds capability to perform fixed wing Electric Transmission Tower patrol • Imagery and video recording improves permanent records keeping | Other - Operations Tech | New | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5790210 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2020-09-30 | NA | FALSE | NA | NA | 2713.0252 | 2713.0252 | 0 | 2638.0252 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2713.0252 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2022 ¦ 2024 | 0 | 2638.0252 | 0 | 75 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 12 | Copperleaf capital T |  |  | NA | Bucket for an Asset Investment Planning Management (AIPM) tool called Copperleaf to enable more informed asset investment decisions and improve the effectiveness of risk-based asset investment plans. Copperleaf will enable Electric Operations to develop risk and benefit models and incorporate different models into a common scale, thereby allowing for more equivalent comparisons of risk reduction or investment value across different types of assets. The tool also provides scenario planning capabilities that enable continuous, automated optimization of investment plans over time based on different constraints or changing conditions. | Other | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 1 | No | 5546960 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 3518.3025 | 3518.3025 | 0 | 0 | 1002.1423 | 2404.6257 | 183.7345 | -72.2 | 0 | 0 | 0 | 0 | 350 | 3590.5025 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 3590.5024 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 13 | PLS-CADD Model - Operability Assessmnt |  |  | NA | Bucket for PLS-CADD modeling project creating detailed electronic models of ~48,000 PG&E Transmission Tower and Pole assets in the Tier 2/3 HFTD. PLS-CADD models refine the baseline of each structure’s design basis in the Risk Model to more accurately predict structural failure under wind load cases to better inform PSPS decision making and asset investment strategy. Models provide an accurate 3D representation of assets in the field (the ‘digital twin’ concept) and unify various PG&E data sources (SDS, Construction Drawings, Photos, LiDAR). PLS-CADD: • Industry-standard overhead power line design software produced by Power Line Systems®. • Supports computer-aided modeling of an entire transmission line • Sophisticated 3-D engineering model including terrain, structures, and wires. • Uses Finite Element Analysis (FEA) to combine a system of structures as a single model (accounts for effect of load on adjacent structures) • The analysis output reports the effect of pre-defined load cases for every structural element of the model (actual stress / allowed stress) | Other | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | NA | Not Available | Tier 1 | No | 5538644 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 18621.0481 | 18621.0481 | 0 | 6918.4398 | 5625.4095 | 4719.9569 | 1357.242 | 0 | 0 | 0 | 0 | 0 | 2000.0001 | 18621.0481 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 6918.4398 | 5625.4095 | 4719.9569 | 1357.242 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 14 | ET Federal Land Authorizations |  |  | NA | Bucket for renewal for a 30-50 year period, authorizations from the U.S. Forest Service (USFS) and the Bureau of Land Management (BLM) for transmission lines that currently have expired authorizations. | Other | Replace | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 25 | Not Available | Not Available | RBPPF - TBD | No | 5721938 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2013 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 9768.9111 | 9768.9111 | 1402.2846 | 697.7285 | 544.6578 | 174.3423 | 145.4313 | 1006.0469 | 0 | 0 | 0 | 0 | 0 | 9762.8642 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1364.4207 | 645.3381 | 1242.476 | 174.3423 | 145.4313 | 8.522 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 15 | TG 2021 Holding Order - Transmission |  |  | NA | Bucket for Temporary Generation Transmission work | Other | New | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5545721 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1802.6981 | 1802.6981 | 0 | 0 | 1593.4087 | 90.4894 | 118.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1802.6981 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 16 | Transmission CIRT Capital |  |  | NA | CIRT is centralized inspection review team and they would come in once the inspection has been complete and review the findings to determine if we repair or replace the asset which will trigger creating notification under maintenance program or other programs which manage the replace of asset which is typically capital. | Other | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5551452 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1203.0016 | 1203.0016 | 0 | 0 | 0 | 1203.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1203.0016 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 1203.0016 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 17 | Wildfire Risk Transmission |  |  | NA | Wildfire Transmission Risk Model (WTRM) is a Composite model framework integrating useful life for all 47 components that have a potential ignition risk upon their failure. The model calculates a probability of failure for each component group under specific threats\hazards which is joined with different types of consequence data to calculate various types of risk. (Wildfire, Public Safety etc.) | Other | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 1 | No | 5551539 | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 8890.1554 | 8890.1554 | 0 | 0 | 0 | 5495.5692 | 3205.9291 | 188.657 | 2000 | 2000 | 2000 | 2000 | 2000 | 8701.4984 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 5495.5692 | 3150.3945 | 331.1436 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 18 | Livermore Substation Training Fac. (TO) |  |  | Livermore, Alameda | The purpose of the Livermore Substation Training Facility project is to build a best-in-class training venue at the Livermore Substation Training Facility to provide training on Electric Transmission substation operations and maintenance. | Substation - Other Equipment | New | NA | Other [See Notes] | System Operations | NA | 2024-02-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.60395 | NA | NA | 361 | Not Available | NA | NA | NA | 5782941 | T.0002104 | Livermore Substation Training Facility | 2 | 23 | NA | 2016 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-11-15 | 2018-10-29 | 2019-12-30 | Completed Early | FALSE | 63000 | NA | 13811.6068 | 13811.6068 | 4830.9979 | 219.7129 | -216.8398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13811.6068 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 | 4830.9979 | 219.7129 | -216.8398 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 19 | Livermore Sub - New Facility (TO) |  |  | Livermore, Alameda | The purpose of the Livermore Substation Training Facility project is to build a best-in-class training venue at the Livermore Substation Training Facility to provide training on Electric Transmission substation operations and maintenance. | Substation - Other Equipment | New | NA | Other [See Notes] | System Operations | NA | 2024-02-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.60395 | NA | NA | 361 | Not Available | NA | NA | NA | 5782943 | T.0002104 | Livermore Substation Training Facility | 2 | 23 | NA | 2016 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-11-15 | 2018-11-30 | 2019-01-01 | NA | FALSE | 63000 | NA | 22756.2992 | 22756.2992 | 5649.8287 | 246.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22756.2992 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 5649.8287 | 246.499 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 20 | SFGO - RAS Relocation |  |  | San Francisco, San Francisco | This project is part of the SFGO RAS Lifecycle and Relocation Project - Phase 1 and is for the associated remote work at Helms. | Other - Remedial Action Scheme/Special Protection Scheme | New | T.0006261 | Other [See Notes] | System Operations | NA | NA | 14 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5788603 | T.0006190 | SFGO RAS LifeCycle and Relocation | 9 | 23 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2022-12-29 | 2022-12-30 | NA | TRUE | 182000 | NA | 54536.0844 | 54882.0842 | 0 | 366.7691 | 9283.225 | 39446.7859 | 5355.8274 | 429.4768 | 0 | 0 | 0 | 0 | 0 | 54452.6076 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 49096.78 | 4207.4589 | 246.8712 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 21 | Rocklin - Real Estate Purchase |  |  | Rocklin, Placer | Real Estate Purchase in Rocklin for Control Center | Other - Civil | New | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5791423 | NA | NA | NA | 23 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2020-09-08 | NA | FALSE | NA | NA | 6784.7301 | 6784.7301 | 0 | 6784.7301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6784.7301 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 6784.7301 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 22 | Bentley-SAP IntegrationCAP-ET Phase 3 |  |  | NA | Build interface between the Bentley Substation design tool and SAP to facilitate automated material ordering.The SAP and Bentley data will be automatically synchronized; the Fresno Materials Team will be able to perform their work in SAP without manually reconciling data across legacy data bases. Automatically populating the Bill of Materials (BoM) into the components screen in the SAP work management PM order, manual process will be minimized and eventually eliminated. The materials populated in the components screen will also be reflected in the Clarity functionality now used by Electric Transmission. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5773912 | NA | NA | NA | 2F | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-06-15 | 2021-12-06 | Project Design | FALSE | 1200 | NA | 2579.8412 | 2579.8412 | 123.6597 | 905.6183 | 809.7275 | 9.3796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2579.8412 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 2570.4616 | 9.3796 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 23 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | New | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5794224 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-07-30 | NA | TRUE | NA | NA | 2517.7191 | 2517.7191 | 0 | 233.1966 | 1266.0529 | 584.7268 | 433.7428 | 0 | 0 | 0 | 0 | 0 | 0 | 2517.7191 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1274.7981 | 327.338 | 915.583 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 24 | IT CNI-PGE-StocktonA_to_Weber_Rep(TO)_C |  |  | NA | FT - Stockton A to Weber MW Replacement Replace D003 and D250 with a new, diverse dark fiber SONET connection between Stockton Station A and Weber Sub. Improves reliability of core business electric protection, GDN, RAS, EMS, and SCADA circuits. AHI = 1.70 | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5798158 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-05-15 | NA | TRUE | NA | NA | 1544.3614 | 1544.3614 | 13.8429 | 34.4642 | 531.7431 | 487.9839 | 476.3273 | 0 | 0 | 0 | 0 | 0 | 0 | 1544.3614 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1544.3614 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 25 | Joint Pole Accelerated Collections (C) |  |  | NA | Item 1: Merge the SAP EES and Joint Pole billing tables Item 2: SAP rule to recognize that a blue bill has been printed and not allow an SAP blue bill to be emailed Item 3: Update reports to include the blue bill number Item 4: Transmission pole intents within TEMACC will pass data to SAP Joint Pole. Item 5: Provide additional enhancements for Form 2 process Implement versioning. Currently, when a revision is made to a Form 2 intent, there is no way to reset the clock and re-send the new version to the Other Utility. This causes process delays and re-work. Assume this is a revision after the Form 2 has already been sent, and than an unlimited number of revisions and re-sends is required. Enhancement to JPORDER email functionality. Item 6: Provide additional enhancements for Form 7 process – Provide the ability to manually set an intent to “F7 Received”. Item 7: Provide additional enhancements for Intent process – Provide ta limited ability to reverse intent statuses to allow for corrections and intent cleanup. Sent to Construction status enhancements. Currently, no changes to any intent can be made from this status. Item 8: Provide additional enhancements for Form 48 and 44 process – There is a gap in our tool that does not provide for a Draft Final Form 48 to be sent to OU for review. Currently, the application directs a completed Form 48 directly to Billing Form 48 process is currently not working. Analysis and cause to be determined. Form 44 process for Final Billing and Payment not working. Analysis and cause will need to be determined. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5804920 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 3 | NA | NA | 2024-12-30 | NA | FALSE | NA | NA | 1284.0858 | 2701.0858 | 0 | 0 | 0 | 0 | 1246.0725 | 1455.0133 | 0 | 0 | 0 | 0 | 0 | 1246.0725 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1246.0725 | 38.0133 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 26 | FT - 2023 Network Lifecycle (TO) |  |  | NA | Replace End of life network gear that supports transmission operations | Other - IT | Replace | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5803335 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 3 | NA | NA | 2024-12-30 | NA | TRUE | NA | NA | 1515.793 | 3140.793 | 0 | 0 | 0 | 1.8072 | 1293.2681 | 1538.7177 | 307 | 0 | 0 | 0 | 0 | 1295.0753 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 1598.6959 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 27 | CS - SAP Unifer Ariba Integration TO (C) |  |  | NA | SAP Unifier and Ariba Integration: The key objective of this phase of Unifier EPM Tools is to build integrations between standard enterprise applications and establish repositories of high quality data that can be used to improve project management, and to provide an appealing, efficient end user experience through automation. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5796838 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2022-12-07 | NA | FALSE | NA | NA | 3239.5236 | 3239.5236 | 0 | 0 | 610.7503 | 2628.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3239.5236 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 3239.5236 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 28 | IO-Kings Craine Microwave Capacity Incre |  |  | NA | This project is to provide a redundant Telecom Transmission route for the Helms Power Generation Plant. A new microwave radio path, using the existing company technology since 2011, from the FOC to Bear Mtn, Bear Mtn to Balch PH (via a Passive Reflector) while upgrading the Balch PH to Haas PH microwave radios. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5794223 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2022-12-07 | NA | TRUE | NA | NA | 2146.309 | 2146.309 | 59.0537 | 608.616 | 839.0042 | 460.618 | 147.6403 | 0 | 0 | 0 | 0 | 0 | 0 | 2146.309 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1998.6687 | 147.6403 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 29 | zEGI Development for Substation |  |  | NA | Develop a new generational EGI project life cycle tool that would encompass Substation and Transmission Line design Review WEB Based tools in the PG&E Cloud Based Center Of Excellence Work with Infrastructure team to determine usability of Planisware scheduling and resource planning tool Tie EGI project drawings into the ProjectWise system Link Project Data sources (EGI to PLS CADD & Substation) Develop Drawing Comparison tools and workflows to improve design file quality Open up the EGI work process to enterprise level to gain visibility on new projects and new customers and their potential delay | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807027 | NA | NA | NA | 2F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 3 | NA | NA | 2024-06-01 | NA | FALSE | NA | NA | 0 | 3079 | 0 | 0 | 0 | 0 | 0 | 1499 | 1580 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 30 | Emerging WF Commit Trans (C) TO |  |  | NA | Forecast placeholder for Wildfire TO reserve cost. In the Wildfire IT portfolio, there may be unforeseen circumstances such project change requests that develop during the year or new projects that PG&E does not have line of sight into at the time we plan the project portfolio. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807719 | NA | NA | NA | 2F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | 2024-12-31 | NA | FALSE | 1410 | NA | 0 | 1410 | 0 | 0 | 0 | 0 | 0 | 1410 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 31 | Sherlock ET System Inspection (Aeria |  |  | NA | PG&E developed an enhanced inspection program as part of the Community Wildfire Safety Program, known as the Wildfire Safety Inspection Program ("WSIP"). The WSIP implemented enhanced inspections to be completed on an accelerated schedule for PG&E to inspect its electric facilities in Tier 2 and Tier 3 HTFD areas and address any high priority repairs identified before the 2019 fire season. Under WSIP, the accelerated inspections focus on conditions that could lead to potential fire ignitions, known as the Failure Modes and Effects Analysis ("FMEA"), and supplement PG&E's baseline inspection and maintenance procedures. Through the FMEA, PG&E has identified single points of failure of electric system components that could lead to fire ignition. The identification of these failure points will aid in the development of inspection methods that can most appropriately identify the condition of such components, which are designed in accordance with GOs 95, 165, and 174 requirements. Sherlock is a tool for performing multiple roles associated with remote desktop inspection of aerial imagery of Transmission and Distribution structures. The software also serves as an image viewer utilized by other departments. As of 2024 Transmission is on version 1 while Distribution was released in version 2. | Other - IT | Upgrade/Retrofit | 5783781 | Other [See Notes] | IT | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807003 | NA | NA | NA | 2F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 4 | NA | NA | 2024-12-31 | NA | FALSE | NA | NA | 0 | 2040 | 0 | 0 | 0 | 0 | 0 | 1389 | 651 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 32 | IGP IT ET (C) |  |  | NA | Objective: use detailed data about the PG&E electric grid, from substation to distribution, to: 1) lower costs for annual grid projects and maintenance; and 2) increase how well the annual grid investments promote key PG&E goals. SCOPE FOR PHASE 1 Develop a high level design, identify data sources, and complete initial data population of the IGP applications. Develop and test the initial IGP Benefits model. Complete Asset, Portfolio, and Investment workshops.Configure investment types, portfolios, and users. Final loads of asset data and creation of the 2025 integrated grid investment recommendations/plan. SCHEDULE FOR PHASE 1 Release: 9/27/2024 go live for investment planning to recommend investments for all addressable Capital Pole Management and Maintenance Tag work: about 38% of the addressable Electric investment portfolio. Compare where feasible to Bain 2025 rrecommendations. Stabilization Complete: 10/31/2024. SCOPE – 2025 Complete Value Framework workshops and create initial Value Model designs. Develop an automated interface from data sources to the application SaaS databases. Deliver training to the teams doing investment planning and go live, including delivery of 2026 IGP plan. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807158 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | 2024-09-15 | NA | FALSE | NA | NA | 0 | 1222 | 0 | 0 | 0 | 0 | 0 | 605 | 617 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 33 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | EX113406 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | 2029-09-15 | NA | FALSE | NA | NA | 0 | 40512 | 0 | 0 | 0 | 0 | 0 | 0 | 7332 | 7698 | 8083 | 8487 | 8912 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Cybersecurity [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 34 | E Trans Underbuild Transmission (C) |  |  | NA | Approximately 60,000 transmission structures have distribution underbuilds. These ~60,000 assets are shared by distribution and transmission but currently show up as separate assets in SAP, ETGIS and EDGIS, without an indication they are the same structure. This allows for inconsistencies with distribution and transmission potentially working on the same asset without knowledge of the other. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5800227 | NA | NA | NA | 2F | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2022-09-21 | NA | FALSE | 1651 | NA | 1080.4708 | 1080.4708 | 0 | 0 | 0 | 1080.4708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080.4708 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 1080.4708 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 35 | WSIP: Pronto Forms Cap (TO) |  |  | NA | As part of PG&E’s WSIP (Wildfire Safety Inspection Program), PG&E used a mobile data asset attribute form application (ProntoForms) to capture the Electric Transmission asset attributes. To gather the necessary Electric Transmission information, PG&E had to build new integrations/connections between the mobile device, the mobile application, and the systems of record. Systems impacted that require the building of new integrations include SAP, ProntoForms, iPad devices, S3-(AWS), etc. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | NA | NA | NA | 5787974 | NA | NA | NA | 2F | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-11-22 | 2019-11-22 | NA | FALSE | 1710 | NA | 1277.1396 | 1277.1396 | 1277.0228 | 0.1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1277.1396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1277.0228 | 0.11682 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 36 | ElecOps - Substa Rcrd-RcrdKeep 2019 TO C |  |  | NA | Build and deploy a software technology solution that will enable a more automated approach to the substation record keeping process. The current software in place does not address these requirements without a significant upgrade to add new functionality. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5773844 | NA | NA | NA | 2F | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2017-12-15 | 2023-06-15 | Vendor Quality/Delays | TRUE | 3584 | NA | 8028.021 | 8028.021 | 2985.1859 | 906.9755 | 79.4316 | 476.8573 | 390.6386 | 0 | 0 | 0 | 0 | 0 | 0 | 8028.021 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2023 ¦ 2024 | 6174.118 | 906.9755 | 0 | 0 | 946.9275 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 37 | CWSP - Construct App (Cap TO) |  |  | NA | Build and deploy the Construct ET mobile application, which provides field personnel the ability to view, coordinate and document corrective work execution. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5785420 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-12-31 | 2020-05-11 | NA | FALSE | 8198 | NA | 1380.7313 | 1380.7313 | 772.0395 | 608.6918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1380.7313 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 1380.7313 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Year of BC] Job Estimate serves as Utility Approval. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 38 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | New | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | RBPPF - TBD | No | 5784618 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | 5775788 | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2024-09-26 | OAI | NA | TRUE | 41311 | NA | 37123.5487 | 42884.4675 | 6687.8065 | 6251.8837 | 5005.9013 | 6366.0866 | 7459.1769 | 9145.5968 | 0 | 0 | 0 | 0 | 0 | 35938.9519 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 2226.0058 | 8794.674 | 1616.6757 | 8832.7137 | 9769.2497 | 1319.5841 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Cybersecurity [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 39 | Electric GIS 2023 Enhancements (CAP) |  |  | NA | Complete at least one release each quarter to deploy GIS enhancements and address production defects | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5804307 | NA | NA | NA | 2F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-12-27 | NA | FALSE | NA | NA | 1069.7812 | 1101.7812 | 0 | 0 | 0 | 0 | 1037.5348 | 64.2464 | 0 | 0 | 0 | 0 | 0 | 1037.5348 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 1073.43 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 40 | Inspect and Engage 2.0 ET (CAP) |  |  | NA | Continue to implement new features and capabilities for the Electric Transmission Patrol & Inspection applications. New features include refining maintenance plans, improving regulatory reporting, and allowing field supervisors to view work progress, and assign / prioritize work geo-spatially. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5785399 | NA | NA | NA | 2F | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2021-11-26 | NA | FALSE | NA | NA | 2462.8234 | 2462.8234 | 0 | 448.6318 | 2028.7816 | -14.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2462.8234 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 2477.4134 | -14.59 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Year of BC] Utility Unique ID #1 5784142 (Inspect and Engage 1.0 ET (CAP)) and #5785399 (Inspect and Engage 2.0 ET (CAP)) share the same business case. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 41 | WF: Elect Trans Compliance (C) |  |  | NA | Create new features for the 2020 inspection program. The new features will support Electric Transmission inspection compliance by collecting newly required detailed inspection information in the Inspect, Engage, and SAP suite of applications. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5790275 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2020-10-30 | 2020-10-31 | NA | FALSE | NA | NA | 1101.1907 | 1101.1907 | 0 | 1101.1907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101.1907 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 1101.1907 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 42 | UO-FWM-Inspect ET (C) |  |  | NA | Data Collection Tool - System Inspections (non-Wildfire) (pge.com).The current Inspect, Engage, MPMT applications have released a minimal viable product (MVP) in 2020. The current System Inspections program requires annual updates to the detailed overhead inspection checklist, including impacts to Inspect Mobile application, Engage Web Portal, MPMT, SAP and BW. The proposed scope ensures that PG&E continues to better the applications for the multitude of needs in the system inspection process with special focus on: 1) The ability to quickly identify and efficiently assign work; 2) Quicker completion and data throughput; 3) Making planning easier and reducing human error with better detective controls. This technology is not in support of the Wildfire Mitigation program. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5798041 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2024-03-30 | NA | TRUE | NA | NA | 4879.0764 | 5401.5665 | 0 | 0 | 650.3224 | 1926.7697 | 2019.0856 | 805.3888 | 0 | 0 | 0 | 0 | 0 | 4596.1776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 3051.1187 | 1939.7492 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 43 | Inspect and Maintain (AI 2.0) (TO) - CAP |  |  | NA | DC will continue to implement new features and capabilities for the current users of the Inspect, Gas Leak Survey, Electric Compliance and Electric Transmission Patrol & Inspection applications. Features include: - Complete development of digital assignment, documentation, approval and reporting of: - Gas Distribution Leak Survey data - Electric Compliance patrol and inspection data - Electric Transmission patrol and inspection data - Develop and deliver inspection and maintenance features for Veg Management and Corrosion; - Design and develop an emergency mode to facilitate the assessment and documentation of corrective work for routine and major emergency conditions. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | NA | NA | NA | 5781521 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2018-10-15 | 2019-01-30 | NA | FALSE | NA | NA | 2585.0598 | 2585.0598 | 240.5642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2585.0598 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2024 | 2585.0598 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Year of BC] Job Estimate serves as Utility Approval. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 44 | ET OH Asset Info Collection (C) |  |  | NA | Define critical components of Electric Transmission towers and other structures in High Fire Threat District areas that require recording of foundational asset information, including asset age. Execute processes as part of the Foundational Asset Knowledge collection effort / phase. Update systems of record component age information using completed data collection template | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5797621 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-12-30 | NA | TRUE | NA | NA | 1861.433 | 1861.4329 | 0 | 0 | 145.8631 | 855.9638 | 864.3709 | -4.7649 | 0 | 0 | 0 | 0 | 0 | 1866.1979 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1866.1978 | -4.3235 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 45 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | New | NA | Other [See Notes] | Security Upgrades | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5785784 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2020-10-30 | 2020-10-20 | NA | FALSE | 2917 | NA | 5039.2335 | 5039.2335 | 2002.1299 | 2945.5563 | 91.5472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5039.2335 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 4947.6863 | 91.5472 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 2 & 7 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 46 | ET Asset Registry - (CAP) |  |  | NA | Develop a source of records for Electric Transmission and Substation asset facilities ratings by integrating multiple data sources; develop a process for easily identifying a customer’s pricing node and be able to provide the information for requesting party. | Other - IT | New | NA | Other [See Notes] | IT | NERC FAC Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5779318 | K.0000044 | ET Asset Registry | 1 | 2F | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2018-12-15 | 2023-09-25 | Project Design | TRUE | 2370 | NA | 6626.6624 | 6626.6623 | 985.7816 | 1301.0768 | 2224.1194 | 1554.4618 | 476.5969 | 0 | 0 | 0 | 0 | 0 | 0 | 6626.6624 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 2818.9845 | 0 | 3127.3142 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC FAC 8, CPUC D.15-11-042, WECC Audit Findings [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 47 | Pole Test & Treat ET 2023 CAP |  |  | NA | Development of a mobile enabled inspection application for Electric Transmission Pole Test & Treat processes. This application would mitigate pole safety and compliance risks that exist with the current process.” | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5804306 | NA | NA | NA | 2F | NA | NA | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 3 | NA | 2024-05-31 | 2024-06-30 | NA | TRUE | 2260 | NA | 951.4289 | 3612.4889 | 0 | 0 | 0 | 0 | 772.7733 | 1621.7156 | 1218 | 0 | 0 | 0 | 0 | 772.7733 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 48 | ET Operability Assessment (C) |  |  | NA | Enable enhancements made to the (Operability Assessment) OA model as directed by Electric Transmission Line Asset Strategy. IT's scope is to host the model, where the algorithm is developed by T-line Asset Strategy. Develop v3 PAF models as additional data are made available that improve the quality of asset health predictions. PAF models are developed by Data Scientists in Data & Analytics. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5795497 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2024-01-03 | NA | TRUE | NA | NA | 4528.2268 | 4528.2268 | 0 | 0 | 1599.2183 | 2106.3478 | 822.6607 | 0 | 0 | 0 | 0 | 0 | 0 | 4528.2268 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2789.5304 | 1738.6964 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 49 | WSIP - Sherlock Tool (C) TO |  |  | NA | Following the catastrophic California wildfires in November 2018, PG&E captured more than 2 million images of our field equipment in high fire-risk areas. We developed a technology solution called “Sherlock” that enables the automation of otherwise manual inspections using industry-leading artificial intelligence (AI) techniques to reduce cost, increase quality, and enable PG&E to have in-depth knowledge of the state of our equipment. The Sherlock Suite allows desktop inspectors to markup potential equipment problems on high-resolution images, further training computer-vision models to automatically detect potential issues and adding metadata to enable searchability of these images across the enterprise. | Other - IT | New | 5807003 | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5783781 | NA | NA | NA | 2F | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-06-15 | 2023-12-29 | Project Design | TRUE | 4509 | NA | 13693.2688 | 14737.0544 | 2184.2874 | 3032.7896 | 2936.7566 | 2856.4889 | 2320.6765 | 976.2698 | 0 | 0 | 0 | 0 | 0 | 13330.999 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1619.7232 | -153.8722 | 5029.6664 | 3091.8484 | 3743.6332 | 504.8853 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 50 | FT-Micro_Radio_CapIncreReliab_Imp_TO_C |  |  | NA | FT - SCADA Radio Capacity and Reliability Improvements (TO) 2022 Project Description: This project migrates SCADA RTUs at substations that are on the ODN and migrated away from DSO leases or private 4 Wire circuits The scope of PO 5794363 is as follows: 1) Install a Tait repeater station at Gato Ridge and a spread spectrum microwave radio link from Gato Ridge to Red Rock. The station is necessary to fill gaps and improve mobile radio coverage in Santa Barbara County and surrounding areas. 2) Provide a diverse fiber optical connection along Electric Transmission 60kV line between Stockton Station A and Weber Substation for resiliency and increased bandwidth. Circuits will be migrated off of the existing microwave path onto the new fiber network. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5794363 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 3 | NA | NA | 2024-10-15 | NA | TRUE | NA | NA | 3003.7564 | 3328.6492 | 138.2829 | 164.4956 | 382.196 | 1095.3502 | 416.4676 | 322.9882 | 379 | 0 | 0 | 0 | 0 | 2915.7682 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 51 | Inspect and Engage 1.0 ET (CAP) |  |  | NA | Implement new features and capabilities for the Electric Transmission Patrol & Inspection applications. New features include completing development of digital assignment, documentation, approval and reporting of Electric Transmission patrol and inspection data, and designing and developing an emergency mode to facilitate the assessment and documentation of corrective work for routine and major emergency conditions. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5784142 | NA | NA | NA | 2F | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-12-31 | 2020-10-30 | Project Design | FALSE | 6000 | NA | 6714.807 | 6714.807 | 2546.8933 | 4116.7658 | 51.1479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6714.807 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 6663.6591 | 51.1479 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Year of BC] Utility Unique ID #1 5784142 (Inspect and Engage 1.0 ET (CAP)) and #5785399 (Inspect and Engage 2.0 ET (CAP)) share the same business case. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 52 | M&C Tower Unit Material Tracking Cap |  |  | NA | Migrate existing unsupported ShopList Access database to a new centralized, managed database platform | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5806062 | NA | NA | NA | 2F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 3 | NA | NA | 2024-06-01 | NA | FALSE | NA | NA | 1346.3807 | 2345.3807 | 0 | 0 | 0 | 0 | 1064.7363 | 781.6444 | 499 | 0 | 0 | 0 | 0 | 1064.7363 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 1508.2439 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 53 | WSIP: TSS Phase 2 (C) TO |  |  | NA | Objectives of this project include a greater understanding of failure modes, establishment of a common repository of data gathered, and effectively updating workflows of key asset systems to align with new data strategies. The project is a series of enhancements to the current TSS application, with no new infrastructure or application software required. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5795571 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2022-01-28 | NA | FALSE | NA | NA | 1709.4561 | 1709.4561 | 0 | 0 | 1549.5107 | 159.9454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1709.4561 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 1709.4561 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 54 | UO-AMR-ETGIS (C) |  |  | NA | PG&E has implemented ETGIS Editor on Esri and Schneider Electric ArcFM 10.2.1 and ETViewer using ArcGIS JS API on operating systems window 2008 R2 and RDBMS 11g, which provides Electric Transmission data capture on ET Editor and viewing asset on the web browser. The technology and infrastructure being used in ETGIS is no longer supported by the product vendor and it is in extended support. Also, the legacy systems are not capable enough to meet future needs and can cause performance issues or even outage of systems, potentially impacting the ability of PG&E employees to perform work. The objective of this program is to upgrade and re-architect the operating system, database, and GIS software by adopting upgraded versions of Esri and Schneider suites of products to improve user experiences. - Build new infrastructure to migrate existing ETGIS - Install Windows OS 2016 (or 2019 is available) - Install ArcGIS, ArcFM, and FME software on new infrastructure - Migrate all ETGIS related databases to new environment - Business functionality for Editor and Viewer will remain the same - Test ArcGIS | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5797622 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2022-12-29 | NA | FALSE | NA | NA | 4486.5451 | 4486.5451 | 0 | 0 | 1777.4 | 2721.6812 | -12.5361 | 0 | 0 | 0 | 0 | 0 | 0 | 4486.5451 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 4499.0812 | -12.5361 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 55 | PLS CADD Ph2 (CAP) |  |  | NA | PLS-CADD Ph2 continues the improvements and integration for Transmission projects delivered in Phase 1. The major areas of improvement are: 1. Integrating with additional applications, including Joint POle SAP, Job Force, and other work management and imaging applkications 2. Further support compliance activities (FERC and CPUC) 3. Deliver a new set of Capital Accounting cost allocations 4. Retire FFE and spreadsheets used by Transmission engineers | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5806061 | NA | NA | NA | 2F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 3 | NA | NA | 2025-12-22 | NA | FALSE | NA | NA | 2198.3773 | 3196.3773 | 0 | 0 | 0 | 0 | 1994.2331 | 687.1442 | 515 | 0 | 0 | 0 | 0 | 1994.2331 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1994.2331 | 376.1318 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 56 | STAR for Transmission Line CAP |  |  | NA | STAR is currently part of the Asset Data Foundation (ADF) program as PG&E’s first-of-its-kind unified Transmission & Distribution Asset data set where attributes are defined, sources are known, and data pipelines are established and governed. Planning Order 5784102 contains costs associated with Electric Transmission work only. By linking multiple utility systems of record into one data warehouse using the AWS cloud platform, STAR’s mission is to operationalize electric asset intelligence at lower cost and greater repeatability with more trustworthy analytical results for wildfire risk reduction. Two primary data products that PG&E is currently developing that leverage STAR include the Electric Transmission Operability Assessment (OA) Tool and Probability of Asset Failure (PAF). OA is an engineering model that calculates Electric Transmission structure fragility and aids in the determination of Electric Transmission lines within scope during PSPS events. PAF is an Electric Transmission Asset tool that will help Asset Strategy prioritize maintenance and replacement of assets such as conductors, insulators, structures and switches. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5784102 | NA | NA | NA | 2F | NA | NA | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-06-15 | 2021-06-30 | Project Design | FALSE | 11773 | NA | 6411.3272 | 6411.3272 | 2190.8209 | 2853.9102 | 1366.5961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6411.3272 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 4047.4644 | 2363.8628 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 57 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5788501 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2021-03-26 | NA | FALSE | NA | NA | 2103.2871 | 2103.2871 | 0 | 1456.3348 | 646.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2103.2871 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 2103.2871 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 58 | TO Radio System Expansion CAP |  |  | NA | FT - SCADA Radio Capacity and Reliability Improvements (TO) 2022 Project/Work Description: This project migrates SCADA RTUs at substations that are on the ODN and migrated away from DSO leases or private 4 Wire circuits. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | RBPPF - TBD | No | 5750578 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 3 | NA | NA | 2024-07-30 | NA | TRUE | NA | NA | 7491.4112 | 7866.9646 | 342.802 | 136.0019 | 251.3299 | 529.7729 | 540.9517 | 752.9249 | 412 | 0 | 0 | 0 | 0 | 7443.4863 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 271.1594 | 0.05834 | 973.047 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [Year of BC] Job Estimate serves as Utility Approval. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 59 | Sys-Insp WF-Mitigation-ET (C) |  |  | NA | The System Inspections organization in Wildfire Risk has an annual workplan that requires a technology suite of applications to appropriately document the detailed overhead inspection of Electric Transmission and Distribution structures. This is accomplished using Inspect Mobile, Engage Web, Maintenance Plan Management Tool, and SAP/BW applications. The current System Inspections program requires annual updates to the detailed overhead inspection checklist, modifications to the data collected, updates to the process, data clean-up and data requests. The proposed scope ensures that PG&E continues to enhance the applications for the multitude of needs in the system inspection process. This technology is directly supporting the Wilfire Mitigation program | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5798268 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2021-11-30 | NA | FALSE | NA | NA | 1057.5714 | 1057.5714 | 0 | 0 | 1057.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1057.5714 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 1057.5714 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 60 | Sys-Insp-WF-Mitigation 21-22 ET (C) |  |  | NA | The System Inspections Wildfire Mitigation Program Carryover project supports the Wildfire Mitigation Program.. The current Inspect, Engage, MPMT applications have released an MVP in 2020. The current System Inspections program requires annual updates to the detailed overhead inspection checklist including impacts to Inspect Mobile application, Engage Web Portal, MPMT, SAP and BW. The proposed scope ensures that we are continuing to better the applications for the multitude of needs in the system inspection process with special focus on 1) The ability to quickly identify and efficiently assign work, 2) Quicker completion and data throughput, 3) Making planning easier and reducing human error with better detective controls. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5798270 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2024-03-30 | NA | TRUE | NA | NA | 3492.7287 | 4366.4686 | 0 | 0 | 630.1012 | 1692.4567 | 1023.9163 | 550.9944 | 469 | 0 | 0 | 0 | 0 | 3346.4743 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2525.6596 | 1065.3057 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 61 | WSIP: Trans Support Structures (C) TO |  |  | NA | The Transmission Support Structures (TSS) software pulls all structure data related to transmission poles and towers from six different PG&E internal and external sources into a single unified view of the asset. PG&E staff use the unified view to model transmission structures more quickly and accurately, and to automatically populate other asset systems of record. The pole/tower load calculation results are maintained in the PG&E Transmission GIS application; and reports of the calculations and safety factors are produced per regulatory requirements. The TSS application creates a closed loop between SAP, Transmission GIS, and TSS structure modeling to ensure that data are synchronized across all three, eliminating data inconsistencies that existed previously. As a result, processes for estimating, engineering, and mapping transmission structures are simplified and more efficient. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ TRUE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5779478 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-12-15 | 2020-09-17 | Project Design | FALSE | 4797 | NA | 5313.0542 | 5313.0542 | 1804.4533 | 1859.1172 | 0.1709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5313.0542 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 5312.8833 | 0.17086 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Wildfire Related] IT/Risk tool for Wildfire Mitigation support [Year of BC] Job Estimate serves as Utility Approval. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 62 | UO-AMR-Remote Sensing Data-CAP - Tran |  |  | NA | This project seeks a centralized, ESRI compatible platform that acts as a centralized coordinator of the various data sets, allowing for greater data access and minimizing duplication of remote sensing data capture. In addition, chosen platform would require an open API architecture, allowing for greater collaboration with external partners (labs, universities, vendors). Engineers will customize | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5797623 | NA | NA | NA | 2F | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 4 | NA | 2021-12-31 | 2025-12-30 | Project Design | TRUE | 4193 | NA | 1169.4994 | 1746.4994 | 0 | 0 | 148.1489 | 595.4254 | 405.9755 | 288.9496 | 308 | 0 | 0 | 0 | 0 | 1149.5498 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 63 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | NA | NA | NA | 5783312 | P.12020 | Electric Transmission Cyber Security Upgrade | 1 | 2F | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-11-15 | 2019-12-17 | NA | FALSE | 6992 | NA | 4588.4762 | 4588.4762 | 4566.7068 | 21.7695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4588.4762 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 4566.7068 | 21.7695 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 64 | PLS-CADD Integration (CAP) |  |  | NA | T-Line Engineering & Estimating has migrated to PLS CADD to perform design and estimating work. However, this tool is not currently integrated with SAP. The proposed solution is to integrate PLS CADD with SAP to streamline material ordering, cost estimating, and settlement rule generation. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5797224 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-04-30 | NA | TRUE | NA | NA | 4566.752 | 4566.7521 | 0 | 0 | 726.0323 | 2947.0232 | 893.6966 | 0 | 0 | 0 | 0 | 0 | 0 | 4566.752 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 4566.752 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 65 | ElecOps - Bentley SAP Integratn P3 (C) |  |  | NA | Upgrade the existing Substation Product from Substation v8i to Substation Connect. Build interfaces to and from Substation Connect and SAP for Materials and Job Orders which is currently a manual process. In addition, replace the Engineering Materials Database and TSM&C which are Access databases to support end-to-end integrations. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5773843 | NA | NA | NA | 2F | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-06-15 | 2021-03-31 | Project Design | FALSE | 6390 | NA | 6404.4845 | 6404.4845 | 642.3865 | 2908.0783 | 773.8639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6404.4845 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 6404.4845 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 66 | ElecOps - CCSF WDT Load Controls CAP |  |  | NA | WDT (Wholesale Distribution Tariff) Interconnection workflow steps are time bound, mandated by FERC. The current process was fully manual and did not enable PG&E to fulfill these timelines. In 2019, PG&E identified at least 80 WDT non-conformance events related to City and County of San Francisco (CCSF). There was Excel-based tracking, no single system of the truth and no central records management, no automation in customer communications. Status tracking was done through weekly coordination meetings that requires multiple business unit coordination. This project alleviates these issues by automation & task management in SAP, online portal for customers for every action, Document management via Documentum, online payment, electronic signature, and automatic creation of FERC Contracts. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5779319 | NA | NA | NA | 2F | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-03-31 | 2022-12-15 | Project Design | FALSE | NA | NA | 9575.7583 | 9575.7583 | 3069.4407 | 4218.5753 | 930.342 | 721.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9575.7583 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 7910.7267 | -0.62744 | 1665.6591 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 67 | ET Composite Model - CAP |  |  | NA | Wildfire Risk Composite Models that Electric Operations has committed to the Federal Monitor and the CPUC. PO 5797825 represents the development of composite models to understand the fire ignition risk from Electric Transmission Assets. Multiple groups are developing sub-models which act as inputs to the composite model. Each sub-model accesses specific threat data. As of mid-2021, some sub-models exist and require some to little refinement. Once refined, these sub-models need to be composited into one comprehensive model for risk ranking of Electric Tansmission assets to make inspection priority decisions. Develop 3 sub-models for the Electric Wildfire Risk Composite Models: - Bird - 3rd Party - Animal (non-bird) Each sub-model will predict the probability of an outage being caused by the specific threat for a discrete portion of the system. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5797825 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-05-15 | NA | TRUE | NA | NA | 2128.0683 | 2128.0683 | 0 | 0 | 713.8071 | 1133.8875 | 280.3736 | 0 | 0 | 0 | 0 | 0 | 0 | 2128.0683 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 879.8182 | 1248.2501 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 68 | TRANSMISSION SCADA B/R (Break/Replace) |  |  | NA | Bucket for a web- or cloud-based relational database that would house all historical T-line and substation outage and relevant asset data so that users could easily perform custom queries to help with analyses related to improving grid reliability. The tables contained in this database would be designed to facilitate acquisition of specific outage data in a prescribed format required by the various regulatory agencies (e.g., CAISO, North America Transmission Forum (NATF), NERC-TADS) and for several benchmarking studies.Why:Currently historical outage data for electric transmission and substation are kept in various Excel workbooks which are not effectively linked with one another. Some, but not all, of these data are updated on our share point, but much of the data reside on an individual PC hard drive. This project would enable us to comply with the Records Information Management (RIM) process. Moreover, the current process is inefficient, prone to errors and does not enable users to acquire data and/or generate reports easily or automatically. The proposed system brings efficiency by automating data acquisition, minimizing errors associated with manual data entry and enabling many more users to gather data specific to their needs, including but not limited to report generation for both internal (executive leadership reliability meetings, RIBA score calculation, corrective action committees) and external (e.g., CAISO, NATF, NERC-TADS and various benchmarking studies) use. Note: This outage database is first phase of Transmission Data Management System, eventually this will house non outage related information as well. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5509119 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 3652.2846 | 3652.2846 | 108.0839 | 29.4666 | 35.3488 | 9.8842 | 32.1659 | 0.3379 | 0 | 0 | 0 | 0 | 0 | 3651.9467 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Year of BC] Job Estimate serves as Utility Approval. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 69 | SCADA Electric Trans - SCADA MS (LC M |  |  | NA | Bucket for ongoing ET&S Work Management System configuration changes and enhancements- Systems scope includes P6, Clarity, Click, SAP WM components (including tables and forms), EPPM, AMS, ET GIS, and Unit Based Planning used in Capital and Expense Work Mgmt Implement system enhancements and configuration changes to maintain alignment between work management systems and related business processes; This is critical to keeping the work management systems and tools aligned to business needs. | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5508146 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 23698.734 | 23698.734 | 1135.2527 | 2377.0228 | 1376.3086 | 168.1435 | 83.108 | 0 | 0 | 0 | 0 | 0 | 0 | 23698.734 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 309.4693 | 2262.535 | 1860.3721 | -1.115 | 2579.152 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [Year of BC] Job Estimate serves as Utility Approval. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 70 | Electric Transmission Cyber Security Upgrade |  |  |  |  | Other - Cybersecurity | Replace | NA | Other [See Notes] | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5541386 | NA | Electric Transmission Cyber Security Upgrade | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 5766.5872 | 5885.5873 | 281.7235 | 876.0705 | 2333.8457 | 1438.5655 | 768.7398 | 186.6423 | 0 | 0 | 0 | 0 | 0 | 5698.9449 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 3491.6397 | 1438.5655 | 768.7398 | 93.0747 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 71 | FT - Teleprotection (TO)_Multi-sites_C |  |  | NA | FT - Teleprotection (TO) Replace manufacturer discontinued Electric Protection Relays at third party Cogens. Ensuring continued safe and reliable operation of the electric lines. Approximately 4 sites. Risk: Working with 3rd parties can cause delays. Determine if this can be done in one year or needs to be done over two years and reallocate budget appropriately. | Other - IT | Replace | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5541385 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1747.6933 | 2709.6933 | 0 | 401.8891 | 194.4057 | 279.9285 | 636.156 | 921.314 | 276 | 0 | 0 | 0 | 0 | 1512.3793 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 72 | SCADA Electric Trans - SCADA Comm (LC |  |  | NA | Bucket to construct a redundant Telecom Transmission path from Helms PGP to Fresno Operations Center by constructing new microwave radio paths and overbuild of a fiber cable. | Other - IT | New | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5508145 | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 55717.3709 | 55717.3709 | 3956.2144 | 1479.3907 | 622.0181 | 22.9919 | 10.8986 | 0 | 0 | 0 | 0 | 0 | 0 | 55717.3709 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 5848.2537 | 1684.8603 | 2462.8564 | 696.7822 | 338.2225 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 73 | FT- FiberMaint/Replace Metcalf-Eden_TO_C |  |  | San Jose, Santa Clara ¦ Santa Clara | Metcalf Sub - Edenvale Sub. ADSS Replacement. Replace failing ADSS fiber cable between Metcalf Sub and Endenvale Sub. Certain spans of this cable have already fallen putting the public at risk. This cable carries critical core business circuits including but not limited to electric protection, electric and gas SCADA, and EMS. ( Total route = 5 miles) | Other - IT | Replace | NA | Other [See Notes] | IT | NA | 2024-03-18 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5791976 | T.0006243 | IO - Fiber Optic Maintenance and Replace | 1 | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-11-29 | NA | 2026-12-31 | NA | TRUE | NA | NA | 1037.3055 | 2886.3053 | 3.5806 | 156.1316 | -27.8757 | 708.8953 | 175.141 | 283.4325 | 576 | 1011 | 0 | 0 | 0 | 1015.873 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2026 | 0 | 74.8996 | -74.8948 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 74 | Midway: Repl Building |  |  | Buttonwillow CDP, Kern | The existing 500kV control building at Midway has deficiencies that prevent completion of in-flight and future projects. These deficiencies include wire trays that are filled to twice the allowable capacity in some locations, and overly congested outdoor-to-indoor building wiring egress points . PG&E project management, substation engineering, and the construction departments have met on-site on several occasions to review a variety of possible solutions and have determined that these deficiencies cannot be mitigated in a safe and reliable manner in the existing building. The recommended course of action is to implement future protection and control projects in a new modular building. The problem identification and solution is similar to Moss Landing (New modular building design is nearly complete)•The new building(s) will be designed to address single point vulnerabilities. The “System A” and “System B” relaying be placed in different buildings, or different rooms within the same building. •The building(s) will be sized for the ultimate substation plan with predetermined locations for equipment (Layout). •Use the Moss Landing 500 kV control building design as the go-by.•The dual battery system is not needed at this time (it’s not the acute issue that we are solving now), but the two buildings should be set-up to allow easy future implementation of a dual battery system (Reference Moss Landing DWG: 4131039)•Procure buildings that are ready for populating with protection and control racks. Unlike Moss Landing where the building will be delivered fully populated with Protection and Control equipment, each independent Midway project will fund and install the required bay protection and control racks within the new building by following a preplanned layout. | Substation - Modular Protection and Automation Control Building | Replace | T.0002454 ¦ T.0002455 ¦ T.0006402 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-15 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 kV | 707 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5782198 | T.0004292 | Midway: Repl 500k Building | 1 | 3F | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-08-10 | 2022-02-15 | 2023-03-15 | Workforce | TRUE | 7400 | NA | 18896.9328 | 19015.9718 | 297.0379 | 372.9435 | 2165.5461 | 11921.4298 | 3651.2437 | 588.02 | 0 | 0 | 0 | 0 | 0 | 18427.9518 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 18427.9519 | 983.7596 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 75 | Midway Bank 11 Relay Project |  |  | Buttonwillow CDP, Kern | The scope of the replacement includes installing new microprocessor relays following new 500/230 kV standard on Midway Bank 11. | Substation - Protection Relay | Replace | T.0004292 ¦ T.0002455 ¦ T.0006402 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-15 | 11 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 ¦ 230 kV | 245 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5773128 | T.0002454 | Midway Bank 11 Relay Project | 1 | 3F | NA | 2016 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2023-01-03 | 2022-08-31 | 2025-03-17 | Bundling Dependencies | TRUE | 5876 | NA | 12407.2663 | 15976.5457 | 269.8695 | 150.2692 | 383.0356 | 1521.738 | 9492.7167 | 1841.5419 | 2217.3356 | 0 | 0 | 0 | 0 | 11917.6682 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 76 | Midway Bank 13 Relay Project |  |  | Buttonwillow CDP, Kern | The scope of the replacement includes installing new microprocessor relays following new 500/230 kV standard on Midway Bank 13. | Substation - Protection Relay | Replace | T.0002454 ¦ T.0004292 ¦ T.0006402 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-15 | 22 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 ¦ 230 kV | 245 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5773129 | T.0002455 | Midway Bank 13 Relay Project | 1 | 3F | NA | 2016 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2022-07-01 | 2022-08-31 | 2024-09-03 | Bundling Dependencies | TRUE | 7500 | NA | 5076.3585 | 8268.9274 | 97.58 | 337.9909 | 506.9821 | 2370.3979 | 910.6538 | 3909.2044 | 0 | 0 | 0 | 0 | 0 | 4359.723 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 77 | TABLE MOUNTAIN: Repl 500 KV TM-RM RLY 2 |  |  | Butte | The scope of this project is to replace the line relays at Table Mtn. on the Round Mountain – Table Mountain #2 500kV Line as well as upgrade the operator interface (Install associated network architecture necessary to incorporate this line in existing HMI at both Round Mountain and Table Mountain). The newly installed relaying package will include two sets of line protection relays, (SEL-411L’s and GE L90’s), and breaker failure relays, (SEL 451’s). | Substation - Protection Relay | Replace | T.0002458 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-06 | 18 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 47.516 | NA | 500 kV | 978 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5773133 | T.0002459 | TM:ROUND MTN - TABLE MTN #2 | 1 | 3F | NA | 2016 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-12-14 | 2021-05-06 | 2021-04-25 | NA | FALSE | 3840 | NA | 3089.9712 | 3089.9712 | 422.5565 | 647.6603 | 1654.4045 | 52.677 | 3.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.9712 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 2542.4197 | 43.7656 | 2.8658 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 78 | Midway Los Banos #2 Relay Upgrade |  |  | Merced | The scope of this project is to replace the line relays on the Midway-Vincent #2 500kV Line and Los Banos-Midway #2 500kV Line at Midway substation only. The scope includes the upgrade of the operator interface on the Midway terminal of the Midway-Vincent 500kV line #2, consisting of installation of associated network architecture necessary to incorporate this line in existing HMI. | Substation - Protection Relay | Upgrade/Retrofit | T.0002454 ¦ T.0002455 ¦ T.0004292 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-06 | 11 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 53.2803 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 3 | No | 5802726 | T.0006402 | MIDWAY: REP VINCENT AND LB RELAYS | 2 | 3F | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-07-18 | NA | 2024-12-03 | NA | TRUE | NA | NA | 183.4008 | 849.4782 | 0 | 0 | 0 | 0 | 133.9611 | 257.9798 | 0 | 0 | 0 | 0 | 0 | 167.6902 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 79 | MIDWAY: REP VINCENT AND LB RELAYS |  |  | Buttonwillow CDP, Kern | The scope of this project is to replace the line relays on the Midway-Vincent #2 500kV Line and Los Banos-Midway #2 500kV Line at Midway substation only. The scope includes the upgrade of the operator interface on the Midway terminal of the Midway-Vincent 500kV line #2, consisting of installation of associated network architecture necessary to incorporate this line in existing HMI. | Substation - Protection Relay | Replace | T.0002454 ¦ T.0002455 ¦ T.0004292 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-15 | 32 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 kV | Not Available | 5a. Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5792705 | T.0006402 | MIDWAY: REP VINCENT AND LB RELAYS | 2 | 3F | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-06 | NA | 2025-12-03 | NA | TRUE | NA | NA | 776.3259 | 10072.9651 | 0 | 0 | 0 | 183.7951 | 555.2989 | 3835.7152 | 2885.9952 | 0 | 0 | 0 | 0 | 739.094 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 80 | ROUND MOUNTAIN: Repl 500 KV RM-TM RLY 2 |  |  | Round Mountain CDP, Shasta | The scope of this project is to replace the line relays on the Round Mountain – Table Mountain #2 500kV Line at Round Mtn.as well as upgrade the operator interface (Install associated network architecture necessary to incorporate this line in existing HMI). The newly installed relaying package will include two sets of line protection relays, (SEL-411L’s and GE L90’s), and breaker failure relays, (SEL 451’s). | Substation - Protection Relay | Replace | T.0002459 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-06 | 34 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 500 kV | 978 | 3. Emergency Preparedness | Not Available | NA | NA | 5773132 | T.0002458 | RM:ROUND MTN - TABLE MTN #2 | 1 | 3F | NA | 2016 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-12-16 | 2020-12-31 | 2021-04-25 | NA | FALSE | 3630 | NA | 2090.0015 | 2110.0015 | 337.5884 | 403.1211 | 1187.4596 | 11.9394 | 4.5855 | 21.4768 | 0 | 0 | 0 | 0 | 0 | 2088.5247 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1719.3296 | 9.8279 | 3.7745 | 1.2156 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 81 | ROUND MOUNTAIN: Repl 500 KV Relay |  |  | Round Mountain CDP, Shasta | This course of action directly correlates to PG&E’s vision and values through the company’s goal of improving reliability. Replace the Round Mountain – Table Mountain #1 500kV Project. | Substation - Protection Relay | Replace | T.0002457 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-06 | 37 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 500 kV | 978 | 3. Emergency Preparedness | NA | NA | NA | 5773130 | T.0002456 | RM:Round Mountain # Table Mountain #1 | 1 | 3F | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-16 | 2018-08-24 | 2019-03-05 | Clearances | FALSE | 2160 | NA | 2155.1576 | 2155.1576 | 958.0094 | -0.2636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2155.1576 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1849.4111 | -0.16303 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 82 | TABLE MOUNTAIN: Repl 500 KV TM-RM RLY 1 |  |  | Butte | This course of action directly correlates to PG&E’s vision and values through the company’s goal of improving reliability. Replace the Round Mountain – Table Mountain #1 500kV Project. | Substation - Protection Relay | Replace | T.0002456 | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-06 | 37 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 47.516 | NA | 500 kV | 978 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5773131 | T.0002457 | TM:Round Mountain # Table Mountain #1 | 1 | 3F | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-04 | 2018-08-08 | 2019-03-05 | Project Design | FALSE | 2965 | NA | 3303.0768 | 3303.0768 | 1421.61 | -0.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3303.0768 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 2895.1403 | 0.0481 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 83 | LOS BANOS: Upgrade ML 500 KV Remote End |  |  | Monterey | This project will resolve current configuration issues and address reliability concerns. This project will rebuild Moss Landing 500kV Substation within the existing substation fence line. The project will replace the existing 500kV breakers and switches in a BAAH configuration, and upgrade the protection schemes. This will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-12 | 34 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 41.3213 | NA | 500 kV | 321 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5760484 | T.0000678 | MOSS LANDING 500KV Upgrade | 6 | 3F | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-03 | 2017-10-13 | 2020-06-22 | Bundling Dependencies | FALSE | 46400 | NA | 3033.8794 | 3033.8794 | 630.8449 | 1939.2035 | 45.1713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3033.8794 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 2644.4293 | 39.7381 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 84 | METCALF: Upgrade ML 500 KV Remote End |  |  | Santa Clara | This project will resolve current configuration issues and address reliability concerns. This project will rebuild Moss Landing 500kV Substation within the existing substation fence line. The project will replace the existing 500kV breakers and switches in a BAAH configuration, and upgrade the protection schemes. This will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-13 | 34 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 500 kV | 321 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5769038 | T.0000678 | MOSS LANDING 500KV Upgrade | 6 | 3F | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-03 | 2019-11-14 | 2020-06-29 | Bundling Dependencies | FALSE | 46400 | NA | 5814.248 | 5956.3746 | 1204.4993 | 4144.1574 | -86.2355 | 13.1268 | 0 | 142.4146 | 0 | 0 | 0 | 0 | 0 | 5813.9601 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 5192.8303 | -75.6837 | -162.5017 | 0 | 0.24369 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 85 | MOSS LANDING: Inst 500 KV Ctrl Building |  |  | Monterey | This project will resolve current configuration issues and address reliability concerns. This project will rebuild Moss Landing 500kV Substation within the existing substation fence line. The project will replace the existing 500kV breakers and switches in a BAAH configuration, and upgrade the protection schemes. This will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Modular Protection and Automation Control Building | Replace | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-12 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 41.3213 | NA | 500 kV | 321 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5760568 | T.0000678 | MOSS LANDING 500KV Upgrade | 6 | 3F | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-05-17 | 2017-06-30 | 2020-06-22 | Bundling Dependencies | FALSE | 46400 | NA | 14301.5367 | 14301.5367 | 4460.3472 | 3430.4058 | 1121.5607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14301.5367 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 13037.2357 | 1108.3708 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 86 | PACIRAS 500kV VGCC - Fern Road |  |  | Round Mountain CDP, Shasta | This project will support connection of the new 500kV substation between Round Mountain (RM) and Table Mountain (TM) Substations to the PG&E system. The new 500kV substation, installed by the third party (LS Power), is needed for Northern Area Voltage Support. Dynamic Voltage Support (+/- 500MVAR) is required to address both high and low voltages in this area. This project will connect both RM to TM 500kV lines to the new substation. In addition, this project will modify Round Mountain 500kV Series Capacitor Banks 3&4 Reactance to 5.28 ohm, and Table Mountain 500kV Series Capacitor Banks 1&2 Reactance to 36.32 ohm. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - 500 kV Relay Replacement | NA | 2024-03-06 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5798639 | T.0006815 | Round Mountain Area 500kV Dynamic React | 5 | 3F | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-14 | 2024-04-30 | 2024-12-12 | Construction Delays | TRUE | 77900 | NA | 10.373 | 1222.4113 | 0 | 0 | 0 | 1.0104 | 3.2596 | 1201.5372 | 16.604 | 0 | 0 | 0 | 0 | 4.2701 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 87 | Ames: Repl 115 kV Bus Diff Relay |  |  | Mountain View, Santa Clara | Ames serves as a critical 115kV switching station with (4) lines to Newark, (2) lines to Ravenswood, (2) lines to Monta Vista and (2) lines to customer owned NASA Ames Research facility. (1) of the lines to Newark is looped through Ames Distribution substation and the (2) lines to Monta Vista are looped through Whisman and Mountain View substation respectively. Mountain View and Whisman substations serve 37,600 customers and 7,700 customers respectively. Google is currently planning a major expansion in the area. This year, transmission planning decided to permanently reconnect lines to Whisman and Mountain View substation(s) into Ames 115kV bus. As a result, the fault duty has increased and exceeds over 40kA. Existing bus differential scheme was originally installed in 1973 and the current selector switches are installed in an outdoor cabinet. Due to exposure to weather and lack of scheduled maintenance activity on these outdoor cabinets number of issues have surfaced system wide that could potentially affect performance of the scheme. Ames being a critical substation, system protection recommends to install redundant bus differential scheme(s) at this facility to provide safe and reliable operating conditions. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-05 | 34 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.8814 | NA | 115 kV | 131 | 5a. Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5782002 | T.0004239 | Ames: Repl 115 kV Bus Diff Relay | 1 | 3F | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-07-28 | NA | 2027-11-23 | NA | FALSE | NA | NA | 0 | 2998.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 88 | Applied Materials: Replace Bus Diff Rel |  |  | Sunnyvale, Santa Clara | Applied Materials substation is part of the transmission path between Newark and Monta Vista substation that serves number of customers at Britton, Lockheed 2 substations as well as other critical transmission customers including Lockheed Martin and Applied Materials. Existing KBCH relays used for bus protection are 1998 vintage and are at the end of their life time. KBCH relays are obsolete relays as field technicians do not have necessary software to interface with the relays for maintenance and troubleshooting purpose(s). Besides, existing scheme implementation creates challenges during relay maintenance activity as trip relays associated with bus protection scheme are also used as part of Breaker Fail scheme. Existing bus protection scheme is not redundant and redundant bus protection is deemed essential for safe and reliable transmission system per current standards. Considering these factors, system protection recommends to upgrade Bus Protection at Applied Materials substation per current standards. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-05 | 26 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.0337 | NA | 230 kV | 133 | 5a. Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5783118 | T.0004401 | Applied Materials: Replace Bus Diff Rel | 1 | 3F | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-12-07 | NA | 2027-04-02 | NA | FALSE | NA | NA | 36.0625 | 2567.6286 | 0 | 23.2168 | 7.7014 | 2.2491 | 2.4735 | 2.6057 | 0 | 0 | 0 | 0 | 0 | 35.6407 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 89 | EASTSHORE: REPL CB322 and CB332 Relays |  |  | Hayward, Alameda | Eastshore-Mt Eden #1 and #2 lines are short line slightly longer than 1.00 mile. For such a short line, one set of line differential relay plus another set of overcurrent relay configuration does not meet current PG&E protection standard and results in significant coordination problems when line differential protection is not available for any reason (e.g., relay or communication channel maintenance or failure). The primary relay L90 is the only relay that provides high speed fault clearance. If L90 is out of service due to relay/channel failure or scheduled maintenance, etc., the line is only protected by non-pilot phase & ground overcurrent relays, which are inherently difficult to coordinate for the short line protection in this area, and have delayed fault clearance time. This is especially true for phase overcurrent protection, which have to be set above max load current. The sensitivity, selectivity and speed of the existing protection is not at the level desirable for transmission lines in this particular area. In addition, the SEL-267 is an older vintage product. It is close to the end of the useful life. Coordination problems during the time of differential protection unavailability might result in unnecessary customer loss. System Protection recommends that the backup relays at both ends be replaced with new SEL line differential relays with separate communication channel from the primary relay. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-11 | 24 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.9849 | NA | 115 kV | 177 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5760302 | T.0001220 | EASTSHORE-MT EDEN #1&#2 115KV RELAY | 2 | 3F | NA | 2014 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-05-24 | 2023-04-12 | 2023-07-05 | NA | TRUE | 4419 | NA | 2037.0984 | 2046.0639 | 0.0356 | 82.2415 | 176.3088 | 1645.7254 | 110.7066 | 30.3709 | 0 | 0 | 0 | 0 | 0 | 2015.6931 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1849.1137 | 24.0014 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $3 Mil -$5 Mil ¦ $3 Mil -$5 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 90 | Mt Eden: REPL CB142 and CB182 Relays |  |  | Hayward, Alameda | Eastshore-Mt Eden #1 and #2 lines are short line slightly longer than 1.00 mile. For such a short line, one set of line differential relay plus another set of overcurrent relay configuration does not meet current PG&E protection standard and results in significant coordination problems when line differential protection is not available for any reason (e.g., relay or communication channel maintenance or failure). The primary relay L90 is the only relay that provides high speed fault clearance. If L90 is out of service due to relay/channel failure or scheduled maintenance, etc., the line is only protected by non-pilot phase & ground overcurrent relays, which are inherently difficult to coordinate for the short line protection in this area, and have delayed fault clearance time. This is especially true for phase overcurrent protection, which have to be set above max load current. The sensitivity, selectivity and speed of the existing protection is not at the level desirable for transmission lines in this particular area. In addition, the SEL-267 is an older vintage product. It is close to the end of the useful life. Coordination problems during the time of differential protection unavailability might result in unnecessary customer loss. System Protection recommends that the backup relays at both ends be replaced with new SEL line differential relays with separate communication channel from the primary relay. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-05 | 32 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.6074 | NA | 115 kV | Not Available | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5785439 | T.0001220 | EASTSHORE-MT EDEN #1&#2 115KV RELAY | 2 | 3F | NA | 2014 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-05-24 | 2023-04-12 | 2023-10-10 | Prioritization | TRUE | 4419 | NA | 2584.2366 | 2594.7936 | 0 | 74.5363 | 176.2458 | 1849.084 | 459.9387 | 34.9887 | 0 | 0 | 0 | 0 | 0 | 2559.8049 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2426.2533 | 37.3807 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $3 Mil -$5 Mil ¦ $3 Mil -$5 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 91 | SAN LEANDRO: Replace CB 152 Line Relays |  |  | San Leandro, Alameda | Edes CEY/CEY/IBC/IBC/RC are E/M phase distance and ground overcurrent relays, whose performance and functionality are not as good as the latest digital relays. They have no fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers.Replace the following relays with dual SEL-311C per latest PG&E standard:•Edes CB 112 Device 121Z1-1, 121Z2BU-1, 167N-1, 167NBU-1, and 179-1 (CEY, CEY, IBC, IBC, RC – Electromechanical relays) installed in 1974 oThis will be a complete panel replacement.•San Leandro U CB 152 Device 121/167N-4, 121Z1-4, 121Z2BU-4, 167N-4, 167NBU-4, 150-4 and 179-4 (SEL-221H, CEY, CEY, JBCG, JBCG, PJC, RC) installed in 1971oThis will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-07 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2372 | NA | 115 kV | 439 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5779580 | T.0003870 | Oakland J-San Leandro U Relay | 3 | 3F | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-12-14 | 2020-08-30 | 2021-03-01 | Bundling Dependencies | FALSE | 587 | NA | 1050.0771 | 1050.0771 | 124.7251 | 158.7928 | 687.0022 | 36.9274 | 0.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 1050.0771 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 903.5942 | -4.9071 | 0.04122 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 92 | ARCATA: Repl Bus Total OC PSPS |  |  | Arcata, Humboldt | Existing bus protection does not coordinate with remote end line relays for 60kV faults. System Protection recommends upgrade the 60kV bus protection from bus total overcurrent to bus differential protection. System Protection recommends the following: • Replace the existing SEL 501 bus TOC scheme with two (2) SEL 487B bus differential relays (1 panel of two 3-phase relays for redundancy); see Electra PH as a go-by (dwg #s 401348, 4123327, 4148424, 4148423, 432512). These relays would need to be wired to the high-side bank CTs (same CTs shared with the bank relays), and the scheme would have to be modified to enable the SW 36 pallet contact to drive the bus differential between 2 sections, and 1 overall section mode. • Upgrade the existing GE T60 bank relays for Banks 1 & 2 to firmware version 7.2x which has distance elements that include a reverse directionality option and VT fuse fail logic. Wire in 3-phase PTs from the 12kV source, and use both low-side phase distance elements and low-side ground overcurrent elements to speed up tripping for 12kV bus faults. • Install two (2) SEL 311C relays, one on the low-side of Bank 1 and one on the low-side of Bank 2. These relays are necessary to achieve redundant low-side phase distance protection which is not available in the SEL 387E relay. Wire in 3-phase PTs from the 12kV source, and use both low-side phase distance elements and low-side ground overcurrent elements to speed up tripping for 12kV bus faults. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-06 | 14 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.53072 | NA | 60 kV | Not Available | Not Available | Not Available | Tier 3 | No | 5795424 | T.0007077 | ARCATA: Repl Bus & Bk Relays-PSPS | 1 | 3F | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-06-05 | NA | 2025-08-25 | NA | TRUE | NA | NA | 317.2582 | 4310.2722 | 0 | 0 | 0 | 117.2476 | 185.693 | 1575.1905 | 1809.425 | 0 | 0 | 0 | 0 | 302.9407 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 93 | LA PALOMA: Repl PACIRAS GG3 & GG Relays |  |  | Buttonwillow CDP, Kern | Existing PACIRAS equipment for Midway Gen Groups (1 through 5) consists of RFL transfer trip and RFL telemetry equipment that is in need of life cycle replacements. This equipment is located at Midway and at the Gen Group tripping locations. Analog communication circuits are used for the existing transfer trip and megawatt telemetry from the Gen Group sites to Midway. Midway is a hub where the analog equipment is connected to RFL GARD 8000 digital equipment that communicate to RFL GARD 8000 transceivers at SFGO and VGCC. This project proposes to replace all of the RFL equipment with GE N60 relays at the Gen Group tripping locations and at SFGO and VGCC, and to install digital communication circuits from SFGO and VGCC to the Gen Group tripping locations. This project is being driven by the need for life cycle replacements and deteriorated/failing equipment. Additionally, this work is tied into the relocation of RAS controllers from SFGO to Rocklin and is part of “pre-migration” work to replace RAS RFL equipment with GE N60 relays. Gen Groups 3 and 5 (to La Paloma) are the highest priority due to the frequent transducer failures for the PACIRAS megawatt telemetry. | Substation - Protection Relay | Replace | T.0006190 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-15 | 22 | Lifecycle Replacement Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 230 kV | Not Available | 5a. Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5790394 | T.0006261 | Midway Sub 230kV Replace PACIRAS | 10 | 3F | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-08-01 | 2023-08-31 | 2024-10-11 | Prioritization | TRUE | 11400 | NA | 622.509 | 1255.3851 | 0 | 19.1236 | 79.6653 | 205.2663 | 248.5586 | 680.7205 | 22.0507 | 0 | 0 | 0 | 0 | 552.6139 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 94 | SUNRISE: Replace PACIRAS GG 4 Relays |  |  | Buttonwillow CDP, Kern | Existing PACIRAS equipment for Midway Gen Groups (1 through 5) consists of RFL transfer trip and RFL telemetry equipment that is in need of life cycle replacements. This equipment is located at Midway and at the Gen Group tripping locations. Analog communication circuits are used for the existing transfer trip and megawatt telemetry from the Gen Group sites to Midway. Midway is a hub where the analog equipment is connected to RFL GARD 8000 digital equipment that communicate to RFL GARD 8000 transceivers at SFGO and VGCC. This project proposes to replace all of the RFL equipment with GE N60 relays at the Gen Group tripping locations and at SFGO and VGCC, and to install digital communication circuits from SFGO and VGCC to the Gen Group tripping locations. This project is being driven by the need for life cycle replacements and deteriorated/failing equipment. Additionally, this work is tied into the relocation of RAS controllers from SFGO to Rocklin and is part of “pre-migration” work to replace RAS RFL equipment with GE N60 relays. Gen Groups 3 and 5 (to La Paloma) are the highest priority due to the frequent transducer failures for the PACIRAS megawatt telemetry. | Substation - Protection Relay | Replace | T.0006190 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-15 | 22 | Lifecycle Replacement Analysis | Other - Deferral | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 230 kV | Not Available | 5a. Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5790395 | T.0006261 | Midway Sub 230kV Replace PACIRAS | 10 | 3F | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-01 | 2023-08-31 | 2024-11-18 | Prioritization | TRUE | 11400 | NA | 354.6833 | 1251.5311 | 0 | 11.8747 | 70.1338 | 103.0893 | 155.852 | 894.7096 | 15.8716 | 0 | 0 | 0 | 0 | 340.9498 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 95 | EM: HAMILTON BRANCH: REPL CB 12 RELAYS |  |  | East Shore CDP, Plumas | Hamilton Branch CB12 protects the Hamilton Branch-Chester 60kV line branch of the Caribou-Westwood 60kV line. This is the only source to Chester Sub and Collins Pine. CB12 is currently protected by two (2) existing SEL-167 relays that were both installed in 2004. These relays are nearing the life expectancy of a microprocessor relay. These relays have been showing failure and have been experiencing intermittent relay fail alarm. System protection recommends replacing these relays with the current line protection standard. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-13 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.1317 | NA | 60 kV | 720 | 3. Emergency Preparedness | Not Available | NA | NA | 5781587 | T.0004191 | EM: HAMILTON BRANCH: Repl CB 12 Relays | 1 | 3F | NA | 2018 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-10-01 | 2020-10-09 | 2020-10-09 | NA | FALSE | 1220 | NA | 1200.8724 | 1200.8724 | 156.7448 | 970.9856 | 44.0404 | 7.4128 | 0.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 1200.8724 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1193.151 | 6.4683 | -103.4025 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 96 | CARIBOU PH 1: Repl BF Project |  |  | Plumas | install a breaker failure relay to insure people safety, system reliability and asset protection in case CB 62 failed to trip under a fault condition. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-14 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.96252 | NA | 60 kV | 430 | 3. Emergency Preparedness | Not Available | NA | NA | 5758501 | T.0000829 | CARIBOU PH 1 BF PROJECT | 1 | 3F | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-08-03 | 2018-11-19 | 2020-09-29 | Prioritization | FALSE | 989 | NA | 1295.1783 | 1295.1783 | 140.9624 | 783.547 | 7.8863 | 2.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1295.1783 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 1285.1689 | 7.8863 | 2.123 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 97 | MARTIN: Upgrade 115 KV Differential |  |  | Brisbane, San Mateo | Install Martin 115kV Bus Section “E”, “F” and “G” SET B bus 1 & 2 differential scheme with the current Standard integrated SEL-587Z scheme. | Substation - Protection Relay | Replace | NA | Address Results of Protection Studies | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-20 | 15 | Protection Studies | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 18.2105 | NA | 115 kV | 483 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5764431 | T.0001236 | MARTIN 115KV DIFFERENTIAL UPGRADE | 1 | 3F | NA | 2015 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-12-17 | 2023-06-12 | 2024-12-30 | Prioritization | TRUE | 8911 | NA | 6033.9604 | 8472.7269 | 3.771 | 267.6793 | 2553.3688 | 3062.7952 | 68.819 | 2420.8779 | 95.4157 | 0 | 0 | 0 | 0 | 5956.4333 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 98 | Los Estero 115kV Differential upgrade |  |  | San Jose, Santa Clara | Install redundant bus differential scheme Los Estero 115kV Bus. | Substation - Protection Relay | Replace | NA | Address Results of Protection Studies | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-12 | 21 | Protection Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.1703 | NA | 115 kV | 483 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5521171 | T.0003192 | Los Estero 115kV Differential upgrade | 1 | 3F | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-02-23 | NA | 2026-10-09 | NA | FALSE | NA | NA | 98.4052 | 4401.1155 | 0 | 0 | 18.7081 | 75.8084 | 3.8886 | 0 | 1814.5928 | 0 | 0 | 0 | 2010.538 | 98.4052 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2026 ¦ 2027 | 0 | 0 | 12.4721 | 50.5389 | 2.5924 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 99 | CHICO A: Repl CB 42 Relays |  |  | Chico, Butte | Install the emergency replacement of CB 42 RELAYSat CHICO A SUB, which failed on or around 04/23/2018 | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-05 | 33 | Lifecycle Replacement Analysis | Other - Deferral | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.90513 | NA | 60 kV | 720 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5781579 | T.0004183 | CHICO A: Repl CB 42 Relays | 1 | 3F | NA | 2018 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-10-04 | 2021-11-18 | 2021-11-18 | NA | FALSE | 1038 | NA | 1018.4414 | 1018.4414 | 166.6469 | 289.9917 | 453.7885 | 93.9161 | 0.1718 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.4414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 924.3535 | 93.9161 | -75.1785 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 100 | APM: Applied Materials |  |  | Sunnyvale, Santa Clara | Line relays at Applied Materials substation were installed in 1998 and the relays include LFCB 102, SEL-321, BE1-BPR and SEL-279. Applied Materials – Britton 115kV line is 1.0 mile long with a section of underground cable; however, the line is protected by one level of high speed protection. The lines in Newark – Monta Vista corridor are mutually coupled and pose coordination challenges. LFCB relays belong to early generation microprocessor relays and do not provide backup line protection functions. Other existing relays on the line terminal are older vintage approaching end of their life which include obsolete Basler BPR and SEL-279 relays. System protection recommends upgrading the line terminal per currently approved protection standards to provide redundant line current differential protection for the line. Require upgrading remote terminal line relays at Britton substation. | Substation - Protection Relay | Replace | T.0003266 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-05 | 27 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.0337 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5776119 | T.0003265 | APM: APM-Britton Relay 74013112 | 1 | 3F | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-06-26 | NA | 2026-11-23 | NA | TRUE | NA | NA | 57.671 | 983.3608 | 0 | 0 | 0 | 45.1963 | 10.0251 | 4.7442 | 0 | 0 | 0 | 0 | 917.3254 | 56.4257 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 101 | BRITTON: Repl 115 KV APM-Britton Relay |  |  | Sunnyvale, Santa Clara | Line relays at Applied Materials substation were installed in 1998 and the relays include LFCB 102, SEL-321, BE1-BPR and SEL-279. Applied Materials – Britton 115kV line is 1.0 mile long with a section of underground cable; however, the line is protected by one level of high speed protection. The lines in Newark – Monta Vista corridor are mutually coupled and pose coordination challenges. LFCB relays belong to early generation microprocessor relays and do not provide backup line protection functions. Other existing relays on the line terminal are older vintage approaching end of their life which include obsolete Basler BPR and SEL-279 relays. System protection recommends upgrading the line terminal per currently approved protection standards to provide redundant line current differential protection for the line. Require upgrading remote terminal line relays at Britton substation. | Substation - Protection Relay | Replace | T.0003264 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-05 | 27 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.4779 | NA | 115 kV | 483 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5776120 | T.0003266 | Britton: APM-Britton Relay 74013113 | 1 | 3F | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-06-26 | NA | 2026-11-23 | NA | FALSE | NA | NA | 45.2956 | 1005.1862 | 0 | 0 | 0 | 37.8564 | 6.5265 | 3.6388 | 0 | 0 | 0 | 0 | 936.7465 | 44.3829 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 102 | Livermore: Replace 60kV Relays |  |  | Livermore, Alameda | Livermore CB 52 System protection recommends that line relays and reclosing/breaker fail relays will be replaced with two new SMP standard panels. Livermore CB 62 System protection recommends that these relays will be replaced with new line relay protection package per the latest standard with two new SMP standard panels.Livermore CB 42 System protection recommends that line relays and reclosing/breaker fail relays will be replaced with two new SMP standard panels.Livermore SW 77 System protection recommends that reclosing relay will be replaced with one new SMP standard panel.Livermore 60kV Bus Total OCSystem protection recommends that these relays will be replaced with new bus total overcurrent protection package per the latest standard with one new SMP standard panel.Livermore Bank 2 (PO 5778221 Distribution Project) System protection recommends that these relays be replaced with new distribution bank protection package per the latest standard with one new SMP standard panel. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-05 | 25 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.60395 | NA | 60 kV | 718 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5784220 | T.0003653 | Livermore Sub Replace Relays and CB 1104 | 1 | 3F | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-01-21 | NA | 2025-05-22 | NA | TRUE | NA | NA | 358.633 | 2141.2107 | 0 | 0 | 16.785 | 257.7708 | 75.5909 | 442.5766 | 1344.4739 | 0 | 0 | 0 | 0 | 350.1467 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 103 | MAGUNDEN: Repl CB 22 Relay |  |  | East Niles CDP, Kern | Magunden CB 22 has two sets of electromechanical (EM) directional OC relays, installed in 1970, protecting the 70kV line both directions – the Kern-Magunden 70kV line and the Kern Canyon-Magunden-Weedpatch 70kV line. There are coordination issues with phase distance relays. In addition, the relays are at the end of their useful life cycle. The performance and functionality are not as good as the latest digital relays. They have no fault recording capability, do not provide self-monitoring, and will not issue alarms when it fails. Due to the lack of self-monitoring, the relay needs shorter maintenance cycle. They are no longer adequately supported by the manufacturers. Recommend replacing the EM relays with two sets of SEL 411L relays with phase distance and directional ground OC elements. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-07 | 55 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.2256 | NA | 70 kV | 718 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5776248 | T.0003320 | Magunden CB 22 Relay Project | 1 | 3F | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-04-08 | NA | 2026-08-25 | NA | FALSE | NA | NA | 419.2434 | 2075.8011 | 1.7714 | 1.6611 | 47.4142 | 299.0127 | 64.854 | 30.0468 | 0 | 0 | 0 | 0 | 0 | 414.7134 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 104 | NEWARK: Upgrade 115 KV Bus Differential |  |  | Fremont, Alameda | Newark 115kV bus is one of the most critical busses in the system as identified by Transmission Planning and Transmission Operations. If existing bus differential is cut our or fails to clear the fault, remote backup protection cannot clear the fault fast enough to maintain stability. NERC requirement for TPL (planning) standard requires the fully redundant bus protection on all the critical busses. Based on that, System Protection strongly recommends to add fully redundant bus differential protection for Newark 115kV bus sections D, E and F. This installation will significantly improve reliability of bus protection and eliminate existing deficiencies related to maintenance and clearances. | Substation - Protection Relay | Replace | NA | Address Results of Protection Studies | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-08 | 16 | Protection Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 27.7611 | NA | 115 kV | 177 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5764434 | T.0001238 | NEWARK 115KV BUS DIFFERENTIAL | 1 | 3F | NA | 2015 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-02-13 | NA | 2028-07-28 | NA | FALSE | NA | NA | 153.4984 | 23305.137 | 0 | 4.1365 | 41.007 | 83.322 | 9.3605 | 283.8245 | 2205.4033 | 842.7634 | 5.1722 | 0 | 0 | 137.826 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 105 | EDENVALE: Repl 115 KV Recl & Bus Relays |  |  | San Jose, Santa Clara | Project shall replace/upgrade the following components per the latest standard: 1. Reclosing relays for sectionalizing switches 177 and 187. 2. Bus Total overcurrent scheme for Bus sections ‘D’ & ‘H’. 3. Bus protection for Bus section ‘G’. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-08 | 44 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3853 | NA | 115 kV | 177 | 5a. Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5776823 | T.0003369 | Edenvale 115kV Recloser and Bus Diff | 1 | 3F | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-03-24 | NA | 2026-04-20 | NA | FALSE | NA | NA | 0 | 4646.5035 | 0 | 0 | 0 | 0 | 0 | 4.0947 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 106 | VASONA: Repl Bus Diff and Recloser Relay |  |  | Los Gatos, Santa Clara | Protection recommends replacing the bus differential KBCH with Bus Total Overcurrent relays and add a SEL 451 relay for automatics on the bus sectionalizing switch, SW 237. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-05 | 25 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.5367 | NA | 230 kV | 124 | Not Available | NA | NA | NA | 5758499 | T.0000788 | VASONA BUS DIFFERENTIAL AND RELOSER PROJ | 1 | 3F | NA | 2014 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-03-01 | 2020-02-28 | 2019-11-19 | NA | FALSE | 1934 | NA | 1023.9867 | 1023.9867 | 607.1063 | 77.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1023.9867 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 919.1988 | -8.9916 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 107 | Henrietta: Repl CB 42 Relays |  |  | Kings | Replace electro-mechanical relays for Lemoore NAS 70kV Line (CB 42) and Lemoore 70kV Line (CB 52). | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-05 | 61 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.0079 | NA | 70 kV | 718 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5776243 | T.0003312 | Henrietta CB 42 and CB 12 Relay Project | 1 | 3F | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-10 | NA | 2024-11-08 | NA | TRUE | NA | NA | 551.1419 | 1502.0644 | 3.4886 | 0.254 | 41.5165 | 429.5952 | 61.3807 | 965.8294 | 0 | 0 | 0 | 0 | 0 | 536.2349 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 108 | TEJON: Repl CB 12- 22 Relay |  |  | Kern | Replace EM relays on CB 12, 22, & 32 . Tejon CB 12, CB 22 and CB 32 70kV line relays are EM relays installed in 1950. The relays are at the end of their useful life cycle. The performance and functionality are not as good as of the latest digital relays. They have no fault recording capability, do not provide self-monitoring, and will not issue alarms when it fails. Due to the lack of self-monitoring, the relay needs shorter maintenance cycle. They are no longer adequately supported by the manufacturers. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-08 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.0602 | NA | 70 kV | 718 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5776254 | T.0003318 | Tejon CB 12 and CB 22 Relay Project | 1 | 3F | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-23 | 2019-12-30 | 2019-10-29 | NA | FALSE | 1672 | NA | 1028.9052 | 1028.9052 | 862.0951 | 75.5005 | 3.6709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1028.9052 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 913.5991 | 71.7 | 3.4812 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 109 | Vaca Dixon : Rep 230kV Bus Sec E-F Relay |  |  | Solano | Replace existing Bus Diff with two levels (System A & System B) SEL487B/SEL451 (SMP design) | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-12 | 55 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 42.1076 | NA | 230 kV | Not Available | 5a. Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5782038 | T.0004232 | Vaca Dixon - Rep 230kV Bus Sec E-F Relay | 1 | 3F | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-02-19 | NA | 2026-07-03 | NA | FALSE | NA | NA | 98.1319 | 10350.4947 | 0 | 0 | 0 | 86.2449 | 10.6411 | 7.2185 | 5346.1409 | 0 | 0 | 0 | 0 | 96.8861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 110 | SAN LEANDRO: Upgrade 115 KV Differential |  |  | San Leandro, Alameda | Replace San Leandro “U” Substation 115 kV buss differential relays with latest standard relays. Existing relays are no longer supported by the manufacturers. | Substation - Protection Relay | Replace | NA | Address Results of Protection Studies | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-07 | 53 | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2372 | NA | 115 kV | 131 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5764446 | T.0001256 | SAN LEANDRO 115KV BUS DIFFERENTIAL | 1 | 3F | NA | 2015 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-02-04 | 2019-06-15 | 2020-06-29 | Clearances | FALSE | 1300 | NA | 2681.6403 | 2681.6403 | 1255.5019 | 785.7262 | 2.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2681.6403 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 2615.9115 | 2.8304 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 111 | HUMBOLDT BAY PP: Repl Generator Relays |  |  | Humboldt | Replace the existing VAMP 210 and 265 generator protection relays for each of the 10 generators at Humboldt Bay Generating Station. Due to reliability issues at other sites, the lack of breaker failure protection, and the VAMP relays not being on the list of approved PG&E relay equipment, it has been determined that the VAMP relays should be replaced with the most current PG&E approved generator relays (redundant SEL 700G) and SCADA equipment. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-06 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.2745 | NA | 60 kV | 1259 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5774820 | T.0002968 | Humboldt Bay PP Generator Relays | 1 | 3F | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-10-22 | 2019-08-20 | 2020-01-15 | NA | FALSE | 3600 | NA | 1654.1208 | 1654.1208 | 319.1866 | 705.2863 | 94.8211 | 151.8664 | 113.7299 | 19.891 | 0 | 0 | 0 | 0 | 0 | 1634.2298 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 112 | PALERMO: Repl 60 KV Relay |  |  | Palermo CDP, Butte | Replace the following relays with dual SEL-411L relays per latest PG&E standard: • Palermo CB32 o Phase directional overcurrent GE-JBC53 relays o Ground directional overcurrent GE-JBCG53 relay o Westinghouse RC reclosing relay  This will be a complete panel replacement. • Palermo CB42 o Phase directional overcurrent GE-JBC53 relays o Ground directional overcurrent GE-JBCG53 relay o Westinghouse RC reclosing relay  This will be a complete panel replacement. • Palermo CB52 o Phase directional overcurrent GE-JBC53 relays o Ground directional overcurrent GE-JBCG53 relay o Westinghouse RC reclosing relay o RFL-6745 - terminal sends a DTT to Oroville cogen  This will be a complete panel replacement. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-04 | 77 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 8.0464 | NA | 60 kV | 483 | 3. Emergency Preparedness | Not Available | Tier 3 | No | 5776821 | T.0003367 | Palermo 60kV Project | 1 | 3F | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-09-14 | NA | 2027-05-11 | NA | TRUE | NA | NA | 450.6938 | 1875.8373 | 0 | 0 | 0 | 9.4814 | 195.335 | 668.7761 | 0 | 0 | 0 | 0 | 0 | 204.8164 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 113 | APM: Repl APM-Newark Relay |  |  | Sunnyvale, Santa Clara | Replace the line relays at Applied Materials Substation for the Newark-Applied Material 115kV Line. SMP relays for CB142, GPS clock, annunciator and ODN is in the scope of this project to replace and install. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-05 | 25 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.0337 | NA | 115 kV | 483 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5775588 | T.0003264 | APM: Newark- Applied Materials Relay | 1 | 3F | NA | 2017 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-04-26 | 2022-08-16 | 2022-08-16 | NA | FALSE | 1540 | NA | 1476.1501 | 1476.1501 | 0.6863 | 27.8787 | 291.7061 | 1155.5163 | 0.3628 | 0 | 0 | 0 | 0 | 0 | 0 | 1476.1501 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1372.9969 | 0.33683 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 114 | RADUM: Upgrade Protection |  |  | Pleasanton, Alameda | Replace the line relays to bring up to current standard for breakers 22, 72 and 82. Add CT's to breakers 22,72, 82 and add three new CCVT/PT to measure bus section E voltage. | Substation - Protection Relay | Replace | NA | Address Results of Protection Studies | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-04 | 51 | Protection Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.61928 | NA | 60 kV | 124 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5758487 | T.0001252 | RADUM PROTECTION UPGRADE | 1 | 3F | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-09-01 | 2020-12-15 | 2021-05-03 | NA | FALSE | 3900 | NA | 3247.7101 | 3247.7101 | 226.5659 | 1254.6468 | 1420.5532 | -0.3185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3247.7101 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 3162.8321 | -0.30964 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $2 Mil - $3 Mil ¦ $3 Mil -$5 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 115 | SAN LEANDRO U: Repl Bart Relay |  |  | San Leandro, Alameda | Replacement of the San Leandro "U" Sub - Replace BART Relay Project at the San Leandro "U" Substation to develop the detailed scope and engineering. This project’s scope is to remove old relays and install Line Protection to enhance efficiency, safety, and reliability. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-07 | 41 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2372 | NA | 115 kV | 483 | Not Available | NA | NA | NA | 5776121 | T.0003267 | San Leandro U Bart Relay Project | 1 | 3F | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-01 | 2019-12-01 | 2019-12-15 | NA | FALSE | 1300 | NA | 1629.3105 | 1629.3105 | 978.5732 | 546.9727 | 0.8945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1629.3105 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1586.0443 | 0.87085 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 116 | Colgate: Repl 60kV Relays |  |  | Yuba | System Protection recommends replacement of relay on Colgate CB 52, CB 32, 42, 62, 72, and the 60kV Bus Differential using the latest Protection standard.these relays have exceeded their life cycle, thus a higher probability of failure. The performance and functionality are not as good as the latest digital relays. The electro-mechanical relays have no fault recording capability, do not provide self-monitoring, and will not issue alarms when fail. Due to the lack of self-monitoring, the relay needs shorter maintenance cycle. They are no longer adequately supported by the manufacturers | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-12 | 80 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.5839 | NA | 60 kV | 174 | 3. Emergency Preparedness | Not Available | Tier 3 | No | 5786079 | T.0004829 | Colgate: Repl 60kV Relays | 1 | 3F | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-08-10 | NA | 2028-02-22 | NA | FALSE | NA | NA | 234.0904 | 6316.5584 | 0 | 0 | 3.2799 | 203.0964 | 24.9765 | 16.9167 | 0 | 0 | 0 | 0 | 561.2733 | 231.3527 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 117 | AMES DIS: Install Redundant Bus Relay |  |  | Mountain View, Santa Clara | System Protection recommends to install redundant bus protection at this facility per current standards.Redundant bus protection is deemed necessary to provide safe and reliable operating conditions. Fault duty at this facility is 40470 A and the station serves 153 customers. Providing redundant bus protection also helps ensure coordination for the relays at the remote ends. System Protection recommends to install redundant bus protection at this facility per current standards. | Substation - Protection Relay | Replace | NA | Address Results of Protection Studies | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-07 | 25 | Protection Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.5685 | NA | 115 kV | 133 | 5a. Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5787899 | T.0005207 | AMES DIS: Install Redundant Bus Relay | 1 | 3F | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-01-21 | NA | 2027-05-19 | NA | FALSE | NA | NA | 0 | 1287.2242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 118 | RAVENSWOOD: Repl 115 KV RD-PA 1-2 RLY |  |  | Menlo Park, San Mateo | System Protection recommends to replace the existing electromechanical relays and POTT over lease line with two levels of current differential protection (GE L90 and SEL311L) over redundant channels on existing PG&E’s fiber optics for the Ravenswood - Palo Alto 115 KV #1 and #2 Line Relay Replacement Project. | Substation - Protection Relay | Replace | T.0000786 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-06 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.3472 | NA | 115 kV | 459 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5758486 | T.0000787 | RAVENSWOOD LINE RELAY 74002153 | 1 | 3F | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-01 | 2019-06-28 | 2021-08-22 | Workforce | FALSE | 1395 | NA | 3083.938 | 3083.938 | 112.5574 | 769.2264 | 1379.0967 | 30.8996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3083.938 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 2907.4301 | 29.2638 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 119 | CONTRA COSTA PP: Repl 230 kV Bus Diff |  |  | Antioch, Contra Costa | System Protection strongly recommends to replace Contra Costa PP with two levels of bus differential protection schemes per latest standard. This installation will significantly improve reliability of bus protection and eliminate existing deficiencies related to the outdoor paddle switch cabinets, maintenance and clearances. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-06 | 21 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 19.1042 | NA | 230 kV | 177 | 5a. Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5789528 | T.0007721 | CONTRA COSTA PP_Repl 230 kV Bus Diff | 1 | 3F | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-01-25 | NA | 2027-06-04 | NA | FALSE | NA | NA | 0 | 16524.2646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 120 | CONTRA COSTA: Upgrade 115 KV Bus Diff |  |  | Antioch, Contra Costa | The Contra Costa Sub 115kV Bus Differential Replacement Project will remove old equipment and install new Bus Differential relaying. | Substation - Protection Relay | Replace | NA | Address Results of Protection Studies | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-07 | 55 | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.1779 | NA | 115 kV | 483 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5760291 | T.0001613 | CONTRA COSTA: UPGRADE 115KV BUS DIFF | 1 | 3F | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-05-14 | 2019-12-31 | 2020-02-19 | NA | FALSE | 2971 | NA | 3109.2692 | 3109.2692 | 2137.8491 | 425.8648 | 3.5511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3109.2692 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 3014.1303 | 3.4414 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 121 | ATLANTIC: Repl CB 52- 62 Relay |  |  | Roseville, Placer | The line and reclosing relays at Atlantic CB 52 are old relays, and they were in service for 24 years. The line and reclosing relays are no longer supported by their manufacturers and are at the end or nearing the end of their useful life. The model of the line relays are SEL 221G and SEL 221F. The reclosing relay is a Basler BE1-25/79TR. The line relays at Atlantic CB 62 are old relays, and they were in service for 25 years. The original reclosing relay Basler BE1-25/79TR failed, and it was replaced with a used SEL 279 relay on 2013. The line and reclosing relays are no longer supported by its manufacturer and are at the end or nearing the end of their useful life. The model for both the line relays is SEL 121B. The line relays will need to be replaced with new SEL relays. The standard relaying package SMP will consist of two SEL 411L and two SEL 451 relays for an integrated design. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-01 | 30 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.6984 | NA | 60 kV | 220 | 5a. Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5777560 | T.0003533 | Atlantic CB 52 and CB 62 Relay Project | 1 | 3F | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-06-11 | NA | 2024-06-17 | NA | TRUE | NA | NA | 0.3374 | 1017.231 | 0 | 0 | 0 | 0.2246 | 0.1088 | 1016.8975 | 0 | 0 | 0 | 0 | 1034.3962 | 0.3335 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 122 | LOS ESTEROS: Repl CB 652 Line Relay |  |  | San Jose, Santa Clara | The Montague Substation Bundle and Remote End projects will replace Circuit Breaker (CB) 132, CB 142, Circuit Switcher (CSW) 176, CSW 186, replace protection relays for Bank 1, Bank 2, Bank 3, line and bus protection relays, install Distribution SCADA on CB 2100, CB 2200 and CB 2300. In addition, the line and bus protection relays at the Remote End Substations Los Esteros and Trimble will be replaced. The Montague Substation Bundle and Remote Ends are comprised of multiple projects that contribute to the betterment of the PG&E Electric System. CB132 and CB142 are being replaced as part of the Deteriorated Breakers Replacement Program to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. The replacement of the old Protection relays at Montague Substation, as well as the Remote Ends will improve system reliability, whereas installing SCADA on all the distribution equipment in Montague Substation will provide system visibility for low side devices at Montague Substation. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-12 | 20 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.1703 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5525505 | T.0000706 | MONTAGUE SUB 115 KV CB 132, 142 | 4 | 3F | NA | 2017 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-01-03 | 2023-02-01 | 2022-04-08 | NA | TRUE | 9841 | NA | 1848.3513 | 1848.3513 | 11.6593 | 358.4662 | 292.8014 | 1093.045 | 30.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 1848.3513 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 11.6593 | 358.4662 | 272.1468 | 1061.9 | 29.5646 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 123 | MONTAGUE: Replace Line Relay |  |  | San Jose, Santa Clara | The Montague Substation Bundle and Remote End projects will replace Circuit Breaker (CB) 132, CB 142, Circuit Switcher (CSW) 176, CSW 186, replace protection relays for Bank 1, Bank 2, Bank 3, line and bus protection relays, install Distribution SCADA on CB 2100, CB 2200 and CB 2300. In addition, the line and bus protection relays at the Remote End Substations Los Esteros and Trimble will be replaced. The Montague Substation Bundle and Remote Ends are comprised of multiple projects that contribute to the betterment of the PG&E Electric System. CB132 and CB142 are being replaced as part of the Deteriorated Breakers Replacement Program to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. The replacement of the old Protection relays at Montague Substation, as well as the Remote Ends will improve system reliability, whereas installing SCADA on all the distribution equipment in Montague Substation will provide system visibility for low side devices at Montague Substation. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-07 | 29 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2309 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5774460 | T.0000706 | MONTAGUE SUB 115 KV CB 132, 142 | 4 | 3F | NA | 2017 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-01-03 | 2023-02-01 | 2023-03-20 | NA | TRUE | 9841 | NA | 2126.34 | 2126.34 | 7.6181 | 100.9997 | 433.0661 | 941.8198 | 606.6244 | 0 | 0 | 0 | 0 | 0 | 0 | 2126.34 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2084.3248 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 124 | Geyser 11: Repl CB 312 Relays |  |  | Sonoma | The project will replace the LFCB102 with SEL 411L relays on both Eagle Rock CB 162 and Geysers unit 11 CB 312 due to the fact PGE owns both relay terminals. The existing fiber is the communication medium and will be retained. The work will improve the dependability and reliability of the protection scheme. This will also help the voltage stability with Geysers unit 11 on line in the Mendocino Area. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | NA | 46 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.83 | NA | 115 kV | 761 | 3. Emergency Preparedness | Not Available | Tier 3 | No | 5782718 | T.0004357 | Geyser 11: Repl CB 312 Relays | 1 | 3F | NA | 2018 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-09-21 | 2023-12-31 | 2024-02-06 | NA | TRUE | 985 | NA | 1076.9742 | 1082.8955 | 0 | 0 | 1.1434 | 186.7624 | 765.467 | 129.5227 | 0 | 0 | 0 | 0 | 0 | 953.3728 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 1084.5086 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 125 | MARICOPA: Repl Relay |  |  | Taft, Kern | The replacement of the Maricopa CB 42 and CB 52 Relay Project at the Maricopa Substation to develop the detailed scope and engineering. This project’s scope is to remove old electro mechanical relays and install Line Protection for CB 42, CB 52 and Bus Total OC to enhance efficiency, safety, and reliability. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-13 | 59 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.8868 | NA | 70 kV | 437 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5776249 | T.0003317 | Maricopa Relay Project | 1 | 3F | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-07-08 | 2020-01-27 | 2019-11-05 | NA | FALSE | 3900 | NA | 2228.1926 | 2228.1926 | 1975.9642 | 177.6125 | 6.6131 | 1.2892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2228.1926 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 1995.6685 | 173.7166 | 6.4586 | 1.2591 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 126 | RM: COLGATE REPL CB 12 AND CB 22 RELAYS |  |  | Yuba | The targeted existing relays are at the end of their useful life cycle and are no longer supported by the manufacturer. Their performance and functionality are not as good as the latest digital relays. The relays have no or limited fault recording capability. In addition, the manufacturer’s software that is used for relay maintenance and testing is not compatible with the modern operating systems on PG&E Test Department laptops. This situation creates a risk of maintenance non-compliance. This project includes the relaying upgrade for the 60kV CB 12 & CB 22 at Colgate PH. The existing SEL-121G relays will be upgraded with the installation of SEL-311C relays. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-12 | 31 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.5839 | NA | 60 kV | 176 | 3. Emergency Preparedness | Not Available | NA | NA | 5781580 | T.0004184 | EM: COLGATE: Repl CB 12 and CB 22 Relays | 1 | 3F | NA | 2018 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-01-04 | 2021-05-03 | 2021-05-03 | NA | FALSE | 2101 | NA | 2080.5193 | 2080.5193 | 233.6667 | 716.2986 | 1108.3295 | 5.4289 | 0.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 2080.5193 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 2074.7818 | 4.4739 | -206.791 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 127 | Tesla 230kV Bus Section E - Diff Repl |  |  | Alameda | The Tesla 230kV Bus Differential Replacement Project will remove old equipment and install new Bus Differential relaying. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-15 | 51 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5793949 | T.0002021 | Tesla 230kV Bus Differential Replacement | 2 | 3F | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-11-20 | 2019-07-31 | 2022-03-25 | Workforce | FALSE | 14900 | NA | 2341.2525 | 2341.2525 | 0 | 73.1201 | 1085.5946 | 1168.5466 | 30.5881 | -16.5969 | 0 | 0 | 0 | 0 | 0 | 2357.8494 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2319.391 | 30.4822 | -16.5394 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 128 | TESLA: Repl 230 KV Bus Differential |  |  | Alameda | The Tesla 230kV Bus Differential Replacement Project will remove old equipment and install new Bus Differential relaying. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-15 | 50 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 627 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5764661 | T.0002021 | Tesla 230kV Bus Differential Replacement | 2 | 3F | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-11-20 | 2019-07-31 | 2020-11-23 | Workforce | FALSE | 14900 | NA | 15300.9309 | 15300.9309 | 3967.5722 | 3339.9678 | 97.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15300.9309 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 15154.3801 | 97.0173 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 129 | Cottonwood:Install 115kV Bus Diff Relay |  |  | Cottonwood CDP, Shasta | There is a single level of bus protection for 115 kV double bus single breaker at Cottonwood. We are adding a parallel breaker for 115 kV bus and upgrading protection to CB 172 and CB 192 as part of the Transmission Banks replacement. Additionally, there are plans to add two sectionalizing breakers for 115 kV bus. Proposal for Redundant Bus ProtectionNew bus protection calls for redundant bus protection for bulk electric supply. ABB is proposing Distributed Busbar Protection performed by one set of the protection relay REB500 mainly using fiber optic connections in a redundant scheme with the existing GE B90 Busbar relay. ABB proposal reduces the number of additional switch racks for bus differential from 6 to 1 inside the control room and eliminates copper wiring from yard to the control room. Elimination of copper wiring saves lot of cable trenching time in the energized yard. ABB solution consists of Central Unit installed inside the control room and bay units (REG500BU) installed outdoor in cabinets close to existing breaker cabinets. Each individual bay distributed around the station is connected to the central unit by optical fiber cables. Since this is the first installation for PG&E, we have discussed the cybersecurity concerns of distributed busbar protection and ABB addressed the concerns raised by System Automation and CIP Compliance in the revised proposal.We are also excited to use process bus technology that has lot of promise for future jobs especially where cable trenching is limiting protection upgrades.New bus protection calls for redundant bus protection for bulk electric supply. ABB is proposing Distributed Busbar Protection performed by one set of the protection relay REB500 mainly using fiber optic connections in a redundant scheme with the existing GE B90 Busbar relay. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-06 | 18 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 26.1945 | NA | 115 kV | 483 | 3. Emergency Preparedness | Not Available | Tier 3 | No | 5784719 | T.0004659 | Cottonwood Install 115kV Bus Diff Relay | 1 | 3F | NA | 2019 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-06-09 | 2022-03-31 | 2025-03-05 | Workforce | TRUE | 9866 | NA | 7077.2947 | 9796.389 | 99.0984 | 686.7893 | 4312.82 | 1287.0421 | 537.8953 | 1796.4647 | 1029.073 | 0 | 0 | 0 | 0 | 6923.6451 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 130 | LAS POSITAS: INSTALL 230KV & 60KV RELAY |  |  | Livermore, Alameda | This planned project will replace Las Positas Substation’s failed CKT SW 286 and Motor Operated Air Switch (MOAS) 289 with four (4) 230 kV circuit breakers (CBs) that will be interconnected in a “Ring” bus configuration, install one (1) new control building to be installed near the 60 kV yard, install new relays on all new 230 kV CBs (Nos. 222, 232, 262, 272). This planned project is needed to maintain safe and reliable power to the East Bay area and will support PG&E top-level initiatives such as improved service reliability, improved operational flexibility, and reducing operating costs. | Substation - Protection Relay | New | NA | Asset Condition | Relay Upgrades | NA | 2024-03-05 | 27 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.2184 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5791153 | T.0000185 | LAS POSITAS: REPL CKT SWS 286 & 289 | 5 | 3F | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-11-01 | 2023-06-30 | 2023-06-30 | NA | TRUE | 7851 | NA | 7345.7153 | 7345.7153 | 0 | 349.2404 | 1456.6548 | 4251.3101 | 1263.0746 | 25.4354 | 0 | 0 | 0 | 0 | 0 | 7320.2799 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 7320.2799 | 42.5363 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 131 | HERDLYN: Repl 60 KV Relay |  |  | Contra Costa | This project includes the relaying upgrade for the 60kV Vasco – Herdlyn line, Herdlyn – Balfour Line, Herdlyn Bank 1, Herdlyn Bank 2 and Herdlyn – Tracy Line and the Breaker controls for HVCB 32 & HVCB 62 at Herdlyn substation. The existing relays will be upgraded with the installation of SMP relays. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-05 | 28 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.81884 | NA | 60 kV | 771 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5780244 | T.0003959 | Herdlyn 60kV Relay Project | 1 | 3F | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-07-01 | 2019-09-04 | 2022-03-31 | Workforce | TRUE | 4146 | NA | 5255.6739 | 5255.6739 | 1287.125 | 1910.7811 | 1116.2525 | 265.1417 | 468.7647 | 0.8054 | 0 | 0 | 0 | 0 | 0 | 5254.8685 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 4590.8046 | 447.1889 | 1.8734 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 132 | OROVILLE: Repl 60kV relays |  |  | Oroville, Butte | This project is to install new relays per the latest standard on Oroville CB 12, 22 and bus. Oroville CB 12 protects the Centerville – Table Mountain, 60kV line. CB12 is currently protected by Electromechanical Relays These relays are very well beyond the life expectancy of a Electromechanical relay resulting in the higher probability of failure. System protection recommends replacing these relays with the current line protection standard. Oroville CB 22 protects the Palermo - Oroville, 60kV line. CB22 is currently protected by Electromechanical Relays These relays are very well beyond the life expectancy of a Electromechanical relay resulting in the higher probability of failure. System protection recommends replacing these relays with the current line protection standard. There is no bus protection currently installed at Oroville 60kV Bus, therefore, a 60kV bus fault must be cleared remotely thereby losing other customers such as Kelly Ridge PH, Oroville Energy, Pacific Oroville Power and Highway 70 Industrial Park. System Protection recommends installing a bus total overcurrent protection which will locally trip the existing three (3) 60kV line breakers. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-05 | 62 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.75208 | NA | 60 kV | 174 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5764439 | T.0001246 | OROVILLE: Repl 60kV Relays on CB 12 & 22 | 1 | 3F | NA | 2015 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-05-07 | NA | 2027-06-29 | NA | FALSE | NA | NA | 355.4793 | 1635.6438 | 0.0306 | 34.3093 | 95.7165 | 160.3213 | 64.5223 | 21.7127 | 0 | 0 | 0 | 0 | 1182.4351 | 355.4793 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 133 | FAMOSO: Repl CB 132 & CB 152 RELAY PROJ |  |  | Kern | This project is to replace outdated protection relays with new microprocessor relays would reduce maintenance and provide event recording capability allowing for timely evaluation of line faults and proved line fault locations on our transmission lines on CB 152 and CB 132. The relays on Famoso CB 132 and 152 are GYC and JBCG GE electromechanical relays are over 50 years old and have reached end of their life cycle. The performance and functionality of electromechanical relays are not as good as the latest digital relays. They have no fault recording capability, do not provide self-monitoring, and will not issue alarming when they fail. Due to the lack of self-monitoring, they need shorter maintenance cycle. They are no longer adequately supported by the manufacturers. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-02 | 15 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.8913 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5764419 | T.0001223 | FAMOSO CB 132 & CB 152 RELAY PROJECT | 1 | 3F | NA | 2015 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-08-19 | 2023-12-29 | 2024-11-27 | Construction Delays | TRUE | 4553 | NA | 3142.5782 | 3507.1592 | 18.2204 | 9.9483 | 60.6773 | 2332.857 | 596.6483 | 487.61 | 1.1979 | 0 | 0 | 0 | 0 | 3018.3513 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 134 | OAKLAND X: Upgd 115 KV Diff EDR |  |  | Oakland, Alameda | This project supports the replacement of Oakland X 115kV Bus Differential. This requires the installation of new bus protection relays. The new microprocessor relays will also be easier to maintain than the old relays. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-14 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.1294 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5764437 | T.0001244 | OAKLAND X 115KV DIFFERENTIAL UPGRADE | 1 | 3F | NA | 2015 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-01-15 | 2019-04-11 | 2020-01-31 | Workforce | FALSE | 8445 | NA | 5982.2437 | 5982.2437 | 3882.0983 | 936.6772 | 94.8164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5982.2437 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 5683.7578 | 91.3941 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 135 | PITTSBURG: Repl 452 Relay |  |  | Pittsburg, Contra Costa | This project will address a combination of critical problems related to the protection on 230/115 kV Bank 13 and 230 kV breaker 452. New relays will comply with SMP design. Low side breaker 352 and 362 associated with the Bank 13 will be re-configured. Breaker 352 will become a bus parallel breaker and will be number as breaker 302. Relays associated with breakers 352 and 362 will be replaced under a different project. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-06 | 25 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 28.8512 | NA | 230 kV | 184 | Not Available | NA | NA | NA | 5775558 | T.0003206 | Pittsburg BK 13 & CB 452 Relay Project | 1 | 3F | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-02-01 | 2019-03-15 | 2019-11-08 | Clearances | FALSE | 1500 | NA | 1078.1695 | 1078.1695 | 545.6787 | 93.9025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.1695 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 1028.2942 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 136 | PA SW STA: Repl PA-Ravenswood Relay |  |  | Palo Alto, Santa Clara | This project will replace the electromechanical relays on Ravenswood - Palo Alto Switching Station (PASS) 115kV #1 and #2 with two levels of high speed protection in accordance with the latest microprocessor protection standards thus addressing a combination of critical problems related to the protection on the following circuit by replacing aged, unreliable, and unsafe relays with standard packages: • Ravenswood - Palo Alto Switching Station 115kV #1 and #2 By completing this project within the timeframe specified, the Company will be diligently addressing known reliability issues attributed to the existing protection equipment. This course of action directly correlates to PG&E’s vision and values through the company’s goal of improving reliability. | Substation - Protection Relay | Replace | T.0000787 | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-05 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.0138 | NA | 115 kV | 124 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5758485 | T.0000786 | PALO ALTO LINE RELAY 74002152 | 1 | 3F | NA | 2014 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-01 | 2019-06-28 | 2021-09-28 | Workforce | FALSE | 1000 | NA | 2933.3546 | 2933.3546 | 91.9063 | 695.0285 | 1463.9729 | 60.1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2933.3546 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 2682.0598 | 55.6999 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 137 | MENDOCINO: Replace CB 32 Relays |  |  | Mendocino | This project will replace the Mendocino CB 32 and 52 relays with the current SMP standard line and breaker relay packages. This upgrade will provide better protection during PSPS events and remove old relays that are at the end of their useful life. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-05 | 29 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.7328 | NA | 60 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5787917 | T.0005227 | MENDOCINO: Replace CB 32 Relays | 1 | 3F | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-06-28 | 2021-10-21 | 2021-10-15 | NA | FALSE | 1315 | NA | 1649.6669 | 1649.6669 | 0 | 32.3231 | 1541.2239 | 76.1199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1649.6669 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1487.0768 | 71.8394 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 138 | SAN RAFAEL: Repl CB 132- 142 Relay |  |  | San Rafael, Marin | To improve the service reliability on the San Rafael area, this job proposes to replace the existing electromechanical relays described above with a primary and backup SEL 311C. This will simplify relay maintenance, improve the transmission loop reliability and provide fault location with load monitoring capabilities to the transmission lines. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-08 | 61 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2052 | NA | 115 kV | 483 | 5a. Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5775586 | T.0003262 | San Rafael CB 132 & CB 142 Relay Project | 3 | 3F | NA | 2017 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-12-15 | 2023-12-31 | 2026-03-13 | Prioritization | FALSE | 500 | NA | 437.702 | 1569.2497 | 0 | 0 | 2.7029 | 300.8843 | 129.2391 | 31.5159 | 0 | 0 | 0 | 0 | 540.3455 | 432.8264 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 139 | TRACY: REPL CB 162 & BUS TOTAL OC RELAY |  |  | Tracy, San Joaquin | Tracy CB162 has a combination of electromecahnical relays and microprocessor relay. These relays were installed in 1998 and are 19 years old. The microprocessor relay is past its lifecycle and the electromechanical relays are at their life cycle. In order to improve system reliability, System Protection proposes to replace the line relays with new SMP standard relays using 400 series SEL relays. | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-03-01 | 50 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.7469 | NA | 115 kV | 131 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5778258 | T.0000887 | TRACY SUB 115 KV CB 152, 162 | 2 | 3F | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-09-10 | NA | 2027-03-23 | NA | FALSE | NA | NA | 41.4113 | 1407.0388 | 1.5225 | 2.9097 | 2.3849 | 2.5827 | 2.8403 | 2.9922 | 0 | 0 | 0 | 0 | 0 | 40.927 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 140 | EVERGREEN: Upgrade 60 KV Protection |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Protection Relay | Replace | T.0000147 | Address Results of Protection Studies | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-02 | 41 | Protection Studies | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.3776 | NA | 60 kV | 579 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5770123 | T.0001685 | Evergreen Substation Upgrade | 7 | 3F | 5738678 | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-05-28 | 2018-05-21 | 2020-07-31 | Prioritization | FALSE | 27200 | NA | 3810.0224 | 3810.0224 | 586.3283 | 1287.071 | 98.9747 | 16.6347 | 1.1457 | 0 | 0 | 0 | 0 | 0 | 0 | 3810.0224 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 3459.4028 | 91.5542 | 15.3876 | 1.0598 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 141 | CONTRA COSTA: Repl 230 KV fault Recorder |  |  | Antioch, Contra Costa | Project recommend action: • Upgrade a subset of the existing PG&E Fault Recorders and Sequence of Event Recorders to support PG&E’s efforts to meet the PRC-002-2 Implementation Plan. • New fault recorder(s) at Contra Costa 230kV will monitor 230kV breaker status points. | Substation - Other Equipment | Replace | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | 2024-03-07 | 20 | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.1779 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5772218 | T.0002236 | PRC 002-2 Contra Costa 230kV FR | 1 | 3F | NA | 2017 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-09-01 | 2021-06-15 | 2021-10-27 | NA | FALSE | 1740 | NA | 1373.0935 | 1373.0935 | 1.9687 | 1164.9383 | 181.9804 | 24.2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1373.0935 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1348.089 | 25.0045 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC PRC 002-2 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 142 | PITTSBURG: Repl 230 KV Fault Recorder |  |  | Pittsburg, Contra Costa | Project scope: • Upgrade a subset of the existing PG&E Fault Recorders and Sequence of Event Recorders to support PG&E’s efforts to meet the PRC-002-2 Implementation Plan. • New fault recorder(s) at Pittsburg PP 230kV will monitor 18 PG&E breaker status points. New Fault Recorder will not monitor NRG breakers. | Substation - Other Equipment | Replace | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | 2024-03-05 | 22 | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.72358 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5772224 | T.0002234 | PRC 002-2 Pittsburg 230kV FR | 1 | 3F | NA | 2017 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-01 | 2020-07-23 | 2021-10-27 | Project Design | FALSE | 1000 | NA | 1509.746 | 1509.746 | 42.865 | 1230.3388 | 204.3884 | 31.3767 | 0.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 1509.746 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1477.5922 | 31.3767 | 0.77708 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC PRC 002-2 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 143 | PRC-002-2 - TESLA 230KV FR |  |  | Alameda | The Tesla substation Fault Recorders and Sequence of Event Recorders capabilities are required to ensure PG&E meets the NERC PRC-002-02. PRC-002-2 | Substation - Other Equipment | Replace | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | 2024-03-15 | 52 | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 627 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5522608 | T.0001939 | PRC-002-2 - Tesla 230kV FR | 1 | 3F | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-03 | 2021-06-15 | 2022-01-07 | Workforce | TRUE | 1375 | NA | 1978.8082 | 1978.8082 | 344.2032 | 252.6578 | 105.2151 | 96.6108 | 122.4521 | 22.5427 | 0 | 0 | 0 | 0 | 0 | 1956.2655 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 344.2032 | 252.6578 | 105.2151 | 96.6108 | 122.4521 | 22.7759 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC PRC 002-2 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 144 | Enhanced Powerline Safety Settings - Relay replacement |  |  | NA | This forecast placeholder is a proposal to install New SMP relays 14 terminals with in PGE so they are operable for EPSS | Substation - Protection Relay | Replace | NA | Address Results of Protection Studies | Protection NERC Compliance | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 3 | No | EX113137 | NA | NA | NA | 3F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28000 | 21500 | 21500 | 21500 | 21500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 145 | BAIR: EM Repl 60 KV CB 22- 32- 42 Relay |  |  | Redwood City, San Mateo | This project replaces the relays for Circuit Breakers 22, 32, and 42 at Bair Substation. PG&E’s NERC Compliance Relay Upgrade Program funds relay replacements to allow relay settings to meet PRC-23-line loadability requirements. | Substation - Protection Relay | Replace | NA | Address Results of Protection Studies | Protection NERC Compliance | NERC PRC Compliance | 2024-02-07 | 63 | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.6857 | NA | 60 kV | 718 | Not Available | NA | NA | NA | 5525945 | T.0002853 | PRC-023: Bair CB 22, 32 & 42 74011021 | 1 | 3F | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-07-02 | 2018-12-10 | 2019-02-04 | NA | FALSE | 900 | NA | 1107.1865 | 1107.1865 | 45.0076 | 0.1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107.1865 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 40.5069 | -0.15809 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC PRC 023 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 146 | EM: HONEY LAKE,AMEOLE,WINGL REPL 3RD DTT |  |  | Plumas | Honey Lake Generation facility has a DTT application between their facility and LMUD facility located next to PGE Westwood Substation. The DTT in the LMUD facility is initiated by the CB 22 in the PGE Westwood Substation via a copper cable. Due to lease line failures, and the difficulty accessing the LMUD facility, PGE will relocate new DTT equipment to the Westwood Substation and change the existing circuit from 2 wire to 4 wire. | Substation - Other Equipment | Relocate | NA | Address Results of Protection Studies | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | 2024-02-14 | 22 | Protection Studies | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.96252 | NA | 60 kV | 437 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 3 | No | 5526944 | T.0003298 | EM: IT Replacements | 40 | 3F | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-07-23 | 2019-07-31 | 2024-07-30 | Project Design | TRUE | 1001 | NA | 885.1611 | 1165.2974 | 88.1216 | 53.2661 | 450.1058 | 121.3619 | -1.1943 | 252.0927 | 48.1889 | 0 | 0 | 0 | 0 | 865.0159 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 88.1216 | 53.2661 | 450.1058 | 121.3619 | -1.1943 | 26.9103 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 147 | WEEDPATCH SUB - NU INSTALL DTT |  |  | Kern | This project will establishthe necessary protection and metering to separate the Kern Canyon Powerhouse from PG&E ownership. In response to the changing energy landscape in California, combined with increasing costs associated with relicensing and aging generation infrastructure, PG&E launched its small hydro disposition program in 2016. The current strategy is focused on removing small uneconomic hydro assets from the portfolio to reduce operational risk and improve overall value of the generation provided to PG&E customers. Kern Canyon PH is one of the facilities in the generation deposition portfolio.. The implementation of this project is necessary to execute the safe transfer of ownership to the 3rd Party. | Substation - Protection Relay | New | NA | Address Results of Protection Studies | Relay Upgrades | NA | 2024-02-07 | NA | Protection Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.2535 | NA | 70 kV | 124 | 5. Compliance/Commitments With Strong Safety Link | Not Available | NA | NA | 5791073 | T.0005987 | KERN PH DIVESTITURE | 2 | 3F | NA | 2020 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-11-17 | 2020-12-31 | 2023-04-19 | Prioritization | TRUE | 3500 | NA | 1508.8158 | 1508.8158 | 0 | 119.4241 | 823.6164 | 391.2724 | 174.448 | 0.055 | 0 | 0 | 0 | 0 | 0 | 1508.7608 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1471.23 | 0.05347 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 148 | SOBRANTE: EM REPL 230KV BUS DIFFERENTIAL |  |  | Orinda, Contra Costa | After the Sobrante 230kV inspection was completed it was determined that the Bus Differential may not operate for an internal bus fault. If a bus fault occurs and the scheme does not operate, all lines and transformers connected to the 230kV bus will trip on a time delay. This may cause system stability issues, additional thermal and mechanical stress, and customer power quality complains. Additionally, Crockett Cogen will be out of service. On this project the existing Sobrante 230kV paddle scheme and electromechanical relays will be replaced on an emergency basis with a redundant low impedance SMP Bus Differential System A and System B design. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-03-07 | 50 | NA | Other - Deferral | $3 Mil -$5 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.0767 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5791193 | T.0005995 | Sobrante 230 kV Differential | 1 | 3F | NA | NA | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-03-01 | 2022-03-23 | 2022-03-23 | NA | FALSE | 3020 | NA | 3001.054 | 3001.054 | 0 | 153.6234 | 1830.9488 | 1016.9004 | 0.2863 | -0.705 | 0 | 0 | 0 | 0 | 0 | 3001.759 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2710.7903 | 67.7314 | -0.65086 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 149 | Emergency Replacement of Protective Equi |  |  | NA | Bucket for Emergency Replacement of Protective Equipment | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 ¦ 115 ¦ 70 ¦ 60 kV | 1013 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 5 | No | 5512259 | NA | NA | NA | 3F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8088.2363 | 8999.5408 | 9000 | 9000 | 9000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 150 | Bucket: One for One Relay 2018 |  |  | NA | Bucket to replace existing relays at various sites with in Pacific Gas And Electric that are considered obsolete. These relay replacements will involve one for one replacement or full panel replacement based upon need at each job site. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 797 | Not Available | Not Available | NA | NA | 5528799 | T.0003721 | One to One Relay Projects | 53 | 3F | NA | 2017 | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1096.9341 | 1096.9341 | -20.5582 | 13.4753 | 23.355 | -75.0549 | -6.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 1096.9341 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | -20.5582 | 13.4753 | 23.355 | -75.0549 | -6.2778 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 151 | WEIMAR: EM Repl CB 52 Relays |  |  | Placer | Due to failed electro-mechanical relays associated to 60kV CB 52 line protection at Weimar Substation, System Protection approved the emergency replacement of the entire line protection package to the latest SMP design standards. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-04-02 | 41 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.82438 | NA | 60 kV | 797 | Not Available | NA | NA | NA | 5529106 | T.0003799 | Weimar: Emerg Repl CB 52 Relays | 1 | 3F | NA | NA | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-03-11 | 2019-11-14 | 2019-09-22 | NA | FALSE | 1264 | NA | 1242.8878 | 1242.8878 | 1002.9062 | -5.8587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.8878 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 902.6157 | 67.1656 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 152 | BOLINAS: REPLACE CB 12 RELAYS |  |  | Bolinas CDP, Marin | Emergency replaced failed Bolinas CB 12 relays | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-02-13 | 47 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.81301 | NA | 60 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5553079 | T.0009325 | Bolinas: Repl CB 12 Relays | 1 | 3F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | NA | Marin County - Coastal Commission delegate | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-23 | NA | 2024-11-18 | NA | TRUE | NA | NA | 367.9418 | 1593.1251 | 0 | 0 | 0 | 0 | 252.9646 | 1326.1531 | 14.0073 | 0 | 0 | 0 | 0 | 252.9647 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 227.6681 | 178.1955 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 153 | Gregg: EM Repl 230 KV BUS DIFF RELAYS |  |  | Madera | Emergency replacement of bus differential relays on Gregg 230 kV Bus | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-03-01 | 40 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.266 | NA | 230 kV | 426 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5783412 | T.0004631 | GREGG: EM REP 230 KV BUS DIFF RLYS | 1 | 3F | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-06-01 | 2021-03-12 | 2021-05-19 | NA | FALSE | 2000 | NA | 1978.5763 | 1978.5763 | 297.3678 | 959.6408 | 721.5678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1978.5763 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1978.5763 | -271.0285 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 154 | WEIMAR: EM REPL CB 72 Relay |  |  | Placer | Emergency Replacement of CB 72 Relays at Weimar substation. Weimar Substation has a single 60kV Main Bus with 3-60kV lines and TB 1 connected to it. The 3 lines connected to the main bus are: Weimar # 1 60kV Line (CB 52), Drum-Grass Valley-Weimar 60kV line (CB 62) and Weimar-Halsey 60kV line (CB 72). Transformer Bank # 1 is comprised of three-single phase transformers rated 3.125MVA and a spare rated 2MVA. During this project we will be replacing CB 72 protective relays inside the existing control building. The Existing control building is 12’W x 16’L and has 7 panels. Panel 1-6 are relay and control panels and Panel 7 is the SCADA panel. The plan is to expand the control building by a minimum of 9’ to the west. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-04-02 | 64 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.82438 | NA | 60 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5548202 | T.0007900 | WEIMAR-EM REPL CB 72 RELAYS-74045078 | 1 | 3F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-06-12 | NA | 2024-01-25 | NA | TRUE | NA | NA | 1170.7042 | 1184.5976 | 0 | 0 | 0.7664 | 156.2279 | 730.9469 | 296.6564 | 0 | 0 | 0 | 0 | 0 | 887.9412 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 141.2948 | 657.8521 | 273.5276 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 155 | METCALF: EM Repl Diff Cabinet Bus 2 Sec |  |  | Santa Clara | Emergency replacement of Metcalf 230kV Differential Cabinet Bus 2 Sect. E. This work supports System Protection’s concern that the differential cabinet could fail and potentially cause an unplanned sustained outage of Metcalf 230kV bus. This project will replace the 230kV Bus Section E outdoor differential cabinet at Metcalf. Replacement of this cabinet is complicated by the necessary construction sequence. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-03-13 | 28 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 230 kV | 1013 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5774779 | T.0002867 | METCALF 230KV DIFF CAB BUS 2E 74011033 | 1 | 3F | NA | NA | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-07-22 | 2020-05-31 | 2020-07-29 | NA | FALSE | 4326 | NA | 3057.4979 | 3057.4979 | 1615.3903 | 674.0729 | 15.4833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3057.4979 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 2864.5313 | 14.5423 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 156 | RIO DELL JCT: EM REPL 42 and 22 Relays |  |  | Hydesville CDP, Humboldt | Emergency replacement of relays for CB 22, 42 and Rio Dell Tap due to equipment failure. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-02-07 | 18 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.41044 | NA | 60 kV | Not Available | Not Available | Not Available | NA | NA | 5543979 | T.0006948 | RIODELLJCT:EM REPL CB42&22 REPL 74037904 | 1 | 3F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-08-15 | NA | 2023-08-04 | NA | TRUE | NA | NA | 1791.4174 | 1835.0405 | 0 | 0.957 | 190.2751 | 617.9597 | 977.4707 | 48.378 | 0 | 0 | 0 | 0 | 0 | 1786.6624 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 191.2321 | 537.0404 | 879.7234 | 5.1295 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 157 | Midway: EM Diablo RAS |  |  | San Luis Obispo | Emergency replacement of relays st EM Diablo. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-03-07 | 30 | NA | Other - Deferral | $3 Mil -$5 Mil | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 35.6227 | NA | 500 ¦ 230 kV | 1416 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5783638 | T.0004511 | DIABLO: EM DIABLO SPS RELAY | 3 | 3F | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-07-09 | 2019-12-21 | 2019-12-22 | NA | FALSE | 2500 | NA | 1444.0959 | 1444.0959 | 1281.7035 | 160.8035 | 0.2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1444.0959 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1283.0915 | 83.3087 | 0.18988 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 158 | POE PH: EM Repl CB212/252 Com |  |  | Butte | Install new SMP Style relays for a Current Differential Scheme on the 230kV Belden - Rock Creek – Poe Transmission Line | Substation - Protection Relay | Replace | T.0004687 | Emergency Event | Age/Condition - Replace Relays | NA | 2024-02-06 | 13 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.9596 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5790909 | T.0006046 | POE PH: Em Repl CB 212/252 Com | 1 | 3F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-05-02 | NA | 2024-06-13 | NA | TRUE | NA | NA | 694.2392 | 1025.4141 | 0 | 21.0095 | 199.3471 | 283.3886 | 159.5231 | 362.1457 | 0 | 0 | 0 | 0 | 0 | 663.2684 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 159 | REDBUD: EM Repl CB 152 Relays |  |  | Clearlake Oaks CDP, Lake | Redbud CB 152 & 162 Relay Replacement. The following protection requirements are based on the existing PG&E transmission system. 1.Remove all existing equipment on Panel 1R & 1C. 2.Remove equipment on Panel 2R related to CB 162, including 125-2, 127-2, 125X-2, 194BU-2, 127B-2, 127X-2, 194-2, 150B-2, 162B-2. Retain equipment related to 115kV Bus protection. 3.Remove CB 162 line relaying equipment from Panel 4C. This includes Device 185-2, 121/167N-2, 121/167NBU-2, 143T-2, 143C-2, FT switches, and Cut-Outs. Also, remove equipment related to Sync Check scheme, including 125RE, 162RE, RE104SC-1, RE104SC-2, 125REX. Sync check for 115kV breakers will be performed by SMP relays. The only remaining equipment on 4C will be the annunciator and D20S-1 board. Confirm with Automation regarding these two devices. We may consider moving this equipment to 5C to completely spare out 4C. 4.Verify whether Sync swing panel is still needed. If not needed, then remove. 5.Install (2) SMP Line Panels & (2) SMP Breaker Panels as shown in Table 1. 6.Confirm existing broker delta PT winding is no longer used and rewire second winding on existing Bus PTs from broken delta to wye. Wire CB 162 new relays to separate PT windings, per standard. 7.Install three new CCVTs on CB 152 side of Sw 357. Wire new CB 152 relays to separate PT windings, per standard 8.Wire relay fail and relay operate alarms to station annunciator. 9.Connect new relays for remote communication access per Automation requirements. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-02-16 | 29 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.1825 | NA | 115 kV | Not Available | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5537442 | T.0005148 | REDBUD: EM REPL CB 152 RELAYS 74029062 | 1 | 3F | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 3 | 2024-03-11 | 2022-12-03 | 2025-02-28 | Project Design | TRUE | 1430 | NA | 834.338 | 1983.3473 | 46.0447 | 414.7384 | 42.9263 | 75.3689 | 133.9581 | 837.8292 | 432.4817 | 0 | 0 | 0 | 0 | 713.0364 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 41.4402 | 373.2643 | 38.6338 | 67.832 | 120.5621 | 366.1637 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 160 | DIXON: Repl CB 142 Relay |  |  | Dixon, Solano | Replace old electromechanical IRD and IRV relays with newer relays on Dixon CB 142. Polarizing potential is from low side of bank that is non-standard. With bank outage, we can lose line protection. Relays are obsolete (installed in 1987) | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-02-07 | 34 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.89932 | NA | 115 kV | 437 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5521163 | T.0003200 | Dixon CB 142 Relay Replacment | 1 | 3F | NA | 2016 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-06-23 | 2021-06-07 | 2021-03-26 | NA | FALSE | 1332 | NA | 1313.4521 | 1313.4521 | 334.6571 | 547.1551 | 419.1149 | 2.3188 | 0.0232 | 0 | 0 | 0 | 0 | 0 | 0 | 1313.4521 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 301.1915 | 492.4395 | 377.2035 | 38.7398 | 0.02149 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 161 | BELDEN PH: EM REPL CB252 REL |  |  | Belden CDP, Plumas | Replacement of CB 212 relays at Belden PH. A relay failure on CB 212 initiated System Protection to recommend upgrading the whole relay package to SMP. The relays on the Poe PH and Rock Creek PH ends will also be upgraded to SMP. | Substation - Protection Relay | Replace | T.0006046 | Emergency Event | Age/Condition - Replace Relays | NA | 2023-05-17 | 18 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.55874 | NA | 230 kV | Not Available | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 5 | No | 5784989 | T.0004687 | BELDEN PH: EM REPL CB252 RELAY | 1 | 3F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-05-02 | NA | 2024-06-13 | NA | TRUE | NA | NA | 984.1547 | 1157.1184 | 29.2472 | 65.9678 | 221.4462 | 396.6776 | 229.7794 | 214.0003 | 0 | 0 | 0 | 0 | 0 | 943.1182 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 162 | RIVERBANK: EM Repl CB 132- 142 |  |  | Stanislaus | Riverbank substation is located in Stanislaus County and is a critical part of PG&E's 115kV transmission system. The existing line relays and CB 132 & CB 142 relays are are at the end of their useful life cycle time. Their performance and functionality are not as good as the latest digital relays, This project includes relaying upgrade for Bellota - Riverbank line, Bellota - Riverbank - Melones SW Sta line and breaker controls for HVCB 132 & 142. The existing line relays will be upgraded with the installation of redundant SEL-411L relays. The existing breaker controls for HVCB 132 & 142 will also be replaced with the installation of SEL-451 relays. The existing potential device on the line side of CB 142 will be replaced with the installation of CCVTs. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-02-07 | 25 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.3123 | NA | 115 kV | 516 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5528847 | T.0003721 | One to One Relay Projects | 53 | 3F | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-01 | 2019-12-31 | 2021-04-08 | Prioritization | FALSE | 832 | NA | 1312.2724 | 1312.2724 | 288.4183 | 927.4493 | -14.3578 | 4.6467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.2724 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 273.7687 | 893.0118 | -13.8247 | 4.4741 | -116.8446 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 163 | EM ROUND MOUNTAIN REP CB 222 RELAY |  |  | Round Mountain CDP, Shasta | Round Mountain CB 212 and CB 222 protect the Pit #5–Round Mountain #1 and Pit #5–Round Mountain #2 230kV lines respectively. The existing electromechanical line relays on these terminals were installed in 1966. They have no fault locating capability and are old, obsolete and failing relays. They are no longer manufactured and spare parts are not available if they fail. Both lines run through Tier 3 – Extreme Fire Risk Zone. The scope summary is to replace Protection Relay’s and install a new SMP relay package for CB 212 & CB 222 at Round Mountain and add digital communications to Pit #5 PH CB 232 & 252 relays. This relay scheme will become a “mirror bit” piloted relay scheme and there will be C37.94 circuits provisioned for this Round Mountain to Pit #5 line. System Protection will build and set the relays to accept the C37.94 circuits once these circuits get built should the emergency relay replacement installation precede the new telecom circuit installation. There are requirements for connections to terminal servers for relay access. Round Mountain Substation has existing ODN network devices for relay DNP Polling and Remote Relay Access. There will be a total of eight (8) new SMP Relays and four (4) SEL 2411 relays being installed. At Round Mountain, each relay will have fiber runs between the control panels and the Cisco Switches located in the Telecom Room. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-03-06 | 57 | NA | Other - Deferral | $1 Mil - $2 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 230 kV | 210 | 3. Emergency Preparedness | Not Available | NA | NA | 5534119 | T.0004524 | ROUND MOUNTAIN: EM REP CB 222 RELAY | 1 | 3F | NA | NA | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-06-01 | 2022-08-10 | 2022-08-10 | NA | TRUE | 1406 | NA | 1412.7413 | 1412.7413 | 128.7882 | 256.1473 | 167.8422 | 828.6783 | 31.2853 | 0 | 0 | 0 | 0 | 0 | 0 | 1412.7413 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 128.7882 | 256.1473 | 167.8422 | 828.6783 | -110.2642 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 164 | SAN RAFAEL: EM Repl Automatics |  |  | San Rafael, Marin | The existing automatics scheme should be removed and SEL 451 relays with interlocks installed. This will simplify the design and improve the testing and operation of the automatics scheme at San Rafael substation. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-03-08 | 41 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2052 | NA | 115 kV | 469 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5762565 | T.0000648 | San Rafael Em Replace Automatics | 1 | 3F | NA | 2015 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-01-28 | 2020-07-01 | 2020-07-17 | NA | FALSE | 1058 | NA | 1057.8386 | 1057.8386 | 275.7245 | 759.6818 | 3.4263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1057.8386 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 990.7848 | 3.2136 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 165 | EAGLE ROCK: Repl CB 112 Relay |  |  | Sonoma | The Geysers #3 – Eagle Rock is one of three 115kv lines that serves the Mendocino and Lake counties. It is a critical line that provides power flow from Cortina and Geysers units to maintain the voltage stability in this area. This line is 1.8 miles long that located over rough and hilly terrain in the Calpine facility. The protection is two SPD 11A line current differential and a backup SEL 121G relays. The communication path for the differential is a twisted pair of copper wires with isolating transformers. While the SPD11A differential relays are still testing good, the isolating transformers are failing. There are no spare parts available to replace the isolating transfomers, thus making the scheme useless. The Set B differential scheme is cutout for this reason. The remaining Set A differential and backup SEL 121G relays will provide line protection for the duration. Protection recommends replacing the entire scheme with new SMP SEL 411L and 451 relays for line protection and automatics control. This will be a non-integrated design. This proposal will correct the potential failure of the high speed protection scheme and maintain the service reliability in the Mendocino and Lake areas. | Substation - Protection Relay | Replace | T.0003269 | Emergency Event | Age/Condition - Replace Relays | NA | 2024-03-01 | 34 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.8266 | NA | 115 kV | 131 | 3. Emergency Preparedness | Not Available | NA | NA | 5775579 | T.0003257 | Eagle Rock: Repl Relay 187-A6 & 187-B6 | 1 | 3F | NA | 2017 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-01-29 | 2021-04-22 | 2021-04-22 | NA | FALSE | 3700 | NA | 3058.1245 | 3058.1245 | 3.024 | 309.8493 | 753.9394 | 1904.4385 | 86.2671 | 0.6061 | 0 | 0 | 0 | 0 | 0 | 3057.5184 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 962.3325 | 1713.9948 | 77.0991 | 0.73904 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 166 | MANTECA: EM Repl CB144-154 RELAYS |  |  | Manteca, San Joaquin | The project proposes to replace all line & breaker panel relays for CB 144,154 & 164 at Manteca Substation and the relays will be installed in the new MPAC building. | Substation - Protection Relay | Replace | NA | Emergency Event | Age/Condition - Replace Relays | NA | 2024-03-12 | 30 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.8539 | NA | 115 kV | Not Available | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5788361 | T.0005445 | MANTECA: EM REPL CB144-154 RELAYS | 2 | 3F | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-07-03 | NA | 2024-03-14 | NA | TRUE | NA | NA | 4064.6338 | 4654.8742 | 7.4423 | 137.2431 | 83.1996 | 510.4004 | 2585.0284 | 1331.5605 | 0 | 0 | 0 | 0 | 0 | 3323.3137 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 4286.8051 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 167 | GEYSER 3: Repl Eagle R-Geyser 3 Relays |  |  | Sonoma | The scope of work for the this project: Remove the following relays: Geyser 3 & 4 115kV 121Z2/167N-1 – SEL 121G 187L-1 – GE SPD relay 187LB-1 – GE SPD relay Eagle Rock 115kV 121/167N-6 – SEL 121G 187A-6 – GE SPD relay 187B-6 – GE SPD relay 150-6 – GE PJC Relay Install new SMP SEL 411L and 451relays for line protection and automatics control.Since the line is 1.8 miles long, fiber (twoseparate paths) will be required | Substation - Protection Relay | Replace | T.0003257 | Emergency Event | Age/Condition - Replace Relays | NA | 2024-03-01 | 34 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.31702 | NA | 115 kV | 437 | 3. Emergency Preparedness | Not Available | NA | NA | 5776123 | T.0003269 | Geyser 3&4: Repl Relays 187L-1 187LB-1 | 1 | 3F | NA | 2017 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-01 | 2021-05-26 | 2021-05-26 | NA | FALSE | 176 | NA | 2115.5269 | 2115.5269 | 2.7569 | 450.9423 | 633.9097 | 1003.2816 | 22.9955 | 1.6409 | 0 | 0 | 0 | 0 | 0 | 2113.886 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1049.3463 | 967.1231 | 22.1667 | 1.7892 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 168 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5803546 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | NA | NA | 2024-06-30 | NA | FALSE | NA | NA | 1021.6405 | 1327.6405 | 0 | 0 | 0 | 127.4427 | 705.2016 | 494.9962 | 0 | 0 | 0 | 0 | 0 | 832.6443 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 107.7491 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 169 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NA | NA | NA | NA | Wires - Minimum Required Scope (spot repair) Alternative | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5545863 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2024-12-31 | OAI | NA | TRUE | 964 | NA | 702.1714 | 3241.8731 | 0 | 0 | 19.0256 | 283.0645 | 340.9026 | 655.1788 | 574.4915 | 1369.2101 | 0 | 0 | 0 | 642.9926 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 19.0256 | 147.701 | 132.0903 | 7.4364 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 170 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | 30 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5803040 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | NA | NA | 2024-04-15 | NA | TRUE | 3700 | NA | 10593.2444 | 12835.1951 | 0 | 0 | 0 | 0 | 10555.0249 | 90.2194 | 0 | 0 | 0 | 0 | 0 | 10555.025 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 10555.0249 | 52.4591 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 & 6 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 171 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5809298 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | 2024-12-15 | NA | FALSE | NA | NA | 0 | 16100 | 0 | 0 | 0 | 0 | 0 | 16100 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 172 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5788368 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 14500 | 0 | 0 | 0 | 0 | 0 | 2450 | 2410 | 2410 | 2410 | 2410 | 2410 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 173 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Replace | NA | Physical Security | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5517419 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1679.6391 | 6906.0206 | 60.4005 | 163.9554 | 209.1569 | 101.5376 | 38.8499 | 1157.7303 | 1072 | 1056.56 | 1035.86 | 1015.28 | 994.69 | 1615.9088 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 57.7937 | 147.9156 | 227.8035 | 101.5376 | 38.8499 | 163.0379 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 174 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | New | NA | Physical Security | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5788371 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1083.0518 | 9126.2518 | 0 | 51.3992 | 210.7767 | 298.0999 | 490.3234 | 1441.4526 | 1380.82 | 1353.38 | 1326 | 1300 | 1274 | 1050.5992 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 71.7407 | 435.5682 | 409.0035 | 8.7545 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 175 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5800016 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-12-29 | NA | FALSE | NA | NA | 3164.527 | 3212.5269 | 0 | 0 | 0 | 865.8554 | 2257.2606 | 89.4109 | 0 | 0 | 0 | 0 | 0 | 3123.1161 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 0 | 0 | 989.9972 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 6 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 176 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | NERC CIP Compliance | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | NA | NA | NA | 5783345 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2019-03-22 | NA | FALSE | 1272 | NA | 1389.1861 | 1389.1861 | 411.1628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1389.1861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2024 | 1389.1861 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 177 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | New | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 42.1076 | NA | 500 kV | Not Available | Not Available | Not Available | NA | NA | 5788377 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | 2019 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2020-11-04 | 2021-11-15 | Workforce | FALSE | 1200 | NA | 1419.4292 | 1419.4292 | 505.0743 | 848.1276 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1419.4292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1353.2019 | 66.2273 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 178 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | New | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5788374 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | 5784566 | 2020 | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-12-15 | NA | FALSE | NA | NA | 14272.92 | 14272.92 | 0 | 1161.1195 | 9702.7292 | 3600.8301 | -191.7588 | 0 | 0 | 0 | 0 | 0 | 0 | 14272.92 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 9784.8808 | 4488.0391 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 179 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5781555 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2022-12-31 | NA | FALSE | 3500 | NA | 3493.4312 | 3493.4312 | -22.5666 | 310.5049 | 2142.8168 | 1053.2631 | -13.3836 | 0 | 0 | 0 | 0 | 0 | 0 | 3493.4312 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 3506.8148 | -13.3836 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 180 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5788220 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2021-12-15 | NA | FALSE | 2400 | NA | 2603.9745 | 2603.9745 | 45.1801 | 2639.7557 | -80.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2603.9745 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 2684.9358 | -93.8811 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 181 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5794298 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2022-11-15 | NA | FALSE | NA | NA | 8822.6638 | 8822.6638 | 0 | 904.6992 | 3997.4515 | 3937.1977 | -16.6846 | 0 | 0 | 0 | 0 | 0 | 0 | 8822.6638 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 2260.3645 | 6578.9838 | -16.6846 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 182 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5793242 | NA | Electric Transmission Substation Security Upgrade | NA | 3N | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-12-31 | NA | FALSE | NA | NA | 1457.9749 | 1669.5942 | 0 | 18.8983 | 974.8356 | 144.477 | 299.5408 | 150.2232 | 81.6193 | 0 | 0 | 0 | 0 | 1437.7517 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 883.1342 | 255.0767 | 299.5408 | 25.7427 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 183 | Dinuba Sub BESS: Orosi Sub Relay |  |  | Tulare | This project proposes to build an approximately 7MW 4 hour energy storage system connected to the PG&E’s Dinuba Substation. The Dinuba Substation will be upgraded to accommodate the new energy storage device. It is recommended to connect the energy storage device to the distribution system at Dinuba Substation. The energy storage device will be a PG&E-owned transmission asset. Currently, the Dinuba Substation consists of a 70 kV loop bus arrangement with four elements (two 70 kV lines and two 70/12 kV transformers). This project is needed to mitigate thermal loading and voltage concerns in the Reedley 70 kV system. | Substation - Protection Relay | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-02 | 15 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.8943 | NA | 70 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | No | 5785519 | T.0004115 | Dinuba 70 kV Energy Storage Project | 2 | 3R | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-03-25 | 2017-05-01 | 2026-09-29 | Prioritization | FALSE | 14000 | NA | 210.2729 | 1000 | 102.1983 | 103.2391 | 4.8355 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 210.2729 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $15 Mil - $20 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 184 | DINUBA: INSTALL ENERGY STORAGE |  |  | Tulare | This project proposes to build an approximately 7MW 4 hour energy storage system connected to the PG&E’s Dinuba Substation. The Dinuba Substation will be upgraded to accommodate the new energy storage device. It is recommended to connect the energy storage device to the distribution system at Dinuba Substation. The energy storage device will be a PG&E-owned transmission asset. Currently, the Dinuba Substation consists of a 70 kV loop bus arrangement with four elements (two 70 kV lines and two 70/12 kV transformers). This project is needed to mitigate thermal loading and voltage concerns in the Reedley 70 kV system. | Substation - Multiple | New | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-06 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.8203 | NA | 70 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | No | 5781262 | T.0004115 | Dinuba 70 kV Energy Storage Project | 2 | 3R | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2025-01-28 | 2017-05-01 | 2026-02-18 | Prioritization | FALSE | 14000 | NA | 994.6719 | 14430 | 563.3727 | 182.759 | 158.6678 | 0 | 0 | 3779 | 0 | 0 | 0 | 0 | 0 | 994.6719 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $15 Mil - $20 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 185 | Herndon #1 115 kV bus redundent relay |  |  | Fresno, Fresno | Add redundent relay for Herndon #1 115 kV bus | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.3414 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112159 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | NA | 2027-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1020 | 3100 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 186 | Moraga 230kV Bus Upgrade ( Part of project: Northern Oakland Area Reinforcement) |  |  | Orinda, Contra Costa | Add sectionalizing breakers and a bus tie breaker to Moraga 230 kV bus | Substation - Circuit Breaker | New | TBD | Reliability | System Design Upgrade | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 15.8714 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113255 | T.0006159 | Moraga_ Upgrade 230kV Bus | 1 | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-01-01 | 2024-12-31 | 2028-12-01 | Prioritization | FALSE | 17000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1000 | 10000 | 7000 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
| 187 | Round Mountain Bus 1 and Bus 2 Section E 230 kV Redundant Relay Project |  |  | Round Mountain CDP, Shasta | Adding redundant bus relay for Round Mountain Bus 1 and Bus 2 Section E 230 kV buses | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Extreme Heat |  | NA | 29.1389 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112244 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-12-01 | NA | 2028-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 1130 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 188 | MORAGA 230kV Bus #1 &2 Bus Redundant Relay |  |  | Orinda, Contra Costa | As done on previous upgrades, GE recommends that all relay cards be removed and later version cards for 7.2x be installed. he overview of the program is a s follows: • GE relays with firmware versions of 3 and below, are no longer supported by GE. • GE released service bulletin GER-4654A to address this vulnerably. • GE Multilin UR / URPlus / B95Plus Protection Relay Cryptographic Algorithm o UR relays below firmware 5.83 have the possible susceptibility. o Some relays such as firmware versions 3.x and 4.x are not provided firmware updates by GE and no upgrade to eliminate the vulnerability is available. o The remainder of relays with firmware family’s 5.x and 6.x will be evaluated for potential upgrade when GE relays are scheduled for regular relay maintenance according to SAP relay scheduled work • We can capitalize on the maintenance outage cycle – replace these relays during maintenance. o Will need to do full replacements due to new designs on equipment. Chassis is same size, but conversion settings are required, will need to put together instructions, etc. o 88 relays that are at Medium NERC sites o Program will be completed in 6 Years • Will need to get Automation involved as they were polling some of these devices for SCADA. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 15.8714 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112160 | T.0009400 | MORAGA_REPL 115kV BUS E DIFF GE RELAY | 1 | 60 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | NA | 2027-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1000 | 2700 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 189 | Placeholder Emergent Need in MWC 60/61 |  |  | NA | Forecast placeholder for CAISO Transmission Plan Approved Projects | Transmission Line/Substation | New | NA | CAISO Transmission Planning Standards | T-Line Capacity | NERC TPL Standards | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113287 | NA | NA | NA | 60 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 0 | 147000 | 190000 | 378000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5
| 190 | Bellota RAS (original project:Bellota 230 kV Bus Upgrade) |  |  | San Joaquin | Install Bellota RAS for Voltage recovery and overload prevention. | Other - Remedial Action Scheme/Special Protection Scheme | New | TBD | CAISO Transmission Planning Standards | Special Protection Scheme | NERC TPL Standards | 2024-03-01 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113220 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-01 | NA | 2026-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 1000 | 100 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 191 | Jefferson 230 kV BAAH Bus #1&2 redundant relay |  |  | San Mateo | Install Jefferson 230 kV BAAH Bus #1&2 redundant relay to resolve P5 issues. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.7091 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | Tx000752 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-01 | NA | 2026-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 1700 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 192 | Lakeville 115 kV Redundant Relay |  |  | Sonoma | Install Lakeville 115 kV Redundant Relay to resolve P5 issues. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-11 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 14.7021 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113218 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | NA | 2027-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 2000 | 5500 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 193 | Salinas 115kV BAAH Bus #1 &2 redundant relay |  |  | Salinas, Monterey | Install Salinas 115kV BAAH Bus #1 &2 redundant relay to resolve P5 issues. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.4966 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113219 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | NA | 2027-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1160 | 3380 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 194 | Las Positas 230 kV Redundant Bus Diffrential Relay |  |  | Livermore, Alameda | Install the redundant bus protection relay mitigate overloads identified for P5 contingency on Las Positas 230 kV Bus. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.2184 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112165 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-01 | NA | 2026-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 900 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 195 | Mendocino 115 kV Redundant Relay |  |  | Mendocino | Install the redundant bus protection relay mitigate overloads identified for P5 contingency on Mendocino 115 kV bus. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.7328 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112158 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | NA | 2028-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1400 | 2800 | 2800 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 196 | Caribou SPS#2 Upgrade |  |  | Plumas | Modify scheme to be triggered by any contingency on the Caribou – Table Mountain 230kV line, including opening a line section without a fault to comply with TPL-001-4 P2-1. The project scope is to add monitoring element (breaker 242) to the Caribou PH Generation Shedding Scheme#2 (Caribou SPS#2). | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | TBD | CAISO Transmission Planning Standards | Special Protection Scheme | NERC TPL Standards | 2024-03-22 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 2.2068 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112246 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-12-01 | NA | 2028-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 1100 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 197 | Willow Creek Voltage Support (T1132: Maple Creek Reactive Support) |  |  | Willow Creek CDP, Humboldt | One previously approved project, Maple Creek Reactive support, is recommended to be relocated to Willow Creek 60kV due to infrastructure limitations at the Maple Creek Substation. Since Willow Creek is an adjacent station and would address the need in the area for a lower cost, it is recommended that a 10 MVA STATCOM be installed at Willow Creek 60kV substation. | Substation - Voltage Support Equipment | New | TBD | Reliability | Voltage Support | NERC TPL Standards | 2024-02-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.40072 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113264 | T.0007205 | Willow Creek Reactive Support (Maple Creek Reactive Support) | 1 | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2009 ¦ 2021 | FALSE | 2009 ¦ 2021 | NA | https://www.caiso.com/Documents/BoardApproved2020-2021TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-01 | 2011-03-01 | 2027-10-01 | Prioritization | FALSE | $7,000 ¦ $14,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 10000 | 7000 | 500 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2020-2021TransmissionPlan.pdf
| 198 | Salinas-Firestone #1 and #2 60 kV Lines |  |  | Monterey ¦ Salinas, Monterey | Reconductor Salinas-Firestone #1 & #2 60 kV Lines with a higher capacity conductor. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2023-09-21 | 124 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 12.3 | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113254 | T.0005977 | Salinas-Firestone #1 & #2 60 kV Lines Reconductoring | 1 | 60 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-12-01 | 2024-12-31 | 2027-12-01 | Prioritization | FALSE | $19,000 ¦ $38,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 8000 | 1000 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
| 199 | Christie-Sobrante 115 kV Line Reconductor |  |  | Contra Costa ¦ Orinda, Contra Costa | Reconductor the Christie - Sobrante 115 kV line with a larger capacity conductor | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-04-09 | 70 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 7.8 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113223 | T.0005969 | Christie - Sobrante 115 kV Line Reconductor | 1 | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-01-01 | 2022-12-31 | 2028-02-01 | Prioritization | FALSE | 10500 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 13000 | 1800 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 200 | Lakeville #2 60 kV Line Upgrade Project |  |  | Marin ¦ Novato, Marin ¦ Petaluma, Sonoma ¦ Sonoma | Reconductor the line sections on the Lakeville #2 60 kV Line between Petaluma A to Lakeville Junction (tower 4/100) and Cotati to tower 11/236 (approx. 3.39 miles) with 397.5 AAC. Upgrade the capacity of the Petaluma A bus. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2023-12-21 | 23 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 3.4 | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112208 | TBD | Lakeville 60 kV Area Reinforcement | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-10-01 | 2021-12-01 | 2028-12-01 | Prioritization | FALSE | 7000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1500 | 5000 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 201 | Reconductor Rio Oso–SPI Jct–Lincoln 115kV line |  |  | Lincoln, Placer ¦ Placer ¦ Sutter | Reconductoring 11-mile Rio Oso-Lincoln 115 kV Line • Reconductor ~11 miles (full line) • Replace 8 wood poles with TSP • Replace insulators and hardware at 197 structures • Remove any limiting components as necessary to achieve full conductor capacity. This is a policy-driven capacity project to mitigate overload on io Oso –Lincoln 115 kV line under P6 and P7 contingencies. P6 contingency of Rio Oso – Atlantic and Atlantic – Gold Hill 230 kV lines overload Rio Oso –Lincoln 115 kV line starting 2023. In addition, the P7 contingency of Rio Oso – Atlantic and Rio Oso – Gold Hill 230 kV lines causes overload on the Rio Oso – Lincoln 115 kV line in the long term as well. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Policy | Line Reconductoring | NERC TPL Standards | 2021-11-19 | 124 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 11 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112249 | T.0008394 | Reconductor Rio Oso–SPI Jct–Lincoln 115kV line | 1 | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-01-01 | 2028-01-01 | 2028-12-01 | Prioritization | FALSE | $10,600 ¦ $21,200 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 2900 | 7400 | 9300 | 800 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 202 | Plainfield substation reconfiguration |  |  | Yolo | Reconfigure Plainfield substation and energize bank #1 through Nicolaus-Plainfield 60KV and Bank#2 through Vaca-Plainfield 60KV. It can be achieved with opening SW#167 and closing SW#177. Upgrade SW 167, 177 and 179 to Circuit Breakers. Make protection system upgrades as required. | Substation - Circuit Breaker | Upgrade/Retrofit | TBD | CAISO Transmission Planning Standards | System Design Upgrade | NERC TPL Standards | 2024-03-01 | 16 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.82985 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112242 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | NA | 2027-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1500 | 4500 | 500 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 203 | Plumas Separation and Load Shedding Scheme Upgrade |  |  | Plumas Lake CDP, Yuba | The project scope is to add monitoring element (Table Mountain 230 kV Circuit Breaker 242) to the Plumas Separation and Load Shedding Scheme. Table Mountain CB 242 status will be added as additional input to the scheme. | Substation - Circuit Breaker | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-02-13 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.2058 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112245 | TBD | TBD | TBD | 60 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-12-01 | NA | 2028-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 1100 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 204 | Clearlake 60 kV System Reinforcement |  |  | Lake ¦ Mendocino | The project scope of work involves the following: • Install a new 115/60 kV transformer bank at Middletown Substation with at least 100 MVA capacity. • Install two circuit breakers (115 kV and 60 kV) and associated disconnect switches at Middletown Substation to protect the new transformer. • Build a new 115 kV line from Lower Lake to Middletown substations with at least 345 Amps emergency capacity. This project is needed to provide transmission capacity to serve customers in the Humboldt Division. | Transmission Line/Substation | New | TBD | Reliability | New T-Line | NERC TPL Standards | 2023-07-14 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | TBD | NA | 115 | 115 ¦ 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113216 | TBD | Clear Lake 60 kV Reinforcement | TBD | 60 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-01-01 | 2012-03-01 | 2029-07-01 | Prioritization | FALSE | 30000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 3000 | 30000 | 30000 | 10000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 205 | EO-SYSPLN 60 - ET Line Cap TO-LINE |  |  | NA | Forecast placeholder for transmission line capacity work | Transmission Line - Multiple | New | NA | CAISO Transmission Planning Standards | T-Line Capacity | NERC TPL Standards | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5533237 | NA | NA | NA | 60 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 2048 | 0 | 0 | 0 | 0 | 0 | 2048 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5
| 206 | ROW Union-San Miguel/Paso Robles 70kV |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Transmission Line - Right of Way | New | NA | Reliability | T-Line Capacity | NERC TPL Standards | 2024-02-08 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 9.9 | NA | 70 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5554011 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 60 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Planning | NA | NA | 2019-05-01 | OAI | NA | TRUE | $35,000 ¦ $45,000 | NA | 0 | 1126.2484 | 0 | 0 | 0 | 0 | 0 | 43.82 | 419.168 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 207 | WRJ NONCOMPETITIVE_CPUC LIC/PER |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Other | New | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.403 | 230 ¦ 115 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767233 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 60 | 5756004 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | NA | 2020-05-01 | 2026-11-20 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 14090.7599 | 19063.8769 | 1458.3618 | 1246.0702 | 399.3553 | 0 | 0 | 1194.8564 | 1174.0196 | 1260.0705 | 1352.4287 | 2368.309 | 2684.2703 | 13904.5217 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 208 | North Tower 115 kV Looping Project |  |  | Vallejo, Solano | This project proposes to loop North Tower Substation into the Martinez-Sobrante 115 kV Line by utilizing an idle 115 kV line into North Tower and reconfiguring the connection points at Martinez JCT. This project is needed to provide transmission capacity to serve customers in the North Bay Division. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | System Design Upgrade | NERC TPL Standards | 2024-03-11 | 58 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 5.8111 | 115 | NA | Not Available | 8. Compliance/Commitments (But Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5783314 | T.0004418 | North Tower 115 kV Looping Project | 1 | 60 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-01-01 | 2015-05-01 | 2028-02-01 | Prioritization | FALSE | $5,000 ¦ $10,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 12000 | 2000 | 450 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 209 | ESTRELLA - SAN MIGUEL 70kV Line Loop In |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Transmission Line - Conductor | New | NA | Reliability | New T-Line | NERC TPL Standards | 2024-02-08 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 70 | NA | 61 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5771719 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 60 | 5757620 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2027-11-12 | 2019-05-01 | 2029-07-03 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 9466.5141 | 32008.1703 | 0 | 0.1104 | 0.3821 | 1.9285 | 9290.0459 | 1312.2762 | 5518.728 | 5483.6511 | 6521.8431 | 7023.5451 | 4022.0487 | 9292.4669 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 210 | Estrella Paso Robles 70kV Line Loop In |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Transmission Line - Conductor | New | NA | Reliability | New T-Line | NERC TPL Standards | 2024-02-08 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 70 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767231 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 60 | 5757620 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2025-03-03 | 2019-05-01 | 2026-01-30 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 3947.0577 | 15508.2805 | 0.4015 | 0.647 | 4.6013 | 218.9252 | 3537.2202 | 708.1898 | 3477.9421 | 1901.6972 | 6.6636 | 0 | 0 | 3769.3645 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 211 | ESTRELLA_CPUC LIC/PER - NON-COMPETITIVE |  |  | Paso Robles, San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Other | New | NA | Reliability | T-Line Capacity | NERC TPL Standards | NA | 15 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | 230 ¦ 70 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767230 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 60 | 5757620 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | NA | 2019-05-01 | 2024-09-30 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 935.8656 | 1246.0238 | 1473.3835 | 2073.6613 | 2245.3985 | 6944.1063 | -27721.5643 | 388.4734 | 0 | 2322.3713 | 0 | 0 | 0 | 857.5504 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 212 | Estrella-Morro Bay 230kV Interconnection |  |  | El Paso de Robles, San Luis Obispo ¦ Fresno ¦ Kings ¦ Monterey ¦ San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Transmission Line - Conductor | New | NA | Reliability | New T-Line | NERC TPL Standards | 2024-04-08 | 69 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | TBD | NA | 230 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767208 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 60 | 5757620 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2027-07-01 | 2019-05-01 | 2027-08-27 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 1293.4747 | 9044.5385 | 36.037 | 58.5773 | 162.0752 | 163.2229 | 178.6983 | 94.1678 | 647.4755 | 149.6472 | 6086.9009 | 1.3 | 0 | 1278.033 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 213 | Morro Bay-Cal Flats 230kV Shoofly |  |  | El Paso de Robles, San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Transmission Line - Conductor | New | NA | Reliability | T-Line Capacity | NERC TPL Standards | 2024-03-13 | 68 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion, Flooding |  | TBD | 1.6272 | 230 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5771718 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 60 | 5757620 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2027-07-01 | 2019-05-01 | 2027-08-27 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 103.8028 | 1469.4638 | 0.2908 | 0.6573 | 41.9105 | 39.5365 | 14.4304 | 7.8114 | 14.259 | 15.3042 | 615.6277 | 0 | 0 | 102.3092 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 214 | Union-San Miguel/Paso Robles 70kV - Eng |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | T-Line Capacity | NERC TPL Standards | 2024-02-08 | 96 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion, Flooding |  | 9.9 | NA | 70 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806384 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 60 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2027-11-12 | 2019-05-01 | 2029-07-03 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 4651.3736 | 15151.8488 | 0 | 0 | 0 | 0 | 4585.8925 | 651.5364 | 0 | 0 | 0 | 0 | 0 | 4585.8925 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 215 | Purchase Land for New Transmission Line |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Other | New | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.403 | NA | NA | 236 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5523422 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 60 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 3 | NA | 2020-05-01 | 2029-03-06 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 216 | RECONDUCTOR KERN PP_STOCKDALE 230KV |  |  | Bakersfield, Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Transmission Line - Conductor | New | T.0000220 ¦ T.0000144 | Reliability | New T-Line | NERC TPL Standards | 2022-10-25 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.25 | NA | 230 ¦ 115 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767236 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 60 | 5756004 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-10-20 | 2020-05-01 | 2026-07-03 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 15.8301 | 1987.1075 | 6.5875 | 0.806 | 0 | 0 | 0 | 153.5026 | 6479.3431 | 8367.8851 | 8248.2576 | 52457.5616 | 12892.8837 | 7.3935 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 217 | RECONDUCTOR STOCKDALE_MAGUNDEN 115KV |  |  | Bakersfield, Kern ¦ Fuller Acres CDP, Kern ¦ Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Transmission Line - Conductor | Upgrade/Retrofit | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | 2024-01-23 | 122 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 6 | NA | 115 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767237 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 60 | 5756004 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-07-25 | 2020-05-01 | 2025-12-05 | ISO Action | TRUE | $90,000 ¦ $140,000 | NA | 13.8851 | 1949.2608 | 7.0082 | 0.6142 | 0 | 0 | 0 | 145.11 | 155.1934 | 1.2436 | 1.3348 | 1.4326 | 2106.6521 | 13.7227 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 218 | VOLTAGE UPGRADE STOCKDALE_ LAMONT 115KV |  |  | Bakersfield, Kern ¦ East Niles CDP, Kern ¦ Fairfax CDP, Kern ¦ Fuller Acres CDP, Kern ¦ Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Transmission Line - Conductor | Upgrade/Retrofit | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | 2024-02-14 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 18.23 | NA | 115 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767235 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 60 | 5756004 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-10-17 | 2020-05-01 | 2027-04-05 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 6.5465 | 2030.4986 | 6.1881 | 0.2818 | 0 | 0 | 0 | 187.9989 | 0.5463 | 0.5863 | 0.6293 | 2421.7436 | 5278.4955 | 6.4699 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 219 | VOLTAGE UPGRADE WHEELER RIDGE_LAMONT 115 |  |  | Bakersfield, Kern ¦ Fuller Acres CDP, Kern ¦ Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Transmission Line - Conductor | Upgrade/Retrofit | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | 2024-01-23 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 19.65 | NA | 115 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767234 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 60 | 5756004 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-10-20 | 2020-05-01 | 2026-05-26 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 9.2907 | 1889.3082 | 6.2185 | 0.3101 | 0 | 0 | 0 | 146.8628 | 0.5992 | 0.6431 | 0.6902 | 2734.989 | 11831.4255 | 7.0959 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 220 | W R -WEEDPATCH (9/119 - WR) |  |  | Bakersfield, Kern ¦ Kern ¦ Weedpatch CDP, Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Transmission Line - Conductor | Upgrade/Retrofit | T.0000220 ¦ T.0000144 | Reliability | T-Line Capacity | NERC TPL Standards | 2021-11-09 | 71 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 22.4 | NA | 70 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | 490 | RBPPF - TBD | Yes | 5773278 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 60 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-07-10 | 2020-05-01 | 2025-09-17 | ISO Action | TRUE | $90,000 ¦ $140,000 | NA | 9.0645 | 2035.534 | 6.3079 | 0.3955 | 0 | 0 | 0 | 0.6577 | 0.7564 | 0.8119 | 0.8714 | 0.9352 | 46.9746 | 8.9585 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 221 | LOOP 2 PANOCHE-TRANQ LINES IN MANNING |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Transmission Line - Conductor | Upgrade/Retrofit | T.0009550 | Policy | T-Line Capacity | NERC TPL Standards | 2020-06-04 | 77 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804801 | T.0009194 | Manning New 500kV Sub Connection | 10 | 60 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | NA | TBD | NA | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2027-01-12 | 2028-01-01 | 2028-07-24 | Prioritization | FALSE | $325,000 ¦ $485,000 | NA | 141.8429 | 21298.1674 | 0 | 0 | 0 | 0 | 75.1229 | 694.5066 | 0 | 0 | 0 | 0 | 0 | 75.1229 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 222 | LOOP LOS BAN-GATES#1 & LOS BANO-MID#2 |  |  | Fresno ¦ Merced | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Transmission Line - Conductor | Upgrade/Retrofit | T.0009550 | Policy | T-Line Capacity | NERC TPL Standards | 2024-04-08 | 57 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | NA | 500 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804800 | T.0009194 | Manning New 500kV Sub Connection | 10 | 60 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | NA | TBD | NA | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2027-01-12 | 2028-01-01 | 2028-07-24 | Prioritization | FALSE | $325,000 ¦ $485,000 | NA | 138.2095 | 20827.5309 | 0 | 0 | 0 | 0 | 85.5375 | 665.0584 | 0 | 0 | 0 | 0 | 0 | 85.5375 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 223 | RECONDUCTOR 230KV MANNING -TRANQUILITY#1 |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Transmission Line - Conductor | New | T.0009550 | Policy | T-Line Capacity | NERC TPL Standards | 2020-06-04 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | TBD | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804811 | T.0009194 | Manning New 500kV Sub Connection | 10 | 60 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | NA | TBD | NA | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2027-04-12 | 2028-01-01 | 2028-07-24 | Prioritization | FALSE | $325,000 ¦ $485,000 | NA | 138.2945 | 35299.9863 | 0 | 0 | 0 | 0 | 50.226 | 1024.5553 | 1176 | 1176 | 6000 | 71400 | 72000 | 50.2261 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 224 | Wilson 115kV STATCOM T-Line Relocation |  |  | Brentwood, Contra Costa ¦ Contra Costa | Install a 115kV +100/-100 Mega Volt-Ampere reactive (MVAR) voltage control system (STATCOM) at Wilson Substation. | Transmission Line - Conductor | Relocate | NA | Reliability | T-Line Capacity | NERC TPL Standards | 2023-08-17 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | 318 | 8. Compliance/Commitments With Low Safety Risk | 7 | NA | NA | 5773698 | T.0001381 | Wilson 115kv STATCOM | 2 | 60 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-07-01 | 2020-05-01 | 2021-03-30 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 1004.379 | 1004.379 | 166.5457 | 812.3817 | 24.3053 | 1.0972 | 0.0491 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.379 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 785.7605 | 0.85318 | 0.03786 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
| 225 | Wilson Transmssion Line Work |  |  | Merced ¦ Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Transmission Line - Conductor | Upgrade/Retrofit | T.0001381 ¦ T.0002231 | Reliability | T-Line Capacity | NERC TPL Standards | 2022-09-28 | 69 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 230 ¦ 115 | NA | 58 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5783478 | T.0004116 | WILSON: 115 kV ARP - BAAH | 6 | 60 | NA | 2012 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-05-12 | 2015-05-01 | 2026-02-13 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 36.0297 | 6981.9987 | 21.9611 | 13.4399 | 0.6286 | 0 | 0 | 881.8579 | 4729.1016 | 1169.4523 | 0 | 0 | 0 | 36.0297 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 226 | Loop HZ1 into Egbert Sw. Stat |  |  | Brisbane, San Mateo ¦ Daly City, San Mateo ¦ San Francisco, San Francisco | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Transmission Line - Conductor | Relocate | T.0008764 | Reliability | T-Line Capacity | NERC TPL Standards | 2024-03-16 | 50 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 7 | NA | 230 | NA | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | RBPPF - TBD | Yes | 5767213 | T.0000159 | Egbert 230kV Switching Station | 9 | 60 | 5763199 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Engineering more than 50% complete | 4 | 2027-12-23 | 2021-12-01 | 2028-09-15 | Prioritization | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 3153.2551 | 35007.3257 | 84.6107 | 414.2639 | 219.9909 | 760.7488 | 866.5053 | 645.2388 | 0 | 0 | 0 | 0 | 2398.2926 | 3106.3289 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf
| 227 | REROUTE JEFFERSON_MARTIN 230KV |  |  | Millbrae, San Mateo ¦ San Bruno, San Mateo ¦ San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Transmission Line - Conductor | Relocate | T.0008764 | Reliability | T-Line Capacity | NERC TPL Standards | 2023-11-22 | 17 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | TBD | NA | 230 | NA | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | RBPPF - TBD | Yes | 5767217 | T.0000159 | Egbert 230kV Switching Station | 9 | 60 | 5763199 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Engineering more than 50% complete | 4 | 2028-03-16 | 2021-12-01 | 2028-10-17 | Prioritization | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 34515.3654 | 89974.1175 | 122.5497 | 988.8708 | 790.8575 | 21258.0216 | 10929.1741 | 2510.2085 | 0 | 0 | 0 | 0 | 27388.1219 | 34105.9001 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf
| 228 | Loop Vaca Dixon-Tesla in Collinsville |  |  | Alameda ¦ Byron CDP, Contra Costa ¦ Contra Costa ¦ Discovery Bay CDP, Contra Costa ¦ Knightsen CDP, Contra Costa ¦ Oakley, Contra Costa ¦ Sacramento ¦ Solano ¦ Vacaville, Solano | This project will support connection of a new 500kV substation between Vaca Dixon and Tesla Substations to the PG&E electric system. The new 500kV substation (named Collinsville), to be installed by the third-party entity (LS Power), is needed to address a number of identified transmission constraints and provide an additional supply from the 500kV system into the northern Greater Bay Area, to increase reliability to the area and advance additional renewable generation in the northern area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Vaca Dixon – Tesla 500kV line into the new 500kV Collinsville substation and build the associated transmissioin line. • Modify Vaca Dixon 500kV Series Capacitor Bank 2 reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Connect two 230kV lines to Pittsburg 230kV bus in separate bus sections and install 115kV bus reactors in bus sections D&E. • Upgrade line protection of Tesla 500kV line at Tesla substation as needed | Transmission Line - Conductor | Upgrade/Retrofit | T.0004581 | Policy | T-Line Capacity | NERC TPL Standards | 2024-04-11 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 500 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804858 | T.0009189 | Loop Vaca Dixon-Tesla in Collinsville | 4 | 60 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-10-29 | 2028-01-01 | 2028-05-12 | NA | FALSE | $475,000 ¦ $675,000 | NA | 176.2268 | 20076.4008 | 0 | 0 | 0 | 0 | 113.7176 | 553.5644 | 5189.5038 | 5833.2646 | 1965.9982 | 1184.7402 | 0 | 113.7176 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 229 | Newark - HVDC Connection - TLine |  |  | Fremont, Alameda | This project will support the interconnection of the Voltage-Sourced Converter (VSC)-HVDC converter station into the 230kV bus at Newark Substation. The VSC-HVDC converter station will be installed by the third party entity (LS Power) to transport power from Newark to NRS. The proposed PG&E scope of work for the project includes: • Install a 230kV breaker complete with new structure and all associated switches at Newark. • Modify protection scheme, as required • Upgrade grounding and grading as required. • Construct 230kV line from the new circuit breaker at Newark up to the PG&E property line for making connection to LS Power’s HVDC converter station. | Transmission Line - Conductor | New | NA | Reliability | T-Line Capacity | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | TBD | 27.7611 | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806599 | T.0009168 | Newark - HVDC Connection | 2 | 60 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | NA | TBD | NA | 851 | TBD | TBD | TBD | Planning | 5 | 2027-11-08 | 2028-01-01 | 2028-01-04 | NA | FALSE | $325,000 ¦ $510,000 | NA | 43.9296 | 1455.5205 | 0 | 0 | 0 | 0 | 34.0988 | 211.0543 | 0 | 0 | 0 | 0 | 0 | 34.0988 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 230 | San Jose B - HVDC Connection - TLine |  |  | San Jose, Santa Clara | This project will support the interconnection of the Voltage-Sourced Converter (VSC)-HVDC converter station into the 500kV bus at Metcalf substation and into the 115kV bus at the San Jose B substation. The VSC-HVDC converter stations and the HVDC line will be installed by the third-party entity (LS Power) to transport power from Metcalf to San Jose B. The proposed PG&E scope of work for the project includes: Metcalf Subsattion • Install a partial 500kV bay at Metcalf, complete with breakers, switches, bus work and other associated equipment. • Install protection scheme for the new breakers and HVDC line connection. • Expand substation yard and fence as required. • Upgrade grounding, grading and security as required. • Construct 500kV line from the 500kV bus to the Point of Change of Ownership (PCO) switch location for HVDC converter connection.. San Jose B Substation • Convert San Jose B 115kV bus to GIS BAAH, complete with clean-air 115kV breakers and associoated equipment. (The GIS will be designed to accommodate existing four lines, four distribution transformers and a new HV cable connection for LS Power HVDC converter connection.) • Install temporary breaker and other associated equipment to make provision for GIS equipment installation. • Install HV cable from GIS building to PCO location for HVDC converter connection. | Transmission Line - Conductor | New | T.0003803 | Reliability | T-Line Capacity | NERC TPL Standards | 2024-02-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | TBD | 2.1017 | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806625 | T.0009169 | Metcalf - 500kV HVDC Connection | 8 | 60 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | NA | TBD | NA | NOC | TBD | TBD | TBD | Planning | 5 | 2027-11-08 | 2028-01-01 | 2028-06-02 | NA | FALSE | $425,000 ¦ $615,000 | NA | 34.7433 | 7796.7164 | 0 | 0 | 0 | 0 | 31.8588 | 579.0197 | 0 | 0 | 0 | 0 | 0 | 31.8587 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 231 | PLAINFIELD SUB - RELOCATE TSPS |  |  | Hartley CDP, Solano ¦ Monument Hills CDP, Yolo ¦ Solano ¦ Winters, Yolo ¦ Woodland, Yolo ¦ Yolo | The California ISO’s 2018-2019 Transmission Planning Process (TPP) has identified the need for the Vaca – Dixon Area Reinforcement Project. This project will mitigate overloads and voltage criteria violations in the 115kV and 60kV transmission systems among Vaca Dixon, Davis, Rio Oso and Brighton Substations. The project will include the following work: 1. Install two 5.0 MVAR capacitor banks at Plainfield Substation. 2. Replace Vaca Dixon 115/60kV Bank 5 with a larger unit. 3. Replace the limiting elements on the 60kV equipment at Dixon Substation. 4. Re-rate the Woodland - Davis 115kV Line and the Rio Oso - West Sac 115kV Line. 5. Modify the existing special protection schemes (SPS) or add new SPS’s to trip load for select multiple contingencies. | Transmission Line - Pole/Tower | Relocate | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2023-11-03 | 64 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5785807 | T.0000007 | VACA-DAVIS: VOLTAGE CONVERSION PROJECT | 6 | 60 | NA | 2012 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-06-26 | 2023-12-01 | 2026-09-21 | Prioritization | FALSE | $70,000 ¦ $107,000 | NA | 410.1754 | 5636.2559 | 0 | 0 | 0 | 16.4884 | 338.2082 | 453.3595 | 2363.9869 | 184.448 | 0 | 0 | 0 | 354.6967 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 232 | RERATE WOODLAND - DAVIS T-LINE |  |  | Davis, Yolo ¦ Woodland, Yolo ¦ Yolo | The California ISO’s 2018-2019 Transmission Planning Process (TPP) has identified the need for the Vaca – Dixon Area Reinforcement Project. This project will mitigate overloads and voltage criteria violations in the 115kV and 60kV transmission systems among Vaca Dixon, Davis, Rio Oso and Brighton Substations. The project will include the following work: 1. Install two 5.0 MVAR capacitor banks at Plainfield Substation. 2. Replace Vaca Dixon 115/60kV Bank 5 with a larger unit. 3. Replace the limiting elements on the 60kV equipment at Dixon Substation. 4. Re-rate the Woodland - Davis 115kV Line and the Rio Oso - West Sac 115kV Line. 5. Modify the existing special protection schemes (SPS) or add new SPS’s to trip load for select multiple contingencies. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2024-02-06 | 122 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 11.7 | NA | 115 | NA | 137 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5766694 | T.0000007 | VACA-DAVIS: VOLTAGE CONVERSION PROJECT | 6 | 60 | 5738753 | 2012 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-10-15 | 2023-12-01 | 2025-12-19 | Prioritization | TRUE | $70,000 ¦ $107,000 | NA | 978.736 | 8195.8986 | 27.0424 | 61.031 | 104.3332 | 71.199 | 188.4017 | 707.4469 | 6353.3971 | 61.27 | 0 | 0 | 0 | 893.8969 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 233 | Banta Sub, Replace Bank 1 |  |  | San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Transmission Line - Conductor | Relocate | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2024-02-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.54319 | 60 | NA | Not Available | 5. Compliance / Commitments with Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5798131 | T.0006962 | Banta: Repl 60/12kV Bank 1 | 7 | 60 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-07-16 | 2024-12-31 | 2026-12-31 | Prioritization | FALSE | 17500 | NA | 158.0935 | 268.7479 | 0 | 0 | 0 | 0 | 17.1045 | 51.0701 | 2200 | 0 | 0 | 0 | 0 | 132.4502 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 234 | Birds Landing-Contra Costa 230kV Swap |  |  | Antioch, Contra Costa ¦ Contra Costa ¦ Sacramento ¦ Solano | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Transmission Line - Conductor | Relocate | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2020-08-10 | 19 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5800030 | T.0008048 | Contra Costa PP Line Swaps | 9 | 60 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-03 | 2025-05-01 | 2025-03-25 | NA | TRUE | $5,000 ¦ $10,000 | NA | 980.0624 | 6034.7986 | 0 | 0 | 0 | 265.8149 | 464.1632 | 3995.3673 | 1237.456 | 0 | 0 | 0 | 0 | 729.9781 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 235 | Contra Costa-Delta Yard Swap |  |  | Alameda ¦ Antioch, Contra Costa ¦ Brentwood, Contra Costa ¦ Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Transmission Line - Conductor | Relocate | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2021-10-13 | 44 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence, Corrosion |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5800032 | T.0008048 | Contra Costa PP Line Swaps | 9 | 60 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-02-28 | 2025-05-01 | 2025-05-22 | NA | TRUE | $5,000 ¦ $10,000 | NA | 186.8906 | 4656.3859 | 0 | 0 | 0 | 24.524 | 80.2305 | 757.4447 | 3737.1101 | 21.1753 | 0 | 0 | 0 | 104.7546 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 236 | Contra Costa-Lone Tree 230kV Swap |  |  | Antioch, Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Transmission Line - Conductor | Relocate | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2024-03-19 | 15 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence, Corrosion |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5800031 | T.0008048 | Contra Costa PP Line Swaps | 9 | 60 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-03 | 2025-05-01 | 2025-03-25 | NA | TRUE | $5,000 ¦ $10,000 | NA | 240.3527 | 5585.3985 | 0 | 0 | 0 | 38.84 | 100.2092 | 3633.5214 | 1754.3637 | 0 | 0 | 0 | 0 | 139.0491 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 237 | Pease Transformer Addition - T Line |  |  | Sutter | Install a second 115/60kV transformer and upgrade the 115kV and 60kV buses at Pease Substation. | Transmission Line - Conductor | Relocate | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2024-02-08 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.6809 | 115 | NA | 76 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5771838 | T.0000598 | Pease Transformer Add & Bus Upgrade | 3 | 60 | NA | 2013 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-10-30 | 2016-05-31 | 2020-12-10 | Material | FALSE | $25,000 ¦ $35,000 | NA | 2466.9077 | 2466.9077 | 187.4991 | 301.7242 | 366.172 | 82.4473 | 1.9617 | 0 | 0 | 0 | 0 | 0 | 0 | 2466.9077 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 1949.2756 | 352.7643 | 79.4259 | 1.8898 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 238 | Vierra 115 kV Looping (Tline) |  |  | Lathrop, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Transmission Line - Conductor | Relocate | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2024-02-06 | 14 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 2 | 1.355 | 115 | NA | 102 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5746744 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 13 | 60 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2020-10-16 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 4 | 2024-12-30 | 2014-05-01 | 2026-05-31 | Prioritization | FALSE | $10,000 ¦ $15,000 | NA | 6441.1064 | 15551.3264 | 674.1676 | 926.993 | 687.7113 | 612.6252 | 976.2231 | 5257.1571 | 739.6594 | 10.9534 | 0 | 0 | 0 | 6066.5079 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 239 | VIERRA ACQUIRE PERM LAND RIGHTS |  |  | Lathrop, San Joaquin ¦ San Joaquin ¦ Tracy, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other | New | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2023-11-20 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5527666 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 13 | 60 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2020-10-16 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 4 | 2024-12-30 | 2014-05-01 | 2026-06-01 | Prioritization | TRUE | $10,000 ¦ $15,000 | NA | 1963.0997 | 1663.0997 | 0 | 539.5382 | 246.792 | 291.0599 | 585.7096 | 0 | 0 | 0 | 0 | 0 | 0 | 1663.0997 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 0 | 539.5382 | 246.792 | 291.0599 | 585.7096 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 240 | Carbona Sub, 60kV Line Work |  |  | San Joaquin | Replace Carbona Transformer Bank 2 with a larger transformer, upgrade 60kV equipment, replace the Carbona Bank 1 foundation, replace the entire 12kV bus with switchgear, and establish a new distribution circuit outside of the substation. The capacity increase is needed to eliminate a 30 percent normal overload of Carbona Bank 1, a 33 percent normal overload of the Carbona 1104 distribution feeder, and a 38 percent normal overload of the Tracy 1102 distribution feeder. These overloads are forecasted to occur by summer 2022 and are the result of several large new business applications including Amazon and Home Depot warehouse-distribution centers. Transmission Substation Work (MWC 61) under this Project – Planning Order 5797580: • Install 60 kV main bus comprised of 2300Al bare conductor. • Install two 60 kV, 1200 A circuit breakers and associated disconnect switches. • Install one 60 kV, 1200 motor-operated air switch (MOAS) to sectionalize the 60 kV bus. • Install current and potential transformers and surge arresters as required for system protection. • Install 60kV control and protection racks inside the new switchgear building. | Transmission Line - Conductor | Relocate | NA | Load Growth | System Design Upgrade | NA | 2024-03-06 | NA | NA | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.27151 | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5802121 | T.0007094 | Carbona Substation Bank 2 Replacement | 4 | 60 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2022-11-17 | 2023-09-30 | 2024-12-06 | Prioritization | TRUE | 32000 | NA | 463.3795 | 1354.7893 | 0 | 0 | 0 | 144.9963 | 247.5129 | 894.3951 | 67.8849 | 0 | 0 | 0 | 0 | 392.5093 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 241 | CASCADE: Support Tline Configuration |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Transmission Line - Conductor | Relocate | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2024-02-12 | 23 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | 115 | NA | 58 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5780281 | T.0000651 | Cascade Substation Upgrade | 10 | 60 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2019-10-01 | 2014-03-01 | 2025-07-21 | Prioritization | TRUE | $20,000 ¦ $30,000 | NA | 2327.7995 | 3651.9631 | 1210.409 | 275.2578 | 190.2037 | 143.1207 | 332.7432 | 1335.7891 | 15.8073 | 0 | 0 | 0 | 0 | 2300.3667 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 242 | San Ardo Tap: T-Line Voltage Support |  |  | Monterey | The 60 kV system serving Oil Fields Substation and the large Chevron and Aera Energy oil production facilities in San Ardo, CA, could experience low voltages and a potential voltage collapse under certain outage situations. To strengthen the local 60 kV system a voltage support project has been proposed to install 10 MVAR of shunt capacitors at Oil Fields Substation. The CAISO supports the project and will approve it in their 2017-2018 Transmission Plan. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | System Design Upgrade | NERC TPL Standards | 2020-07-21 | 61 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.05 | NA | 60 | NA | 76 | Not Available | Not Available | RBPPF - TBD | Yes | 5791730 | T.0004889 | San Ardo: Oil Fields Voltage Support | 4 | 60 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-08-05 | 2022-05-01 | 2027-12-08 | Prioritization | FALSE | $7,000 ¦ $10,000 | NA | 81.4001 | 3210.9533 | 0 | 77.5362 | 3.864 | 0 | 0 | 184.7509 | 300 | 300 | 2000 | 100 | 0 | 81.4001 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 243 | Ravenswood Sub: Build Ravenswood Dsub T-Line |  |  | Menlo Park, San Mateo | This project proposes to install two 115/12 kV, 60 MVA banks with LTC, two 12 kV metal-clad switchgears, each with six feeder bays and install four 12 kV feeders at Ravenswood Substation to serve the requested demand of 37.1 MVA at new Meta (Facebook) Willow Village Campus in Menlo Park, starting in 2024. Transmission Substation Work (MAT 61A) • Extend the 115 kV bus to build Bus Section F with five bay spaces • Install two 115 kV bus sectionalizing breakers with disconnects • Install one 115 kV MPAC building • Upgrade Ravenswood 230 kV BAAH with redundant relays to mitigate against thermal overload on San Mateo-Belmont 115 kV Line caused by failure of non-redundant relay at Ravenswood 230 kV BAAH Bus #2 | Transmission Line - Conductor | Relocate | NA | Load Growth | System Design Upgrade | NA | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799746 | T.0007874 | RAVENSWOOD SUB:BUILD RAVENSWOOD DSUB | 2 | 60 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-07-01 | NA | 2026-07-29 | NA | FALSE | NA | NA | 15.3978 | 2229.0235 | 0 | 0 | 0 | 12.9821 | 2.2129 | 89.5515 | 1584.8585 | 247.4372 | 0 | 0 | 0 | 15.195 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 244 | Lerdo-Kern Oil-7th Standard 115kV Rerate |  |  | Bakersfield, Kern ¦ Kern ¦ Oildale CDP, Kern | This project proposes to reconductor approximately 15 miles of 115 kV line from Kern to Kern Oil substations. In addition, the project will upgrade the limiting equipment at the Live Oak, Kern Oil, and Petrol substations. Load and generation balance is difficult in this area as demand increases and more private generation retires. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | T-Line Capacity | NERC TPL Standards | 2023-11-17 | 123 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 16.3 | NA | 115 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 881 | RBPPF - TBD | Yes | 5784386 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 9 | 60 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | TBD | NOC | TBD | TBD | TBD | Planning | 5 | 2028-03-06 | 2016-03-01 | 2028-05-05 | Prioritization | FALSE | $40,000 ¦ $65,000 | NA | 0.8222 | 2656.953 | 0.8125 | 0.0096 | 0 | 0 | 0 | 0 | 100 | 300 | 500 | 750 | 2600 | 0.8222 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 245 | Lodi Sub: 60 kV T-Line Rearrangement |  |  | Lockeford CDP, San Joaquin ¦ Lodi, San Joaquin ¦ San Joaquin ¦ Victor CDP, San Joaquin | This project will replace all 60kV circuit breakers, 60kV Main and Auxiliary bus structure and the associated equipment at Lodi Substation.The replacement criteria were developed based on technical assessments of the switches including design characteristics, system criticality, historical failure rates, onsite inspections, vintage, environmental factors, and operating conditions. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Asset Condition | System Design Upgrade | NA | 2023-12-04 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | 48 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5774920 | T.0000303 | LODI SUB: REPL CB 12, 22 AND 32 | 2 | 60 | NA | 2013 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-12-10 | 2019-10-17 | 2021-01-14 | Clearances | TRUE | 7215 | NA | 2160.3927 | 2179.5455 | 288.2313 | 764.6987 | 418.6112 | 376.9374 | 41.5102 | 21.0648 | 0 | 0 | 0 | 0 | 80.0388 | 2158.4807 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1533.5626 | 330.8741 | 36.4349 | 5.3473 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ NA
| 246 | Pit PH1 Install TSP's for Malacha Line |  |  | Shasta | This project will replace the aging and deteriorated Bank 3 with a new transformer, as well as add a Bank 5 for redundancy and additional operational flexibility. The Load-Tap-Changer (LTC) built into Bank 3 will also provide flexibility in regulating voltage. The oil from the existing transformer banks will be disposed of per standard PG&E process; PSC, a contractor, will remove the oil from site and either recycle it (if low polychlorinated biphenyl (PCBs) count) or dispose of it at a hazardous waste facility (if high PCBs count). The project scope of work includes the following:  Install a new 30MVA, 60/11kV three-phase transformer with LTC, as replacement for Bank 3.  Install a new 70MVA, 230/60kV Bank 5.  Remove the existing Bank 3 and structures.  Install or upgrade spill prevention control and countermeasure (SPCC) as needed.  Install a new control building, protection package, and SCADA. | Transmission Line - Conductor | Relocate | NA | Asset Condition | System Design Upgrade | NA | 2024-03-20 | NA | NA | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | NA | 60 | NA | 202 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5774101 | T.0000623 | Pit No. 1 PH Transformer Upgrade | 3 | 60 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-04 | 2018-11-06 | 2020-01-14 | Bundling Dependencies | FALSE | 27000 | NA | 1630.1934 | 1630.1934 | 460.01 | 275.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1630.1934 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 1573.1151 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 247 | Rio Oso Sub: T-Line Re-String Conduc |  |  | Lincoln, Placer ¦ Placer ¦ Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2021-11-19 | 70 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | 1782 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5777058 | T.0000614 | Rio Oso Substation Upgrade | 12 | 60 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-29 | 2009-05-01 | 2025-06-17 | Prioritization | TRUE | $10,000 ¦ $20,000 | NA | 1165.4382 | 3329.7009 | 189.5597 | 137.9064 | 390.9557 | 262.9666 | 86.1491 | 1343.5987 | 458.7456 | 171.729 | 0 | 0 | 0 | 1152.0218 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 248 | KERN 230 KV AREA REINFORCEMENT (TLINE) |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Relocate | T.0000220 ¦ T.0003350 ¦ T.0000980 | Reliability | System Design Upgrade | NERC TPL Standards | 2024-04-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | 37.7504 | 230 | NA | 764 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5767328 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 60 | 5748541 | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-22 | 2013-05-01 | 2021-03-29 | Prioritization | FALSE | $32,000 ¦ $44,000 | NA | 3493.8506 | 3493.8506 | 580.0368 | 661.8887 | 169.7584 | 4.7196 | 3.6543 | 0 | 0 | 0 | 0 | 0 | 0 | 3493.8506 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 3487.1129 | 4.7196 | 3.6543 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 249 | KERN 230 KV AREA REINFORMCEMENT (TLINE) |  |  | Bakersfield, Kern ¦ Kern ¦ Oildale CDP, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Relocate | T.0000220 ¦ T.0003350 ¦ T.0000980 | Reliability | System Design Upgrade | NERC TPL Standards | 2022-10-06 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | NA | 230 | NA | 764 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5767359 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 60 | 5748541 | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-12-12 | 2013-05-01 | 2021-03-29 | Prioritization | FALSE | $32,000 ¦ $44,000 | NA | 4582.5096 | 4582.5096 | 493.3861 | 1002.3612 | 373.0205 | 6.7546 | 4.4216 | 0 | 0 | 0 | 0 | 0 | 0 | 4582.5096 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 4573.8166 | 6.7546 | 4.4216 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 250 | KERN 230KV BAAH 115KV LINE RELOCATION |  |  | Bakersfield, Kern ¦ Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Relocate | T.0000220 ¦ T.0003350 ¦ T.0000980 | Reliability | System Design Upgrade | NERC TPL Standards | 2024-03-25 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | NA | 115 | NA | 764 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5774778 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 60 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-11-07 | 2013-05-01 | 2020-02-20 | Prioritization | FALSE | $32,000 ¦ $44,000 | NA | 2759.097 | 2759.097 | 229.4703 | 594.9846 | 4.3567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2759.097 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 2749.7676 | 4.3573 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 251 | Wilson-Oro Loma 115 kV Reconductoring |  |  | El Nido CDP, Merced ¦ Fresno ¦ Madera ¦ Merced ¦ Merced, Merced | Reconductor approximately 9 circuit miles between Wilson and El Nido on the Wilson-Oro Loma 115 kV Line with a larger conductor to achieve at least 650 Amps of summer emergency rating. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2023-10-13 | 75 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 9 | NA | 115 | NA | Not Available | 8. Compliance/Commitments (But Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5791341 | T.0006016 | Wilson-Oro Loma 115 kV Reconductoring | 2 | 60 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | 2026-12-31 | 2027-05-01 | NA | FALSE | $11,300 ¦ $22,700 | NA | 9.0661 | 9.0661 | 0 | 0.11652 | 0.0084 | 2.1089 | 6.5665 | 0.1061 | 1500 | 3500 | 1000 | 0 | 0 | 8.9601 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
| 252 | Ignacio Area Upgrade: Ignacio-Alto |  |  | Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin | Reconductor Ignacio - San Rafael No. 1 115 kV Line, Ignacio - Alto 60 kV Line, and Ignacio - San Rafael No. 3 115 kV Line section from Ignacio - Las Gallinas as well as upgrade limiting equipment on lines. Add a 10 MVAR shunt capacitor at Greenbrae 60 kV Substation and associated substation upgrades to accommodate this installation | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-02-28 | 48 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 17.8 | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807460 | T.0009719 | Ignacio Area Upgrade | 4 | 60 | EX113201 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | 2012 ¦ 2018 | FALSE | 2012 ¦ 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-02-26 | 2023-12-01 | 2029-05-10 | Prioritization | FALSE | 37000 | NA | 6.2933 | 9374.7466 | 0 | 0 | 0 | 0 | 0 | 465.0756 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 253 | Ignacio Area Upgrade: Ignacio-Las Gallinas |  |  | Marin ¦ Novato, Marin ¦ San Rafael, Marin | Reconductor Ignacio - San Rafael No. 1 115 kV Line, Ignacio - Alto 60 kV Line, and Ignacio - San Rafael No. 3 115 kV Line section from Ignacio - Las Gallinas as well as upgrade limiting equipment on lines. Add a 10 MVAR shunt capacitor at Greenbrae 60 kV Substation and associated substation upgrades to accommodate this installation | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-03-19 | 48 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 4.1 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807461 | T.0009719 | Ignacio Area Upgrade | 4 | 60 | EX113201 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | 2012 ¦ 2018 | FALSE | 2012 ¦ 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-02-26 | 2023-12-01 | 2029-05-10 | Prioritization | FALSE | 37000 | NA | 8.5048 | 9391.1756 | 0 | 0 | 0 | 0 | 0 | 481.5662 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 254 | Ignacio Area Upgrade: Ignacio-San Rafael |  |  | Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin | Reconductor Ignacio - San Rafael No. 1 115 kV Line, Ignacio - Alto 60 kV Line, and Ignacio - San Rafael No. 3 115 kV Line section from Ignacio - Las Gallinas as well as upgrade limiting equipment on lines. Add a 10 MVAR shunt capacitor at Greenbrae 60 kV Substation and associated substation upgrades to accommodate this installation | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2023-08-19 | 63 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 11.4 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807459 | T.0009719 | Ignacio Area Upgrade | 4 | 60 | EX113201 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | 2012 ¦ 2018 | FALSE | 2012 ¦ 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-02-26 | 2023-12-01 | 2029-03-23 | Prioritization | FALSE | 37000 | NA | 5.2698 | 9307.3529 | 0 | 0 | 0 | 0 | 0 | 520.9821 | 5000 | 21200 | 13000 | 700 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 255 | Tulucay-Napa 60kV Line Reconductoring |  |  | Napa ¦ Napa, Napa | Reconductor the Tulucay-Napa #2 60 kV line from Tulucay to Basalt | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2023-11-17 | 124 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | 1.4 | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807341 | T.0009607 | Tulucay-Napa #2 60 kV line Reconductoring projec | 1 | 60 | EX113226 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-12-01 | 2028-12-31 | 2026-12-31 | NA | FALSE | 14600 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 500 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 256 | Fulton-Santa Rosa#1 115kV Reconductor |  |  | Cotati, Sonoma ¦ Penngrove CDP, Sonoma ¦ Petaluma, Sonoma ¦ Rohnert Park, Sonoma ¦ Santa Rosa, Sonoma ¦ Sonoma | Reconductoring of the Fulton-Santa Rosa #1 and #2, Santa Rosa-Corona and Corona-Lakeville 115 kV lines | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-04-09 | 20 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 33.1 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807463 | T.0009626 | Fulton-Santa Rosa#1 115kV Reconductor | 1 | 60 | EX113227 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-08-16 | 2028-12-31 | 2029-10-31 | Prioritization | FALSE | 74000 | NA | 11.5338 | 867.0264 | 0 | 0 | 0 | 0 | 0 | 617.636 | 950 | 3000 | 15000 | 20000 | 1000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 257 | Borden-Storey 230 kV 1 & 2 Recond |  |  | Chowchilla, Madera ¦ Madera ¦ Madera Acres CDP, Madera ¦ Merced ¦ Merced, Merced ¦ Parksdale CDP, Madera | Reconductoring the Borden – Storey section(s) of the Wilson – Borden #1 and #2 230 kV lines | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Policy | Line Reconductoring | NERC TPL Standards | 2023-09-29 | 18 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 10 | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807523 | T.0009662 | Borden-Storey 230 kV 1 and 2 Line Reconductoring | 2 | 60 | EX113239 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-10-01 | 2032-12-31 | 2029-05-01 | NA | FALSE | 50000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 4000 | 5000 | 9000 | 700 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-F-Board-Approved_2022-2023_Transmission-Plan.pdf
| 258 | Cortina #1 60050: Reconductor |  |  | Arbuckle CDP, Colusa ¦ Colusa ¦ Yolo | The Cortina #1 60 kV transmission line, located in Colusa County, is approximately 26.2 miles long and supported by 447 structures. The Arbuckle, Harrington and Dunnigan 60 kV substations are radially served by the Cortina #1 60 kV line with the Cortina #2 60 kV line serving as an alternate source with normally open switches. This project will help facilitate the delivery of an additional 10 MW to serve increased load in the Cortina area due to the addition of Tesla charging banks. The project scope of work includes: • Reconductor approximately 26.2 miles of the Cortina #1 60 kV Line between Cortina Substation and Dunnigan Substation with a conductor able to achieve at least 818 Amps of summer interior normal rating. • If new structures are required, they will be sized to accommodate a future distribution underbuild conductor of 715 AAC. • Existing distribution underbuild will be relocated to new transmission structures. • Removal of the idle Drake Substation tap and Switch 25. • Upgrade substation terminal equipment to achieve full conductor capacity. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NA | 2023-11-20 | 124 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 26.2 | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807078 | T.0009641 | Cortina 1 60050_Reconductor | 1 | 60 | 5807521 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-01 | NA | 2028-12-31 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 17000 | 33000 | 42300 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 259 | NEWARK-DIXON LANDING 10227: Reconductor |  |  | San Jose, Santa Clara ¦ Santa Clara | The project work will involve upgrading the capacity of the Piercy – Metcalf, Swift – Metcalf and Newark – Dixon Landing 115 kV Lines, so that the three lines have an emergency rating of at least 1,100 Amps. Substation equipment at Metcalf and Evergreen will be upgraded, as needed. The project may also include upgrading the Newark – Milpitas No. 1 Line, which shares towers with the Newark – Dixon Landing Line. (The project team will evaluate this additional work.) | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2023-09-06 | 28 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 8.9 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806850 | T.0009536 | Metcalf-Piercy, Swift-Metcalf, and Newark-Dixon Landing 115 kV Lines | 3 | 60 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-01 | 2008-12-31 | 2027-03-01 | Prioritization | FALSE | $5,000 ¦ $10,000 | NA | 0.3345 | 0.3345 | 0 | 0 | 0 | 0 | 0 | 0.3345 | 300 | 1100 | 4100 | 100 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 260 | PIERCY-METCALF 10390: Reconductor |  |  | Fremont, Alameda | The project work will involve upgrading the capacity of the Piercy – Metcalf, Swift – Metcalf and Newark – Dixon Landing 115 kV Lines, so that the three lines have an emergency rating of at least 1,100 Amps. Substation equipment at Metcalf and Evergreen will be upgraded, as needed. The project may also include upgrading the Newark – Milpitas No. 1 Line, which shares towers with the Newark – Dixon Landing Line. (The project team will evaluate this additional work.) | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2020-09-15 | 28 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | 4.7 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806848 | T.0009536 | Metcalf-Piercy, Swift-Metcalf, and Newark-Dixon Landing 115 kV Lines | 3 | 60 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-01 | 2008-12-31 | 2027-03-01 | Prioritization | FALSE | $5,000 ¦ $10,000 | NA | 0.3345 | 0.3345 | 0 | 0 | 0 | 0 | 0 | 0.3345 | 765 | 4500 | 200 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 261 | SWIFT-METCALF 10326: Reconductor |  |  | San Jose, Santa Clara ¦ Santa Clara | The project work will involve upgrading the capacity of the Piercy – Metcalf, Swift – Metcalf and Newark – Dixon Landing 115 kV Lines, so that the three lines have an emergency rating of at least 1,100 Amps. Substation equipment at Metcalf and Evergreen will be upgraded, as needed. The project may also include upgrading the Newark – Milpitas No. 1 Line, which shares towers with the Newark – Dixon Landing Line. (The project team will evaluate this additional work.) | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2022-10-06 | 28 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 4.7 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806849 | T.0009536 | Metcalf-Piercy, Swift-Metcalf, and Newark-Dixon Landing 115 kV Lines | 3 | 60 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-01 | 2008-12-31 | 2027-03-01 | Prioritization | FALSE | $5,000 ¦ $10,000 | NA | 0.3345 | 0.3345 | 0 | 0 | 0 | 0 | 0 | 0.3345 | 1435 | 8400 | 200 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 262 | S of SM Cap Incr: Ravenswood-San Mateo |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The project work will involve upgrading the capacity of the Ravenswood-San Mateo 115 kV Line. Specifically, this work will include: • Reconductoring of the 12-mile Ravenswood-San Mateo 115 kV Line, with a conductor having an emergency capability of at least 1,100 Amps; • Reinforcing the lattice steel towers, where needed, to support the new conductor; and • Replacement of limiting equipment within the substations. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-03-28 | 65 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 12 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807522 | T.0009639 | S of SM Cap Incr Ravenswood San Mateo | 1 | 60 | EX113213 | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-04-21 | 2009-05-01 | 2028-07-05 | Prioritization | FALSE | $10,000 ¦ $20,000 | NA | 3.095 | 3.095 | 0 | 0 | 0 | 0 | 0 | 2.0767 | 900 | 3100 | 29500 | 10700 | 0 | 1.0183 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 263 | Redwood City Area 115kV Syst Reinf |  |  | Menlo Park, San Mateo ¦ Redwood City, San Mateo | The scope of this project is to install a new 230/115 kV Transformer at Ravenswood Substation, and reconductor 6.5 circuit miles of the San Mateo - Belmont 115 kV Line and 7.5 circuit miles of the Ravenswood - Bair 115 kV Line #1. | Transmission Line/Substation | New | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-04-10 | 122 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 14 | NA | 115 | 230 ¦ 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807418 | T.0009638 | Redwood City 115kV System Reinforcement | 1 | 60 | EX113232 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | 2030-12-31 | 2029-12-01 | NA | FALSE | 110800 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 17000 | 22000 | 12500 | 1500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 264 | Coppermine 70 kV Reinforcement Tline |  |  | Fresno ¦ Fresno, Fresno ¦ Madera ¦ Madera Ranchos CDP, Madera ¦ Rolling Hills CDP, Madera | This project proposes to reconductor roughly 13 circuit miles of the Borden - Coppermine 70 kV Line and to install a voltage support device in the area. This will provide additional transmission capacity to serve electric customers in Madera and Fresno Counties. The project scope of work includes following: •Reconductor roughly 9.5 circuit miles of line between Borden and Cassidy Substations (from Pole 19/10A to Cassidy Substation) on the Borden-Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 700 Amps during summer normal conditions •Reconductor roughly 3.6 circuit miles of line between Cassidy and Coppermine Substations (from Pole 03/07 to Coppermine Substation) on the Borden - Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 500 Amps during summer normal conditions. •Remove any limiting components to achieve the full conductor capability •Install 20 MVar voltage support device at Coppermine Substation. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2023-09-20 | 61 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 13 | NA | 70 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803379 | T.0008870 | Coppermine 70 kV Reinforcement Project | 3 | 60 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | 2027-05-01 | 2027-05-01 | NA | FALSE | $15,800 ¦ $31,600 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 5500 | 500 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 265 | NorthEast Kern 115kV Reconductor |  |  | Buttonwillow CDP, Kern ¦ Kern | This project proposes to: • Reconductor ~13.6 circuit miles of Midway – Shafter 115 kV Line • Reconductor ~8.3 circuit miles on the Shafter-Rio Bravo 115 kV • Reconductor ~3.9 circuit miles on the Midway-Tupman-Rio Bravo-Renfro 115 kV (between Rio Bravo and Renfro Junction From 11/62 To Rio Bravo Sub) • Reconductor ~3.5 circuit miles on the Lerdo-Kern Oil-7th Standard 115 kV Line (between Lerdo J and Kern Oil, from 023/005 To Kern Oil Sub) • Reconductor ~6.8 circuit miles on the Smyrna-Semitropic-Midway 115 kV Line (between Midway and Ganso from Midway to 081/634 and from 081/634 to Ganso) • Reconductor ~14.1 circuit miles on the Semitropic-Midway #1 115 kV Line (between Midway and Semitropic_E) • Convert the existing control point to a summer setup to open line section from Wasco to McFarland 70 kV line. • Convert the existing control point to a summer setup to open line section from Famoso to Cawelo C 115 kV line. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-03-29 | 76 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 13.6 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807525 | T.0009633 | NorthEast Kern 115kV Reconductor | 2 | 60 | EX113342 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | 2032-12-31 | 2029-12-31 | NA | FALSE | 256000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 8000 | 26000 | 22000 | 32500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 266 | Garberville 60kV Area Reinforcement |  |  | Garberville CDP, Humboldt ¦ Humboldt | This project proposes to: • Reconductor the entire Bridgeville-Garberville 60 kV line to achieve at least 631Amps of summer normal rating (715 AAC conductor) which is about 36 circuit miles in length. • Install a 20 MVAR STATCOM at Fort Seward 60 kV Substation. • Establish a control point to open line section from Garberville to Kekawaka 60 kVline. • Establish a control point to open line section from Rio Dell Jct. to Carlotta 60 kV line. | Transmission Line/Substation | New | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-03-14 | 123 | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | 36.2 | NA | 60 | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807359 | T.0009603 | Garberville Area Reinforcement | 1 | 60 | EX113225 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-12-01 | 2032-12-31 | 2030-12-31 | NA | FALSE | 204000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 10600 | 13600 | 19300 | 26400 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 267 | Recond. SanMiguel-Paso Robles70kV lineP2 |  |  | El Paso de Robles, San Luis Obispo ¦ San Luis Obispo ¦ San Miguel CDP, San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2024-02-08 | 96 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion, Flooding |  | 9.9 | NA | 70 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805505 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 60 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2026-01-30 | 2019-05-01 | 2026-12-30 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 3167.5417 | 15743.9011 | 0 | 0 | 0 | 0 | 3129.3728 | 230.9582 | 0 | 0 | 0 | 0 | 0 | 3129.3728 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 268 | METCALF-GREEN VALLEY 115KV: LINE RECONDU |  |  | Interlaken CDP, Santa Cruz ¦ Morgan Hill, Santa Clara ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2024-04-10 | 95 | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 15 | NA | 115 | NA | 2135 | 8. Compliance/Commitments With Low Safety Risk | 50 | RBPPF - TBD | Yes | 5782106 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 7 | 60 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-03-08 | 2021-12-01 | 2028-04-17 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 5731.349 | 104920.4183 | 1054.3733 | 1110.7044 | 610.6841 | 443.1191 | 1.4268 | 1893.4185 | 18000 | 28000 | 20000 | 100 | 0 | 5692.0697 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 269 | METCALF-GREEN VLY 115kV: ACQUIRE EASE |  |  | Interlaken CDP, Santa Cruz ¦ Morgan Hill, Santa Clara ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Other | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2024-04-10 | 38 | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 15 | NA | 115 | NA | 137 | 8. Compliance/Commitments With Low Safety Risk | 50 | RBPPF - TBD | Yes | 5531782 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 7 | 60 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-07-29 | 2021-12-01 | 2026-05-25 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 0 | 3378.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1500 | 500 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 270 | VALLEYSPRINGS-MARTELL NO.2 SCADA |  |  | Amador ¦ Calaveras ¦ Jackson, Amador ¦ Martell CDP, Amador | Phase 1 of this project will replace 6 manually operated switches with SCADA-operable switches on the Valley Springs-Martell No. 1, Valley Springs – Clay, and the Pardee No. 2 Tap 60kV lines. The associated wood poles will be replaced with 4 Tubular Steel Poles (TSP) and 2 Engineered Direct Embedded Poles (EDEP) as required. This project will improve customer electric service reliability by reducing outage durations and allowing greater operational flexibility. Phase 2 of this project will replace 4 manually operated switches with SCADA-operable switches on the Clay - Martell 60kV line. The associated wood poles will be replaced with 3 Fiberglass Poles and one Engineered Direct Embedded Poles (EDEP) as required. The manual switches will be replaced with either Cleveland/Price or SEECO switches. The project is being constructed in 2 phases due to testing required for the new fiberglass pole design. | Transmission Line - Switch | Upgrade/Retrofit | NA | Reliability | T-Line Reliability | NA | 2023-09-29 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 58 | 5. Compliance/Commitments With Strong Safety Link | 41 | NA | NA | 5775027 | T.0003024 | ValleySprings-Martell No.2 SCADA | 3 | 60 | NA | 2010 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5801-E | 2020-04-03 | Approved | 2020 | Operational | 2 | 2019-12-06 | 2021-03-31 | 2020-07-03 | NA | FALSE | 10500 | NA | 3962.8553 | 3962.8553 | 759.4816 | 1421.7051 | 82.3715 | 2.2797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3962.8553 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 3799.0325 | 80.0036 | 2.214 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ $50 Mil – $75 Mil
| 271 | East Shore-Oakland J 115 kV Reconductor |  |  | Alameda ¦ Hayward, Alameda ¦ San Leandro, Alameda ¦ San Lorenzo CDP, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Transmission Line - Conductor | Upgrade/Retrofit | T.0004580 | Reliability | Line Reconductoring | NERC TPL Standards | 2021-09-28 | 103 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 15 | NA | 115 | NA | 2167 | 8. Compliance/Commitments With Low Safety Risk | 425 | NA | NA | 5747763 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 60 | 5767363 | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E/AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020/2022 | Operational | 2 | 2021-06-01 | 2015-03-01 | 2023-09-13 | Prioritization | TRUE | $15,000 ¦ $30,000 | NA | 48346.2838 | 49104.4573 | 852.5317 | 1825.6787 | 21238.9048 | 8584.9668 | 12685.948 | 97.8553 | 885.0013 | 0 | 0 | 0 | 0 | 48121.6008 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0.05923 | 0 | 0 | 46621.6606 | 152.6454 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 272 | LEMOORE NAS 70 KV SCADA SW#55 65 |  |  | Fresno ¦ Kings ¦ Lemoore Station CDP, Kings ¦ Riverdale CDP, Fresno | Reconductor 25 circuit miles of 70 kV electric transmission lines between Caruthers, Camden and Lemoore Naval Air Station (NAS) Substations, construct a new 2 mile 70 kV line from Lemoore NAS to Henrietta Substation and upgrade protection at Henrietta Substation.. This project will increase transmission capacity, improve operational flexibility and service reliability, and modernize electric equipment for serving electric customers in Fresno and Kings County, resulting in increased customer satisfaction. | Transmission Line - Switch | Upgrade/Retrofit | NA | Reliability | T-Line Reliability | NA | 2024-04-10 | 107 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | 318 | 8. Compliance/Commitments With Low Safety Risk | 455 | RBPPF - TBD | Yes | 5767093 | T.0000134 | LEMOORE NAS SCADA SW 55, 65 | 1 | 60 | 5734813 | 2010 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2024-02-21 | 2019-04-23 | 2024-03-08 | Prioritization | TRUE | 3953 | NA | 4743.3798 | 5194.4504 | 307.1561 | 75.5088 | 419.918 | 544.0664 | 0 | 437.9577 | 13.1129 | 0 | 0 | 0 | 0 | 4743.3798 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $15 Mil - $20 Mil ¦ $20 Mil - $30 Mil
| 273 | ELECTRA-VALLEY SPRINGS CAP REC |  |  | Amador ¦ Calaveras ¦ Mokelumne Hill CDP, Calaveras ¦ Pine Grove CDP, Amador ¦ Pioneer CDP, Amador ¦ Red Corral CDP, Amador | Reconductor a 10.9-mile section on the West Point – Valley Springs 60 kilovolt (kV) Line. This project will increase transmission capacity to reliably serve electric customers in Calaveras County. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2024-04-12 | 61 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $100 Mil – $125 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 10.9 | NA | 60 | NA | 20 | 8. Compliance/Commitments With Low Safety Risk | 1 | NA | NA | 5767632 | T.0000458 | West Point-Valley Springs 60kV Reinforce | 3 | 60 | 5726146 | 2007 | 2007 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5327-E | 2018-07-06 | Approved | 2018 | Operational | 2 | 2019-03-18 | 2009-05-01 | 2020-05-05 | ISO Action | FALSE | $5,000 ¦ $10,000 | NA | 21360.6501 | 21360.6501 | 11980.5826 | 5116.0398 | -59.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21360.6501 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 19417.0418 | -52.9746 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 274 | Midway-Kern PP #2 230 kV Line |  |  | Bakersfield, Kern ¦ Buttonwillow CDP, Kern ¦ Greenacres CDP, Kern ¦ Kern ¦ Rosedale CDP, Kern | Reconductor and split 42 circuit miles of the Midway-Kern No. 1 230kV Line and relocate Stockdale 230kV lines 1 and 2. The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Multiple | New | T.0001650 ¦ T.0003202 | Reliability | New T-Line | NERC TPL Standards | 2024-04-09 | 81 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | 21 | NA | 230 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5756002 | T.0000220 | Midway-Kern Nos. 1 and 2 230kV Line | 4 | 60 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5026-E | 2017-02-21 | Approved | 2017 | Operational | 2 | 2018-11-01 | 2019-05-01 | 2019-03-25 | NA | FALSE | $60,000 ¦ $90,000 | NA | 22597.7315 | 22597.7315 | 7370.4962 | -200.9173 | 0.3615 | -38.1858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22597.7315 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 20558.8766 | -179.4521 | 0.32387 | -34.209 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $40 Mil - $50 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 275 | Midway-Kern PP #2 230 kV Line - Ph 2 |  |  | Bakersfield, Kern ¦ Buttonwillow CDP, Kern ¦ Greenacres CDP, Kern ¦ Kern ¦ Rosedale CDP, Kern | Reconductor and split 42 circuit miles of the Midway-Kern No. 1 230kV Line and relocate Stockdale 230kV lines 1 and 2. The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | New | T.0001650 ¦ T.0003202 | Reliability | New T-Line | NERC TPL Standards | 2024-04-09 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | 21 | NA | 230 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 404 | RBPPF - TBD | Yes | 5777198 | T.0000220 | Midway-Kern Nos. 1 and 2 230kV Line | 4 | 60 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5026-E | 2017-02-21 | Approved | 2017 | Planning | 5 | 2026-11-04 | 2019-05-01 | 2027-04-29 | Prioritization | FALSE | $60,000 ¦ $90,000 | NA | 96.893 | 7174.4989 | 16.4737 | 9.51 | 7.5434 | 2.402 | 0 | 0 | 445.3082 | 2781.0316 | 3816.9339 | 69.6715 | 0.0003 | 96.893 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $40 Mil - $50 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 276 | STOCKDALE 230 KV TAP #1 AND #2 REMOVALS |  |  | Bakersfield, Kern | Reconductor and split 42 circuit miles of the Midway-Kern No. 1 230kV Line and relocate Stockdale 230kV lines 1 and 2. The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Removal | T.0001650 ¦ T.0003202 | Reliability | System Design Upgrade | NERC TPL Standards | 2022-10-25 | 119 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | 0.1 | NA | 230 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767356 | T.0000220 | Midway-Kern Nos. 1 and 2 230kV Line | 4 | 60 | 5756002 | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5026-E | 2017-02-21 | Approved | 2017 | Operational | 2 | 2019-10-15 | 2019-05-01 | 2019-11-01 | Prioritization | FALSE | $60,000 ¦ $90,000 | NA | 1484.4732 | 1484.4732 | 295.6619 | 22.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1484.4732 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1467.6075 | 22.4159 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $40 Mil - $50 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 277 | Stockdale 230kV Tap #1 & 2 Removal Ph. 2 |  |  | Bakersfield, Kern | Reconductor and split 42 circuit miles of the Midway-Kern No. 1 230kV Line and relocate Stockdale 230kV lines 1 and 2. The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Removal | T.0001650 ¦ T.0003202 | Reliability | System Design Upgrade | NERC TPL Standards | 2022-10-21 | 45 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 12.4 | NA | 230 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 962 | NA | NA | 5785941 | T.0000220 | Midway-Kern Nos. 1 and 2 230kV Line | 4 | 60 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5026-E | 2017-02-21 | Approved | 2017 | Operational | 2 | 2021-01-08 | 2019-05-01 | 2021-02-10 | Clearances | FALSE | $60,000 ¦ $90,000 | NA | 1843.5264 | 1843.5264 | 461.5066 | 849.7257 | 532.2941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1843.5264 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 1871.6268 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $40 Mil - $50 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 278 | Giffen 70 kV Tap Line Reconductoring |  |  | Fresno | Reconductor approximately 5 miles of the Giffen 70 kV Tap Line with a conductor having summer emergency (SE) rating of at least 742 Amps (715 AAC conductor or equivalent) | Transmission Line - Conductor | Upgrade/Retrofit | NA | Economic | Line Reconductoring | NERC TPL Standards | 2020-06-02 | 79 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 5 | NA | 70 | NA | Not Available | 5. Compliance/Commitments With Strong Safety Link | 1209 | NA | NA | 5785942 | T.0004833 | Giffen 70 kV Tap Line Reconductoring | 1 | 60 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6600-E | 2022-05-23 | Approved | 2022 | Operational | 2 | 2023-11-01 | TBD | 2023-12-21 | Prioritization | TRUE | 5000 | NA | 3845.2725 | 4064.4952 | 0 | 84.8016 | 410.8895 | 352.239 | 2884.1198 | 332.4453 | 0 | 0 | 0 | 0 | 0 | 3732.0498 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 3389.0611 | 116.6388 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 279 | WHEELER RIDGE-WEEDPATCH 70 KV (KALTR |  |  | Bakersfield, Kern ¦ Kern ¦ Weedpatch CDP, Kern | Reconductor approximately 5.5 miles of limiting conductor at Wheeler Ridge – Weedpatch 70 kV Line from Pole No. 009/120 to Weedpatch Substation. The project expects to improve service reliability in core operations by reconductoring the Wheeler Ridge- Weedpatch 70kV Line that will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | T.0001604 | Reliability | Line Reconductoring | NERC TPL Standards | 2021-11-09 | 71 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 15 | NA | 70 | NA | 137 | Not Available | NA | NA | NA | 5767281 | T.0000144 | WHEELER RIDGE-WEEDPATCH 70 KV (KALTR)(SU | 1 | 60 | 5756005 | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5092-E | 2017-06-15 | Approved | 2017 | Operational | 2 | 2018-11-01 | 2018-05-31 | 2019-03-11 | Prioritization | FALSE | $15,000 ¦ $25,000 | NA | 4644.6083 | 4644.6083 | 483.2446 | 36.4045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4644.6083 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 4320.9623 | 33.9694 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 280 | Fulton-Fitch Mountain 60 kV Reconductori |  |  | Fulton CDP, Sonoma | Reconductor approximately 8 miles of the Fulton-Hopland 60kV Line and 1.3 miles of the Geysers 12-Fulton 230kV Line, rerate another section of the Fulton-Hopland 60kV Line and Fitch Mountain #2 60kV Tap, and upgrade switches and associated equipment at Fitch Mountain Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2024-03-05 | 51 | Steady State Power Flow System Analysis | Wires - System Configuration Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 8 | 13.4076 | 60 | NA | 490 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5735399 | T.0000039 | Fulton-Fitch Mtn 60kV Reconductor | 5 | 60 | NA | 2015 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-10-11 | IS/MND | NA | CPUC | NA | PTC: A.15-12-005 | 2015-12-03 | Approved | 2017 | Operational | 2 | 2018-10-01 | 2013-05-01 | 2019-03-18 | Prioritization | FALSE | 5000 | NA | 28267.9424 | 28267.9424 | 9146.0098 | 2762.294 | 81.1073 | 17.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28267.9424 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 23586.5479 | 2547.1699 | 74.7722 | 16.4754 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 281 | NRS-Scott Transmission Line Work |  |  | Santa Clara, Santa Clara | Reconductor the NRS – Scott Nos. 1 and 2 Lines with a conductor having a capacity of at least 1,500 Amps. This project will reduce safety risk and improve service reliability. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2022-10-28 | 16 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 2 | NA | 115 | NA | 58 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5752089 | T.0000113 | NRS-SCOTT NO. 1 LINE RECONDUCTORING | 2 | 60 | 5767086 | 2013 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5325-E | 2018-07-03 | Approved | 2018 | Operational | 2 | 2019-01-14 | 2016-05-31 | 2019-02-25 | Prioritization | FALSE | $2,000 ¦ $4,000 | NA | 6480.7572 | 6480.7572 | 3063.9138 | 33.432 | 6.5258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6480.7572 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 6359.9484 | 32.9603 | 6.4334 | 1e-05 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 282 | Stockton 'A' - Weber 60 kV Lines Reconductor |  |  | Kennedy CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | Reconductor the Stockton ‘A’-Weber 60kV Line Nos. 1 and 2 (8.8 circuit miles) and upgrade terminal equipment at Stockton ‘A’ and Weber 60kV substations | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2023-11-21 | 10 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 4.4 | NA | 60 | NA | 58 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5739682 | T.0000454 | STOCKTON 'A' - WEBER Reconductor | 2 | 60 | NA | 2010 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | 2010 | FALSE | 2010 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5264-E | 2018-04-02 | Approved | 2018 | Operational | 2 | 2018-08-02 | 2011-05-01 | 2019-09-23 | Project Design | FALSE | $5,000 ¦ $10,000 | NA | 9495.5801 | 9495.5801 | 4448.1218 | 74.8064 | 10.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9495.5801 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 8487.5756 | 73.1377 | 9.8194 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 283 | WEBER-SANTA FE JUNCTION 60 KV RECONDUCTOR |  |  | Stockton, San Joaquin | Reconductor the Stockton ‘A’-Weber 60kV Line Nos. 1 and 2 (8.8 circuit miles) and upgrade terminal equipment at Stockton ‘A’ and Weber 60kV substations | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2024-02-09 | 10 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 4.4 | 2.4271 | 60 | NA | 58 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767625 | T.0000454 | STOCKTON 'A' - WEBER Reconductor | 2 | 60 | 5738191 | 2010 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2010 | FALSE | 2010 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5264-E | 2018-04-02 | Approved | 2018 | Operational | 2 | 2019-02-12 | 2011-05-01 | 2019-07-09 | Project Design | FALSE | $5,000 ¦ $10,000 | NA | 11227.3471 | 11227.3471 | 8066.2331 | 41.5609 | -30.3175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11227.3471 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 9975.4008 | 41.2666 | -26.9246 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 284 | Panoche - Oro Loma Phase 2 |  |  | Fresno | Reconductoring the Panoche-Oro Loma 115kV Line will increase transmission capacity and grid reliability in the area, as well as provide capability for future interconnections. The project scope are as follows: • Reconductor approximately 17 miles of the Panoche-Oro Loma 115kV Line with a conductor capable of handling at least 825 Amps and 975 Amps under summer normal and emergency conditions, respectively. The conductor type proposed by the project team is 1113 AAC conductor. • Upgrade the 115kV bus and install two SCADA switch automatics at Hammonds Substation • Upgrade terminal equipment at Panoche, Oro Loma and Hammonds substations • Install new SCADA switches at Panoche and De Francesco Junctions • Remove 183 wood poles and install 156 new light duty steel poles (LDSP), reframe 35 existing LDSPs | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2023-11-27 | 14 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 10.7 | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5800299 | T.0002127 | PANOCHE-ORO LOMA 115 KV RECONDUCTORING | 7 | 60 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5390-E | 2018-09-28 | Approved | 2018 | Operational | 2 | 2022-10-18 | 2021-05-01 | 2023-02-22 | Prioritization | TRUE | 20000 | NA | 3326.9249 | 3326.9249 | 0 | 0 | 0 | 2889.7092 | 437.2156 | 0 | 0 | 0 | 0 | 0 | 0 | 3326.9249 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2812.9364 | -1e-05 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
| 285 | Panoche - Oro Loma Phase 3 |  |  | Fresno | Reconductoring the Panoche-Oro Loma 115kV Line will increase transmission capacity and grid reliability in the area, as well as provide capability for future interconnections. The project scope are as follows: • Reconductor approximately 17 miles of the Panoche-Oro Loma 115kV Line with a conductor capable of handling at least 825 Amps and 975 Amps under summer normal and emergency conditions, respectively. The conductor type proposed by the project team is 1113 AAC conductor. • Upgrade the 115kV bus and install two SCADA switch automatics at Hammonds Substation • Upgrade terminal equipment at Panoche, Oro Loma and Hammonds substations • Install new SCADA switches at Panoche and De Francesco Junctions • Remove 183 wood poles and install 156 new light duty steel poles (LDSP), reframe 35 existing LDSPs | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2023-11-27 | 14 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.6 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804579 | T.0002127 | PANOCHE-ORO LOMA 115 KV RECONDUCTORING | 7 | 60 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5390-E | 2018-09-28 | Approved | 2018 | Construction (under 10%) | 3 | 2024-03-11 | 2021-05-01 | 2024-04-30 | Prioritization | TRUE | 20000 | NA | 63.6454 | 2075.5394 | 0 | 0 | 0 | 0 | 43.3376 | 2032.2018 | 0 | 0 | 0 | 0 | 0 | 43.3375 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
| 286 | Panoche- Oro Loma 115 kV Reconductoring |  |  | Fresno | Reconductoring the Panoche-Oro Loma 115kV Line will increase transmission capacity and grid reliability in the area, as well as provide capability for future interconnections. The project scope are as follows: • Reconductor approximately 17 miles of the Panoche-Oro Loma 115kV Line with a conductor capable of handling at least 825 Amps and 975 Amps under summer normal and emergency conditions, respectively. The conductor type proposed by the project team is 1113 AAC conductor. • Upgrade the 115kV bus and install two SCADA switch automatics at Hammonds Substation • Upgrade terminal equipment at Panoche, Oro Loma and Hammonds substations • Install new SCADA switches at Panoche and De Francesco Junctions • Remove 183 wood poles and install 156 new light duty steel poles (LDSP), reframe 35 existing LDSPs | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2023-11-27 | 13 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 5.7 | NA | 115 | NA | 604 | 8. Compliance/Commitments With Low Safety Risk | 365 | NA | NA | 5760564 | T.0002127 | PANOCHE-ORO LOMA 115 KV RECONDUCTORING | 7 | 60 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5390-E | 2018-09-28 | Approved | 2018 | Operational | 2 | 2022-01-17 | 2021-05-01 | 2022-03-18 | Prioritization | FALSE | 20000 | NA | 7146.2861 | 7146.2861 | 235.8753 | 275.5633 | 2057.1132 | 3464.4635 | 3.6115 | 0 | 0 | 0 | 0 | 0 | 0 | 7146.2861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 6096.2833 | 3.0436 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
| 287 | PANOCHE-ORO LOMA 115 JCT SW |  |  | Fresno | Reconductoring the Panoche-Oro Loma 115kV Line will increase transmission capacity and grid reliability in the area, as well as provide capability for future interconnections. The project scope are as follows: • Reconductor approximately 17 miles of the Panoche-Oro Loma 115kV Line with a conductor capable of handling at least 825 Amps and 975 Amps under summer normal and emergency conditions, respectively. The conductor type proposed by the project team is 1113 AAC conductor. • Upgrade the 115kV bus and install two SCADA switch automatics at Hammonds Substation • Upgrade terminal equipment at Panoche, Oro Loma and Hammonds substations • Install new SCADA switches at Panoche and De Francesco Junctions • Remove 183 wood poles and install 156 new light duty steel poles (LDSP), reframe 35 existing LDSPs | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2023-11-27 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 69 | 8. Compliance/Commitments With Low Safety Risk | 365 | NA | NA | 5777458 | T.0002127 | PANOCHE-ORO LOMA 115 KV RECONDUCTORING | 7 | 60 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5390-E | 2018-09-28 | Approved | 2018 | Operational | 2 | 2020-01-24 | 2021-05-01 | 2020-05-14 | NA | FALSE | 20000 | NA | 3349.0669 | 3349.0669 | 509.5779 | 2531.4804 | 2.1946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3349.0669 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 3319.9477 | 2.1732 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
| 288 | Reconductor Bellota-Cottle 230 kV |  |  | East Oakdale CDP, Stanislaus ¦ Oakdale, Stanislaus ¦ San Joaquin ¦ Stanislaus | Reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations. Key construction elements are as follows: • Replace 22.5 miles of the Bellota-Warnerville 230 kV circuit • Replace 19.9 miles of the Bellota-Cottle 230 kV circuit • Replace 2.5 miles of the Cottle-Melones 230 kV circuit • Replace 0.1 mile of the Warnerville-Wilson 230 kV circuit • Upgrade transmission line terminals at Bellota, Cottle, and Warnerville substations | Transmission Line - Conductor | Upgrade/Retrofit | NA | Policy | Line Reconductoring | NERC TPL Standards | 2023-10-25 | 92 | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 45 | NA | 230 | NA | 318 | 5. Compliance/Commitments With Strong Safety Link | 498 | RBPPF - TBD | Yes | 5785878 | T.0000043 | Bellota-Warnerville 230kV Reinforcement | 8 | 60 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6047-E | 2021-01-06 | Approved | 2021 | Operational | 2 | 2023-11-01 | 2024-12-31 | 2024-03-31 | NA | TRUE | 28000 | NA | 14252.6997 | 15543.6173 | 0 | 5.6811 | 1.5763 | 3855.097 | 4702.4345 | 6944 | 16 | 14.7531 | 0 | 0 | 0 | 7642.6997 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 14252.6997 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 289 | Warnerville-Bellota 230 kV line reconduc |  |  | East Oakdale CDP, Stanislaus ¦ Oakdale, Stanislaus ¦ San Joaquin ¦ Stanislaus | Reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations. Key construction elements are as follows: • Replace 22.5 miles of the Bellota-Warnerville 230 kV circuit • Replace 19.9 miles of the Bellota-Cottle 230 kV circuit • Replace 2.5 miles of the Cottle-Melones 230 kV circuit • Replace 0.1 mile of the Warnerville-Wilson 230 kV circuit • Upgrade transmission line terminals at Bellota, Cottle, and Warnerville substations | Transmission Line - Conductor | Upgrade/Retrofit | NA | Policy | Line Reconductoring | NERC TPL Standards | 2024-04-09 | 33 | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 23 | NA | 230 | NA | 318 | 8. Compliance/Commitments With Low Safety Risk | 1067 | NA | NA | 5756012 | T.0000043 | Bellota-Warnerville 230kV Reinforcement | 8 | 60 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6047-E | 2021-01-06 | Approved | 2021 | Operational | 2 | 2022-06-01 | 2024-12-31 | 2023-04-28 | NA | TRUE | 28000 | NA | 77428.0496 | 81062.8888 | 1092.0303 | 1285.201 | 1286.234 | 54985.3305 | 17193.1914 | 3490.7961 | 244.0184 | 0 | 0 | 0 | 0 | 77326.6335 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 74177.666 | 128.2969 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 290 | Reconductor Delevan-Cortina 230kV line |  |  | Colusa | The Delevan – Cortina 230 kV transmission line, located in Colusa county, is 18.0 miles long and supported by 122 structures. The Delevan – Cortina 230 kV line is a critical component of the 230 kV corridor in the North Valley connecting the Round Mountain and Vaca-Dixon substations. This project will help facilitate the delivery of an additional 437 MW of renewable generation and energy storage to PG&E’s local grid. The project scope of work includes: • Reconductor approximately 17.7 miles of the Delevan – Cortina 230 kV Line with a conductor able to achieve at least 1517 Amps of summer interior emergency rating. The use of Aluminum conductor composite reinforced (ACCR) or Aluminum conductor composite core (ACCC) conductors will be investigated to minimize unnecessary structure replacement. • Conduct a field verification to determine if the existing structures will need to be replaced, repaired or recoated. • Replace all insulators and insulator hardware. When reinsulating and reconductoring on double circuit structures, the scope is limited to insulators and hardware on the subject line. • Upgrade terminal equipment at Delevan and Cortina substations, as needed, to accommodate transmission line conductor capacity. • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Policy | Line Reconductoring | NERC TPL Standards | 2021-11-16 | 122 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 18 | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804245 | T.0009013 | Delevan-Cortina 230 kV Line Reconductoring | 1 | 60 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | NA | TBD | NA | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2027-04-27 | 2028-01-01 | 2027-09-02 | NA | FALSE | $17,700 ¦ $35,400 | NA | 34.0763 | 24223.5257 | 0 | 0 | 0 | 0 | 0 | 857.5296 | 2500 | 4200 | 12400 | 14000 | 1400 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 291 | Kingsburg-Lemoore 70 kV Line Reconduct |  |  | Armona CDP, Kings ¦ Fresno ¦ Hanford, Kings ¦ Kings ¦ Lemoore, Kings | The following work scope is required to complete the Kingsburg – Lemoore 70 kV Line Reconductoring Project:•Continue permitting and environmental activities.•Acquire temporary construction easements for pull and crane sites.•Procure long lead time materials in accordance with the construction schedule.•Complete approximately 8.3 miles of reconductoring.•Reconductor the line with a conductor capable of handling at least 742 Amps during emergency conditions.•To gain efficiencies, the substation scope of upgrading and relocation of the terminal equipment (Lemoore CB 12 and associated switches) will be completed as part of the Lemoore 70 kV Disconnect Switches project. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-02-06 | 14 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 8.3 | NA | 70 | NA | 564 | 8. Compliance/Commitments With Low Safety Risk | 609 | RBPPF - TBD | Yes | 5738261 | T.0000105 | KINGSBURG-LEMOORE 70KV RECONDUCTOR | 1 | 60 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | TBD | FALSE | 2019 | TBD | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5236-E | 2018-02-21 | Approved | 2018 | On Hold | 4 | 2025-11-18 | NA | 2026-03-09 | NA | FALSE | NA | NA | 2619.0345 | 10416.5618 | 149.3803 | 62.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5265.1588 | 2619.0345 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 292 | LOS BANOS-SANTA NELLA RECONDUCTOR |  |  | Los Banos, Merced ¦ Merced ¦ Santa Nella CDP, Merced ¦ Volta CDP, Merced | The Oro Loma 70 kV Area Reinforcement project will reconductor 70 kV lines in the Oro Loma area to help ensure reliable electric service to customers in the Merced County. The project will reconductor 2.4 miles of the Los Banos - Livingston Jct – Canal 70 kV Line, from Los Banos to Santa Nella substations and 10.8 miles of the Mercy Springs SW STA – Canal – Oro Loma 70 kV Line, from Mercy Springs SW STA to Canal Substation. The conductor should be capable of handling at least 825 Amps and 975 Amps during summer normal and emergency conditions, respectively. Associated substation terminal equipment will be upgraded as needed to meet the ratings of the new line conductor. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2023-11-07 | 39 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | 2.4 | NA | 70 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | 304 | RBPPF - TBD | Yes | 5767204 | T.0000157 | Ora Loma 70kV Reinforcement | 4 | 60 | 5746746 | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-09-21 | 2015-05-01 | 2026-11-13 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 276.0805 | 7530.809 | 169.693 | 68.8754 | 0 | 0 | 0 | 617.1773 | 636.7943 | 6067.7874 | 0.5639 | 0 | 0 | 276.0805 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 293 | MERCY SPRINGS - CANAL SS T-LINE RECONDUT |  |  | Fresno ¦ Los Banos, Merced ¦ Merced | The Oro Loma 70 kV Area Reinforcement project will reconductor 70 kV lines in the Oro Loma area to help ensure reliable electric service to customers in the Merced County. The project will reconductor 2.4 miles of the Los Banos - Livingston Jct – Canal 70 kV Line, from Los Banos to Santa Nella substations and 10.8 miles of the Mercy Springs SW STA – Canal – Oro Loma 70 kV Line, from Mercy Springs SW STA to Canal Substation. The conductor should be capable of handling at least 825 Amps and 975 Amps during summer normal and emergency conditions, respectively. Associated substation terminal equipment will be upgraded as needed to meet the ratings of the new line conductor. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2023-12-21 | 71 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 10.8 | NA | 70 | NA | 213 | 8. Compliance/Commitments With Low Safety Risk | 578 | RBPPF - TBD | Yes | 5767240 | T.0000157 | Ora Loma 70kV Reinforcement | 4 | 60 | 5746746 | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-01-23 | 2015-05-01 | 2026-05-28 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 4763.8901 | 15348.0521 | 408.8228 | 187.5715 | 2609.703 | 27.6674 | 0 | 1187.1671 | 5053.4577 | 4439.4983 | 0 | 0 | 0 | 4763.8901 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 294 | Kearney-Caruthers 70 kV Line Reconductor |  |  | Fresno | The project scope of work includes following:•Reconductor approximately 12 miles of the Kearney – Caruthers 70 kV Line with a conductor capable of handling at least 600 Amps and 700 Amps during summer normal and summer emergency conditions, respectively.•Replace wood poles as needed •Upgrade terminal equipment at Kearney and Caruthers substations as necessary to accommodate the rating of the transmission line conductor. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2021-10-05 | 81 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 12 | NA | 70 | NA | 58 | Not Available | NA | NA | NA | 5755977 | T.0000022 | Kearney-Caruthers_70kV Line Reconductor | 1 | 60 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5153-E | 2017-10-05 | Approved | 2017 | Operational | 2 | 2019-01-22 | 2016-05-31 | 2019-06-10 | Prioritization | FALSE | $13,000 ¦ $20,000 | NA | 6292.929 | 6292.929 | 3554.2603 | -40.6244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6292.929 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 5835.3518 | -37.1312 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - System Configuration Alternative ¦ Wires - Voltage Support/Reactive Support Alternative [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 295 | Weber-Mormon Jct Line Section Reconductoring Project |  |  | Garden Acres CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | The project will increase operating flexibility, load serving capability, customer reliability, eliminate normal overloads and improve asset health by performing the following scope: • Rebuild 6.2 circuit miles between Weber (000/004) and Mormon (006/103) of the Weber - Mormon Jct. 60 kV Line and conductor with a larger conductor to achieve at least 742 Amps of summer interior emergency rating. • New poles will be sized to accommodate future distribution under build conductor. • Upgrade substation terminal equipment to achieve full conductor capacity, if needed. • Include all open maintenance tags within the project scope where applicable. • When replacing structures, all insulators and insulator hardware should be replaced. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2023-12-20 | 124 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.2 | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803222 | T.0008749 | Weber - Mormon Jct 60 kV Line Section Reconductoring | 1 | 60 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2027-05-11 | 2027-05-01 | 2027-06-08 | NA | FALSE | $9,300 ¦ $18,600 | NA | 65.0828 | 8228.1706 | 0 | 0 | 0 | 0 | 5.0164 | 1161.5038 | 6200 | 7400 | 3500 | 0 | 0 | 5.0164 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 296 | METCALF - EVERGREEN RECONDUCTORING (TL) |  |  | San Jose, Santa Clara ¦ Santa Clara | The project work will involve upgrading the capacity of the Metcalf – Evergreen Nos. 1 and 2 115 kV Lines, so that both lines have an emergency rating of at least 1,100 Amps. Substation equipment at Metcalf and Evergreen will be upgraded, as needed. The proposed line reinforcement work will involve reconductoring these 115 kV lines with a conductor having an emergency capability of at least 1,100 Amps. Substation equipment will also be upgraded as needed to meet the capability of the new transmission line conductor. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2023-12-07 | 71 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 21.4 | NA | 115 | NA | 137 | Not Available | NA | NA | NA | 5767164 | T.0000147 | METCALF - EVERGREEN RECONDUCTORING (TL) | 2 | 60 | 5731270 | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5200-E | 2017-12-19 | Approved | 2018 | Operational | 2 | 2018-10-08 | 2019-05-21 | 2019-05-22 | NA | FALSE | $5,000 ¦ $10,000 | NA | 21873.0358 | 21873.0358 | 10499.8324 | -98.8558 | 32.12 | -4.4324 | -205.8008 | 0 | 0 | 0 | 0 | 0 | 0 | 21873.0358 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 22122.1582 | -98.734 | 32.0735 | -4.4259 | -205.5013 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $40 Mil - $50 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 297 | Mosher-Lockeford 60kv Reconductor |  |  | Lockeford CDP, San Joaquin ¦ Morada CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | This project proposes to reconductor 11.6 miles of the Lockeford 60 kV Line No. 1 with a higher capacity conductor. Completion of this project would allow both the Hammer-Country Club and Lockeford 60 kV Line No. 1 to normally serve Mosher Substation. This will increase transmission capacity and reliability for PG&E’s customers in San Joaquin County. This project will increase transmission capacity, improve operational flexibility and service reliability for the electric customers in San Joaquin County. Upon completion of this project, the risk of electric service interruptions due to a single line outage will be mitigated for the customers served by Mosher Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2023-11-29 | 16 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 11 | NA | 60 | NA | 236 | 8. Compliance/Commitments With Low Safety Risk | 727 | RBPPF - TBD | Yes | 5738689 | T.0000304 | MOSHER-LOCKEFORD RECONDUCTOR | 1 | 60 | 5767827 | 2010 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-01-20 | 2017-12-01 | 2027-12-15 | Prioritization | FALSE | $10,000 ¦ $15,000 | NA | 4484.2912 | 22430.1307 | 367.9761 | 739.1816 | -260.8814 | -0.0001 | 0 | 0 | 20.5743 | 3029.0549 | 13755.6996 | 100.3577 | 0 | 4484.2912 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 298 | KEARNEY-HERNDON 230 KV LINE RECONDUCTOR |  |  | Fresno, Fresno | This project proposes to reconductor approximately 10 miles of the Herndon – Kearney 230 kV Line. This project is needed to provide additional transmission capacity and reliability to serve electric customers; and to address potential overload conditions in the Greater Fresno area. | Transmission Line - Conductor | Upgrade/Retrofit | T.0000158 ¦ T.0000022 | Reliability | Line Reconductoring | NERC TPL Standards | 2024-03-08 | 6 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 10 | 13.3414 | 230 | NA | 318 | 8. Compliance/Commitments With Low Safety Risk | 1126 | NA | NA | 5767158 | T.0000141 | HERNDON-KEARNEY 230 KV LINE RECONDUCTOR | 1 | 60 | 5752081 | 2013 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5123-E | 2017-08-15 | Approved | 2017 | Operational | 2 | 2018-10-04 | 2017-05-01 | 2019-01-25 | Prioritization | FALSE | $15,000 ¦ $25,000 | NA | 15166.2768 | 15166.2768 | 2174.6682 | 188.2186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15166.2768 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 14302.356 | 178.9564 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 299 | Wilson - Le Grand 115 kV line reconductor |  |  | Merced ¦ Merced, Merced | This project proposes to reconductor approximately 14 miles of the Wilson -LeGrand 115kV Line with 477 ACSS conductor or equivalent and replaces 146 wood poles with new light duty steel poles (LDSP). This project was recommended by the CAISO as a policy driven upgrade.. Completion of this project will provide additional transmission capacity to serve over 30,000 electric customers in Merced County. | Transmission Line - Conductor | Upgrade/Retrofit | T.0001381 | Policy | Line Reconductoring | NERC TPL Standards | 2022-09-28 | 62 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 14 | NA | 115 | NA | 102 | 8. Compliance/Commitments With Low Safety Risk | 512 | NA | NA | 5763769 | T.0002231 | Wilson-LeGrand | 3 | 60 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5293-E | 2018-05-15 | Approved | 2018 | Operational | 2 | 2021-01-05 | 2020-12-31 | 2021-12-03 | Prioritization | FALSE | 15000 | NA | 8670.1277 | 8670.1277 | 1997.8359 | 1153.1272 | 3863.4181 | 142.3734 | 1.2913 | 0 | 0 | 0 | 0 | 0 | 0 | 8670.1277 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 7582.214 | 125.3426 | 1.1369 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 300 | LAND PURCHASE_MARTIN BUS EXTENSION |  |  | Bakersfield, Kern ¦ East Niles CDP, Kern ¦ Kern ¦ Oildale CDP, Kern | This project proposes to reconductor approximately 15 miles of 115 kV line from Kern to Kern Oil substations. In addition, the project will upgrade the limiting equipment at the Live Oak, Kern Oil, and Petrol substations. Load and generation balance is difficult in this area as demand increases and more private generation retires. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2021-11-17 | 44 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 19.6 | NA | 60 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 336 | RBPPF - TBD | Yes | 5767363 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 9 | 60 | 5747850 | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-03-06 | 2016-03-01 | 2028-05-05 | Prioritization | FALSE | $40,000 ¦ $65,000 | NA | 636.4101 | 3302.1958 | 32.2879 | 6.8705 | 0 | 0 | 0 | 0 | 25 | 50 | 100 | 750 | 2600 | 636.4101 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 301 | WESTPARK-MAGUNDEN RECONDUCTOR |  |  | Bakersfield, Kern ¦ Kern | This project proposes to reconductor approximately 15 miles of 115 kV line from Kern to Kern Oil substations. In addition, the project will upgrade the limiting equipment at the Live Oak, Kern Oil, and Petrol substations. Load and generation balance is difficult in this area as demand increases and more private generation retires. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2021-11-18 | 123 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 12.3 | NA | 60 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 361 | RBPPF - TBD | Yes | 5767364 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 9 | 60 | 5747850 | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-03-06 | 2016-03-01 | 2028-05-05 | Prioritization | FALSE | $40,000 ¦ $65,000 | NA | 700.6647 | 3355.5877 | 35.9725 | 7.5642 | 0 | 0 | 0 | 0 | 100 | 300 | 500 | 750 | 2600 | 700.6647 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 302 | Bakersfield-Kern Ph1 Tap 2 |  |  | Bakersfield, Kern ¦ Buttonwillow CDP, Kern ¦ Greenacres CDP, Kern ¦ Kern ¦ Rosedale CDP, Kern | This project proposes to reconductor approximately 42 circuit miles of the Midway - Kern No. 1 230 kV Line, and split the No. 1 line into Midway - Kern No. 1 and No. 2 230 kV Lines, and remove crosstie connections to split the Midway - Kern No. 1 230 kV Line. The Project will also reconductor approximately 13 circuit miles of the Bakersfield Nos. 1 and 2 230 kV Tap Lines. Remove the Stockdale Nos. 1 and 2 230 kV Tap Lines from the Midway – Kern 230 kV lines and relocate directly to the Kern PP 230 kV bus. This project is needed to provide additional transmission capacity and reliability to serve electric customers in Kern County. | Transmission Line - Conductor | Upgrade/Retrofit | T.0000220 ¦T.0001650 | Reliability | Line Reconductoring | NERC TPL Standards | 2024-04-09 | 75 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 14 | NA | 230 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 404 | RBPPF - TBD | Yes | 5767355 | T.0003202 | Bakersfield-Kern Taps 1&2 230kV Recon | 3 | 60 | 5756002 | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5924-E | 2020-08-19 | Approved | 2020 | Engineering more than 50% complete | 4 | 2026-11-30 | 2019-05-01 | 2027-05-14 | Prioritization | FALSE | $60,000 ¦ $90,000 | NA | 1056.5562 | 10631.5927 | 364.6761 | 202.7892 | 35.8187 | 0 | 0 | 70.6117 | 87.6502 | 372.1191 | 4105.5494 | 9328.1237 | 0 | 1050.2507 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 303 | Herndon - Bullard Nos. 1 and 2 115 kV RC |  |  | Fresno, Fresno ¦ Madera | This project proposes to reconductor roughly 8 circuit miles (4 miles of double circuit transmission line) between Pinedale Jct and Bullard Substation on the Herndon - Bullard Nos. 1 and 2 115 kV lines. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2022-11-03 | 16 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 22.8 | NA | 115 | NA | 69 | 8. Compliance/Commitments With Low Safety Risk | 415 | RBPPF - TBD | Yes | 5782638 | T.0004347 | Herndon - Bullard Nos. 1 and 2 115 kV RC | 3 | 60 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-06-05 | 2021-01-01 | 2026-11-04 | Prioritization | FALSE | $6,000 ¦ $8,000 | NA | 397.2999 | 11162.8423 | 101.9876 | 241.4414 | 26.9297 | 26.9412 | 0 | 326.2323 | 2114.022 | 7735.0594 | 170 | 0 | 0 | 397.2999 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 304 | Manteca #1: Recon. From 9/147 to 10/165 |  |  | Grayson CDP, Stanislaus ¦ Manteca, San Joaquin ¦ San Joaquin ¦ Stanislaus | This project proposes to reconductor the 1.13-mile section from Manteca Junction (Jct) to Banta Carbona Jct on the Manteca #1 60 kV Line with a conductor rated for a minimum of 368 Amps for summer normal conditions to mitigate normal overloads | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2023-12-20 | 23 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 1.13 | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5795383 | T.0007053 | Manteca #1 Recon. From 9/147 to 10/165 | 1 | 60 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2021 | FALSE | 2021 | NA | https://www.caiso.com/Documents/BoardApproved2020-2021TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | NA | TBD | NA | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-06-24 | 2024-12-31 | 2025-09-19 | Prioritization | TRUE | $1,400 ¦ $2,800 | NA | 408.0725 | 3047.6681 | 0 | 0 | 15.9375 | 29.2373 | 325.5676 | 1059.0405 | 1570.6593 | 0 | 0 | 0 | 0 | 370.7424 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2020-2021TransmissionPlan.pdf
| 305 | Coleman - RB 60 kV Phase II |  |  | Gerber CDP, Tehama ¦ Los Molinos CDP, Tehama ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama ¦ Tehama, Tehama | This project proposes to reconductor the Coleman-Red Bluff 60 kV line. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2023-12-20 | 74 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 48.3 | NA | 60 | NA | Not Available | 5. Compliance/Commitments With Strong Safety Link | 65 | RBPPF - TBD | Yes | 5784598 | T.0000013 | Coleman - Red Bluff Project | 5 | 60 | 5738259 | 2011 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-01-06 | 2021-12-01 | 2028-09-07 | Prioritization | FALSE | $43,000 ¦ $57,000 | NA | 504.2569 | 15360.7941 | 0 | 6.2516 | 238.8814 | 218.1229 | 35.1038 | 45.3871 | 2273.0666 | 6987.1022 | 6937.437 | 0 | 0 | 498.3596 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 306 | RED BLUFF-COLEMAN REINFORCEMENT Phase 1 |  |  | Cottonwood CDP, Shasta | This project proposes to reconductor the Coleman-Red Bluff 60 kV line. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-03-06 | 23 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 48 | 26.1945 | 60 | NA | 137 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5766750 | T.0000013 | Coleman - Red Bluff Project | 5 | 60 | 5738259 | 2011 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-09-28 | 2021-12-01 | 2027-05-18 | Prioritization | FALSE | $43,000 ¦ $57,000 | NA | 4274.8392 | 21838.3119 | 205.1726 | 749.7804 | 678.6917 | 403.12 | 295.9382 | 717.9141 | 12077.0132 | 5645.8483 | 0 | 0 | 0 | 4224.6089 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 307 | Ravenswood-Cooley Landing 115 kV |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo | This project proposes to reconductor the Ravenswood-Cooley Landing Nos. 1 & 2 115 kV Lines. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2024-04-08 | 62 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1.8 | NA | 115 | NA | 270 | 8. Compliance/Commitments With Low Safety Risk | 577 | NA | NA | 5743555 | T.0000612 | RAVENSWOOD-COOLEY LANDING 115 KV Recondu | 1 | 60 | NA | 2012 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2019-04-04 | IS/MND | NA | CPUC | NA | PTC: A.17-12-010 | 2017-12-23 | Approved | 2019 | Operational | 2 | 2022-09-22 | 2015-12-01 | 2022-12-20 | Project Design | TRUE | $5,000 ¦ $10,000 | NA | 14200.9601 | 14268.9821 | 489.3626 | 832.9827 | 1577.6778 | 8391.3818 | 364.5435 | 76.8078 | 0 | 0 | 0 | 0 | 0 | 14192.1743 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 12770.3848 | 1131.4018 | 10.5655 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 308 | Midway-Temblor 115kV Recon & Voltage Sup |  |  | Buttonwillow CDP, Kern ¦ Kern | This project proposes to upgrade 14.5 miles of conductor and four (4) transmission switches (Nos. 137, 139, and 157) on the Midway – Temblor 115 kV Line, and install 40 MVAR shunt capacitors at Temblor Substation in order to provide additional transmission capacity and reliability to serve electric customers in Kern County. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-04-08 | 51 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | 14.5 | NA | 115 | NA | 137 | 8. Compliance/Commitments With Low Safety Risk | 417 | RBPPF - TBD | Yes | 5781145 | T.0004113 | Midway-Temblor 115kV Recon & Voltage Sup | 2 | 60 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2029-09-24 | 2018-05-01 | 2030-03-15 | Prioritization | FALSE | $25,000 ¦ $35,000 | NA | 291.6638 | 16959.8967 | 257.9207 | 7.9993 | 21.7897 | 3.9541 | 0 | 58.6477 | 29.2604 | 436.4283 | 777.8419 | 14494.8126 | 4330.5738 | 291.6638 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 309 | South of Mesa Upgrade - Tline Recond |  |  | Santa Barbara ¦ Sisquoc CDP, Santa Barbara | This project proposes to upgrade approximately 21.3 miles of conductor on the Sisquoc – Santa Ynez SW STA 115 kV Line, install 20 Mega Volt-ampere reactive (MVAR) shunt capacitors at Cabrillo Substation and install Remedial Action Scheme (RAS) (formerly known as Special Protection Scheme (SPS)) on the Sisquoc – Santa Ynez SW STA 115 kV Line. Completion of this project is needed to improve the electric transmission system reliability and operational flexibility in the Santa Barbara County. This project will be funded under Major Work Category (MWC) 60, Electric Transmission Line Capacity and 61, Electric Transmission Substation Capacity. The project has a Risk Informed Budget Allocation (RIBA) score of 137. The RIBA score is based on the impact and frequency of three risk categories: safety, reliability and environmental. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Line Reconductoring | NERC TPL Standards | 2024-04-10 | 35 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 21.3 | NA | 115 | NA | 137 | 8. Compliance/Commitments With Low Safety Risk | 30 | RBPPF - TBD | Yes | 5785927 | T.0004832 | South Of Mesa Upgrade Project | 5 | 60 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | NA | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-10-17 | 2023-12-31 | 2027-04-15 | Prioritization | FALSE | $29,600 ¦ $59,200 | NA | 945.0258 | 13748.4371 | 9.3041 | 753.5457 | 182.176 | 0 | 0 | 0 | 150 | 1500 | 2000 | 5500 | 5500 | 945.0258 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 310 | Riverbank-Ripon - Line Reconductor |  |  | Ripon, San Joaquin ¦ San Joaquin ¦ Stanislaus | This project will increase operating flexibility, load serving capability, customer reliability, eliminate contingency overloads, and harden the transmission system by performing the following scope: • Reconductor 1.3 circuit miles between Riverbank Jct. SW STA and Structure 035/212 of the Stanislaus – Melones SW STA – Riverbank Jct. SW STA 115 kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating. • Reconductor 1.8 circuit miles between Riverbank SW STA and Valley Home Tap (038/233) of the Riverbank SW STA – Ripon 115 kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating. • Include all open maintenance tags within the project scope where applicable. • Replace structures, all insulators and insulator hardware to accommodate the increase in conductor size. | Transmission Line - Conductor | Upgrade/Retrofit | T.0004301 ¦ T.0007979 ¦ T.0004515 | Reliability | Line Reconductoring | NERC TPL Standards | 2021-10-01 | 88 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 1.8 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803072 | T.0008743 | Riverbank-Ripon - Line Reconductor | 2 | 60 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2028-08-09 | 2028-05-01 | 2029-06-08 | Prioritization | FALSE | $6,800 ¦ $13,600 | NA | 33.5074 | 9895.8144 | 0 | 0 | 0 | 0 | 19.5435 | 950.629 | 1102 | 2262 | 3074 | 1044 | 0 | 19.5435 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 311 | Stanislaus-Melones Sw Sta-Riverbank Jct |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | This project will increase operating flexibility, load serving capability, customer reliability, eliminate contingency overloads, and harden the transmission system by performing the following scope: • Reconductor 1.3 circuit miles between Riverbank Jct. SW STA and Structure 035/212 of the Stanislaus – Melones SW STA – Riverbank Jct. SW STA 115 kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating. • Reconductor 1.8 circuit miles between Riverbank SW STA and Valley Home Tap (038/233) of the Riverbank SW STA – Ripon 115 kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating. • Include all open maintenance tags within the project scope where applicable. • Replace structures, all insulators and insulator hardware to accommodate the increase in conductor size. | Transmission Line - Conductor | Upgrade/Retrofit | T.0004301 ¦ T.0007979 ¦ T.0004515 | Reliability | Line Reconductoring | NERC TPL Standards | 2023-04-19 | 98 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 1.3 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803073 | T.0008743 | Riverbank-Ripon - Line Reconductor | 2 | 60 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2028-08-09 | 2028-05-01 | 2029-06-08 | Prioritization | FALSE | $6,800 ¦ $13,600 | NA | 35.1801 | 9472.2761 | 0 | 0 | 0 | 0 | 15.5877 | 642.4158 | 798 | 1638 | 2226 | 756 | 0 | 15.5877 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 312 | SOUTH OF PALERMO REINFORCEMENT (PH-1) |  |  | Palermo CDP, Butte | This project will reinforce 80.3 circuit miles of the 115kV transmission lines between Palermo, Pease, Bogue, and Rio Oso substations with 477 kcmil steel-supported aluminum conductors with emergency capability of 970 Amps. This includes the installation of five Supervisory Control and Data Acquisition (SCADA) controlled transmission line switches on the Palermo – Pease, Pease – Rio Oso, Palermo – Bogue, and Bogue – Rio Oso 115kV lines to improve reliability and service restoration time. Key construction elements are as follows:  Replacement of 238 steel electric transmission lattice towers with 238 new hybrid tubular steel poles (HTSP), which include a concrete foundation and steel pole on top  Replacement of 21 steel electric transmission lattice towers with 21 tubular steel poles (TSP).  Replacement of 45 steel electric transmission lattice steel poles with new lattice steel poles.  Replacement of 2 steel electric transmission lattice towers with new steel lattice towers.  Reinforcement of 61 steel electric transmission lattice tower foundations with screw anchors.  Reinforcement of 23 steel electric transmission lattice towers with 19 top or waist cage extensions.  Upgrade 8 transmission relay terminals at 4 surrounding substations. This project has been divided into three construction phases as follows:  Phase 1: Rio Oso Substation to Pease Junction  Phase 2: Pease Substation to Palermo Substation  Phase 3: Bogue Substation to Bogue Junction | Transmission Line - Conductor | Upgrade/Retrofit | T.0000598 | Reliability | Line Reconductoring | NERC TPL Standards | 2024-03-04 | 119 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 34 | 8.0464 | 115 | NA | 180 | 5. Compliance/Commitments With Strong Safety Link | Not Available | NA | NA | 5767546 | T.0000450 | South of Palermo 115kV Reinforcement | 12 | 60 | 5743570 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-08-30 | IS/MND | NA | CPUC | NA | PTC: A.16-04-23 | 2016-04-28 | Approved | 2018 | Operational | 2 | 2020-02-03 | 2014-05-01 | 2021-01-14 | Prioritization | FALSE | $80,000 ¦ $100,000 | NA | 38518.8528 | 38518.8528 | 13323.8202 | 16133.0025 | 1741.1675 | -70.2669 | 0.0918 | 0 | 0 | 0 | 0 | 0 | 0 | 38518.8528 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 36032.2653 | -310.0864 | 0.08437 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 313 | SOUTH OF PALERMO REINFORCEMENT (PH-2) |  |  | Palermo CDP, Butte | This project will reinforce 80.3 circuit miles of the 115kV transmission lines between Palermo, Pease, Bogue, and Rio Oso substations with 477 kcmil steel-supported aluminum conductors with emergency capability of 970 Amps. This includes the installation of five Supervisory Control and Data Acquisition (SCADA) controlled transmission line switches on the Palermo – Pease, Pease – Rio Oso, Palermo – Bogue, and Bogue – Rio Oso 115kV lines to improve reliability and service restoration time. Key construction elements are as follows:  Replacement of 238 steel electric transmission lattice towers with 238 new hybrid tubular steel poles (HTSP), which include a concrete foundation and steel pole on top  Replacement of 21 steel electric transmission lattice towers with 21 tubular steel poles (TSP).  Replacement of 45 steel electric transmission lattice steel poles with new lattice steel poles.  Replacement of 2 steel electric transmission lattice towers with new steel lattice towers.  Reinforcement of 61 steel electric transmission lattice tower foundations with screw anchors.  Reinforcement of 23 steel electric transmission lattice towers with 19 top or waist cage extensions.  Upgrade 8 transmission relay terminals at 4 surrounding substations. This project has been divided into three construction phases as follows:  Phase 1: Rio Oso Substation to Pease Junction  Phase 2: Pease Substation to Palermo Substation  Phase 3: Bogue Substation to Bogue Junction | Transmission Line - Conductor | Upgrade/Retrofit | T.0000598 | Reliability | Line Reconductoring | NERC TPL Standards | 2024-03-04 | 119 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 34.9 | 8.0464 | 115 | NA | 180 | 5. Compliance/Commitments With Strong Safety Link | Not Available | NA | NA | 5767547 | T.0000450 | South of Palermo 115kV Reinforcement | 12 | 60 | 5743570 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-08-30 | IS/MND | NA | CPUC | NA | PTC: A.16-04-23 | 2016-04-28 | Approved | 2018 | Operational | 2 | 2019-02-04 | 2014-05-01 | 2020-02-28 | Prioritization | FALSE | $80,000 ¦ $100,000 | NA | 25473.7715 | 25473.7715 | 13853.1751 | 2345.4877 | -85.3816 | 63.9456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25473.7715 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 24720.9242 | -82.2918 | 61.6316 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 314 | SOUTH OF PALERMO REINFORCEMENT (PH-3) |  |  | Palermo CDP, Butte | This project will reinforce 80.3 circuit miles of the 115kV transmission lines between Palermo, Pease, Bogue, and Rio Oso substations with 477 kcmil steel-supported aluminum conductors with emergency capability of 970 Amps. This includes the installation of five Supervisory Control and Data Acquisition (SCADA) controlled transmission line switches on the Palermo – Pease, Pease – Rio Oso, Palermo – Bogue, and Bogue – Rio Oso 115kV lines to improve reliability and service restoration time. Key construction elements are as follows:  Replacement of 238 steel electric transmission lattice towers with 238 new hybrid tubular steel poles (HTSP), which include a concrete foundation and steel pole on top  Replacement of 21 steel electric transmission lattice towers with 21 tubular steel poles (TSP).  Replacement of 45 steel electric transmission lattice steel poles with new lattice steel poles.  Replacement of 2 steel electric transmission lattice towers with new steel lattice towers.  Reinforcement of 61 steel electric transmission lattice tower foundations with screw anchors.  Reinforcement of 23 steel electric transmission lattice towers with 19 top or waist cage extensions.  Upgrade 8 transmission relay terminals at 4 surrounding substations. This project has been divided into three construction phases as follows:  Phase 1: Rio Oso Substation to Pease Junction  Phase 2: Pease Substation to Palermo Substation  Phase 3: Bogue Substation to Bogue Junction | Transmission Line - Conductor | Upgrade/Retrofit | T.0000598 | Reliability | Line Reconductoring | NERC TPL Standards | 2024-03-04 | 119 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 12.8 | 8.0464 | 115 | NA | 180 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5767548 | T.0000450 | South of Palermo 115kV Reinforcement | 12 | 60 | 5743570 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-08-30 | IS/MND | NA | CPUC | NA | PTC: A.16-04-23 | 2016-04-28 | Approved | 2018 | Operational | 2 | 2018-08-27 | 2014-05-01 | 2019-02-07 | Prioritization | FALSE | $80,000 ¦ $100,000 | NA | 11940.0642 | 11940.0642 | 2526.8545 | -143.5446 | 67.3652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11940.0642 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 11462.4501 | -136.705 | 64.1995 | 243.7213 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 315 | Kern-Stockdale #1 OPGW |  |  | Bakersfield, Kern ¦ East Niles CDP, Kern ¦ Fairfax CDP, Kern ¦ Fuller Acres CDP, Kern ¦ Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | T.0000220 ¦ T.0003350 ¦ T.0000980 | Reliability | Line Reconductoring | NERC TPL Standards | 2024-02-14 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | 6 | NA | 230 | NA | 764 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5777283 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 60 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-03-14 | 2013-05-01 | 2019-05-01 | Prioritization | FALSE | $32,000 ¦ $44,000 | NA | 3762.489 | 3762.489 | 2938.6243 | 0.2703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3762.489 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 3755.4595 | 0.27057 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $100 Mil – $125 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 316 | Stockdale- Bakersfield SC OPGW |  |  | Bakersfield, Kern ¦ Fuller Acres CDP, Kern ¦ Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | T.0000220 ¦ T.0003350 ¦ T.0000980 | Reliability | Line Reconductoring | NERC TPL Standards | 2024-01-23 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 3 | NA | 230 | NA | 764 | 8. Compliance/Commitments With Low Safety Risk | 322 | NA | NA | 5777921 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 60 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-03-08 | 2013-05-01 | 2020-02-03 | Prioritization | FALSE | $32,000 ¦ $44,000 | NA | 2522.0731 | 2522.0731 | 1937.1162 | 26.6683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2522.0731 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 2523.2696 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $100 Mil – $125 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 317 | Kern Oil-Live Oak 115kV Project |  |  | Kern ¦ Oildale CDP, Kern | This project proposes to reconductor approximately 15 miles of 115 kV line from Kern to Kern Oil substations. In addition, the project will upgrade the limiting equipment at the Live Oak, Kern Oil, and Petrol substations. Load and generation balance is difficult in this area as demand increases and more private generation retires. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Voltage Conversion | NERC TPL Standards | 2021-11-24 | 75 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 4.6 | NA | 115 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 561 | RBPPF - TBD | Yes | 5774040 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 9 | 60 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-10-26 | 2016-03-01 | 2028-01-19 | Prioritization | FALSE | $40,000 ¦ $65,000 | NA | 1048.5541 | 4456.1624 | 348.7415 | 32.146 | 0 | 0 | 0 | 0 | 100 | 350 | 10400 | 1000 | 1000 | 1048.5541 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 318 | Kern-Kern Oil 115kV Project |  |  | Bakersfield, Kern ¦ Kern ¦ Oildale CDP, Kern | This project proposes to reconductor approximately 15 miles of 115 kV line from Kern to Kern Oil substations. In addition, the project will upgrade the limiting equipment at the Live Oak, Kern Oil, and Petrol substations. Load and generation balance is difficult in this area as demand increases and more private generation retires. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Voltage Conversion | NERC TPL Standards | 2024-03-04 | 75 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | 8.3 | NA | 115 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | 519 | RBPPF - TBD | Yes | 5774039 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 9 | 60 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-04-07 | 2016-03-01 | 2028-08-01 | Prioritization | FALSE | $40,000 ¦ $65,000 | NA | 1989.9556 | 9217.4166 | 503.7247 | 41.7843 | 0 | 0 | 0 | 0 | 100 | 350 | 10400 | 5000 | 1000 | 1989.9556 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 319 | Borden 230kV Voltage Support |  |  | Madera | This project will connect two additional 230kV lines to Borden Substation from the Wilson-Gregg 230kV Line, which will improve voltage and service reliability, and provide full deliverability needs for new generation. A new Modular Protection and Automation Control (MPAC) building will also be needed to integrate the new equipment to the protection and control system, as well as upgrade terminal equipment at other substations. | Transmission Line - Conductor | Relocate | NA | Reliability | Voltage Conversion | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.1 | 7.1874 | 230 | NA | 20 | Not Available | NA | NA | NA | 5768813 | T.0000924 | BORDEN 230 KV VOLTAGE SUPPORT (SUB) | 6 | 60 | 5747854 | 2010 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-01-02 | 2019-05-01 | 2019-04-24 | NA | FALSE | $15,000 ¦ $20,000 | NA | 2174.996 | 2174.996 | 1274.6569 | -6.2272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2174.996 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 2045.5881 | -5.808 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 320 | GATE 500Kv: T-Line |  |  | Fresno | The reactive support study results noted above indicated that a +/- 800 MVAR dynamic reactive device at Gates Substation is required to address the high voltage and to improve dynamic performance. The recommendation is to approve installation of a total of +/-800 MVAR of dynamic reactive support on the Gates 500kV bus. Interconnect new Transmission Owner (TO) LS Power Grid California’s Orchard Substation STATCOM Facility to Gates 500kV Bus The scope of the proposed project is to install a minimum of two equally sized blocks of reactive devices independently connected to the 500kV system at PG&E’s Gates Substation to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power output over the complete range of the capability (unless the facility experiences a planned or forced outage). Sub-synchronous Resonance studies are required to be completed and any identified mitigation shall be implemented as part of this project. The project scope will include connecting two blocks of the STATCOM to two separate bays of Gates 500kV breaker-and-a-half (BAAH) bus. STATCOM connections will require both overhead and high-voltage underground cables. The high-level scope includes the following: • Install two 550kV, 4000 Amp 63KA breakers with associated switches and structures. • Relocate 500kV Bank 12 connection from BAAH Bay 2 to Bay 1 using GIB. • Build two transition stations (one inside the PG&E substation and one outside on PG&E property) to connect LS Power’s two STATCOM connections to PG&E 500kV bus. • Install overhead conductors, underground high-voltage cables and associated structures and switches to connect two STATCOMs • Relocate Bank 12 tertiary reactors controls and protection equipment from the 500kV control building to new Tertiary Reactors control building installed under Gates Bank 11 project. This is needed to create space in the 500kV control building for new breakers. • Install protection, controls, and IT equipment for new 500 kV breakers needed to support LS Power project. • Upgrade ground grid and grading as required. | Transmission Line - Conductor | Upgrade/Retrofit | T.0001373 | Reliability | Voltage Support | NERC TPL Standards | 2024-03-08 | 33 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.02 | 77.6619 | 500 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5795569 | T.0004672 | Gates:500Kv Dynamic Voltage Support | 5 | 60 | NA | 2019 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2023-05-08 | 2025-07-16 | 2024-12-18 | Workforce | TRUE | $210,000 ¦ $250,000 | NA | 27948.3948 | 31151.3291 | 0 | 0 | 40.4213 | 1432.9869 | 23460.1952 | 6119.7012 | 98.0246 | 0 | 0 | 0 | 0 | 24933.6033 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 321 | LOOP METCALF-LLAGAS 115kV INTO MORG HILL |  |  | Interlaken CDP, Santa Cruz ¦ Morgan Hill, Santa Clara ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2024-04-10 | 38 | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5786320 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 7 | 60 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-07-29 | 2021-12-01 | 2027-03-23 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 1.8601 | 2.3074 | 0 | 0 | 0 | 1 | 1.4213 | 0.1241 | 800 | 1000 | 200 | 0 | 0 | 1.8492 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 322 | Inst New 70kV Line Poleline - Mercy Sprg |  |  | Merced | This project proposes to: • Install 230 kV partial bay at the new generation driven 230 kV switching station adjacent to Dos Amigos PP 230 kV Substation. • Add a new 70 kV Bus in the new generation driven 230 kV switching station, then it will be converted to a new 230/70 kV substation. • Install one 230/70 kV transformer at the new 230/70 kV substation. • Install a new 70 kV transmission line from new 70 kV Bus to Mercy Springs 70 kV Bus, and the new line is about one mile. • Install one breaker at Mercy Springs 70 kV Switching Station. | Transmission Line - Conductor | New | TBD | Reliability | New T-Line | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | TBD | 53.2803 | 70 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807500 | T.0009617 | Los Banos 70 kV Area Reinforcement | 2 | 60 | EX113235 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | 2029-12-31 | 2028-12-01 | NA | FALSE | 60000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 2400 | 3950 | 6750 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 323 | Santa Teresa Substation - T-Line Work |  |  | San Jose, Santa Clara ¦ Santa Clara | Construct a new substation on PG&E property at the Edenvale Service Center in San Jose, CA to serve three new data center loads and correct a normal deficiency on Edenvale Banks 2 and 4 | Transmission Line - Conductor | Relocate | NA | Reliability | T-Line Capacity | NERC TPL Standards | 2022-11-04 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 79 | 8. Compliance/Commitments With Low Safety Risk | 85 | NA | NA | 5764801 | T.0001316 | SANTA TERESA SUB: NEW SUB | 5 | 60 | NA | 2015 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2021 | FALSE | 2021 | NA | https://www.caiso.com/Documents/BoardApproved2020-2021TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5601-E | 2019-07-29 | Approved | 2020 | Operational | 2 | 2020-10-14 | 2021-08-01 | 2021-12-13 | NA | FALSE | 18000 | NA | 2827.0112 | 2827.0112 | 334.4239 | 2039.7309 | 230.4599 | 10.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2827.0112 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 2636.6456 | 9.8031 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2020-2021TransmissionPlan.pdf
| 324 | RIPON SUB: BUILD 2ND 115 KV |  |  | Ripon, San Joaquin | Install a new 4.7-mile 115 kV transmission line from Ripon Substation to the Riverbank Switching Station – Manteca 115 kV Line, including the upgraded Ripon 115 kV Bus to a loop configuration .The Ripon Substation 115 kV Reliability Project will improve electric transmission reliability for customers served by Ripon Substation. The new 4.7-mile 115 kV transmission line will provide Ripon Substation with two sources to eliminate service interruptions for single contingency situations and limiting bus faults to only half the substation. | Transmission Line - Conductor | New | NA | Reliability | New T-Line | NERC TPL Standards | 2024-02-07 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 5 | 2.0603 | 115 | NA | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767284 | T.0000265 | RIPON NEW 115 KV LINE 2ND TAP RELIABILIT | 1 | 60 | 5752061 | 2009 | 2014 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5059-E | 2017-04-28 | Approved | 2017 | Operational | 2 | 2018-07-09 | 2015-05-31 | 2019-05-24 | Prioritization | FALSE | $10,000 ¦ $15,000 | NA | 6849.4129 | 6849.4129 | 313.6207 | 42.0673 | 56.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6849.4129 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 6399.1386 | 39.9355 | 53.2062 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 325 | Sanger Expansion T-Line |  |  | Fresno | Install a new seven bay 115 kV BAAH bus, two MPAC buildings, and relocate all associated 115 kV lines at Sanger Substation. | Transmission Line - Conductor | Relocate | NA | Reliability | T-Line Reliability | NA | 2024-02-07 | NA | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 11.0513 | 115 | NA | 225 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5762399 | T.0000601 | Sanger Substation 115kV Bus Replacement | 4 | 60 | NA | 2014 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2027-07-13 | IS/MND | NA | CPUC | NA | PTC: A.15-09-012 | 2015-09-30 | Approved | 2017 | Operational | 2 | 2019-06-03 | 2019-12-31 | 2020-11-30 | Prioritization | FALSE | 55300 | NA | 5397.7331 | 5397.7331 | 2943.3641 | 1006.0834 | 718.5122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5397.7331 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 4491.2648 | 676.2041 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100%
| 326 | 230 kV T-Line LOCKEFORD - NEW INDUSTRIAL |  |  | Lockeford CDP, San Joaquin | The Lockeford-Lodi Area 230 kV Development Project will loop the Brighton – Bellota 230 kV Line into Lockeford 230 kV Substation to bring a new 230 kV source into the area. A new 230 kV double circuit tower line will be constructed to connect the existing Lockeford 230 kV Substation to a new 230 kV switching to be constructed near the City of Lodi’s existing Industrial 60 kV Subsation. To accommodate the Brighton – Bellota loop-in and the new DCTL, the Lockeford 230 kV Bus will be upgraded to a four-bay breaker-and-a-half (BAAH) bus configuration. The City of Lodi will be constructing a new 230/60 kV Substation which will be connected to the new 230 kV switching station. | Transmission Line - Conductor | New | NA | Reliability | New T-Line | NERC TPL Standards | 2024-03-01 | NA | Steady State Power Flow System Analysis | Non-Wires - Large Scale Energy Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 32 | 10.2719 | 230 | NA | 45 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767239 | T.0000155 | Lockeford - Lodi Area 230 kV Development | 5 | 60 | 5752079 | 2013 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | PEA Deemed Complete | TBD | TBD | NA | CPUC | NA | CPCN: A.23-09-001 | 2023-09-01 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2028-05-26 | 2017-03-01 | 2029-02-02 | Prioritization | FALSE | $80,000 ¦ $105,000 | TBD | 17075.9545 | 50195.0232 | 1472.5574 | 1659.0795 | 1625.0271 | 2081.8356 | 1754.9182 | 2324.5847 | 3918.3119 | 10593.8972 | 5614.4773 | 6152.718 | 1247.9071 | 16823.7642 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 327 | LOOP IN BRIGHTON - BELLOTA INTO LOCKEFOR |  |  | Dogtown CDP, San Joaquin ¦ Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Herald CDP, Sacramento ¦ Lockeford CDP, San Joaquin ¦ Sacramento ¦ Sacramento, Sacramento ¦ San Joaquin ¦ Vineyard CDP, Sacramento ¦ Wilton CDP, Sacramento | The Lockeford-Lodi Area 230 kV Development Project will loop the Brighton – Bellota 230 kV Line into Lockeford 230 kV Substation to bring a new 230 kV source into the area. A new 230 kV double circuit tower line will be constructed to connect the existing Lockeford 230 kV Substation to a new 230 kV switching to be constructed near the City of Lodi’s existing Industrial 60 kV Subsation. To accommodate the Brighton – Bellota loop-in and the new DCTL, the Lockeford 230 kV Bus will be upgraded to a four-bay breaker-and-a-half (BAAH) bus configuration. The City of Lodi will be constructing a new 230/60 kV Substation which will be connected to the new 230 kV switching station. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2023-11-28 | 74 | Steady State Power Flow System Analysis | Non-Wires - Large Scale Energy Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | 4 | NA | 230 | NA | 45 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767209 | T.0000155 | Lockeford - Lodi Area 230 kV Development | 5 | 60 | 5752079 | 2013 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | PEA Deemed Complete | TBD | TBD | NA | CPUC | NA | CPCN: A.23-09-001 | 2023-09-01 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2028-05-25 | 2017-03-01 | 2029-06-05 | Prioritization | FALSE | $80,000 ¦ $105,000 | TBD | 1334.8595 | 23752.1923 | 132.2494 | 149.2498 | 747.3134 | 135.7591 | 103.8973 | 417.3983 | 3119.6904 | 7402.8384 | 2748.0514 | 2709.7651 | 0.2841 | 1319.2568 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 328 | Round Mountain 500kV DRS Fern Road |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Chico, Butte ¦ Cohasset CDP, Butte ¦ Round Mountain CDP, Shasta ¦ Shasta ¦ Tehama ¦ Whitmore CDP, Shasta | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Transmission Line - Multiple | New | NA | Reliability | System Design Upgrade | NERC TPL Standards | 2024-04-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Extreme Heat |  | TBD | NA | 500 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5794601 | T.0006815 | Round Mountain Area 500kV Dynamic React | 5 | 60 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-07-26 | 2024-12-31 | 2024-12-03 | Workforce | TRUE | $160,000 ¦ $190,000 | NA | 2576.7777 | 20546.7976 | 0 | 0 | 320.226 | 646.9113 | 1502.4937 | 9082.7963 | 8730.1188 | 14.6939 | 0 | 0 | 0 | 2469.631 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 329 | Distribution - Logan Creek install bank #3 |  |  | Glenn | It is recommended to extend Logan Creek 2103 to Tesla EV site. Work includes to install 13,800 feet of new 715A conductor, trench & install 2,000 feet of 1100A EPR UG cable, install one 7500 MVA autobank, and install 2 new PMI-9TT & 4 OH switches. | Substation - Circuit Breaker | New | NA | Load Growth | Substation Capacity | NA | 2024-02-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.8188 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113259 | T.0007627 | Willows_Logan Creek Bank Replacement | 3 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-01-01 | NA | 2025-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2100 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 330 | Distribution - Lockeford Sub - Install Bk 5 |  |  | Lockeford CDP, San Joaquin | The project installs one new 115 kV transmission breaker and one new 75 MVA substation transformer in order to mitigate an Emergency Deficiency caused by removal of Transmission Bank 1 at Lockeford. | Substation - Circuit Breaker | New | NA | Load Growth | Substation Capacity | NA | 2024-03-01 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 10.2719 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113198 | T.0005910 | Lockeford Sub- Replace Bank 1 | 1 | 61 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | NA | 2027-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 2000 | 2500 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 331 | Distribution - Terminous install bank #2 |  |  | San Joaquin | This project proposes to add a second 60/12 kV 30 MVA Bank #2 at Terminous sub. This project is being driven by: 1. Greenlaw Development is going through the Entitlement process for their development located at the Northeast Corner of I-5 and Hwy 12. The Phase one “May” include 2 buildings totaling 1.3 million square feet with Freezers. The anticipated power would be 2.5 – 3.0 MW. 2. Tesla – 6.2MW – extend Eight Mile 2106 to pick up the load until Terminous new bank is in place. | Substation - Circuit Breaker | New | NA | Load Growth | Substation Capacity | NA | 2024-03-01 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.27452 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113257 | T.0008554 | Terminous_Replace Bank 1 | 3 | 61 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-01-01 | NA | 2025-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 332 | Distribution - Giffen Sub - Install Bk 2 |  |  | Fresno | This project proposes to extend the existing 70 kV tap to a new bank, install one 70 kV breaker, install one 30 MVA bank and four 12 kV breakers, and reconductor existing overhead lines to support new applications for agricultural processing plants | Substation - Circuit Breaker | New | NA | Load Growth | Substation Capacity | NA | 2024-02-07 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.2938 | NA | 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113261 | T.0007301 | Giffen- Install Bank 2 | 4 | 61 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-12-01 | NA | 2026-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 1300 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 333 | Distribution - Garberville Sub - Install Bk 2 |  |  | Garberville CDP, Humboldt | This project proposes to install Garberville Bank 2, install two 21 kV feeders, add 2 60 kV circuit breakers, and convert existing circuit distribution voltage to 21 kV for a Garberville Bank deficiency caused by new cannabis cultivation greenhouses in the Garberville area. | Substation - Circuit Breaker | New | NA | Load Growth | Substation Capacity | NA | 2024-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.3065 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113197 | T.0004853 | Repl Garberville 12 kV Bus - V Reg | 1 | 61 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-01 | NA | 2026-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 334 | Distribution - Semitropic Sub - Install Bk |  |  | Kern | This project proposes to install one 115 kV circuit breaker, one 45MVA bank, and 3 new feeders | Substation - Circuit Breaker | New | NA | Load Growth | Substation Capacity | NA | 2024-02-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.2701 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113253 | T.0009434 | SEMITROPIC_Install Bank 4 | 4 | 61 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-12-01 | NA | 2026-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 1300 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 335 | Distribution - Chualar Sub - Install Bk |  |  | Chualar, Monterey | This project proposes to install three 60 kV breakers, one 30 MVA bank, one 3-bay 12 kV bus, two 12 kV circuit breakers, and new overhead lines to support greenhouse cannabis cultivation | Substation - Circuit Breaker | New | NA | Load Growth | Substation Capacity | NA | NA | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113262 | T.0007304 | Chualar Substation- Inst Transf Bank | 3 | 61 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | NA | 2027-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2500 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 336 | Distribution - Fulton replace bank #5 |  |  | Fulton CDP, Sonoma | This project proposes to replace Fulton Bk 5 with a 60 MVA transformer, install one 12 kV feeder, add 60kV circuit breaker, and install new underground cable and overhead line in order to mitigate overloads caused by commercial, EV, warehouse, and cannabis applications for service. | Substation - Circuit Breaker | New | NA | Load Growth | Substation Capacity | NA | 2024-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.4076 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113200 | T.0007811 | Fulton Bank 5 Replacement | 3 | 61 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-01-01 | NA | 2025-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2400 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 337 | Distribution - Airways - Install Bank 3 and Switchgear 3, and Airways 1109 and Airways 1110 Feeders |  |  | Fresno, Fresno | This project will install a fifth 115 kV circuit breaker and a third 115/12 kV transformer bank (60 MVA) with an indoor switchgear building at Airways Substation and install two new 12 kV distribution feeders outside of the substation. | Substation - Circuit Breaker | New | NA | Load Growth | Substation Capacity | NA | 2024-02-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.2092 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113199 | T.0007300 | Airways- Install Bank 3 | 4 | 61 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-12-01 | NA | 2026-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 2000 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 338 | PLAINFIELD: AQUIRE LAND |  |  | Yolo | The California ISO’s 2018-2019 Transmission Planning Process (TPP) has identified the need for the Vaca – Dixon Area Reinforcement Project. This project will mitigate overloads and voltage criteria violations in the 115kV and 60kV transmission systems among Vaca Dixon, Davis, Rio Oso and Brighton Substations. The project will include the following work: 1. Install two 5.0 MVAR capacitor banks at Plainfield Substation. 2. Replace Vaca Dixon 115/60kV Bank 5 with a larger unit. 3. Replace the limiting elements on the 60kV equipment at Dixon Substation. 4. Re-rate the Woodland - Davis 115kV Line and the Rio Oso - West Sac 115kV Line. 5. Modify the existing special protection schemes (SPS) or add new SPS’s to trip load for select multiple contingencies. | Other | New | NA | Reliability | New Substation | NERC TPL Standards | 2024-03-01 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.82985 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5554308 | T.0000007 | VACA-DAVIS: VOLTAGE CONVERSION PROJECT | 6 | 61 | NA | 2012 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | NA | 2023-12-01 | 2025-05-29 | Prioritization | TRUE | $70,000 ¦ $107,000 | NA | 87.8744 | 2700.5849 | 0 | 0 | 0 | 0 | 22.4956 | 436.7702 | 2241.3192 | 0 | 0 | 0 | 0 | 22.4955 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 117.5398 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 339 | MILLBRAE SUB:INSTALL MILLBRAE BK2 |  |  | Millbrae, San Mateo | This project proposes to extend the existing 115 kV bus, install 115 kV breakers, install one 60 MVA bank and switchgear, and install a new underground circuit to support mixed-use redevelopment. | Substation - Circuit Breaker | New | NA | Load Growth | Substation Capacity | NA | 2024-03-12 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.0501 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5800303 | T.0008122 | MILLBRAE SUB-INSTALL BK2_MILLBRAE 1109 | 2 | 61 | EX113258 | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-12-01 | NA | 2026-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 2500 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 340 | SANTA TERESA SUB: T-SUB WORK |  |  | Santa Clara | Construct a new substation on PG&E property at the Edenvale Service Center in San Jose, CA to serve three new data center loads and correct a normal deficiency on Edenvale Banks 2 and 4 | Substation - Line Termination | New | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-13 | NA | Steady State Power Flow System Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 115 kV | 79 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5782343 | T.0001316 | SANTA TERESA SUB: NEW SUB | 5 | 61 | NA | 2015 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2021 | FALSE | 2021 | NA | https://www.caiso.com/Documents/BoardApproved2020-2021TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5601-E | 2019-07-29 | Approved | 2020 | Operational | 2 | 2021-05-18 | 2021-08-01 | 2021-12-13 | NA | FALSE | 18000 | NA | 9048.2514 | 9048.2514 | 63.3758 | 587.8871 | 7977.5224 | 203.6581 | 210.0896 | 0 | 0 | 0 | 0 | 0 | 0 | 9048.2514 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 8634.5038 | 203.6581 | 210.0896 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2020-2021TransmissionPlan.pdf
| 341 | FULTON-FITCH: Reconductoring 60 kV |  |  | Sonoma | Reconductor approximately 8 miles of the Fulton-Hopland 60kV Line and 1.3 miles of the Geysers 12-Fulton 230kV Line, rerate another section of the Fulton-Hopland 60kV Line and Fitch Mountain #2 60kV Tap, and upgrade switches and associated equipment at Fitch Mountain Substation. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Line Reconductoring | NERC TPL Standards | 2024-02-13 | 51 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.53125 | NA | 60 kV | 490 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5741140 | T.0000039 | Fulton-Fitch Mtn 60kV Reconductor | 5 | 61 | NA | 2015 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | 2009 | FALSE | 2009 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2017-10-11 | IS/MND | NA | CPUC | NA | PTC: A.15-12-005 | 2015-12-03 | Approved | 2017 | Operational | 2 | 2018-09-17 | 2013-05-01 | 2020-03-17 | Project Design | FALSE | 5000 | NA | 6783.6922 | 6783.6922 | 2806.9919 | 1071.3915 | 60.3741 | -14.8395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6783.6922 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 6291.174 | 56.0471 | -13.7759 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 342 | NEW 230 kV INDUSTRIAL SWITCHING STATION |  |  | Lockeford CDP, San Joaquin | The Lockeford-Lodi Area 230 kV Development Project will loop the Brighton – Bellota 230 kV Line into Lockeford 230 kV Substation to bring a new 230 kV source into the area. A new 230 kV double circuit tower line will be constructed to connect the existing Lockeford 230 kV Substation to a new 230 kV switching to be constructed near the City of Lodi’s existing Industrial 60 kV Subsation. To accommodate the Brighton – Bellota loop-in and the new DCTL, the Lockeford 230 kV Bus will be upgraded to a four-bay breaker-and-a-half (BAAH) bus configuration. The City of Lodi will be constructing a new 230/60 kV Substation which will be connected to the new 230 kV switching station. | Substation - Multiple | New | NA | Reliability | New Substation | NERC TPL Standards | 2024-03-01 | NA | Steady State Power Flow System Analysis | Non-Wires - Large Scale Energy Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | TBD | NA | 230 kV | 45 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767188 | T.0000155 | Lockeford - Lodi Area 230 kV Development | 5 | 61 | 5752080 | 2013 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | PEA Deemed Complete | TBD | TBD | NA | CPUC | NA | CPCN: A.23-09-001 | 2023-09-01 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2029-01-12 | 2017-03-01 | 2029-06-12 | Prioritization | FALSE | $80,000 ¦ $105,000 | TBD | 1252.6646 | 35085.8476 | 318.0505 | 177.5874 | 196.2828 | 147.2683 | 108.0446 | 186.9487 | 612.6349 | 24674.8315 | 4943.7925 | 1455.3826 | 0 | 1236.6548 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 343 | Ravenswood Sub: Build Ravenswood Dsub |  |  | Menlo Park, San Mateo | This project proposes to install two 115/12 kV, 60 MVA banks with LTC, two 12 kV metal-clad switchgears, each with six feeder bays and install four 12 kV feeders at Ravenswood Substation to serve the requested demand of 37.1 MVA at new Meta (Facebook) Willow Village Campus in Menlo Park, starting in 2024. Transmission Substation Work (MAT 61A) • Extend the 115 kV bus to build Bus Section F with five bay spaces • Install two 115 kV bus sectionalizing breakers with disconnects • Install one 115 kV MPAC building • Upgrade Ravenswood 230 kV BAAH with redundant relays to mitigate against thermal overload on San Mateo-Belmont 115 kV Line caused by failure of non-redundant relay at Ravenswood 230 kV BAAH Bus #2 | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Load Growth | Bus Upgrade | NA | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799747 | T.0007874 | RAVENSWOOD SUB:BUILD RAVENSWOOD DSUB | 2 | 61 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-07-01 | NA | 2026-07-22 | NA | FALSE | NA | NA | 11.555 | 23787.5048 | 0 | 0 | 0 | 9.33 | 2.0372 | 575.371 | 1610.5974 | 165.8236 | 0 | 0 | 0 | 11.3671 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 344 | SAN MIGUEL 70kV Substation Relay Upgrade |  |  | San Miguel CDP, San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Substation - Protection Relay | Upgrade/Retrofit | NA | Reliability | Substation Reliability | NERC TPL Standards | 2024-02-08 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.77704 | NA | 70 kV | 61 | 8. Compliance/Commitments With Low Safety Risk | 17 | RBPPF - TBD | Yes | 5771724 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 61 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Planning | 5 | 2028-01-18 | 2019-05-01 | 2029-01-12 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3795 | 156.5005 | 171.827 | 708.4768 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 345 | Magunden 115kV Substation - New BAAH |  |  | East Niles CDP, Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-07 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 15.2256 | NA | 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 11 | RBPPF - TBD | Yes | 5771735 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 61 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-09-09 | 2020-05-01 | 2027-11-18 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 12.3911 | 17.6011 | 11.6986 | 0.5475 | 0 | 0 | 0 | 0.8987 | 1.034 | 1.1098 | 1.1912 | 1408.7855 | 3758.2762 | 12.2462 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 346 | WRJ COMPETITIVE_CPUC LIC/PER |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Other | New | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.403 | NA | 230 ¦ 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767232 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 61 | 5763622 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | NA | 2020-05-01 | 2026-11-20 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 3041.0673 | 4967.8714 | 264.1343 | 162.9875 | 0 | 0 | 0 | 223.4846 | 253.5289 | 272.1116 | 292.0562 | 695.4125 | 937.3493 | 3002.6742 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 347 | LAND PURCHASE_MARTIN BUS EXTENSION |  |  | Brisbane, San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Other | Upgrade/Retrofit | T.0008764 | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-20 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 18.2105 | NA | 230 kV | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | NA | NA | 5520825 | T.0000159 | Egbert 230kV Switching Station | 9 | 61 | 5763147 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Operational | 2 | NA | 2021-12-01 | 2021-01-28 | NA | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 19036.9722 | 19036.9722 | 0 | 17507.0488 | 1849.0384 | -319.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19036.9722 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 17507.0488 | 1849.0384 | -319.115 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf
| 348 | Pittsburg: Connect 2 230 & inst bus reac |  |  | Pittsburg, Contra Costa | Add 18-ohm reactors in parallel between Bus D and E of the Pittsburg 115kV substation | Substation - Reactive Equipment | New | T.0004581 | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 28.8512 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804803 | T.0009189 | Loop Vaca Dixon-Tesla in Collinsville | 4 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | TRUE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-07-21 | 2028-01-01 | 2028-06-13 | NA | FALSE | 26000 | NA | 160.4882 | 28727.4528 | 0 | 0 | 0 | 0 | 134.265 | 442.9715 | 2063.0968 | 17643.7911 | 6330.5724 | 2195.6006 | 41.4352 | 134.265 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 349 | CALIFORNIA FLATS 230kV Sub Relay Upgrade |  |  | Monterey | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Substation - Protection Relay | Upgrade/Retrofit | NA | Reliability | Substation Reliability | NERC TPL Standards | 2024-03-11 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.4097 | NA | 230 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | 26 | RBPPF - TBD | Yes | 5771721 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 61 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Engineering less than 50% complete | 5 | 2027-07-01 | 2019-05-01 | 2027-07-23 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 57.4677 | 2346.2766 | 0.2774 | 1.2284 | 2.0283 | 4.1785 | 42.2238 | 7.2724 | 9.0922 | 222.4563 | 173.2331 | 625.9736 | 0 | 53.693 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 350 | Morro Bay 230kV Substation Relay Upgrade |  |  | Morro Bay, San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Substation - Protection Relay | Upgrade/Retrofit | NA | Reliability | Substation Reliability | NERC TPL Standards | 2024-03-04 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 12.614 | NA | 230 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | 10 | RBPPF - TBD | Yes | 5771722 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 61 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Engineering less than 50% complete | 5 | 2027-07-01 | 2019-05-01 | 2027-07-23 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 51.574 | 1954.3734 | 0.0746 | 0.1213 | 0.2716 | 0.3421 | 48.137 | 4.3599 | 4.5538 | 4.8875 | 236.424 | 241.5665 | 523.9447 | 50.3531 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 351 | New Estrella 70kV Substation |  |  | Paso Robles, San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Substation - Multiple | New | NA | Reliability | New Substation | NERC TPL Standards | NA | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | TBD | NA | 70 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767207 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 61 | 5737113 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Planning | 5 | 2027-10-29 | 2019-05-01 | 2028-06-02 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 11514.4762 | 39890.2056 | 14.5899 | 29.2584 | 24.4838 | 129.3569 | 10869.0958 | 926.2093 | 314.9891 | 808.2842 | 7325.8893 | 17693.701 | 0 | 11341.8512 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 352 | CASA LOMA JCT SUBST_COMPETITIVE |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Multiple | New | T.0000220 ¦ T.0000144 | Reliability | New Substation | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 230 ¦ 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767215 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 61 | 5763622 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-05-20 | 2020-05-01 | 2026-08-28 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 717.9697 | 63472.5077 | 42.3968 | 32.7334 | 0 | 0 | 0 | 52.9113 | 59.8435 | 64.2298 | 68.9375 | 10990.1319 | 28469.5673 | 708.7569 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 353 | CASA LOMA JUNCTION SUBSTATION |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Multiple | New | T.0000220 ¦ T.0000144 | Reliability | New Substation | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | TBD | NA | 230 ¦ 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767199 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 61 | 5756022 | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-10-13 | 2020-05-01 | 2029-05-04 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 368.838 | 24102.7173 | 31.0255 | 14.3438 | 0 | 0 | 0 | 77.4456 | 26.499 | 28.4413 | 30.5259 | 5944.4643 | 4672.1657 | 313.8414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 354 | Stockdale 230kV Substn Ampacity & Relay |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Line Termination | Upgrade/Retrofit | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 230 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 11 | RBPPF - TBD | Yes | 5771739 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 61 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-10-16 | 2020-05-01 | 2027-02-24 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 20.7974 | 23467.1855 | 9.4196 | 0.5367 | 0 | 0 | 0 | 102.7575 | 1.0118 | 1.086 | 1.1656 | 1.2511 | 6106.3563 | 11.9839 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 355 | Wheeler Ridge 230kV Station - New BAAH |  |  | Kern | Project Description This project will construct a new 230/115 kV transmission substation in the Bakersfield area to provide additional transmission capacity to serve electric customers in Kern County. The 230 kV and 115 kV buses will be constructed to a breaker-and-a-half (BAAH) configuration, each with an arrangement for five interconnections (three line terminations and two new 230/115 kV transformers). The complete project scope of work includes the following: Competitive Portion of Wheeler Ridge Junction Substation: • Construct 230 kV portion of WRJ Substation, including two new 230/115 kV transformers and three 230 kV line terminations • Land rights acquisition and permitting for substation Non-competitive Portion of Wheeler Ridge Junction Substation: • Convert 15.5 miles of single-circuit transmission line between Wheeler Ridge Substation and WRJ Substation. • Swing converted Wheeler Ridge - Lamont 115 kV Line into a new Wheeler Ridge 230 kV terminal • Construct 1 mile of 230 kV between WRJ and the old Wheeler Ridge - Lamont 115 kV Line near Tower 011/065 • Open the 2 Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 • Open the Kern-Tevis-Stockdale-Lamont 115 kV circuits at Tower 005/035 to create the Kern-Tevis-Stockdale 115 kV Lines 1 and 2 • Extend the now idle 115 kV lines out of Lamont to the new WRJ as 1 mile of double-circuit. Use the remaining portion of the Kern-Tevis-Stockdale-Lamont 115 kV Lines to create WRJ-Lamont 115 kV Lines 1 and 2 • Rebuild and convert 5 miles of Kern-Tevis-Stockdale-Lamont 115 kV to 230 kV double-circuit. Convert 5 miles of 115 kV double-circuit to 230 kV double-circuit between Tower 005/035 and WRJ. 115 kV Towers are not suitable for 230 kV • Build 1 mile of new 230 kV between Tower 005/035 and Stockdale CB 212 • Remove the existing Kern-Stockdale Tap #2 from Stockdale CB 212 • Build 1 mile of new 115 kV single-circuit between WRJ and the idle Magunden Line • Open end Kern-Tevis-Stockdale-Lamont 115 kV line at Tower 005/035 and loop Stockdale Substation • Convert and re-conductor 5 miles of the Kern-Tevis-Stockdale-Lamont 115 kV Line section from Towers 005/035 to 011/065 to 230 kV operation on both sides of double circuit tower line (other side is idle circuit). Terminate both circuits at WRJ. Terminate both remaining 115 kV lines to Lamont at WRJ • Remove Stockdale #2 230 kV Tap from Stockdale Substation, and terminate the first newly converted 230 kV circuit bypassing Stockdale Substation • Terminate second newly converted 230 kV circuit at Stockdale Substation for a loop arrangement | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000220 ¦ T.0000144 | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-06 | 113 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 8 | RBPPF - TBD | Yes | 5771737 | T.0000156 | Wheeler Ridge Junction Substation | 18 | 61 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-10-16 | 2020-05-01 | 2026-03-06 | ISO Action | FALSE | $90,000 ¦ $140,000 | NA | 9.875 | 3625.477 | 6.1352 | 0.2794 | 0 | 0 | 0 | 125.2862 | 0.5416 | 0.5813 | 0.6239 | 540.2047 | 760.0272 | 6.4146 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 356 | MANNING SUB: GATES PROTECTION UPGRADE |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Protection Relay | Upgrade/Retrofit | T.0009550 | Policy | Substation Capacity | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804878 | T.0009194 | Manning New 500kV Sub Connection | 10 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-06-24 | 2028-01-01 | 2028-04-28 | NA | FALSE | $325,000 ¦ $485,000 | NA | 223.9936 | 4217.0553 | 0 | 0 | 0 | 0 | 147.1446 | 293.1626 | 0 | 0 | 0 | 0 | 0 | 147.1446 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 357 | MANNING SUB: LOS BANOS PROTECTION UPGRAD |  |  | Merced | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Protection Relay | Upgrade/Retrofit | T.0009550 | Policy | Substation Capacity | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804804 | T.0009194 | Manning New 500kV Sub Connection | 10 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-06-24 | 2028-01-01 | 2028-04-28 | NA | FALSE | $325,000 ¦ $485,000 | NA | 112.1382 | 4257.1628 | 0 | 0 | 0 | 0 | 52.8413 | 406.803 | 0 | 0 | 0 | 0 | 0 | 52.8413 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 358 | MANNING SUB: MANNING TELECOM & TESTING |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Protection Relay | Upgrade/Retrofit | T.0009550 | Policy | Substation Capacity | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5809028 | T.0009194 | Manning New 500kV Sub Connection | 10 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-06-24 | 2028-01-01 | 2028-04-28 | NA | FALSE | $325,000 ¦ $485,000 | NA | 2.7138 | 9355.1531 | 0 | 0 | 0 | 0 | 0 | 89.1004 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 359 | MANNING SUB: MIDWAY PROTECTION UPGRADE |  |  | Buttonwillow CDP, Kern | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Protection Relay | Upgrade/Retrofit | T.0009550 | Policy | Substation Capacity | NERC TPL Standards | 2024-03-15 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804805 | T.0009194 | Manning New 500kV Sub Connection | 10 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-06-24 | 2028-01-01 | 2028-04-28 | NA | FALSE | $325,000 ¦ $485,000 | NA | 54.5444 | 2889.6696 | 0 | 0 | 0 | 0 | 25.5257 | 285.7288 | 0 | 0 | 0 | 0 | 0 | 25.5257 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 360 | MANNING SUB: TRANQUILITY BAAH |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Multiple | New | T.0009550 | Policy | New Substation | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804813 | T.0009194 | Manning New 500kV Sub Connection | 10 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-06-24 | 2028-01-01 | 2028-04-28 | NA | FALSE | $325,000 ¦ $485,000 | NA | 146.283 | 19987.8568 | 0 | 0 | 0 | 0 | 64.1999 | 579.6288 | 392 | 392 | 2000 | 23800 | 24000 | 64.1999 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 361 | MANNING SUB: PANOCHE BAAH |  |  | Fresno | Replace 115 kV circuit breakers 132, 152, 102 and 162, install a new MPAC building for the 115 kV bus section, convert 230 kV Bus Section D to BAAH and replace overstressed breakers in Bus E to 63 kA at Panoche substation | Substation - Bus Arrangement | Upgrade/Retrofit | T.0009550 | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-05 | 23 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804806 | T.0009194 | Manning New 500kV Sub Connection | 10 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | TRUE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-06-24 | 2028-01-01 | 2028-04-28 | NA | FALSE | 184000 | NA | 164.0069 | 85431.3695 | 0 | 0 | 0 | 0 | 82.1099 | 664.8151 | 392 | 392 | 2000 | 23800 | 24000 | 82.1099 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 362 | MARTIN BUS EXT EMBARCADERO PROT UPGRADE |  |  | San Francisco, San Francisco | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Substation - Protection Relay | Upgrade/Retrofit | T.0008764 | Reliability | Substation Reliability | NERC TPL Standards | 2024-03-14 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.55624 | NA | 230 kV | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | RBPPF - TBD | Yes | 5767647 | T.0000159 | Egbert 230kV Switching Station | 9 | 61 | 5763147 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Engineering more than 50% complete | 4 | 2027-02-26 | 2021-12-01 | 2027-03-25 | Prioritization | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 84.6286 | 2094.3839 | 0 | 0 | 14.9511 | 52.312 | 12.1774 | 31.1308 | 0 | 0 | 0 | 0 | 457.075 | 79.4404 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf
| 363 | MARTIN BUS EXT JEFFERSON PROT UPGRADES |  |  | San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Substation - Protection Relay | Upgrade/Retrofit | T.0008764 | Reliability | Substation Reliability | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.7091 | NA | 230 kV | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | RBPPF - TBD | Yes | 5767646 | T.0000159 | Egbert 230kV Switching Station | 9 | 61 | 5763147 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Engineering more than 50% complete | 4 | 2028-03-10 | 2021-12-01 | 2028-04-14 | Prioritization | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 51.9197 | 2853.0597 | 0.0304 | 0.0491 | 15.6606 | 23.5376 | 10.0545 | 24.4243 | 0 | 0 | 0 | 0 | 160.1952 | 49.9024 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf
| 364 | MARTIN BUS EXT MARTIN SUB PROT UPGRADES |  |  | Brisbane, San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Substation - Protection Relay | Upgrade/Retrofit | T.0008764 | Reliability | Substation Reliability | NERC TPL Standards | 2024-03-20 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 18.2105 | NA | 230 kV | 564 | 8. Compliance/Commitments With Low Safety Risk | 1126 | RBPPF - TBD | Yes | 5767645 | T.0000159 | Egbert 230kV Switching Station | 9 | 61 | 5763147 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Engineering more than 50% complete | 4 | 2027-02-26 | 2021-12-01 | 2027-03-25 | Prioritization | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 260.1841 | 4517.8269 | 0 | 0 | 36.8994 | 194.1059 | 24.5206 | 41.1441 | 0 | 0 | 0 | 0 | 201.1244 | 255.5259 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf
| 365 | MARTIN SUB_230KV BUS EXT |  |  | Brisbane, San Mateo | The Martin 230 kV Bus Extension project will: Construct a new 230 kV switching station near, but not adjacent to, Martin Substation. Relocate voltage control and power flow limiting equipment associated with the Jefferson-Martin and Martin-Embarcadero Cables from Martin, if necessary, to the new switching station. Completion of the Martin Bus Extension project will improve service reliability and system resiliency in serving customers in San Francisco and northern San Mateo County. | Substation - Multiple | New | T.0008764 | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-20 | 51 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | TBD | NA | 230 kV | 741 | 8. Compliance/Commitments With Low Safety Risk | 1126 | RBPPF - TBD | Yes | 5767214 | T.0000159 | Egbert 230kV Switching Station | 9 | 61 | 5763147 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2015 | FALSE | 2015 | NA | https://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | FALSE | Final Certified | 2020-07-13 | EIR | NA | CPUC | NA | CPCN: A.17-12-021 | 2017-12-28 | Approved | 2020 | Engineering more than 50% complete | 4 | 2027-05-14 | 2021-12-01 | 2028-11-08 | Prioritization | FALSE | $85,000 ¦ $129,000 | $294,650 ¦ CPUC | 40238.8228 | 116400.3257 | 105.4904 | 583.9741 | 5920.4821 | 16228.3266 | 16470.0052 | 4424.6959 | 0 | 0 | 0 | 0 | 41138.4535 | 39526.8878 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $250 Mil – $300 Mil ¦ Over $500 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2014-2015TransmissionPlan.pdf
| 366 | VACA DIXON: Install 230 KV Smart Wires |  |  | Vacaville, Solano | The project scope is to install about 78 modular power flow control systems deployed on a dedicated bank structure at Vaca Dixon Substation (or adjacent property). Further scoping activities will finalize the substation location(s) to address potential new line overloads. The CAISO recently approved this project in their 2017-2018 Transmission Plan. | Substation - Voltage Support Equipment | New | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-01 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.725 | NA | 230 kV | 103 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5779290 | T.0003844 | Vaca-Dixon 230kV SmartWire Devices | 1 | 61 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-12-25 | 2019-10-01 | 2026-07-17 | Prioritization | FALSE | 11000 | NA | 2779.4897 | 18805.3012 | 546.3391 | 312.0612 | 1.8077 | 0 | 0 | 236.2237 | 3000 | 5000 | 1000 | 0 | 0 | 2779.4897 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 367 | Moraga-Castro Valley 230kV Line Capacity |  |  | Castro Valley CDP, Alameda | The project scope of work involves upgrading the limiting substation equipment (jumper conductors and wave traps) on the Moraga-Castro Valley and Castro Valley-Newark 230 kV lines to utilize their full conductor ratings. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-08 | 72 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 5.428 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806178 | T.0004421 | Moraga-Castro Valley 230 kV Capacity | 3 | 61 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2024-10-02 | 2013-05-01 | 2024-12-26 | Prioritization | TRUE | $1,000 ¦ $5,000 | NA | 79.9847 | 1151.9354 | 0 | 0 | 0 | 0 | 33.9576 | 816.9277 | 301.0501 | 0 | 0 | 0 | 0 | 33.9576 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 368 | COLEMAN-PH SUBSTATION |  |  | Cottonwood CDP, Shasta ¦ Shasta | This project proposes to reconductor the Coleman-Red Bluff 60 kV line. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-04-10 | 83 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | NA | 230 ¦ 60 kV | 137 | Not Available | Not Available | RBPPF - TBD | Yes | 5766751 | T.0000013 | Coleman - Red Bluff Project | 5 | 61 | 5738807 | 2011 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-07-07 | 2021-12-01 | 2028-12-28 | Prioritization | FALSE | $43,000 ¦ $57,000 | NA | 62.0157 | 1231.4395 | 1.1294 | 0.4108 | 47.5198 | 3.7781 | 4.4287 | 4.5835 | 4.9864 | 5.3518 | 287.2337 | 821.3311 | 16.7596 | 61.1929 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 369 | Midway-Temblor 115kV Recon & Voltage Sup |  |  | Kern | This project proposes to upgrade 14.5 miles of conductor and four (4) transmission switches (Nos. 137, 139, and 157) on the Midway – Temblor 115 kV Line, and install 40 MVAR shunt capacitors at Temblor Substation in order to provide additional transmission capacity and reliability to serve electric customers in Kern County. | Substation - Voltage Support Equipment | New | TBD | Reliability | Voltage Support | NERC TPL Standards | 2024-03-06 | 19 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 0.93942 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 20 | RBPPF - TBD | Yes | 5781146 | T.0004113 | Midway-Temblor 115kV Recon & Voltage Sup | 2 | 61 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-08-14 | 2018-05-01 | 2027-09-16 | Prioritization | FALSE | $25,000 ¦ $35,000 | NA | 322.0469 | 9968.2096 | 268.6973 | 26.0818 | 21.383 | 3.727 | 0 | 42.7936 | 2068.7591 | 6979.6733 | 3739.7946 | 0 | 0 | 322.0469 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 370 | HERNDON SUB - NORTHERN FRESNO 115KV AREA |  |  | Fresno, Fresno | This project will sectionalize the 230kV buses at two key substations to ensure reliable electric service to customers in Fresno County. By installing 230kV bus sectionalizing breakers at Herndon and McCall substations, the project will reduce the likelihood of a 230kV bus or internal breaker fault causing 115kV overloads and voltage issues leading to load shedding and service interruptions to customers in the Fresno area. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 13.3414 | NA | 115 kV | 428 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5767191 | T.0000158 | Northern Fresno 115 kV Area Reinforcemnt | 2 | 61 | 5751201 | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-06-28 | 2018-05-01 | 2020-05-13 | Bundling Dependencies | FALSE | $110,000 ¦ $190,000 | NA | 13727.9432 | 13727.9432 | 2587.991 | 1805.2194 | 825.3714 | 74.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13727.9432 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 12489.3821 | 800.5071 | 71.7918 | 0 | 0 | 0% | NA | NA | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - New Substation Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 371 | MCCALL SUB - NORTHERN FRESNO 115KV AREA |  |  | Fresno | This project will sectionalize the 230kV buses at two key substations to ensure reliable electric service to customers in Fresno County. By installing 230kV bus sectionalizing breakers at Herndon and McCall substations, the project will reduce the likelihood of a 230kV bus or internal breaker fault causing 115kV overloads and voltage issues leading to load shedding and service interruptions to customers in the Fresno area. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 16.2494 | NA | 115 kV | 428 | Not Available | NA | NA | NA | 5767193 | T.0000158 | Northern Fresno 115 kV Area Reinforcemnt | 2 | 61 | 5751201 | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-07-03 | 2018-05-01 | 2019-02-15 | Clearances | FALSE | $110,000 ¦ $190,000 | NA | 9513.0447 | 9513.0447 | 1716.5794 | 200.0194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9513.0447 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 9032.72 | 193.5721 | 0 | 0 | 0 | 0 | 0% | NA | NA | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - New Substation Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 372 | Collinsville New 500kV Sub Connection |  |  | Solano | This project will support connection of a new 500kV substation between Vaca Dixon and Tesla Substations to the PG&E electric system. The new 500kV substation (named Collinsville), to be installed by the third-party entity (LS Power), is needed to address a number of identified transmission constraints and provide an additional supply from the 500kV system into the northern Greater Bay Area, to increase reliability to the area and advance additional renewable generation in the northern area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Vaca Dixon – Tesla 500kV line into the new 500kV Collinsville substation and build the associated transmissioin line. • Modify Vaca Dixon 500kV Series Capacitor Bank 2 reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Connect two 230kV lines to Pittsburg 230kV bus in separate bus sections and install 115kV bus reactors in bus sections D&E. • Upgrade line protection of Tesla 500kV line at Tesla substation as needed | Substation - Multiple | New | T.0004581 | Policy | New Substation | NERC TPL Standards | 2024-03-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804724 | T.0009189 | Loop Vaca Dixon-Tesla in Collinsville | 4 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-07-21 | 2028-01-01 | 2028-05-12 | NA | FALSE | $475,000 ¦ $675,000 | NA | 77.5152 | 34181.3801 | 0 | 0 | 0 | 0 | 45.4737 | 705.7683 | 1636.2261 | 9505.3089 | 9026.5408 | 725.4396 | 0 | 45.4737 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 373 | Tesla: Upgrade system protection |  |  | Alameda | This project will support connection of a new 500kV substation between Vaca Dixon and Tesla Substations to the PG&E electric system. The new 500kV substation (named Collinsville), to be installed by the third-party entity (LS Power), is needed to address a number of identified transmission constraints and provide an additional supply from the 500kV system into the northern Greater Bay Area, to increase reliability to the area and advance additional renewable generation in the northern area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Vaca Dixon – Tesla 500kV line into the new 500kV Collinsville substation and build the associated transmissioin line. • Modify Vaca Dixon 500kV Series Capacitor Bank 2 reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Connect two 230kV lines to Pittsburg 230kV bus in separate bus sections and install 115kV bus reactors in bus sections D&E. • Upgrade line protection of Tesla 500kV line at Tesla substation as needed | Substation - Protection Relay | Upgrade/Retrofit | T.0004581 | Policy | Substation Reliability | NERC TPL Standards | 2024-03-15 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Heat Wave |  | NA | 69.382 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804802 | T.0009189 | Loop Vaca Dixon-Tesla in Collinsville | 4 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-07-10 | 2028-01-01 | 2028-05-12 | NA | FALSE | $475,000 ¦ $675,000 | NA | 65.6693 | 3721.192 | 0 | 0 | 0 | 0 | 37.658 | 254.4407 | 413.416 | 1860.7905 | 469.3782 | 800.0793 | 0 | 37.658 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 374 | Newark: HVDC Connection |  |  | Fremont, Alameda | This project will support the interconnection of the Voltage-Sourced Converter (VSC)-HVDC converter station into the 230kV bus at Newark Substation. The VSC-HVDC converter station will be installed by the third party entity (LS Power) to transport power from Newark to NRS. The proposed PG&E scope of work for the project includes: • Install a 230kV breaker complete with new structure and all associated switches at Newark. • Modify protection scheme, as required • Upgrade grounding and grading as required. • Construct 230kV line from the new circuit breaker at Newark up to the PG&E property line for making connection to LS Power’s HVDC converter station. | Substation - Line Termination | New | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | NA | 27.7611 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804787 | T.0009168 | Newark - HVDC Connection | 2 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | NA | TBD | NA | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-09-19 | 2028-01-01 | 2027-05-28 | NA | FALSE | $325,000 ¦ $510,000 | NA | 451.2882 | 5795.8028 | 0 | 0 | 0 | 0 | 345.0878 | 1272.0364 | 1000 | 4000 | 2000 | 500 | 0 | 345.0878 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 375 | Metcalf: 500kV HVDC Connection |  |  | Santa Clara | This project will support the interconnection of the Voltage-Sourced Converter (VSC)-HVDC converter station into the 500kV bus at Metcalf substation and into the 115kV bus at the San Jose B substation. The VSC-HVDC converter stations and the HVDC line will be installed by the third-party entity (LS Power) to transport power from Metcalf to San Jose B. The proposed PG&E scope of work for the project includes: Metcalf Subsattion • Install a partial 500kV bay at Metcalf, complete with breakers, switches, bus work and other associated equipment. • Install protection scheme for the new breakers and HVDC line connection. • Expand substation yard and fence as required. • Upgrade grounding, grading and security as required. • Construct 500kV line from the 500kV bus to the Point of Change of Ownership (PCO) switch location for HVDC converter connection.. San Jose B Substation • Convert San Jose B 115kV bus to GIS BAAH, complete with clean-air 115kV breakers and associoated equipment. (The GIS will be designed to accommodate existing four lines, four distribution transformers and a new HV cable connection for LS Power HVDC converter connection.) • Install temporary breaker and other associated equipment to make provision for GIS equipment installation. • Install HV cable from GIS building to PCO location for HVDC converter connection. | Substation - Line Termination | New | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-13 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804788 | T.0009169 | Metcalf - 500kV HVDC Connection | 8 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-07-11 | 2028-01-01 | 2027-12-15 | NA | FALSE | $425,000 ¦ $615,000 | NA | 487.2615 | 26781.3175 | 0 | 0 | 0 | 0 | 363.6569 | 3971.3345 | 9900 | 33300 | 36900 | 11700 | 0 | 363.6569 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 376 | San Jose B - HVDC - North Transition RE |  |  | San Jose, Santa Clara | This project will support the interconnection of the Voltage-Sourced Converter (VSC)-HVDC converter station into the 500kV bus at Metcalf substation and into the 115kV bus at the San Jose B substation. The VSC-HVDC converter stations and the HVDC line will be installed by the third-party entity (LS Power) to transport power from Metcalf to San Jose B. The proposed PG&E scope of work for the project includes: Metcalf Subsattion • Install a partial 500kV bay at Metcalf, complete with breakers, switches, bus work and other associated equipment. • Install protection scheme for the new breakers and HVDC line connection. • Expand substation yard and fence as required. • Upgrade grounding, grading and security as required. • Construct 500kV line from the 500kV bus to the Point of Change of Ownership (PCO) switch location for HVDC converter connection.. San Jose B Substation • Convert San Jose B 115kV bus to GIS BAAH, complete with clean-air 115kV breakers and associoated equipment. (The GIS will be designed to accommodate existing four lines, four distribution transformers and a new HV cable connection for LS Power HVDC converter connection.) • Install temporary breaker and other associated equipment to make provision for GIS equipment installation. • Install HV cable from GIS building to PCO location for HVDC converter connection. | Substation - Multiple | New | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.0642 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5555160 | T.0009169 | Metcalf - 500kV HVDC Connection | 8 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-01-13 | 2028-01-01 | 2026-05-25 | NA | FALSE | $425,000 ¦ $615,000 | NA | 3.141 | 1046.4004 | 0 | 0 | 0 | 0 | 0 | 355.7657 | 219.8221 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 377 | San Jose B - HVDC - San Jose A RE |  |  | San Jose, Santa Clara | This project will support the interconnection of the Voltage-Sourced Converter (VSC)-HVDC converter station into the 500kV bus at Metcalf substation and into the 115kV bus at the San Jose B substation. The VSC-HVDC converter stations and the HVDC line will be installed by the third-party entity (LS Power) to transport power from Metcalf to San Jose B. The proposed PG&E scope of work for the project includes: Metcalf Subsattion • Install a partial 500kV bay at Metcalf, complete with breakers, switches, bus work and other associated equipment. • Install protection scheme for the new breakers and HVDC line connection. • Expand substation yard and fence as required. • Upgrade grounding, grading and security as required. • Construct 500kV line from the 500kV bus to the Point of Change of Ownership (PCO) switch location for HVDC converter connection.. San Jose B Substation • Convert San Jose B 115kV bus to GIS BAAH, complete with clean-air 115kV breakers and associoated equipment. (The GIS will be designed to accommodate existing four lines, four distribution transformers and a new HV cable connection for LS Power HVDC converter connection.) • Install temporary breaker and other associated equipment to make provision for GIS equipment installation. • Install HV cable from GIS building to PCO location for HVDC converter connection. | Substation - Multiple | New | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-15 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.1997 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807758 | T.0009169 | Metcalf - 500kV HVDC Connection | 8 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-01-13 | 2028-01-01 | 2026-05-25 | NA | FALSE | $425,000 ¦ $615,000 | NA | 12.7593 | 1470.8951 | 0 | 0 | 0 | 0 | 0.7403 | 486.9532 | 0 | 0 | 0 | 0 | 0 | 0.7403 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 378 | San Jose B - HVDC - South Transition RE |  |  | San Jose, Santa Clara | This project will support the interconnection of the Voltage-Sourced Converter (VSC)-HVDC converter station into the 500kV bus at Metcalf substation and into the 115kV bus at the San Jose B substation. The VSC-HVDC converter stations and the HVDC line will be installed by the third-party entity (LS Power) to transport power from Metcalf to San Jose B. The proposed PG&E scope of work for the project includes: Metcalf Subsattion • Install a partial 500kV bay at Metcalf, complete with breakers, switches, bus work and other associated equipment. • Install protection scheme for the new breakers and HVDC line connection. • Expand substation yard and fence as required. • Upgrade grounding, grading and security as required. • Construct 500kV line from the 500kV bus to the Point of Change of Ownership (PCO) switch location for HVDC converter connection.. San Jose B Substation • Convert San Jose B 115kV bus to GIS BAAH, complete with clean-air 115kV breakers and associoated equipment. (The GIS will be designed to accommodate existing four lines, four distribution transformers and a new HV cable connection for LS Power HVDC converter connection.) • Install temporary breaker and other associated equipment to make provision for GIS equipment installation. • Install HV cable from GIS building to PCO location for HVDC converter connection. | Substation - Multiple | New | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8982 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5555161 | T.0009169 | Metcalf - 500kV HVDC Connection | 8 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-01-13 | 2028-01-01 | 2026-05-25 | NA | FALSE | $425,000 ¦ $615,000 | NA | 3.3787 | 1046.6381 | 0 | 0 | 0 | 0 | 0 | 356.0034 | 219.8221 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 379 | San Jose B - HVDC - Trimble RE |  |  | San Jose, Santa Clara | This project will support the interconnection of the Voltage-Sourced Converter (VSC)-HVDC converter station into the 500kV bus at Metcalf substation and into the 115kV bus at the San Jose B substation. The VSC-HVDC converter stations and the HVDC line will be installed by the third-party entity (LS Power) to transport power from Metcalf to San Jose B. The proposed PG&E scope of work for the project includes: Metcalf Subsattion • Install a partial 500kV bay at Metcalf, complete with breakers, switches, bus work and other associated equipment. • Install protection scheme for the new breakers and HVDC line connection. • Expand substation yard and fence as required. • Upgrade grounding, grading and security as required. • Construct 500kV line from the 500kV bus to the Point of Change of Ownership (PCO) switch location for HVDC converter connection.. San Jose B Substation • Convert San Jose B 115kV bus to GIS BAAH, complete with clean-air 115kV breakers and associoated equipment. (The GIS will be designed to accommodate existing four lines, four distribution transformers and a new HV cable connection for LS Power HVDC converter connection.) • Install temporary breaker and other associated equipment to make provision for GIS equipment installation. • Install HV cable from GIS building to PCO location for HVDC converter connection. | Substation - Multiple | New | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8982 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807739 | T.0009169 | Metcalf - 500kV HVDC Connection | 8 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-01-13 | 2028-01-01 | 2026-05-25 | NA | FALSE | $425,000 ¦ $615,000 | NA | 9.6044 | 1197.1923 | 0 | 0 | 0 | 0 | 0.7403 | 434.3611 | 0 | 0 | 0 | 0 | 0 | 0.7404 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 380 | San Jose B: HVDC Connection |  |  | San Jose, Santa Clara | This project will support the interconnection of the Voltage-Sourced Converter (VSC)-HVDC converter station into the 500kV bus at Metcalf substation and into the 115kV bus at the San Jose B substation. The VSC-HVDC converter stations and the HVDC line will be installed by the third-party entity (LS Power) to transport power from Metcalf to San Jose B. The proposed PG&E scope of work for the project includes: Metcalf Subsattion • Install a partial 500kV bay at Metcalf, complete with breakers, switches, bus work and other associated equipment. • Install protection scheme for the new breakers and HVDC line connection. • Expand substation yard and fence as required. • Upgrade grounding, grading and security as required. • Construct 500kV line from the 500kV bus to the Point of Change of Ownership (PCO) switch location for HVDC converter connection.. San Jose B Substation • Convert San Jose B 115kV bus to GIS BAAH, complete with clean-air 115kV breakers and associoated equipment. (The GIS will be designed to accommodate existing four lines, four distribution transformers and a new HV cable connection for LS Power HVDC converter connection.) • Install temporary breaker and other associated equipment to make provision for GIS equipment installation. • Install HV cable from GIS building to PCO location for HVDC converter connection. | Substation - Line Termination | New | T.0003803 | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-02 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.1017 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804789 | T.0009169 | Metcalf - 500kV HVDC Connection | 8 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | TRUE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-08-14 | 2028-01-01 | 2027-12-22 | NA | FALSE | $425,000 ¦ $615,000 | NA | 489.5547 | 104839.4726 | 0 | 0 | 0 | 0 | 329.67 | 9695.8815 | 1100 | 3700 | 4100 | 1300 | 1000 | 329.67 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 381 | Jefferson: 230 kV bus upgrade |  |  | San Mateo | Extend the 230 kV bus at Jefferson substation and convert its configuration to Breaker and a Half. This project will allow for the interconnection of more bus elements. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-06 | 18 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.7091 | NA | 230 kV | 236 | 8. Compliance/Commitments (But Low Safety Risk) | 4 | RBPPF - TBD | Yes | 5785789 | T.0004805 | Jefferson: 230 Kv Bus Upgrade | 1 | 61 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2025-10-01 | 2022-12-31 | 2026-12-01 | Prioritization | FALSE | $6,000 ¦ $11,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 10000 | 300 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 382 | ORTIGA SUB - RING BUS |  |  | Merced | Ortiga Sub: Install one new 70/12 kV, 30 MVA three-phase transformer, four 70 kV breakers, one new 12 kV bus 1/bus 2 structure with four breaker bays, one bus-tie breaker and two circuit breakers, two new 12 kV distribution circuit outlets, and extend two new Ortiga distribution circuits to off-load existing Canal and Ortiga circuits and substation transformers. Transmission Substation Work (MWC 61) • Remove one 70 kW Motor Operated Air Switch 56 that protects existing Bank 1 • Install four 70 kV Circuit Breakers to create four-element ring bus with two 70 kV lines and two substation transformers. | Substation - Bus Arrangement | New | NA | Load Growth | Bus Upgrade | NA | 2024-02-07 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | 0.91773 | NA | 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5800378 | T.0007259 | Ortiga Sub, Replace Bank 1 | 4 | 61 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-09-16 | NA | 2026-10-30 | NA | FALSE | NA | NA | 50.7862 | 6963.091 | 0 | 0 | 0 | 0 | 12.8495 | 411.4515 | 1200 | 1300 | 0 | 0 | 0 | 12.8495 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 383 | New 230 kV Switchyard at Potrero |  |  | San Francisco, San Francisco | The project will involve the construction of a new 230 kV underground transmission line between Embarcadero and Potrero Power Plant (P.P.) Substations, construction of a new 230 kV switchyard at Potrero, the installation of new 230/115 kV transformers at Potrero, and the interconnection of the Project into the Embarcadero 230 kV bus and Potrero P.P. 115 kV buses. | Substation - Multiple | New | T.0003671 | Reliability | New Substation | NERC TPL Standards | 2024-03-28 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 230 kV | 564 | Not Available | NA | NA | NA | 5731443 | T.0003672 | NEW 230 KV SWITCHYARD AT POTRERO | 3 | 61 | NA | 2007 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2013-10-29 | IS/MND | NA | CPUC | NA | CPCN: A.12-12-004 | 2012-12-11 | Approved | 2014 | Operational | 2 | 2014-09-01 | 2015-12-31 | 2019-09-27 | Input Error | FALSE | $130,000 ¦ $150,000 | $197,000 ¦ CPUC | 74588.1933 | 74588.1933 | 1275.5931 | -123.1158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74588.1933 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 | 1275.5931 | -123.1158 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 384 | San Bernard Substation Install Bank 2 |  |  | Kern | This project proposes to install a second transformer bank at San Bernard Substation to eliminate a forecasted 9 percent normal overload of Arvin Transformer Bank 1 and a forecasted 10 percent normal overload of San Bernard Transformer Bank 1. These deficiencies are being caused by a sharp increase in water storage operations by the Arvin Edison Water Storage District that began in 2020. Although reduced by available load transfers, the overloads are expected to continue over the next two summers until capacity can be added in 2023. The installation of San Bernard Bank 2 will provide maximum load relief for San Bernard Bank 1, which is in very poor condition and recommended for replacement Transmission Substation Work (MWC 61): • Modify the San Bernard 70kV bus and 70kV equipment to accommodate a second transformer. | Substation - Structure | Upgrade/Retrofit | TBD | Load Growth | Bus Upgrade | NA | 2024-03-08 | NA | NA | Wires - Location/Route Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.86468 | NA | 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798622 | T.0007229 | San Bernard Substation Install Bank 2 | 1 | 61 | NA | 2021 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-04-19 | 2025-06-30 | 2025-07-25 | NA | TRUE | 18300 | NA | 1324.8243 | 3529.1177 | 0 | 0 | 0 | 207.8821 | 1005.181 | 1503.7062 | 801.7935 | 0 | 0 | 0 | 0 | 1213.0631 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 385 | Borden: Borden BK 1 Capacity Increase |  |  | Madera | This project proposes to replace Borden Bank 1 breaker and upgrade 70kV bus to match the capability of the Borden Bank 1. 1. Upgrade Bank Breaker CB 52 and associated switches to match the Transformer Bank # 1’s full capacity (200 N/220 E MVA) 2. Upgrade Borden 70 kV Bus Section “D” to match the Transformer Bank # 1’s full capacity. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-05 | 19 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 7.1874 | NA | 230 ¦ 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806920 | T.0009562 | Borden 230/70 kV Transformer Bank #1 Capacity Increase | 1 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-10-01 | 2025-07-17 | 2026-04-01 | Prioritization | FALSE | $11,500 ¦ $23,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 500 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
| 386 | Tesla: Reconfigure 115 kV bus |  |  | Alameda | This project will convert the Tesla 115kV bus from DBSB to BAAH. Below is the high-level scope of this project: 1. Install five bays of folded bus design BAAH bays to connect the existing elements 2. Install new MPAC building with protection and controls 3. Upgrade ground grid as needed The project will mitigate the system collapse issue due to the NERC Category P2-4 contingency. Even though load shedding is allowed under P2-4 contingency, the alternative of using RAS to shed load is not recommended due to loss of large amount of loads (about 300 MW in the 2032 study case), complexity of the RAS design and high requirement on the RAS reaction time. As a result, converting the Tesla 115 kV bus from DBSB to BAAH is recommended as shown in Figure 2. With the BAAH configuration, only two elements would be tripped when there is fault on the bay middle breaker, and there is no system collapse issue post any of the middle breaker faults. | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-15 | 49 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Heat Wave |  | NA | 69.382 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806787 | T.0009526 | Tesla 115 kV Bus Reconfiguration | 1 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-07-01 | 2030-12-31 | 2028-06-01 | NA | FALSE | 55000 | NA | 1.0304 | 1.0304 | 0 | 0 | 0 | 0 | 0 | 0.0122 | 2000 | 5000 | 12000 | 10000 | 500 | 1.0183 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 387 | Gates: 500kV Path Rating Upgrade |  |  | Fresno | Upgrade substation terminals at Gates, Los Banos, and Midway for 500 kV Path 15 and Midway for 500 kV Path 26 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NA | 2024-03-08 | 64 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805118 | T.0009205 | Gates Los Banos Midway Path Rating Upgrade | 3 | 61 | NA | 2023 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 3 | 2024-03-01 | 2024-05-31 | 2024-05-31 | NA | TRUE | 2088.777 | NA | 302.3039 | 1414.835 | 0 | 0 | 0 | 0 | 149.2278 | 1264.9318 | 0.6754 | 0 | 0 | 0 | 0 | 149.2278 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 388 | Round Mountain:500kV Path Rating Upgrade |  |  | Round Mountain CDP, Shasta | Upgrade substation terminals at Round Mountain, Table Mountain, and Vaca-Dixon for 500 kV Path 66 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NA | 2024-03-06 | 58 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Extreme Heat |  | NA | 29.1389 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805121 | T.0009211 | ROUND TABLE VACA MOUNTAIN 500KV PATH RATING | 3 | 61 | NA | 2023 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 3 | 2024-02-27 | 2024-05-31 | 2024-05-30 | NA | FALSE | 5165 | NA | 337.7124 | 1482.0706 | 0 | 0 | 0 | 0 | 127.2214 | 1354.8491 | 0 | 0 | 0 | 0 | 0 | 127.2215 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 389 | Table Mountain:500kV Path Rating Upgrade |  |  | Butte | Upgrade substation terminals at Round Mountain, Table Mountain, and Vaca-Dixon for 500 kV Path 66 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NA | 2024-03-06 | 58 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Subsidence |  | NA | 47.516 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805122 | T.0009211 | ROUND TABLE VACA MOUNTAIN 500KV PATH RATING | 3 | 61 | NA | 2023 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 3 | 2024-03-05 | 2024-05-31 | 2024-06-12 | NA | TRUE | 5165 | NA | 337.8479 | 1899.253 | 0 | 0 | 0 | 0 | 103.1011 | 1793.555 | 2.5969 | 0 | 0 | 0 | 0 | 103.1011 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 390 | Vaca Dixon: 500kV Path Rating Upgrade |  |  | Solano | Upgrade substation terminals at Round Mountain, Table Mountain, and Vaca-Dixon for 500 kV Path 66 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NA | 2024-03-12 | 61 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805123 | T.0009211 | ROUND TABLE VACA MOUNTAIN 500KV PATH RATING | 3 | 61 | NA | 2023 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2024-03-18 | 2024-05-31 | 2024-06-12 | NA | FALSE | 5165 | NA | 228.6459 | 1745.2949 | 0 | 0 | 0 | 0 | 82.3829 | 1662.912 | 0 | 0 | 0 | 0 | 0 | 82.3829 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 391 | LLAGAS SUB: 115kV PROTECTION MODS |  |  | Gilroy, Santa Clara | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Substation - Protection Relay | Upgrade/Retrofit | NA | Reliability | Substation Reliability | NERC TPL Standards | 2024-03-03 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3037 | NA | 115 kV | Not Available | 8. Compliance/Commitments With Low Safety Risk | 50 | RBPPF - TBD | Yes | 5786319 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 7 | 61 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-06-18 | 2021-12-01 | 2027-04-07 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 52.9382 | 1149.2078 | 1.9427 | 35.9144 | 3.2671 | 11.0913 | 0.7227 | 16.7124 | 479.8369 | 864.5288 | 48.6083 | 0 | 0 | 52.9382 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 392 | METCALF SUB: 115kV PROTECTION MODS |  |  | Santa Clara | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Substation - Protection Relay | Upgrade/Retrofit | NA | Reliability | Substation Reliability | NERC TPL Standards | 2024-03-13 | NA | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 50 | RBPPF - TBD | Yes | 5782115 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 7 | 61 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-11-04 | 2021-12-01 | 2026-06-29 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 8.532 | 1197.8001 | 0 | 7.4192 | 0.5343 | 0.5785 | 0 | 17.0371 | 1000 | 200 | 0 | 0 | 0 | 8.532 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 393 | MORGAN HILL SUB: 115kV BAAH CONVERSION |  |  | Morgan Hill, Santa Clara | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-02-09 | 16 | Steady State Power Flow System Analysis | Wires - New Substation Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.8017 | NA | 115 kV | 2135 | 8. Compliance/Commitments With Low Safety Risk | 50 | RBPPF - TBD | Yes | 5782117 | T.0004271 | Morgan Hill-Watsonville 115kV Area Reinf | 7 | 61 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-06-29 | 2021-12-01 | 2029-07-06 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 12929.1428 | 54602.7709 | 467.8988 | 776.0526 | 7868.2695 | 995.6401 | 85.1211 | 1165.4973 | 8000 | 37000 | 5000 | 0 | 0 | 12929.1428 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 394 | Manning: Panoche Sub Replace CB 102, 132 |  |  | Fresno | This project will support connection of a new 500kV substation between Los Banos and Gates substations to the PG&E electric system. The new 500kV substation (named Manning), to be installed by the third-party entity (LS Power), is needed to address overloads on the Borden-Storey 230kV lines and allow for the advancement of renewable generation within the Westlands / San Joaquin area. This project will support LS Power’s new 500kV substation connection to the PG&E transmission system. The proposed PG&E scope of work for the project includes: • Loop the Los Banos – Gates No.1 500kV line and the Los Banos – Midway No. 2 500kV line into the new 500kV Manning substation and build associated transmission lines. • Loop the two existing Panoche – Tranquillity 230kV lines into the new 500kV Manning substation and build associated transmission lines. • Reconductor the two Manning – Tranquillity 230kV lines. • Modify the Gates 500kV Series Capacitor Banks 1&2 (SC1 & SC2) reactance to maintain 500kV line compensation and upgrade 500kV line protection. • Upgrade Panoche 230kV Bus section D to BAAH and replace all overstressed breakers in Bus Section E. • Upgrade line terminals at Tranquillity substation. • Upgrade 500kV line protection at Los Banos substation as needed. • Upgrade 500kV line protection at Midway substation as needed. | Substation - Circuit Breaker | Upgrade/Retrofit | T.0009550 | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-05 | 22 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5808684 | T.0009194 | Manning New 500kV Sub Connection | 10 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | TRUE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-06-24 | 2028-01-01 | 2028-04-28 | NA | FALSE | 184000 | NA | 0 | 4735.2973 | 0 | 0 | 0 | 0 | 0 | 263.7831 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 395 | Wilson 230 kV BAAH |  |  | Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Bus Arrangement | Upgrade/Retrofit | T.0001381 ¦ T.0002231 | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-05 | 69 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 22.8151 | NA | 230 kV | 58 | 8. Compliance/Commitments With Low Safety Risk | 7 | RBPPF - TBD | Yes | 5783618 | T.0004116 | WILSON: 115 kV ARP - BAAH | 6 | 61 | NA | 2012 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-05-26 | 2015-05-01 | 2027-06-17 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 150.5506 | 14415.0361 | 87.687 | 60.2365 | 2.6271 | 0 | 0 | 211.8171 | 6641.0939 | 6073.832 | 997.9689 | 100.8183 | 0 | 150.5506 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 396 | WILSON: Reconfigure Bus to 115 KV BAAH |  |  | Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Bus Arrangement | Upgrade/Retrofit | T.0001381 ¦ T.0002231 | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-05 | 17 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 22.8151 | NA | 115 kV | 58 | 8. Compliance/Commitments With Low Safety Risk | 7 | RBPPF - TBD | Yes | 5781259 | T.0004116 | WILSON: 115 kV ARP - BAAH | 6 | 61 | NA | 2012 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-08-18 | 2015-05-01 | 2026-04-09 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 978.2611 | 23252.2586 | 715.0541 | 199.2135 | 18.8656 | 0 | 0 | 1851.7396 | 16345.647 | 3325.3821 | 3.281 | 0 | 0 | 978.2611 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 397 | VIERRA 115 KV BAAH |  |  | Lathrop, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-02-06 | 14 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.355 | NA | 115 kV | 102 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5746745 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 13 | 61 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 4 | 2024-06-03 | 2014-05-01 | 2025-06-02 | Prioritization | TRUE | $10,000 ¦ $15,000 | NA | 6851.713 | 28639.4272 | 124.6441 | 740.7177 | 167.2897 | 423.2744 | 3679.7011 | 14909.4089 | 4353.1759 | 98.5232 | 0 | 0 | 0 | 5581.7947 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 398 | Vierra 115 kV Reinforcement Phase 2 |  |  | Lathrop, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-02-06 | 14 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.355 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805478 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 12 | 61 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 4 | 2025-07-08 | 2014-05-01 | 2026-11-17 | Prioritization | FALSE | $10,000 ¦ $15,000 | NA | 0 | 9942.3422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 399 | SEMITROPIC-MIDWAY: Recond 115 KV Line |  |  | Kern | Reconductor 14.2 miles of the Semitropic-Midway No. 1 115kV Line. The project expects to improve service reliability in core operations by reconductoring the Semitropic-Midway No. 1 115kV Line that will improve system performance and reliability, which will reduce outages. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-08 | 52 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.2701 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 14 | NA | NA | 5767160 | T.0000143 | SEMITROPIC-MIDWAY 115KV LINE RECONDUCTOR | 5 | 61 | 5747849 | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-10-01 | 2016-12-01 | 2021-03-29 | Clearances | FALSE | $15,000 ¦ $20,000 | NA | 5128.2809 | 5128.2809 | 190.6534 | 1835.3226 | 2119.86 | -18.7167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5128.2809 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 4932.0462 | -17.8929 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Non-Wires - System DER Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $125 Mil - $150 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 400 | Cottonwood:Inst 115kV Bus Sectionalizing |  |  | Cottonwood CDP, Shasta | Replace Cottonwood Transformer Banks 1 & 4, replacement of six circuit breakers, addition of bus parallel circuit breaker, and upgrade the aging protection and control equipment at the Cottonwood substation. | Substation - Bus Arrangement | New | T.0004659 | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 26.1945 | NA | 115 kV | 1002 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5786464 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 61 | NA | 2018 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-10-17 | 2022-12-31 | 2026-09-11 | Prioritization | FALSE | $8,500 ¦ $10,500 | NA | 260.3179 | 6615.7065 | 38.7148 | 40.6557 | 30.2892 | 46.9034 | 92.9801 | 1046.3914 | 7545.1728 | 0 | 0 | 0 | 0 | 249.5432 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 401 | LOCKEFORD SUBSTATION NEW 230 KV BAY |  |  | Lockeford CDP, San Joaquin | The Lockeford-Lodi Area 230 kV Development Project will loop the Brighton – Bellota 230 kV Line into Lockeford 230 kV Substation to bring a new 230 kV source into the area. A new 230 kV double circuit tower line will be constructed to connect the existing Lockeford 230 kV Substation to a new 230 kV switching to be constructed near the City of Lodi’s existing Industrial 60 kV Subsation. To accommodate the Brighton – Bellota loop-in and the new DCTL, the Lockeford 230 kV Bus will be upgraded to a four-bay breaker-and-a-half (BAAH) bus configuration. The City of Lodi will be constructing a new 230/60 kV Substation which will be connected to the new 230 kV switching station. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-01 | NA | Steady State Power Flow System Analysis | Non-Wires - Large Scale Energy Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 10.2719 | NA | 230 kV | 45 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5771389 | T.0000155 | Lockeford - Lodi Area 230 kV Development | 5 | 61 | 5752080 | 2013 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | PEA Deemed Complete | TBD | TBD | NA | CPUC | NA | CPCN: A.23-09-001 | 2023-09-01 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2029-03-22 | 2017-03-01 | 2029-12-10 | Prioritization | FALSE | $80,000 ¦ $105,000 | TBD | 305.8312 | 34479.6126 | 102.037 | 51.4535 | 84.5839 | 39.954 | 20.2694 | 74.5577 | 1097.1853 | 10239.8045 | 11584.4272 | 9223.2692 | 0 | 302.4184 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 402 | FIREBAUGH: Install 70 kV SCADA Switch |  |  | Fresno | The project expects to improve service reliability in core operations by replacing a 70 kV switch with a SCADA-operable switch at Firebaugh Substation. This project will improve reliability for over 3,300 electric customers served from Firebaugh Substation by providing remote restoration capabilities and reducing outage duration during contingencies. | Substation - Switch | New | NA | Reliability | Substation Reliability | NA | 2024-02-01 | NA | NA | Wires - System Configuration Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.44475 | NA | 70 kV | 34 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5767767 | T.0000586 | ORO LOMA MENDOTA CONV.-MENDOTA SUB | 2 | 61 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-12-26 | 2019-01-28 | 2019-03-23 | NA | FALSE | 2261 | NA | 2364.852 | 2364.852 | 563.1949 | 1.1802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2364.852 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 2346.3062 | -50.3907 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 403 | MORAGA SUB: 115KV TERMINAL UPGRADES |  |  | Orinda, Contra Costa | The project proposes to replace the structures, conductors, and hardware in the same overhead alignment between Moraga Substation and California State Highway 13 and also to relocate the line sections between Highway 13, and Oakland X underground (UG) within city streets. By replacing the aging facilities PG&E can improve wildfire safety and public safety and increase path capacity into the Oakland area. The project scope of work includes: • Removal of 78 existing lattice steel transmission towers • Removal of approximately 20 circuit miles of conductor • Installation of approximately 60 new lattice steel transmission towers • Installation of approximately 11 miles of Aluminum Conductor Composite Reinforced (ACCR) conductor • Installation of three 115kV underground duct banks with 115kV transmission cables totaling approximately six miles • Installation of new 115kV circuit breakers and air switches at Moraga Substation • Upgrade the 115kV bus at Oakland X Substation to complement the higher capacity ACCR conductor | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Reliability | NA | 2024-03-06 | 61 | NA | Wires - New T-Line Alternative | $250 Mil – $300 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 15.8714 | NA | 115 kV | Not Available | 5. Compliance/Commitments With Strong Safety Link | 55 | RBPPF - TBD | Yes | 5789522 | T.0000349 | Moraga-Oakland #1-#4 Rebuild | 12 | 61 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-08-01 | 2025-07-31 | 2028-11-29 | Prioritization | FALSE | 212000 | NA | 142.628 | 11737.3828 | 0 | 0.562 | 33.6732 | 59.3722 | 39.1305 | 206.5651 | 438.1288 | 271.5588 | 263.7109 | 9150.3908 | 1365.5429 | 132.7379 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 404 | OAKLAND X SUB: 115kV BUS UPGRADE |  |  | Oakland, Alameda | The project proposes to replace the structures, conductors, and hardware in the same overhead alignment between Moraga Substation and California State Highway 13 and also to relocate the line sections between Highway 13, and Oakland X underground (UG) within city streets. By replacing the aging facilities PG&E can improve wildfire safety and public safety and increase path capacity into the Oakland area. The project scope of work includes: • Removal of 78 existing lattice steel transmission towers • Removal of approximately 20 circuit miles of conductor • Installation of approximately 60 new lattice steel transmission towers • Installation of approximately 11 miles of Aluminum Conductor Composite Reinforced (ACCR) conductor • Installation of three 115kV underground duct banks with 115kV transmission cables totaling approximately six miles • Installation of new 115kV circuit breakers and air switches at Moraga Substation • Upgrade the 115kV bus at Oakland X Substation to complement the higher capacity ACCR conductor | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Reliability | NA | 2024-03-14 | 32 | NA | Wires - New T-Line Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 1.1294 | NA | 115 kV | Not Available | 5. Compliance/Commitments With Strong Safety Link | 55 | RBPPF - TBD | Yes | 5789521 | T.0000349 | Moraga-Oakland #1-#4 Rebuild | 12 | 61 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Planning | 5 | 2027-03-17 | 2025-07-31 | 2028-04-10 | Prioritization | FALSE | 212000 | NA | 327.3938 | 12410.7392 | 0 | 17.672 | 78.6894 | 104.2516 | 105.8178 | 164.3882 | 411.0862 | 275.9762 | 292.4242 | 10133.1982 | 1196.1082 | 306.4308 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 405 | MONTEREY_Install Bus & Breakers_P2 |  |  | Monterey, Monterey | The project scope of work includes following:60 kV bus•Remove existing 60kV bus in association with the bank replacement project •Install 60kV line breaker CB12, associated switch SW11, SW13 and bypass switch SW15. •Install 60kV line breaker CB32, associated switch SW31, SW33 and bypass switch SW35.•Install 3 – 1 phase 60kV line Potential Transformers (PTs) for 60kV Del Monte – Monterey line outside the disconnect SW13 towards the line side.•Install 3 – 1 phase 60kV line Potential Transformers (PTs) for 60kV Viejo – Monterey line outside the disconnect SW33 towards the line side.•Install one (1) 60kV bus sectionalizing breaker CB22, associated switch SW21, SW23, and bypass switch SW25.•Install one C phase bus PT in 60kV bus section D.•Install one C phase bus PT in 60kV bus section E.•Install the bus support insulators as needed for longer spans.•Install 2 x 1131 kcmil AL or equivalent conductor for 60kV incoming line, bus and 60kV station equipment connections. If required, one span of 3” AL SPS pipe will be installed from transformer circuit switcher to 60kV bus. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | Load Growth | Bus Upgrade | NA | 2024-03-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.29142 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799060 | T.0000676 | MONTEREY Install 3-D-Banks & 60KV T BRKR | 3 | 61 | NA | 2020 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-20 | 2020-12-15 | 2025-07-23 | Prioritization | TRUE | 20200 | NA | 122.4378 | 4774.845 | 0 | 0 | 0 | 84.4498 | 22.015 | 1519.7174 | 3131.6469 | 2.6707 | 0 | 0 | 0 | 106.4648 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $20 Mil - $30 Mil
| 406 | STAGG: Install Special Protection Scheme |  |  | Stockton, San Joaquin | The project scope of work involves the following•Install a new 4.2 miles of 60 kV line between Stagg and Hammer substations •Install a new 60 kV circuit breaker at Stagg Substation•Upgrade the Hammer 60 kV bus to a six element ring bus•Upgrade associated substation equipment at Stagg and Hammer substations to accommodate the new 60 kV line, if necessary. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | Reliability | Special Protection Scheme | NERC TPL Standards | 2024-03-01 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.5909 | NA | 230 ¦ 60 kV | 102 | 8. Compliance/Commitments With Low Safety Risk | 7 | NA | NA | 5768693 | T.0000016 | Stagg-Hammer 60kV Line Install SPS | 4 | 61 | 5746743 | 2012 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-11 | 2021-04-21 | 2020-11-16 | NA | FALSE | 2056 | NA | 1811.659 | 1811.659 | 698.8464 | 583.3364 | 32.8534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1811.659 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1779.4262 | 32.8534 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 407 | EMBARCADERO-POTRERO: Upgd SF RAS A at SF |  |  | San Francisco, San Francisco | The project will involve the construction of a new 230 kV underground transmission line between Embarcadero and Potrero Power Plant (P.P.) Substations, construction of a new 230 kV switchyard at Potrero, the installation of new 230/115 kV transformers at Potrero, and the interconnection of the Project into the Embarcadero 230 kV bus and Potrero P.P. 115 kV buses. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | T.0003671 | Reliability | Special Protection Scheme | NERC TPL Standards | 2024-03-14 | NA | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.55624 | NA | 230 kV | 564 | 8. Compliance/Commitments With Low Safety Risk | 9 | NA | NA | 5778434 | T.0003672 | NEW 230 KV SWITCHYARD AT POTRERO | 3 | 61 | NA | 2007 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2014-09-02 | 2015-12-31 | 2021-12-08 | Workforce | FALSE | $130,000 ¦ $150,000 | NA | 2014.9352 | 2014.9352 | 483.067 | 647.7047 | 341.757 | 10.3397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014.9352 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 2006.0985 | 10.3397 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 408 | EMBARCADERO-POTRERO: Upgd SF RAS B at VG |  |  | San Francisco, San Francisco | The project will involve the construction of a new 230 kV underground transmission line between Embarcadero and Potrero Power Plant (P.P.) Substations, construction of a new 230 kV switchyard at Potrero, the installation of new 230/115 kV transformers at Potrero, and the interconnection of the Project into the Embarcadero 230 kV bus and Potrero P.P. 115 kV buses. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | T.0003671 | Reliability | Special Protection Scheme | NERC TPL Standards | 2024-03-14 | 23 | Steady State Power Flow System Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.55624 | NA | 230 kV | 564 | 8. Compliance/Commitments With Low Safety Risk | 9 | NA | NA | 5778325 | T.0003672 | NEW 230 KV SWITCHYARD AT POTRERO | 3 | 61 | NA | 2007 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-07-25 | 2015-12-31 | 2021-12-08 | Workforce | FALSE | $130,000 ¦ $150,000 | NA | 2126.7081 | 2126.7081 | 531.4766 | 413.9869 | 321.0433 | 93.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2126.7081 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 2033.3421 | 93.709 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 409 | ORO LOMA: Install BK 3 |  |  | Fresno | This project proposes to install a new 115 kilovolt (kV) BAAH bus at Oro Loma Substation. Completion of this project would increase reliability for the electric customers in Merced County and modernize the Oro Loma 115 kV bus for future expansion of the substation. This work is being done in conjunction with a Modular Protection Automation and Control (MPAC) installation project which will install a new MPAC building for the 115 kV protection and control equipment. | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000891 ¦ T.0003408 ¦ T.0000563 | Load Growth | Bus Upgrade | NA | 2024-02-16 | NA | NA | Wires - Bus Upgrade Alternative | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.8637 | NA | 115 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5769442 | T.0001473 | ORO LOMA BANK NO. 3 INSTALL PHASE | 1 | 61 | NA | 2011 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-07-16 | 2019-07-10 | 2019-11-13 | NA | FALSE | 5792 | NA | 7373.1658 | 7373.1658 | 3182.1738 | 530.77 | 19.7832 | 0.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7373.1658 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 5823.8372 | 451.4222 | 16.8146 | 0.46496 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 410 | Calflax: Add Bank 2 - Ring Bus |  |  | Fresno | This project proposes to install a new 70/12 kV 30 MVA transformer bank at Calflax Substation in order to prevent projected substantial overloads on Coalinga #2 Bank 1. To support the additional transformer bank at Calflax the existing 70 kV transmission tap that serves Calflax Bank 1 will be reconfigured into a four-element ring bus. In addition to the new transformer bank at Calflax Substation one new 12 kV circuit breaker and associated distribution work will be installed to serve the proposed additional 10 MW Tesla EV charging infrastructure load at Harris Ranch. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Load Growth | Bus Upgrade | NA | 2024-03-01 | NA | NA | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.68286 | NA | 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5795019 | T.0003879 | Calflax Substation Bank 2 Installation | 3 | 61 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-11-15 | 2023-02-08 | 2024-01-08 | Prioritization | TRUE | 19400 | NA | 6906.632 | 8213.9795 | 0 | 0 | 2102.5042 | 2649.9927 | 1963.3726 | 1061.7259 | 426.9073 | 0 | 0 | 0 | 0 | 6715.8695 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 6807.2775 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 411 | Panoche Sub: Install 230 kV breaker |  |  | Fresno | This project proposes to install one new 230 kV breaker, one 230/21 kV, 75 MVA three-phase transformer, one 21/12 kV, 30 MVA autotransformer, one new 2000 Ampere-rated 21 kV bus 1/bus 2 structure with six breaker bays, three feeder breakers and one bus tie breaker, three new 21 kV distribution feeder outlets, and three new 21 kV underground distribution circuits from the substation to the customer site. This project will allow 45 MW of new Electric Vehicle (EV) charging load from Tesla and future load from other EV customers to connect to the PG&E system. Transmission Substation Work (MWC 61): Note that Panoche 230 kV has ten 230 kV lines and three substation transformers. Per Standard 073131, if this substation were rebuilt, the desired 230 kV bus configuration would be Breaker-and-a-Half (BAAH). Conversion of Panoche Substation to BAAH is not expected at this time and an extension of the existing Bus 1/Bus 2 arrangement is assumed. • Extend existing 230 kV Bus 1/Bus 2 to accommodate one 230 kV double-bus bay • Install one 230 kV breaker in new bay • Extend 230 kV line south from new breaker in 230 kV yard to distribution substation portion of yard | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Load Growth | Bus Upgrade | NA | 2024-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5800044 | T.0008070 | Panoche Sub: Install 12 kV bank | 1 | 61 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-11-01 | NA | 2026-05-21 | NA | FALSE | NA | NA | 349.8571 | 5635.5175 | 0 | 0 | 0 | 50.4276 | 195.4706 | 3175.9167 | 971.196 | 995.801 | 0 | 0 | 0 | 245.8981 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 412 | Wheeler Ridge Sub: Install BAAH bay |  |  | Kern | This project proposes to install one new 230 kV breaker-and-a-half (BAAH) bay with two new 230 kV breakers, one 230/21 kV, 75 MVA three-phase transformer, one 21/12 kV 30 MVA autotransformer, one 2,000 ampere (A) rated 21 kV bus 1/bus 2 structure with six breaker bays, three 1,200 A 21 kV feeder breakers, one 2,000 A 21 kV bus tie breaker, three 21 kV distribution feeder outlets, and three new 21 kV underground distribution circuits from the substation to the customer site.This project will allow 50 MW of new electric vehicle (EV) charging load from Tesla Motors Company (Tesla) and future load from other EV customers to connect to the PG&E system. Transmission Substation Work (MWC 61): • Install one 230 kV BAAH bay • Install two 230 kV breakers in new BAAH bay • Extend 230 kV line north from new BAAH bay in 230 kV yard to location of new 230/21 kV transformer • Potential rearrangement of Wheeler Ridge-Adobe Switching Station 115 kV and Wheeler Ridge-San Bernard 70 kV lines within substation | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Load Growth | Bus Upgrade | NA | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5800046 | T.0008068 | Wheeler Ridge Sub: Install 12 kV bank | 2 | 61 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-06-04 | NA | 2028-11-30 | NA | FALSE | NA | NA | 69.156 | 6729.0417 | 0 | 0 | 0 | 55.1259 | 13.7799 | 1771.2306 | 2355.9598 | 909.0718 | 0 | 0 | 0 | 68.9059 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 413 | Banta - Replace Bank 1 - Sub |  |  | San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NERC TPL Standards | 2024-02-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.54319 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798130 | T.0006962 | Banta: Repl 60/12kV Bank 1 | 6 | 61 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-07-17 | 2024-12-31 | 2027-01-27 | Prioritization | FALSE | 17500 | NA | 91.6893 | 7085.4866 | 0 | 0 | 0 | 0 | 72.138 | 368.9182 | 2000 | 8000 | 7000 | 500 | 0 | 72.138 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 414 | GREEN VALLEY: Upgd 115 kV BUS BAAH PH 2 |  |  | Interlaken CDP, Santa Cruz | This project will replace the existing 115 kV bus with five bays of breaker-and-a-half (BAAH) configuration. The new 115 kV BAAH bus will be located in the existing substation yard, which will require sequential construction of the new BAAH bays and removal of sections of the existing 115 kV bus. The protection and controls of the new equipment will be moved to the new Modular Protection Automation and Control (MPAC) building | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-02-14 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | 428 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5771880 | T.0000638 | Green Valley Substation Upgrade | 6 | 61 | NA | 2014 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-23 | 2019-12-31 | 2019-12-20 | NA | FALSE | 47000 | NA | 4379.949 | 4379.949 | 3645.7354 | 452.2727 | 28.0383 | 3.9203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4379.949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 3204.3895 | 374.2009 | 22.9785 | 3.2128 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 415 | GREEN VALLEY: Upgd 115 kV BUS BAAH PH 3 |  |  | Interlaken CDP, Santa Cruz | This project will replace the existing 115 kV bus with five bays of breaker-and-a-half (BAAH) configuration. The new 115 kV BAAH bus will be located in the existing substation yard, which will require sequential construction of the new BAAH bays and removal of sections of the existing 115 kV bus. The protection and controls of the new equipment will be moved to the new Modular Protection Automation and Control (MPAC) building | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-02-14 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | 428 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5771881 | T.0000638 | Green Valley Substation Upgrade | 6 | 61 | NA | 2014 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-12-20 | 2019-12-31 | 2020-08-20 | Prioritization | TRUE | 47000 | NA | 5549.6588 | 5557.0549 | 159.5874 | 3743.6492 | 83.8647 | 994.8871 | 549.9734 | 21.7731 | 0 | 0 | 0 | 0 | 0 | 5535.2818 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 3782.9545 | 81.1695 | 962.9159 | 532.2997 | 19.4427 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 416 | Gates Los Banos Midway Path Rating Upggrade |  |  | Buttonwillow CDP, Kern | Upgrade substation terminals at Gates, Los Banos, and Midway for 500 kV Path 15 and Midway for 500 kV Path 26 to increase 500 kV Path ratings | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-15 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805120 | T.0009205 | Gates Los Banos Midway Path Rating Upgrade | 3 | 61 | NA | 2023 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-04-01 | 2024-05-31 | 2024-05-16 | NA | FALSE | 2100 | NA | 215.3495 | 1258.6773 | 0 | 0 | 0 | 0 | 128.5406 | 1130.1367 | 0 | 0 | 0 | 0 | 0 | 128.5406 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements.
| 417 | Evergreen Sub: Install 115kV Phase 2 |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000147 | Reliability | Bus Upgrade | NA | 2024-02-02 | 33 | NA | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.3776 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805220 | T.0001685 | Evergreen Substation Upgrade | 7 | 61 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2023-02-01 | 2018-12-20 | 2027-03-05 | Prioritization | FALSE | 27200 | NA | 5612.9391 | 8286.6416 | 0 | 0 | 0 | 0 | 5680.6034 | 283.9509 | 0 | 0 | 0 | 0 | 0 | 5680.6034 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 418 | EVERGREEN: Upgrade 115 KV Bus |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000147 | Reliability | Bus Upgrade | NA | 2024-02-02 | 33 | NA | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.3776 | NA | 115 kV | 179 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5770124 | T.0001685 | Evergreen Substation Upgrade | 7 | 61 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-06-25 | 2018-12-20 | 2023-06-02 | Prioritization | FALSE | 27200 | NA | 31314.9824 | 31314.9824 | 6301.5532 | 6637.5381 | 8846.6389 | 9642.4386 | -2225.7581 | -78.0336 | 0 | 0 | 0 | 0 | 0 | 31393.016 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 28589.8019 | -21.0513 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 419 | MARKHAM: Upgrade Relay |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Protection Relay | Upgrade/Retrofit | T.0000147 | Reliability | Substation Reliability | NA | 2024-02-02 | 27 | NA | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.3776 | NA | 115 kV | 579 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5776840 | T.0001685 | Evergreen Substation Upgrade | 7 | 61 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2023-02-21 | 2018-12-20 | 2027-03-05 | Prioritization | TRUE | 27200 | NA | 887.5008 | 1132.2734 | 51.5927 | 129.9122 | 177.1129 | 144.4782 | 324.2052 | 62.1002 | 0 | 0 | 0 | 0 | 35.8194 | 886.2669 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 420 | SAN JOSE B: Upgrade Relay |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Protection Relay | Upgrade/Retrofit | T.0000147 | Reliability | Substation Reliability | NA | 2024-02-02 | NA | NA | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.1017 | NA | 115 kV | 579 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5770127 | T.0001685 | Evergreen Substation Upgrade | 7 | 61 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2021-09-01 | 2018-12-20 | 2027-03-05 | Prioritization | TRUE | 27200 | NA | 1426.2323 | 2131.8441 | 414.6016 | 115.0255 | 406.3647 | 235.0162 | 143.3442 | 118.4063 | 0 | 0 | 0 | 0 | 26.7725 | 1406.2416 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 421 | STONE: Upgrade Relay |  |  | San Jose, Santa Clara | Upgrade the 115kV transmission bus configuration and the 115kV and 60kV protection and control systems at Evergreen Substation to improve electric system resiliency: • Install new bus-sectionalizing and bus-parallel circuit breakers on the 115kV buses • Install a new 115kV circuit breaker at Evergreen and connect the 115kV line to Stone into the Evergreen 115V buses | Substation - Protection Relay | Upgrade/Retrofit | T.0000147 | Reliability | Substation Reliability | NA | 2024-02-02 | NA | NA | Wires - Bus Upgrade Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.68753 | NA | 115 kV | 579 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5770126 | T.0001685 | Evergreen Substation Upgrade | 7 | 61 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2021-10-01 | 2018-12-20 | 2027-03-05 | Prioritization | TRUE | 27200 | NA | 3459.6994 | 4343.0337 | 395.2938 | 276.0962 | 1231.0386 | 628.9345 | 647.9566 | 292.9877 | 0 | 0 | 0 | 0 | 43.5364 | 3391.5211 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 422 | MONTA VISTA: Upgrade 230 kV Bus - Ph 1 |  |  | Cupertino, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-11 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8314 | NA | 230 kV | 472 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5756027 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 61 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-06-18 | 2016-05-01 | 2019-02-19 | Prioritization | FALSE | $10,000 ¦ $15,000 | NA | 14112.5022 | 14112.5022 | 2565.2567 | 201.8721 | 35.9463 | 4.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14112.5022 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 13850.7868 | 201.5783 | 35.8937 | 4.4565 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 423 | MONTA VISTA: Upgrade 230 kV Bus Phase 2 |  |  | Cupertino, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-11 | 19 | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8314 | NA | 230 kV | 472 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5772060 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 61 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2021-08-17 | 2016-05-01 | 2025-09-26 | Prioritization | TRUE | $10,000 ¦ $15,000 | NA | 20917.7437 | 27123.4088 | 186.9005 | 2275.5176 | 7761.9947 | 6605.4205 | 2106.1482 | 5575.7042 | 1552.2601 | 55.5918 | 0 | 0 | 0 | 19914.8977 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 424 | KERN PP: Upgrade 230 kV Bus |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000220 ¦ T.0003350 ¦ T.0000980 | Reliability | Bus Upgrade | NERC TPL Standards | 2024-04-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | 37.7504 | NA | 230 kV | 764 | Not Available | NA | NA | NA | 5767360 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 61 | 5748540 | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-05-01 | 2013-05-01 | 2019-03-07 | Prioritization | FALSE | $32,000 ¦ $44,000 | NA | 36997.1444 | 36997.1444 | 2407.7809 | 16.6589 | 5.6904 | 7.6009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36997.1444 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 36386.248 | 16.5464 | 5.5939 | 7.472 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 425 | KERN: Repl 230 KV Bus Phase 2 |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000220 ¦ T.0003350 ¦ T.0000980 | Reliability | Bus Upgrade | NERC TPL Standards | 2024-04-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | 37.7504 | NA | 230 kV | 764 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5775225 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 61 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-02 | 2013-05-01 | 2020-02-10 | Prioritization | FALSE | $32,000 ¦ $44,000 | NA | 4198.2607 | 4198.2607 | 2455.8824 | 1708.5059 | 33.6794 | -0.2235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4198.2607 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 4164.8049 | 33.6794 | -0.2235 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 426 | KERN: Repl 230 KV Bus Phase 3 |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000220 ¦ T.0003350 ¦ T.0000980 | Reliability | Bus Upgrade | NERC TPL Standards | 2024-04-12 | 69 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | 37.7504 | NA | 230 kV | 764 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5775226 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 61 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-06-01 | 2013-05-01 | 2021-03-01 | Prioritization | FALSE | $32,000 ¦ $44,000 | NA | 4408.9848 | 4408.9848 | 1.0282 | 2183.4054 | 2190.0309 | 34.5204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4408.9848 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 4374.4644 | 34.5204 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 427 | MIDWAY: Install Fiber |  |  | Buttonwillow CDP, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Other Equipment | Upgrade/Retrofit | T.0000220 ¦ T.0003350 ¦ T.0000980 | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-15 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 94.5324 | NA | 230 kV | 764 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5778945 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 61 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-08 | 2013-05-01 | 2020-02-05 | Prioritization | FALSE | $32,000 ¦ $44,000 | NA | 1078.42 | 1078.42 | 766.9113 | 194.9728 | 0.9014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.42 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1077.5186 | 0.90139 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 428 | Templeton Sub-Install Reverse Pow.Relays |  |  | San Luis Obispo | Project Description This project will construct a new 230/70/21 kV substation approximately five miles east of the existing Paso Robles Substation to provide robust system reinforcement and system reliability to customers in the Paso Robles area. Key project elements for the scope include: Competitive Scope (230 kV): Awarded to NEET West (PG&E Expended to Date $2.5M) • Construct 230 kV portion of Estrella Substation, including two new 230/115 kV transformers and three 230 kV line terminations. • Acquire land rights and permits for substation. Non-competitive Scope (70/21 kV): ($176.9M) • Construct 70 kV and 21 kV portions of the Estrella Substation. • Procure and install 70/21 kV transformer at Estrella Substation. • Construct 230 kV and 70 kV transmission lines to connect the Morro Bay-Gates 230 kV and San Miguel-Paso Robles 70 kV lines via Estrella Substation. • Reconductor the southernmost portion of the San Miguel-Paso Robles 70 kV line between Estrella and Paso Robles Substations. • Acquire land rights and permits for transmission lines connecting to the substation. • Construct 21 kV distribution feeders to serve Paso Robles customers. | Substation - Protection Relay | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-19 | NA | Steady State Power Flow System Analysis | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.6839 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805698 | T.0000154 | Estrella 230 kV Transmission Substation | 19 | 61 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2014 | TRUE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | CEQA Final Published | 2023-03-31 | EIR | NA | CPUC | NA | PTC: A.17-01-023 | 2017-01-25 | Filed and Under Administrative Review | TBD | Engineering less than 50% complete | 5 | 2027-07-26 | 2019-05-01 | 2027-08-13 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 30.6673 | 1112.8784 | 0 | 0 | 0 | 0 | 29.9809 | 2.5529 | 0 | 0 | 0 | 0 | 0 | 29.9809 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ NextEra | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 429 | Los Banos: Replace 230kV CBs 212 & 222 |  |  | Merced | Based on 2022 Short Circuit Analysis results and study plan , Los Banos 230 kV CBs 212, 222, 252, and 262 will be overstressed in 2030. Planning analyses show that the Los Banos 230 kV CBs 212, 222, 252 and 262 are projected to overload in 2030. Manning 500 kV Project has been added to 2023 TPP project list that contributes overstressed to Los Banos 230 kV CBs. • Replace 230 kV CBs 212, 222 in place with 3,000 Amps, 63 kA CBs, new SMP Relays. Foundations/structures may need to be replaced. • Replace 230 kV CBs 252, 262 with two (2) new BAAH Bays in the new BAAH bus section to meet the ultimate plan. New CBs will be 3,000 Amps, 63 kA CBs. Need T line relocations into new BAAH positions. | Substation - Circuit Breaker | Upgrade/Retrofit | TBD | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-06 | 31 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 53.2803 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806918 | T.0009550 | Los Banos Replace 230kV CBs 212 and 222 | 1 | 61 | EX113236 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-07-01 | 2032-12-31 | 2028-04-01 | NA | FALSE | 66000 | NA | 5.5446 | 5.5446 | 0 | 0 | 0 | 0 | 0 | 5.5446 | 1500 | 9000 | 10000 | 9000 | 4000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 430 | Gates: 230kV Bus SecD&E Redundant Relay |  |  | Fresno | Install Gates Section D & E 230 KV Redundant Bus Differential Relay to resolve P5 issues. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807128 | T.0009583 | Gates Section D & E 230 KV Redundant Bus Differential Relay | 1 | 61 | EX113245 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-10-01 | NA | 2026-06-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 1500 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 431 | Humboldt: 115kV Redundant Bus Diff Rly |  |  | Humboldt | Install Humboldt 115 kV Redundant Bus Differential Relay to resolve P5 issues. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.569 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807201 | T.0009597 | Humboldt_115kV Redundant Bus Diff Rly | 1 | 61 | EX113248 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-03-01 | NA | 2025-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 432 | Lakeville: 230kV Redundant Bus Diff Rly |  |  | Sonoma | Install Lakeville 230 kV Redundant Bus Differential Relay to resolve P5 issues. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-11 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 14.7021 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807202 | T.0009598 | Lakeville_230kV Redundant Bus Diff Rly | 1 | 61 | EX113244 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-06-01 | NA | 2026-06-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4300 | 1200 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 433 | McCall: 115kV Bus#1&#2 Redundant Relay |  |  | Fresno | Install MCCALL 115KV BAAH BUS #1&2 redundant relay to resolve P5 issues. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 16.2494 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807127 | T.0009584 | McCall_115kV Bus 1- 2 Redundant Relay | 1 | 61 | Tx000749 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-03-01 | NA | 2026-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 5320 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 434 | Mesa 230kV BAAH Bus1 Bus2 Redundant Rly |  |  | Nipomo CDP, San Luis Obispo | Install Mesa 230 kV BAAH Bus #1 and #2 Redundant Relay to resolve P5 issues. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 10.5414 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807203 | T.0009582 | Tyler 60 kV Shunt Capacitor | 2 | 61 | EX113249 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-03-01 | NA | 2025-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 435 | Los Esteros:115kV Bus1&2 Redundant Relay |  |  | San Jose, Santa Clara | Install redundant Bus Differential Relays for 115kV Bus 1 & 2 at Los Esteros substation. Los Esteros 115kV fault duty is about 52 kA. Existing one level of bus protection relies on remote tripping for a single contingency of bus differential protection failure to trip for a bus fault. Remote tripping is not high speed, typically each takes 0.3 to 0.8 second. Stability issues may arise as a result of the slow fault clearing and subsequent compromise on transmission network connectivity. Los Esteros 115kV bus interconnects with Calpine Generation at 115kV and it is not desirable to rely on Calpine relays to clear PG&E bus faults. Besides, outage can result in loss of 293MW generation import. With only one level of bus differential protection, there is a need to force open all the breakers on that bus section when bus differential protection is cut-out (for testing etc.). Under this condition, fault on any circuit connected to the remaining bus section could disconnect the other circuit on the same bay and fault on the remaining bus will result in station loss. This can be an operational concern. Los Esteros substation is a critical facility serving Silicon Valley. Considering Reliability and operating flexibility and to address the operational concern, the California Independent System Operator(CAISO) is recommending approval of adding 115kV low impedance Bus Differential Set B relays for Bus 1 & 2 at Los Esteros substation. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807123 | T.0009560 | Los Esteros_115kV Bus1-2 Redundant Relay | 1 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-10-01 | NA | 2026-06-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3750 | 1050 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 436 | Kasson SPS |  |  | San Joaquin | The project scope is to install a SPS that trips Kasson CBs 12, 22, 32, and 42 following a Kasson 115 kV Bus outage. This will eliminate overloads on the Kasson - Louise 60 kV Line, Manteca - Louise 60 kV Line, and Manteca 115/60 kV Transformer. | Other - Remedial Action Scheme/Special Protection Scheme | New | TBD | CAISO Transmission Planning Standards | Special Protection Scheme | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.1988 | NA | 115 ¦ 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5756036 | TBD | TBD | TBD | 61 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-01 | NA | 2026-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 1000 | 100 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 437 | Table Mtn 230 kV Redundant Relay |  |  | Butte | This project proposes to improve the electric transmission grid reliability and operational flexibility by installing redundant Bus Differential relays on the 230kV Bus at Table Mountain substation. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807179 | T.0009575 | Table Mtn 230 kV Redundant Relay | 1 | 61 | EX113250 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-10-01 | NA | 2026-06-01 | NA | FALSE | NA | NA | 0.3434 | 0.3434 | 0 | 0 | 0 | 0 | 0 | 0.004 | 3000 | 1500 | 0 | 0 | 0 | 0.3394 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 438 | Kasson: Upgrade 115kV bus diff protect |  |  | San Joaquin | This project proposes to install a redundant set of 115kV bus protection and replace the 115kV CB 132 to resolve the thermal overloading on three (3) 60kV and two (2) 115kV lines in the near term under the circumstances of the existing bus protection failure. • Replace the CB 132 and associated switches. Foundations/ structures might need to be replaced as well. • Add a “set B” bus overcurrent relay and connect the 115kV line CBs CT to the new relay. | Substation - Protection Relay | New | TBD | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.1988 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806846 | T.0009533 | Kasson 115 kV Redundant Bus Differential Relay | 1 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-03-01 | NA | 2025-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 439 | BIRDS LANDING REMOTE END |  |  | Solano | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Substation - Protection Relay | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-07 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 3.4512 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5549722 | T.0008048 | Contra Costa PP Line Swaps | 9 | 61 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-11 | 2025-05-01 | 2025-03-31 | NA | TRUE | $5,000 ¦ $10,000 | NA | 192.8359 | 1762.8776 | 0 | 0 | 0 | 8.8244 | 145.5417 | 748.2235 | 843.8531 | 0 | 0 | 0 | 0 | 154.3661 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 154.366 | 62.6358 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 440 | LONE TREE REMOTE END |  |  | Antioch, Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Substation - Protection Relay | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-08 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | NA | 2.3791 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5549723 | T.0008048 | Contra Costa PP Line Swaps | 9 | 61 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-11 | 2025-05-01 | 2025-03-31 | NA | TRUE | $5,000 ¦ $10,000 | NA | 203.7236 | 1855.9138 | 0 | 0 | 0 | 13.938 | 174.3722 | 1088.4832 | 562.6854 | 0 | 0 | 0 | 0 | 188.3102 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 188.3102 | 18.9706 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 441 | El Capitan 115kv Protection Upgrade |  |  | Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Protection Relay | Upgrade/Retrofit | T.0001381 ¦ T.0002231 | CAISO Transmission Planning Standards | Substation Reliability | NERC TPL Standards | 2024-03-01 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.954 | NA | 115 kV | 462 | 5. Compliance/Commitments With Strong Safety Link | 11 | RBPPF - TBD | Yes | 5787806 | T.0004116 | WILSON: 115 kV ARP - BAAH | 6 | 61 | NA | 2012 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-02-17 | 2022-08-12 | 2025-04-03 | Prioritization | TRUE | 66700 | NA | 39.3382 | 1210.2564 | 3.3502 | 35.3017 | 0.6863 | 0 | 0 | 108.3762 | 1062.542 | 0 | 0 | 0 | 0 | 39.3382 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 442 | Moraga U: RAS Project |  |  | Orinda, Contra Costa | Modify the existing San Leandro U Substation, which will include all the necessary requirements, including time of day and seasonal setting changes, iterative tripping, and ability to accommodate bypass scenarios. The main driver for this RAS is the ISO planning standard that does not allow for load tripping in Greater Bay Area as a high population density area. The New RAS will monitor the outages and flows on five critical lines in Moraga-Oakland J area and take corrective actions to resolve any overloads on these lines without dropping the load. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | CAISO Transmission Planning Standards | Special Protection Scheme | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.8714 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5791839 | T.0004580 | San Leandro U: Ras Project | 4 | 61 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-12-01 | 2022-09-30 | 2028-10-26 | Prioritization | TRUE | 4000 | NA | 620.6289 | 4516.881 | 0 | 0 | 74.2202 | 127.1494 | 410.4164 | 70.6983 | 0 | 0 | 0 | 0 | 0 | 611.7859 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 443 | Oakland J U: RAS Project |  |  | Oakland, Alameda | Modify the existing San Leandro U Substation, which will include all the necessary requirements, including time of day and seasonal setting changes, iterative tripping, and ability to accommodate bypass scenarios. The main driver for this RAS is the ISO planning standard that does not allow for load tripping in Greater Bay Area as a high population density area. The New RAS will monitor the outages and flows on five critical lines in Moraga-Oakland J area and take corrective actions to resolve any overloads on these lines without dropping the load. | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | CAISO Transmission Planning Standards | Special Protection Scheme | NERC TPL Standards | 2024-02-28 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.5059 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5791857 | T.0004580 | San Leandro U: Ras Project | 4 | 61 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-03-15 | 2022-09-30 | 2027-07-01 | Prioritization | TRUE | 4000 | NA | 768.3178 | 3508.4321 | 0 | 0 | 120.2907 | 142.5106 | 373.0508 | 181.392 | 0 | 0 | 0 | 0 | 0 | 635.8521 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 444 | San Leandro U: RAS project |  |  | San Leandro, Alameda | Modify the existing San Leandro U Substation, which will include all the necessary requirements, including time of day and seasonal setting changes, iterative tripping, and ability to accommodate bypass scenarios. The main driver for this RAS is the ISO planning standard that does not allow for load tripping in Greater Bay Area as a high population density area. The New RAS will monitor the outages and flows on five critical lines in Moraga-Oakland J area and take corrective actions to resolve any overloads on these lines without dropping the load. | Other - Remedial Action Scheme/Special Protection Scheme | New | NA | CAISO Transmission Planning Standards | Special Protection Scheme | NERC TPL Standards | 2024-03-07 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2372 | NA | 115 kV | Not Available | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5534504 | T.0004580 | San Leandro U: Ras Project | 4 | 61 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-11-14 | 2022-09-30 | 2025-08-21 | Prioritization | TRUE | 4000 | NA | 3698.322 | 7049.2611 | 43.0899 | 88.3808 | 656.7866 | 2509.3148 | 338.395 | 1295.6511 | 1729.129 | 0 | 0 | 0 | 0 | 3635.9672 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 43.0899 | 88.3808 | 656.7866 | 2509.3148 | 338.395 | 114.4352 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment:
| 445 | Newark: Add CB to Bank 7 |  |  | Fremont, Alameda | Add a second high side circuit breaker to the Newark 230/115 kV transformer bank #7 | Substation - Transformer | New | TBD | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | NA | 27.7611 | NA | 230 ¦ 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5791252 | T.0006022 | Newark - Add CB to Bank 7 | 1 | 61 | EX113211 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-03-01 | 2024-12-31 | 2026-12-01 | Prioritization | FALSE | $3,000 ¦ $6,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 3000 | 100 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
| 446 | Wilson-Oro Loma 115 kV Reconductoring |  |  | Fresno | Reconductor approximately 9 circuit miles between Wilson and El Nido on the Wilson-Oro Loma 115 kV Line with a larger conductor to achieve at least 650 Amps of summer emergency rating. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-02-16 | 75 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.8637 | NA | 115 kV | Not Available | 8. Compliance/Commitments (But Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5791342 | T.0006016 | Wilson-Oro Loma 115 kV Reconductoring | 2 | 61 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | 2026-12-31 | 2027-05-01 | NA | FALSE | $11,300 ¦ $22,700 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 1500 | 800 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
| 447 | Borden-Storey 230 kV 1 & 2 Recond |  |  | Chowchilla, Madera ¦ Madera ¦ Madera Acres CDP, Madera ¦ Merced ¦ Merced, Merced ¦ Parksdale CDP, Madera | Reconductoring the Borden – Storey section(s) of the Wilson – Borden #1 and #2 230 kV lines | Substation - Line Termination | Upgrade/Retrofit | TBD | Policy | Line Termination | NERC TPL Standards | 2023-09-29 | 18 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807524 | T.0009662 | Borden-Storey 230 kV 1 and 2 Line Reconductoring | 2 | 61 | EX113344 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | 2032-12-31 | 2028-05-01 | NA | FALSE | 50000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1000 | 2000 | 3000 | 300 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-F-Board-Approved_2022-2023_Transmission-Plan.pdf
| 448 | East Shore: Reconfigure 230 kV Bus |  |  | Hayward, Alameda | Reroute Russell City-East Shore and San Mateo-East Shore 230 kV lines at PG&E's East Shore 230 kV Substation | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-11 | 11 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 9.9849 | NA | 230 kV | Not Available | 8. Compliance/Commitments (But Low Safety Risk) | 425 | RBPPF - TBD | Yes | 5791251 | T.0006021 | East Shore - Reconfigure 230 kV Bus | 1 | 61 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2020 | FALSE | 2020 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-04-01 | 2024-12-31 | 2025-12-01 | Prioritization | FALSE | $2,000 ¦ $4,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 100 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApprovedt2019-2020TransmissionPlan.pdf
| 449 | CAPACITOR BANK AT PLAINFIELD SS |  |  | Solano | The California ISO’s 2018-2019 Transmission Planning Process (TPP) has identified the need for the Vaca – Dixon Area Reinforcement Project. This project will mitigate overloads and voltage criteria violations in the 115kV and 60kV transmission systems among Vaca Dixon, Davis, Rio Oso and Brighton Substations. The project will include the following work: 1. Install two 5.0 MVAR capacitor banks at Plainfield Substation. 2. Replace Vaca Dixon 115/60kV Bank 5 with a larger unit. 3. Replace the limiting elements on the 60kV equipment at Dixon Substation. 4. Re-rate the Woodland - Davis 115kV Line and the Rio Oso - West Sac 115kV Line. 5. Modify the existing special protection schemes (SPS) or add new SPS’s to trip load for select multiple contingencies. | Substation - Voltage Support Equipment | New | NA | Reliability | Voltage Support | NERC TPL Standards | 2024-03-12 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 42.1076 | NA | 60 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 16 | RBPPF - TBD | Yes | 5766696 | T.0000007 | VACA-DAVIS: VOLTAGE CONVERSION PROJECT | 6 | 61 | 5738814 | 2012 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | PEA Deemed Complete | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-05-26 | 2023-12-01 | 2027-04-30 | Prioritization | FALSE | $70,000 ¦ $107,000 | NA | 1883.0356 | 25639.1588 | 55.8771 | 139.7947 | 136.6514 | 386.1143 | 941.8825 | 1741.6945 | 1924.755 | 382.3425 | 20.8336 | 0 | 0 | 1850.3899 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 450 | Wolfe: Monta Vista-Wolfe 115kV Line Upgd |  |  | San Jose, Santa Clara | The project scope is to upgrade any limiting elements on the following five lines in the South Bay Area to achieve full conductor rating: 1) Monta Vista –Wolfe 115 kV Line 2) Newark –Jarvis #1 115 kV Line 3) Metcalf-Piercy 115kV Line 4) Metcalf-El Patio#1 115kV Line 5) Los Esteros-Montague 115kV Line | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-02 | 52 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | NA | 2.1017 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5554626 | T.0009571 | South Bay Area Limiting Element Upgrade | 1 | 61 | EX113231 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-06-01 | 2027-12-31 | 2026-03-01 | NA | FALSE | 11000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 500 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 451 | Cooley Landing: Upgrade CB 62 |  |  | East Palo Alto, San Mateo | This project proposes to improve the electric transmission grid reliability by replacing the overstressed CB 62 at Cooley Landing Substation. | Substation - Circuit Breaker | Upgrade/Retrofit | TBD | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-06 | 11 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.1512 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807125 | T.0009566 | Cooley Landing 60 kV Substation Circuit Breaker No #62 Upgrade | 1 | 61 | EX112235 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-03-01 | 2026-01-01 | 2026-12-01 | Prioritization | FALSE | $750 ¦ $1,130 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1000 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 452 | Kern 115kV Reinforce-Magunden CB122 |  |  | East Niles CDP, Kern | This project proposes to reconductor approximately 15 miles of 115 kV line from Kern to Kern Oil substations. In addition, the project will upgrade the limiting equipment at the Live Oak, Kern Oil, and Petrol substations. Load and generation balance is difficult in this area as demand increases and more private generation retires. | Substation - Circuit Breaker | Upgrade/Retrofit | TBD | Reliability | Substation Capacity | NERC TPL Standards | 2024-02-07 | 30 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | 15.2256 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5784620 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 9 | 61 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | NA | TBD | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2028-10-12 | 2016-03-01 | 2029-08-10 | Prioritization | FALSE | $40,000 ¦ $65,000 | NA | 59.276 | 788.6438 | 0 | 0 | 0 | 0 | 59.276 | 0 | 25 | 50 | 100 | 750 | 1000 | 59.276 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 453 | Coppermine 70 kV Reinforcement Sub |  |  | Madera | This project proposes to reconductor roughly 13 circuit miles of the Borden - Coppermine 70 kV Line and to install a voltage support device in the area. This will provide additional transmission capacity to serve electric customers in Madera and Fresno Counties. The project scope of work includes following: •Reconductor roughly 9.5 circuit miles of line between Borden and Cassidy Substations (from Pole 19/10A to Cassidy Substation) on the Borden-Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 700 Amps during summer normal conditions •Reconductor roughly 3.6 circuit miles of line between Cassidy and Coppermine Substations (from Pole 03/07 to Coppermine Substation) on the Borden - Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 500 Amps during summer normal conditions. •Remove any limiting components to achieve the full conductor capability •Install 20 MVar voltage support device at Coppermine Substation. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-03-05 | 61 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 7.1874 | NA | 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803380 | T.0008870 | Coppermine 70 kV Reinforcement Project | 3 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | 2027-05-01 | 2027-05-01 | NA | FALSE | $15,800 ¦ $31,600 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1500 | 200 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 454 | Mercy Springs SW STA: Connect 70kV Line |  |  | Merced | This project proposes to: • Install 230 kV partial bay at the new generation driven 230 kV switching station adjacent to Dos Amigos PP 230 kV Substation. • Add a new 70 kV Bus in the new generation driven 230 kV switching station, then it will be converted to a new 230/70 kV substation. • Install one 230/70 kV transformer at the new 230/70 kV substation. • Install a new 70 kV transmission line from new 70 kV Bus to Mercy Springs 70 kV Bus, and the new line is about one mile. • Install one breaker at Mercy Springs 70 kV Switching Station. | Substation - Transformer | New | TBD | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 53.2803 | NA | 230 ¦ 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807502 | T.0009617 | Los Banos 70 kV Area Reinforcement | 2 | 61 | EX113343 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | 2029-12-31 | 2028-12-01 | NA | FALSE | 60000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 2400 | 3950 | 6750 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 455 | North-East Kern 115 kV Reconductoring Project |  |  | Buttonwillow CDP, Kern ¦ Kern | This project proposes to: • Reconductor ~13.6 circuit miles of Midway – Shafter 115 kV Line • Reconductor ~8.3 circuit miles on the Shafter-Rio Bravo 115 kV • Reconductor ~3.9 circuit miles on the Midway-Tupman-Rio Bravo-Renfro 115 kV (between Rio Bravo and Renfro Junction From 11/62 To Rio Bravo Sub) • Reconductor ~3.5 circuit miles on the Lerdo-Kern Oil-7th Standard 115 kV Line (between Lerdo J and Kern Oil, from 023/005 To Kern Oil Sub) • Reconductor ~6.8 circuit miles on the Smyrna-Semitropic-Midway 115 kV Line (between Midway and Ganso from Midway to 081/634 and from 081/634 to Ganso) • Reconductor ~14.1 circuit miles on the Semitropic-Midway #1 115 kV Line (between Midway and Semitropic_E) • Convert the existing control point to a summer setup to open line section from Wasco to McFarland 70 kV line. • Convert the existing control point to a summer setup to open line section from Famoso to Cawelo C 115 kV line. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-03-29 | 76 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113342 | T.0009633 | NorthEast Kern 115kV Reconductor | 2 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-01 | 2032-12-31 | 2029-12-31 | NA | FALSE | 256000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1500 | 4000 | 8000 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 456 | CONTRA COSTA PP SW STA PHASE 2 |  |  | Antioch, Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Line Termination | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 19.1042 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803600 | T.0008048 | Contra Costa PP Line Swaps | 9 | 61 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-03-18 | 2025-05-01 | 2025-05-27 | NA | TRUE | $5,000 ¦ $10,000 | NA | 10.4506 | 7498.8874 | 0 | 0 | 0 | 0 | 7.8747 | 158.5453 | 7320.4429 | 1.7642 | 0 | 0 | 0 | 7.8747 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 457 | Contra Costa SW STA |  |  | Antioch, Contra Costa | This project proposes to: • Relocate two existing 230 kV transmission lines at the Contra Costa PP 230 kV substation by moving Lone Tree 230 kV line to bus section 2D and the Birds Landing 230 kV line to bus section 2E to mitigate the P2-4 (single contingency, internal breaker fault) thermal overload issue • Relocate the terminal of Windmaster from bus section F to bus section E to mitigate the P2-2 (single contingency, bus section fault) thermal overload issues on the bus section 2F, circuit breaker 820, and switches 601 and 603 which are rated at 1200A. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Line Termination | NERC TPL Standards | 2024-03-06 | 60 | Steady State Power Flow System Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence, Corrosion |  | NA | 19.1042 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5800033 | T.0008048 | Contra Costa PP Line Swaps | 9 | 61 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-23 | 2025-05-01 | 2025-03-19 | NA | TRUE | $5,000 ¦ $10,000 | NA | 5465.009 | 21637.2607 | 0 | 0 | 0 | 201.321 | 2604.3292 | 16796.3937 | 1962.6935 | 0 | 0 | 0 | 0 | 2805.6501 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 458 | TABLE M - SYCAMORE: Inst SPS |  |  | Chico, Butte | Install a Special Protection System (SPS) to monitor load follows on the three 115 kV lines at the Table Mount end and drop up to 45 MWs of load from Sycamore Creek 115 kV, Nord 115 kV, and Chico B 115 kV Substations beyond certain flow on these lines | Other - Remedial Action Scheme/Special Protection Scheme | New | TBD | Reliability | Special Protection Scheme | NA | 2024-02-07 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.5676 | NA | 115 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | 5 | RBPPF - TBD | Yes | 5746692 | T.0000021 | Table Mountain-Sycamore Creek 115kV | 1 | 61 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2028-12-28 | NA | 2029-11-27 | NA | FALSE | NA | NA | 669.3119 | 16797.0654 | 30.4671 | 55.0732 | 41.9103 | 45.3864 | 0 | 529.9005 | 556.6638 | 130.6836 | 140.2622 | 293.98 | 13365.8637 | 669.3119 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 459 | EASTSHORE: Reconductoring 115 KV |  |  | Hayward, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Substation - Line Termination | Upgrade/Retrofit | T.0004580 | Reliability | Line Termination | NERC TPL Standards | 2024-03-11 | 13 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 9.9849 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 425 | NA | NA | 5769866 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 61 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E/AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020/2022 | Operational | 2 | 2021-11-01 | 2015-03-01 | 2023-08-10 | Prioritization | TRUE | $15,000 ¦ $30,000 | NA | 1935.5509 | 1935.5509 | 37.1218 | 43.6746 | 741.0506 | 761.8701 | 248.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 1935.5509 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1785.6568 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 460 | EDES: Reconduct Fiber Interconnect |  |  | Oakland, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Substation - Line Termination | Upgrade/Retrofit | T.0004580 | Reliability | Line Termination | NERC TPL Standards | 2024-03-05 | 18 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 2.4009 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 425 | RBPPF - TBD | Yes | 5778946 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 61 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E/AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020/2022 | Construction (50%-75%) | 3 | 2021-11-01 | 2015-03-01 | 2025-12-12 | Project Design | TRUE | $15,000 ¦ $30,000 | NA | 10217.3421 | 12225.4214 | 298.5695 | 707.2645 | 3307.1917 | 3364.9645 | 2281.3533 | 753.1335 | 1382.7449 | 0 | 0 | 0 | 0 | 10089.543 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 461 | GRANT: Support 115 KV Reconductoring |  |  | San Leandro, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Substation - Line Termination | Upgrade/Retrofit | T.0004580 | Reliability | Line Termination | NERC TPL Standards | 2024-03-04 | 23 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 1.6572 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 425 | NA | NA | 5778947 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 61 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E/AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020/2022 | Operational | 2 | 2021-09-16 | 2015-03-01 | 2023-10-31 | Project Design | TRUE | $15,000 ¦ $30,000 | NA | 3856.9877 | 3899.5552 | 107.2742 | 140.0776 | 1947.9742 | 565.0001 | 935.7042 | 40.5568 | 3.1656 | 0 | 0 | 0 | 0 | 3855.8329 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 3855.8328 | 21.164 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 462 | OAKLAND J: Install 115 kV Reconductor |  |  | San Leandro, Alameda | Provide a third source of power into the Oakland J Substation from Eastshore Substation by reconductoring 14.8 circuit miles of transmission lines, modifying 35 towers (out of 98 towers on this line) and 4 substations, replacing and installing redundant communication fiber. Completion of the project will improve service reliability and mitigate these transmission overload Enterprise Risks in the SO area should the transmission path from Moraga to San Leandro and Oakland J be disrupted. Also, by replacing the 95-year old copper conductors on the Oakland J–Grant 115 kV Line with new, higher-capacity conductors, the project will reduce the risk of conductor failure. | Substation - Line Termination | Upgrade/Retrofit | T.0004580 | Reliability | Line Termination | NERC TPL Standards | 2024-03-04 | 55 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 1.6572 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 425 | NA | NA | 5767558 | T.0000114 | Eastshore - Oakland J 115 kV Reconductor | 7 | 61 | 5747764 | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5872-E/AL 6709-E | 2020-07-06 ¦ 2022-09-22 | Approved | 2020/2022 | Operational | 2 | 2021-09-27 | 2015-03-01 | 2023-09-14 | Prioritization | TRUE | $15,000 ¦ $30,000 | NA | 5282.0588 | 5282.0588 | 84.9678 | 119.2034 | 1710.2883 | 2272.3859 | 758.5508 | 0.5466 | 0 | 0 | 0 | 0 | 0 | 5281.5122 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 4952.349 | 0.5076 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 463 | WARNERVILLE-BELLOTA: Rec 230 KV Line |  |  | San Joaquin | Reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations. Key construction elements are as follows: • Replace 22.5 miles of the Bellota-Warnerville 230 kV circuit • Replace 19.9 miles of the Bellota-Cottle 230 kV circuit • Replace 2.5 miles of the Cottle-Melones 230 kV circuit • Replace 0.1 mile of the Warnerville-Wilson 230 kV circuit • Upgrade transmission line terminals at Bellota, Cottle, and Warnerville substations | Substation - Line Termination | Upgrade/Retrofit | NA | Policy | Line Termination | NERC TPL Standards | 2024-03-01 | 93 | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | 318 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5756037 | T.0000043 | Bellota-Warnerville 230kV Reinforcement | 8 | 61 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6047-E | 2021-01-06 | Approved | 2021 | Operational | 2 | 2023-01-10 | 2024-12-31 | 2023-04-28 | NA | TRUE | 28000 | NA | 1859.492 | 1865.7022 | 111.2519 | 46.8113 | 159.1196 | 557.2565 | 931.845 | 14.5618 | 0 | 0 | 0 | 0 | 0 | 1851.1404 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1604.3074 | 7.6735 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 464 | HERNDON SUB: REPL230kV SW267,269,201,203 |  |  | Fresno, Fresno | Replace Switch Nos. 267, 269, 201 and 203 at Herndon Substation, to provide additional transmission capacity | Substation - Switch | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-08 | 58 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 13.3414 | NA | 230 kV | 236 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5756014 | T.0000252 | HERNDON: REPL 230KV SW 267,269,201,203 | 1 | 61 | 5767970 | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-10-21 | 2015-05-31 | 2020-01-24 | Project Design | FALSE | $1,000 ¦ $2,000 | NA | 1258.6064 | 1258.6064 | 96.4097 | 478.2604 | 133.8655 | -6.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1258.6064 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 1054.8011 | 124.0673 | -5.7406 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 465 | LOS BANOS & SANTE NELLA SS UPGRADES |  |  | Fresno | The Oro Loma 70 kV Area Reinforcement project will reconductor 70 kV lines in the Oro Loma area to help ensure reliable electric service to customers in the Merced County. The project will reconductor 2.4 miles of the Los Banos - Livingston Jct – Canal 70 kV Line, from Los Banos to Santa Nella substations and 10.8 miles of the Mercy Springs SW STA – Canal – Oro Loma 70 kV Line, from Mercy Springs SW STA to Canal Substation. The conductor should be capable of handling at least 825 Amps and 975 Amps during summer normal and emergency conditions, respectively. Associated substation terminal equipment will be upgraded as needed to meet the ratings of the new line conductor. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-02-16 | 71 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 3.8637 | NA | 70 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5777179 | T.0000157 | Ora Loma 70kV Reinforcement | 4 | 61 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-10-12 | 2015-05-01 | 2026-11-06 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 2497.4872 | 3905.6674 | 121.486 | 41.9695 | 1595.3007 | 14.5047 | 0 | 160.5002 | 302.7913 | 1210.5393 | 3.1931 | 0 | 0 | 2497.4872 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 466 | MERCY SPRINGS & CANAL SS UPGRADES |  |  | Los Banos, Merced | The Oro Loma 70 kV Area Reinforcement project will reconductor 70 kV lines in the Oro Loma area to help ensure reliable electric service to customers in the Merced County. The project will reconductor 2.4 miles of the Los Banos - Livingston Jct – Canal 70 kV Line, from Los Banos to Santa Nella substations and 10.8 miles of the Mercy Springs SW STA – Canal – Oro Loma 70 kV Line, from Mercy Springs SW STA to Canal Substation. The conductor should be capable of handling at least 825 Amps and 975 Amps during summer normal and emergency conditions, respectively. Associated substation terminal equipment will be upgraded as needed to meet the ratings of the new line conductor. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-03-01 | 39 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.7007 | NA | 70 kV | 213 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767200 | T.0000157 | Ora Loma 70kV Reinforcement | 4 | 61 | 5746747 | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-10-12 | 2015-05-01 | 2027-01-29 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 64.373 | 1399.6023 | 36.3533 | 4.861 | 0 | 0 | 0 | 72.5012 | 416.202 | 1133.696 | 2.3876 | 0 | 0 | 64.373 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 467 | RMR: MTN VIEW-WHISMAN-AMES PROJECT (AMES |  |  | Mountain View, Santa Clara | The project proposes to reconnect the 115 kV lines from Mountain View and Whisman Substations into the 115 kV bus at Ames Substation. The work will require protection upgrades at the substations and also will require circuit breaker replacement at Mountain and Whisman due to increased fault duty at those substations. This project was one of several projects that are needed to eliminate the need to have a reliability must run (RMR) contract with Calpine’s Metcalf Energy Center. Also, to address substation bus reliability issues at Ames Substation, the project will also install circuit breakers at Ames on the two 115 kV lines that serve the NASA Ames facility. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Line Termination | NERC TPL Standards | 2024-02-05 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.8814 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5779898 | T.0003920 | RMR - Mtn View-Whisman-Ames Project | 9 | 61 | NA | 2018 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-17 | 2019-05-31 | 2019-09-09 | NA | FALSE | 14100 | NA | 2506.4081 | 2506.4081 | 948.5717 | 17.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2506.4081 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 2371.8843 | 16.6712 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 468 | RMR: MTN VIEW-WHISMAN-AMES PROJECT (WHIS |  |  | Mountain View, Santa Clara | The project proposes to reconnect the 115 kV lines from Mountain View and Whisman Substations into the 115 kV bus at Ames Substation. The work will require protection upgrades at the substations and also will require circuit breaker replacement at Mountain and Whisman due to increased fault duty at those substations. This project was one of several projects that are needed to eliminate the need to have a reliability must run (RMR) contract with Calpine’s Metcalf Energy Center. Also, to address substation bus reliability issues at Ames Substation, the project will also install circuit breakers at Ames on the two 115 kV lines that serve the NASA Ames facility. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | Reliability | Line Termination | NERC TPL Standards | 2024-02-06 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.1069 | NA | 115 kV | 137 | Not Available | NA | NA | NA | 5779900 | T.0003920 | RMR - Mtn View-Whisman-Ames Project | 9 | 61 | NA | 2018 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-30 | 2019-05-31 | 2019-02-15 | NA | FALSE | 14100 | NA | 1252.2868 | 1252.2868 | 585.6976 | -14.9553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.2868 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1187.0282 | -13.9866 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 469 | RMR: NASA-AMES 115KV LINE #1 CB INSTALL |  |  | Mountain View, Santa Clara | The project proposes to reconnect the 115 kV lines from Mountain View and Whisman Substations into the 115 kV bus at Ames Substation. The work will require protection upgrades at the substations and also will require circuit breaker replacement at Mountain and Whisman due to increased fault duty at those substations. This project was one of several projects that are needed to eliminate the need to have a reliability must run (RMR) contract with Calpine’s Metcalf Energy Center. Also, to address substation bus reliability issues at Ames Substation, the project will also install circuit breakers at Ames on the two 115 kV lines that serve the NASA Ames facility. | Substation - Circuit Breaker | New | NA | Reliability | Line Termination | NERC TPL Standards | 2024-02-05 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.8814 | NA | 115 kV | 137 | Not Available | NA | NA | NA | 5781026 | T.0003920 | RMR - Mtn View-Whisman-Ames Project | 9 | 61 | NA | 2018 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-02-19 | 2019-05-31 | 2019-04-26 | NA | FALSE | 14100 | NA | 1793.8949 | 1847.0802 | 1222.8765 | 203.1348 | 127.0634 | 54.8234 | 11.3285 | 53.1853 | 0 | 0 | 0 | 0 | 0 | 1793.8949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1364.9579 | 198.3628 | 124.0746 | 53.5337 | 11.0618 | 0.5838 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 470 | RMR: NASA-AMES 115KV LINE #2 CB INSTALL |  |  | Mountain View, Santa Clara | The project proposes to reconnect the 115 kV lines from Mountain View and Whisman Substations into the 115 kV bus at Ames Substation. The work will require protection upgrades at the substations and also will require circuit breaker replacement at Mountain and Whisman due to increased fault duty at those substations. This project was one of several projects that are needed to eliminate the need to have a reliability must run (RMR) contract with Calpine’s Metcalf Energy Center. Also, to address substation bus reliability issues at Ames Substation, the project will also install circuit breakers at Ames on the two 115 kV lines that serve the NASA Ames facility. | Substation - Circuit Breaker | New | NA | Reliability | Line Termination | NERC TPL Standards | 2024-02-05 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.8814 | NA | 115 kV | 137 | Not Available | NA | NA | NA | 5781027 | T.0003920 | RMR - Mtn View-Whisman-Ames Project | 9 | 61 | NA | 2018 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-29 | 2019-05-31 | 2019-06-21 | NA | FALSE | 14100 | NA | 1195.5181 | 1195.5181 | 1003.5233 | 38.7809 | 4.9562 | 10.8232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.5181 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 1115.2123 | 37.9252 | 4.8427 | 10.5754 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 471 | RMR: SAN JOSE B: EM REPL: TRIMBLE-SJ B L |  |  | San Jose, Santa Clara | The project scope is to install modular power flow control systems deployed on a dedicated bank structure at Vaca Dixon Substation (or adjacent property). The project submitted by Smart Wire entail installing modular power flow control system devices electrically in series with the Vaca Dixon – Lakeville and Vaca Dixon – Tulucay 230 kV lines on PG&E property at Vaca Dixon Substation. | Substation - Line Termination | Upgrade/Retrofit | NA | Economic | Line Termination | NERC TPL Standards | 2024-02-02 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.1017 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5779598 | T.0003876 | Trimble-San Jose B 115 kV Line Rerate | 2 | 61 | NA | NA | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-16 | 2018-05-01 | 2019-02-25 | Prioritization | FALSE | 250 | NA | 2647.422 | 2647.422 | 1121.8759 | 82.7831 | 457.3456 | 1.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2647.422 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 1805.6385 | 70.8409 | 391.256 | 1.1905 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 472 | Moraga-Casto Valley 230 kV Line Cap In |  |  | Orinda, Contra Costa | The project scope of work involves upgrading the limiting substation equipment (jumper conductors and wave traps) on the Moraga-Castro Valley and Castro Valley-Newark 230 kV lines to utilize their full conductor ratings. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-03-06 | 72 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 15.8714 | NA | 230 kV | 180 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5747775 | T.0004421 | Moraga-Castro Valley 230 kV Capacity | 3 | 61 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-08-09 | 2013-05-01 | 2024-12-31 | Prioritization | TRUE | $1,000 ¦ $5,000 | NA | 528.1208 | 1189.3563 | 38.7613 | 58.6408 | 14.5695 | 58.3383 | 289.616 | 596.9379 | 132.4925 | 0 | 0 | 0 | 0 | 459.9259 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 473 | STANISLAUS PWR HOUSE SUB UPGRADE |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Manteca, San Joaquin ¦ San Joaquin ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | The project will increase system performance and reduce fire ignition risk in Calaveras, San Joaquin, Stanislaus, and Tuolumne counties by the following: • Replacement of approximately 30.6 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Manteca No. 1 115 kV Line on the following sections: o Stanislaus Powerhouse (PH) to Tower No. 020/132 (21.2 miles) o Tower No. 021/136 to Tower No. 030/195 (9.4 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Manteca No. 2 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Riverbank Jct SS 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 410 existing structures with new steel structures • Upgrade terminal equipment at Stanislaus PH | Substation - Line Termination | Upgrade/Retrofit | T.0004515 ¦ T.0007979 ¦T.0008743 | Asset Condition | Line Termination | NA | 2024-04-12 | 88 | NA | Other - Deferral | $250 Mil – $300 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5784382 | T.0004301 | Stanislaus Manteca T-Line Rebuild-PH2 | 6 | 61 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6382-E | 2021-10-28 | Approved | 2021 | Engineering more than 50% complete | 4 | 2025-09-27 | 2030-05-01 | 2027-06-10 | NA | FALSE | 242000 | NA | 439.6361 | 4947.3093 | 0 | 0 | 148.2934 | 244.9999 | 40.0861 | 100.4269 | 1410.0931 | 2904.9705 | 6.622 | 0 | 0 | 433.3794 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 474 | RAVENSWOOD: Repl T-Line Structure |  |  | Menlo Park, San Mateo | The project will replace the two line termination dead-end structures and associated switches at Ravenswood Substation for the Ravenswood – Cooley Landing 115 kV Lines. This will eliminate a potential failure of either structure, which could result in an extended outage of the line and could impact personnel safety in the substation. This work will also enable the structures to support the new conductor to be installed on the lines as part of the Ravenswood – Cooley Landing 115 kV Reconductoring Project, which is expected to start work in Fall 2020. The substation project is expected to be released to operations by June 30, 2020. | Substation - Structure | Upgrade/Retrofit | NA | Asset Condition | Line Termination | NA | 2024-03-06 | 62 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | NA | 230 kV | 21 | 8. Compliance/Commitments With Low Safety Risk | 11 | NA | NA | 5782143 | T.0004285 | Ravenswood T-Line Structure Replacement | 1 | 61 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-11-02 | 2020-06-22 | 2021-11-17 | Prioritization | FALSE | 2300 | NA | 2191.726 | 2191.726 | 437.0356 | 795.1608 | 727.9613 | 134.7235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2191.726 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1825.2846 | 118.2158 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 475 | METCALF - EVERGREEN RECONDUCTORING #2 |  |  | Santa Clara | The project work will involve upgrading the capacity of the Metcalf – Evergreen Nos. 1 and 2 115 kV Lines, so that both lines have an emergency rating of at least 1,100 Amps. Substation equipment at Metcalf and Evergreen will be upgraded, as needed. The proposed line reinforcement work will involve reconductoring these 115 kV lines with a conductor having an emergency capability of at least 1,100 Amps. Substation equipment will also be upgraded as needed to meet the capability of the new transmission line conductor. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Line Termination | NERC TPL Standards | 2024-03-13 | 71 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5767246 | T.0000147 | METCALF - EVERGREEN RECONDUCTORING (TL) | 2 | 61 | 5749098 | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2002 | FALSE | 2002 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-07-29 | 2019-05-21 | 2020-01-15 | Prioritization | FALSE | $5,000 ¦ $10,000 | NA | 1482.617 | 1482.617 | 951.2785 | 46.4843 | 0.0966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1482.617 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1411.8551 | 0.09176 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 476 | BAKERSFIELD: Upgrade 230 KV Line |  |  | Bakersfield, Kern | This project proposes to reconductor approximately 42 circuit miles of the Midway - Kern No. 1 230 kV Line, and split the No. 1 line into Midway - Kern No. 1 and No. 2 230 kV Lines, and remove crosstie connections to split the Midway - Kern No. 1 230 kV Line. The Project will also reconductor approximately 13 circuit miles of the Bakersfield Nos. 1 and 2 230 kV Tap Lines. Remove the Stockdale Nos. 1 and 2 230 kV Tap Lines from the Midway – Kern 230 kV lines and relocate directly to the Kern PP 230 kV bus. This project is needed to provide additional transmission capacity and reliability to serve electric customers in Kern County. | Substation - Line Termination | Upgrade/Retrofit | T.0000220 ¦T.0001650 | Reliability | Line Termination | NERC TPL Standards | 2024-03-05 | 42 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.6195 | NA | 230 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5767357 | T.0003202 | Bakersfield-Kern Taps 1&2 230kV Recon | 3 | 61 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5924-E | 2020-08-19 | Approved | 2020 | Engineering more than 50% complete | 4 | 2026-01-12 | 2019-05-01 | 2027-02-03 | Prioritization | FALSE | $60,000 ¦ $90,000 | NA | 738.5388 | 8640.8555 | 125.2368 | 44.1933 | 0.3879 | 0 | 0 | 462.4673 | 1322.4079 | 3334.0164 | 0 | 0 | 0 | 724.0418 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 477 | BULLARD SUB: RECONDUCTOR 115KV LINE |  |  | Fresno, Fresno | This project proposes to reconductor roughly 8 circuit miles (4 miles of double circuit transmission line) between Pinedale Jct and Bullard Substation on the Herndon - Bullard Nos. 1 and 2 115 kV lines. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-03-07 | 16 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.363 | NA | 115 kV | 69 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5787499 | T.0004347 | Herndon - Bullard Nos. 1 and 2 115 kV RC | 3 | 61 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-07-24 | 2021-01-01 | 2026-11-25 | Prioritization | FALSE | $6,000 ¦ $8,000 | NA | 88.8345 | 6749.3386 | 16.0907 | 61.1538 | 5.5659 | 6.024 | 0 | 193.0381 | 3408.6373 | 2533.0518 | 21.6974 | 0 | 0 | 88.8345 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 478 | PINEDALE SUB: RECONDUCTOR 115KV LINE |  |  | Fresno, Fresno | This project proposes to reconductor roughly 8 circuit miles (4 miles of double circuit transmission line) between Pinedale Jct and Bullard Substation on the Herndon - Bullard Nos. 1 and 2 115 kV lines. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-03-12 | 16 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.2566 | NA | 115 kV | 69 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5787498 | T.0004347 | Herndon - Bullard Nos. 1 and 2 115 kV RC | 3 | 61 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-06-05 | 2021-01-01 | 2026-12-31 | Prioritization | FALSE | $6,000 ¦ $8,000 | NA | 44.7408 | 2689.3319 | 13.0203 | 25.885 | 2.8017 | 3.0339 | 0 | 149.0877 | 939.5714 | 1298.258 | 41.4159 | 0 | 0 | 44.7408 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 479 | South of Mesa Upgrade - Santa Ynez SS |  |  | Santa Barbara | This project proposes to upgrade approximately 21.3 miles of conductor on the Sisquoc – Santa Ynez SW STA 115 kV Line, install 20 Mega Volt-ampere reactive (MVAR) shunt capacitors at Cabrillo Substation and install Remedial Action Scheme (RAS) (formerly known as Special Protection Scheme (SPS)) on the Sisquoc – Santa Ynez SW STA 115 kV Line. Completion of this project is needed to improve the electric transmission system reliability and operational flexibility in the Santa Barbara County. This project will be funded under Major Work Category (MWC) 60, Electric Transmission Line Capacity and 61, Electric Transmission Substation Capacity. The project has a Risk Informed Budget Allocation (RIBA) score of 137. The RIBA score is based on the impact and frequency of three risk categories: safety, reliability and environmental. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-02-02 | 35 | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.40907 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5792240 | T.0004832 | South Of Mesa Upgrade Project | 5 | 61 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-12-19 | 2023-12-31 | 2026-12-28 | Prioritization | FALSE | $29,600 ¦ $59,200 | NA | 68.4071 | 8030.7412 | 0 | 68.0277 | 0.3794 | 0 | 0 | 0 | 150 | 1500 | 2000 | 5500 | 5500 | 68.4071 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 480 | South of Mesa Upgrade - Sisquoc Sub |  |  | Santa Barbara | This project proposes to upgrade approximately 21.3 miles of conductor on the Sisquoc – Santa Ynez SW STA 115 kV Line, install 20 Mega Volt-ampere reactive (MVAR) shunt capacitors at Cabrillo Substation and install Remedial Action Scheme (RAS) (formerly known as Special Protection Scheme (SPS)) on the Sisquoc – Santa Ynez SW STA 115 kV Line. Completion of this project is needed to improve the electric transmission system reliability and operational flexibility in the Santa Barbara County. This project will be funded under Major Work Category (MWC) 60, Electric Transmission Line Capacity and 61, Electric Transmission Substation Capacity. The project has a Risk Informed Budget Allocation (RIBA) score of 137. The RIBA score is based on the impact and frequency of three risk categories: safety, reliability and environmental. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-02-13 | 35 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.9084 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5792241 | T.0004832 | South Of Mesa Upgrade Project | 5 | 61 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-01-28 | 2023-12-31 | 2026-05-26 | Prioritization | FALSE | $29,600 ¦ $59,200 | NA | 23.2123 | 1006.9446 | 0 | 22.2065 | 1.0059 | 0 | 0 | 0 | 150 | 500 | 1000 | 1000 | 1000 | 23.2123 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 481 | LARKIN A-Y #3 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | 2024-02-15 | NA | NA | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 1.0478 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798621 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA | 2015 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2029-05-21 | 2025-06-20 | 2029-09-17 | Project Design | FALSE | 191100 | NA | 27.1526 | 2738.7189 | 0 | 0 | 1.4266 | 21.9261 | 3.4823 | 0.3175 | 0 | 0 | 0 | 0 | 332.5515 | 26.8351 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 482 | LARKIN X-Y #2 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | 2024-02-15 | NA | NA | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 1.0478 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801473 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA | 2015 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-06-01 | 2025-06-20 | 2028-09-28 | Project Design | FALSE | 191100 | NA | 24.0798 | 2616.2594 | 0 | 0 | 0 | 6.0017 | 17.7943 | 0.2838 | 0 | 0 | 0 | 0 | 338.5794 | 23.796 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 483 | MISSION A-X #2 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | 2024-02-09 | NA | NA | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.83366 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798620 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA | 2015 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-04-12 | 2025-06-20 | 2027-08-06 | Project Design | FALSE | 191100 | NA | 25.8884 | 2480.4906 | 0 | 0 | 0.708 | 21.2856 | 3.5921 | 0.3028 | 0 | 0 | 0 | 0 | 323.2713 | 25.5856 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 484 | MISSION X-Y #2 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | 2024-02-09 | NA | NA | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.83366 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801472 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA | 2015 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-06-01 | 2025-06-20 | 2028-09-28 | Project Design | FALSE | 191100 | NA | 7.527 | 2599.7065 | 0 | 0 | 0 | 6.6395 | 0.7987 | 0.0887 | 0 | 0 | 0 | 0 | 338.6518 | 7.4383 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 485 | POTRERO A-X #2 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | 2024-03-28 | NA | NA | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798619 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA | 2015 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-04-12 | 2025-06-20 | 2027-08-06 | Project Design | FALSE | 191100 | NA | 49.0308 | 2499.5681 | 0 | 0 | 0.708 | 39.8149 | 7.9864 | 0.5215 | 0 | 0 | 0 | 0 | 334.1034 | 48.5093 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 486 | POTRERO A-Y #3 TERMINATION |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Substation - Line Termination | Upgrade/Retrofit | T.0002705 ¦ T.0000557 ¦ T.0000934 | Reliability | Line Termination | NA | 2024-03-28 | NA | NA | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801471 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 61 | NA | 2015 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2029-05-21 | 2025-06-20 | 2029-09-17 | Project Design | FALSE | 191100 | NA | 67.9704 | 2779.5367 | 0 | 0 | 0 | 8.9742 | 58.1951 | 0.801 | 0 | 0 | 0 | 0 | 338.8355 | 67.1694 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 487 | SOUTH OF PALERMO - BOGUE SUB |  |  | Yuba City, Sutter | This project will reinforce 80.3 circuit miles of the 115kV transmission lines between Palermo, Pease, Bogue, and Rio Oso substations with 477 kcmil steel-supported aluminum conductors with emergency capability of 970 Amps. This includes the installation of five Supervisory Control and Data Acquisition (SCADA) controlled transmission line switches on the Palermo – Pease, Pease – Rio Oso, Palermo – Bogue, and Bogue – Rio Oso 115kV lines to improve reliability and service restoration time. Key construction elements are as follows:  Replacement of 238 steel electric transmission lattice towers with 238 new hybrid tubular steel poles (HTSP), which include a concrete foundation and steel pole on top  Replacement of 21 steel electric transmission lattice towers with 21 tubular steel poles (TSP).  Replacement of 45 steel electric transmission lattice steel poles with new lattice steel poles.  Replacement of 2 steel electric transmission lattice towers with new steel lattice towers.  Reinforcement of 61 steel electric transmission lattice tower foundations with screw anchors.  Reinforcement of 23 steel electric transmission lattice towers with 19 top or waist cage extensions.  Upgrade 8 transmission relay terminals at 4 surrounding substations. This project has been divided into three construction phases as follows:  Phase 1: Rio Oso Substation to Pease Junction  Phase 2: Pease Substation to Palermo Substation  Phase 3: Bogue Substation to Bogue Junction | Substation - Line Termination | Upgrade/Retrofit | T.0000598 | Reliability | Line Termination | NERC TPL Standards | 2024-02-17 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.7823 | NA | 115 kV | 180 | Not Available | NA | NA | NA | 5767552 | T.0000450 | South of Palermo 115kV Reinforcement | 12 | 61 | 5763937 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-01 | 2014-05-01 | 2019-02-07 | Prioritization | FALSE | $80,000 ¦ $100,000 | NA | 1633.7792 | 1633.7792 | 532.0532 | 32.6986 | 4.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1633.7792 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 924.7525 | 18.6998 | 2.3417 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 488 | SOUTH OF PALERMO - PALERMO SUB |  |  | Palermo CDP, Butte | This project will reinforce 80.3 circuit miles of the 115kV transmission lines between Palermo, Pease, Bogue, and Rio Oso substations with 477 kcmil steel-supported aluminum conductors with emergency capability of 970 Amps. This includes the installation of five Supervisory Control and Data Acquisition (SCADA) controlled transmission line switches on the Palermo – Pease, Pease – Rio Oso, Palermo – Bogue, and Bogue – Rio Oso 115kV lines to improve reliability and service restoration time. Key construction elements are as follows:  Replacement of 238 steel electric transmission lattice towers with 238 new hybrid tubular steel poles (HTSP), which include a concrete foundation and steel pole on top  Replacement of 21 steel electric transmission lattice towers with 21 tubular steel poles (TSP).  Replacement of 45 steel electric transmission lattice steel poles with new lattice steel poles.  Replacement of 2 steel electric transmission lattice towers with new steel lattice towers.  Reinforcement of 61 steel electric transmission lattice tower foundations with screw anchors.  Reinforcement of 23 steel electric transmission lattice towers with 19 top or waist cage extensions.  Upgrade 8 transmission relay terminals at 4 surrounding substations. This project has been divided into three construction phases as follows:  Phase 1: Rio Oso Substation to Pease Junction  Phase 2: Pease Substation to Palermo Substation  Phase 3: Bogue Substation to Bogue Junction | Substation - Line Termination | Upgrade/Retrofit | T.0000598 | Reliability | Line Termination | NERC TPL Standards | 2024-03-04 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.0464 | NA | 115 kV | 180 | Not Available | NA | NA | NA | 5767550 | T.0000450 | South of Palermo 115kV Reinforcement | 12 | 61 | 5763937 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-01 | 2014-05-01 | 2019-04-25 | Prioritization | FALSE | $80,000 ¦ $100,000 | NA | 1817.9 | 1817.9 | 521.6323 | 143.1272 | 5.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1817.9 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1669.5025 | 143.1272 | 5.0049 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 489 | SOUTH OF PALERMO - RIO OSO SUB |  |  | Sutter | This project will reinforce 80.3 circuit miles of the 115kV transmission lines between Palermo, Pease, Bogue, and Rio Oso substations with 477 kcmil steel-supported aluminum conductors with emergency capability of 970 Amps. This includes the installation of five Supervisory Control and Data Acquisition (SCADA) controlled transmission line switches on the Palermo – Pease, Pease – Rio Oso, Palermo – Bogue, and Bogue – Rio Oso 115kV lines to improve reliability and service restoration time. Key construction elements are as follows:  Replacement of 238 steel electric transmission lattice towers with 238 new hybrid tubular steel poles (HTSP), which include a concrete foundation and steel pole on top  Replacement of 21 steel electric transmission lattice towers with 21 tubular steel poles (TSP).  Replacement of 45 steel electric transmission lattice steel poles with new lattice steel poles.  Replacement of 2 steel electric transmission lattice towers with new steel lattice towers.  Reinforcement of 61 steel electric transmission lattice tower foundations with screw anchors.  Reinforcement of 23 steel electric transmission lattice towers with 19 top or waist cage extensions.  Upgrade 8 transmission relay terminals at 4 surrounding substations. This project has been divided into three construction phases as follows:  Phase 1: Rio Oso Substation to Pease Junction  Phase 2: Pease Substation to Palermo Substation  Phase 3: Bogue Substation to Bogue Junction | Substation - Line Termination | Upgrade/Retrofit | T.0000598 | Reliability | Line Termination | NERC TPL Standards | 2024-03-04 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $200 Mil - $250 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.3219 | NA | 115 kV | 180 | Not Available | NA | NA | NA | 5767553 | T.0000450 | South of Palermo 115kV Reinforcement | 12 | 61 | 5763937 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-01 | 2014-05-01 | 2019-02-21 | Prioritization | FALSE | $80,000 ¦ $100,000 | NA | 1849.8895 | 1849.8895 | 834.5147 | 124.9471 | 0.9394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1849.8895 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1723.9125 | 124.9471 | 0.93942 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 490 | Lone Tree-Cayetano-Newark Series Reactor |  |  | Alameda ¦ Antioch, Contra Costa ¦ Brentwood, Contra Costa ¦ Contra Costa | Add 6 SmartValve units (2 SmartValve 10-1800 units per phase) to the Cayetano – Lone Tree 230 kV line Add 6 SmartValves units (2 SmartValve 10-1800 units per phase) to the Las Positas - Newark 230 kV Line | Substation - Voltage Support Equipment | New | TBD | Reliability | Voltage Support | NERC TPL Standards | 2023-04-01 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | NA | NA | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807124 | T.0009573 | Lone Tree–Cayetano–Newark Corridor Series Compensation | 1 | 61 | EX113233 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-03-01 | 2027-12-31 | 2027-12-01 | NA | FALSE | 25000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 4000 | 10000 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 491 | Moss Landing-Las Aguilas Series Reactor |  |  | San Benito | Install 10 Ohms series reactor on the Moss Landing-Las Aguilas 230kV Line at Las Aguilas Substation. CAISO recommended the Moss Landing-Las Aguilas 230kV series reactor(10 Ohm) project in 2021-2022 Transmission plan. The series reactor can mitigate the transmission congestion on Moss Landing-Las Aguilas path during summer high solar generation hours in Fresno area. Based on CAISO's economic analysis, the economic benefit to be brought by Moss Landing to Las Aguilas series reactor project will be 3 to 4 times of the project cost. This project will bring net saving and benefit the ratepayers. To address the transmission congestion on Moss Landing-Las Aguilas path, the CAISO is recommending approval of adding series compensation devices on the Moss Landing-Las Aguilas 230kV line. Current studies show that adding about 10 Ohm reactor on the Moss Landing-Las Aguilas 230kV line would be an optimal solution. | Substation - Voltage Support Equipment | New | TBD | Economic | Voltage Support | NERC TPL Standards | 2024-02-14 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.0534 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807121 | T.0009559 | Moss Landing – Las Aguilas 230 kV Series Reactor Project | 1 | 61 | EX112240 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | 2026-01-01 | 2028-04-01 | Prioritization | FALSE | $30,000 ¦ $40,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 7000 | 9000 | 1000 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 492 | Tyler 60 kV Shunt Capacitor |  |  | Tehama | PG&E has observed high voltages on the Bulk Electric System in recent years, these observations have been made system wide, however, the most sever and frequent occurrences have been in the northern area. This project proposal is for Tyler Substation, located in Tehama County. Rawson JCT and Tyler#2 60kV buses have been identified as exceeding normal high operating limits in the minimum load base case, and further confirmed through the review of real-time data. To address these high-voltage problems, couple projects were been initiated throughout the system to install shunt reactors at several transmission substations to help control system voltages. The scope of this project is to install 20 MVAR, two steps (2X10 MVAR) shunt capacitor at Tyler 60 kV substation in North Valley area. A switch or circuit breaker might need to protect the shunt capacitor. | Substation - Voltage Support Equipment | New | TBD | Reliability | Voltage Support | NERC TPL Standards | 2024-02-13 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.7115 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807178 | T.0009582 | Tyler 60 kV Shunt Capacitor | 2 | 61 | EX112166 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-03-01 | 2022-12-31 | 2027-03-01 | Prioritization | FALSE | $5,800 ¦ $7,000 | NA | 0.3435 | 0.3435 | 0 | 0 | 0 | 0 | 0 | 0.0041 | 1000 | 2000 | 3000 | 500 | 0 | 0.3395 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 493 | Ignacio Area Upgrade: Grenbrae Sub |  |  | Larkspur, Marin | Reconductor Ignacio - San Rafael No. 1 115 kV Line, Ignacio - Alto 60 kV Line, and Ignacio - San Rafael No. 3 115 kV Line section from Ignacio - Las Gallinas as well as upgrade limiting equipment on lines. Add a 10 MVAR shunt capacitor at Greenbrae 60 kV Substation and associated substation upgrades to accommodate this installation | Substation - Voltage Support Equipment | New | TBD | Reliability | Voltage Support | NERC TPL Standards | 2024-02-16 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.0901 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807462 | T.0009719 | Ignacio Area Upgrade | 4 | 61 | EX113201 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | 2012 ¦ 2018 | FALSE | 2012 ¦ 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-02-26 | 2023-12-01 | 2029-05-10 | Prioritization | FALSE | 37000 | NA | 6.6347 | 9362.103 | 0 | 0 | 0 | 0 | 0 | 459.8516 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 494 | Coppermine 70 kV Reinforcement Caps |  |  | Fresno | This project proposes to reconductor roughly 13 circuit miles of the Borden - Coppermine 70 kV Line and to install a voltage support device in the area. This will provide additional transmission capacity to serve electric customers in Madera and Fresno Counties. The project scope of work includes following: •Reconductor roughly 9.5 circuit miles of line between Borden and Cassidy Substations (from Pole 19/10A to Cassidy Substation) on the Borden-Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 700 Amps during summer normal conditions •Reconductor roughly 3.6 circuit miles of line between Cassidy and Coppermine Substations (from Pole 03/07 to Coppermine Substation) on the Borden - Coppermine 70 kV Line. The new conductor should have a load serving capability of at least 500 Amps during summer normal conditions. •Remove any limiting components to achieve the full conductor capability •Install 20 MVar voltage support device at Coppermine Substation. | Substation - Voltage Support Equipment | New | TBD | Reliability | Voltage Support | NERC TPL Standards | 2024-02-09 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.0827 | NA | 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803381 | T.0008870 | Coppermine 70 kV Reinforcement Project | 3 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | 2027-05-01 | 2027-05-01 | NA | FALSE | $15,800 ¦ $31,600 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 4000 | 300 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 495 | Fort Seward: Install 60kV Statcom |  |  | Humboldt | Humboldt County is experiencing rapid growth of agriculture loads with high concentrations in the Garberville area. To help increase the capacity and provide more immediate voltage support by installing the 60kV STATCOM. Install a new 20 MVAr STATCOM on Fort Seward 60kV bus • Expand 60kV Bus to accommodate STATCOM connection • Install breakers and associated equipment as needed • Upgrade associated substation equipment to accommodate the SVC, if necessary. • Expand substation fence line and expand or purchase new control building to accommodate 60kV bus upgrade and STATCOM. | Substation - Voltage Support Equipment | New | TBD | Reliability | Voltage Support | NERC TPL Standards | 2024-02-07 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.35457 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803223 | T.0008748 | Fort Seward_Install 60kV Statcom | 1 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-12-03 | 2032-12-31 | 2027-02-03 | NA | FALSE | 204000 | NA | 109.8143 | 7802.0167 | 0 | 0 | 0 | 0 | 67.3007 | 3838.0174 | 8000 | 6500 | 500 | 0 | 0 | 67.3007 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 496 | Wilson 115kV STATCOM |  |  | Merced, Merced | Install a 115kV +100/-100 Mega Volt-Ampere reactive (MVAR) voltage control system (STATCOM) at Wilson Substation. | Substation - Voltage Support Equipment | New | NA | Reliability | Voltage Support | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 22.8151 | NA | 115 kV | 318 | 8. Compliance/Commitments With Low Safety Risk | 7 | NA | NA | 5768820 | T.0001381 | Wilson 115kv STATCOM | 2 | 61 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-08-03 | 2020-05-01 | 2021-05-10 | Prioritization | TRUE | $35,000 ¦ $45,000 | NA | 37614.3349 | 40709.4469 | 8747.2434 | 18228.0127 | 8434.6808 | 652.2538 | 56.5171 | 1792.2889 | 1293.6931 | 0 | 0 | 0 | 0 | 37623.4649 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 35633.2248 | 628.1203 | 54.4259 | -7.094 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
| 497 | RIO OSO: SVC |  |  | Sutter | Install a 230kV +200/-260 Mega Volt-Ampere reactive (MVAR) SVC at Rio Oso Substation | Substation - Voltage Support Equipment | New | T.0000614 | Reliability | Voltage Support | NERC TPL Standards | 2024-03-04 | NA | Steady State Power Flow System Analysis | Wires - System Configuration Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 9.3219 | NA | 230 kV | 1002 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5770538 | T.0001739 | RIO OSO Substation 230kV SVC | 1 | 61 | 5725553 | 2012 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-09-18 | 2016-05-01 | 2026-05-15 | Workforce | FALSE | $35,000 ¦ $45,000 | NA | 23481.6814 | 58702.6983 | 199.3063 | 229.4784 | 3758.1703 | 7006.1151 | 5190.1307 | 23128.6782 | 10302.1537 | 0 | 0 | 0 | 0 | 18437.0431 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 498 | SPENCE: Upgrade Transmission 60 KV |  |  | Monterey | Install new Bank 1 (one 30 MVA 60/12 kV transformer) with 60 kV circuit switcher at Spence Substation. Install two 60 kV breakers and one 60 kV circuit switcher on the 60 kV bus. Install one new 12 kV outdoor bus and add two new 12 kV feeders and place these feeders | Substation - Transformer | New | NA | Load Growth | Transformer Addition/Replacement | NA | 2024-02-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.96235 | NA | 60 kV | 25 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5779934 | T.0000977 | SPENCE SUB INSTALL BK1 FOR CAPACITY | 1 | 61 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-12-05 | 2018-12-10 | 2019-03-26 | NA | FALSE | 4792 | NA | 5506.1151 | 5506.1151 | 1652.0446 | 5.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5506.1151 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 5282.3373 | 4.9068 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 499 | IGNACIO: Install 230 kV Shunt Reactor |  |  | Novato, Marin | Install shunt reactor at Ignacio 230kV Substation consisting of two steps of 75 MVar2 to help control system voltages. | Substation - Voltage Support Equipment | New | NA | Reliability | Voltage Support | NERC TPL Standards | 2024-03-14 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.9486 | NA | 230 kV | 1002 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5768313 | T.0001128 | Ignacio 230 kV Shunt Reactor Project | 1 | 61 | NA | 2016 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-02-14 | 2020-05-01 | 2019-08-16 | NA | FALSE | $23,000 ¦ $35,000 | NA | 12840.2664 | 12840.2664 | 7091.2838 | 126.7126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12840.2664 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 12713.5542 | 126.7126 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
| 500 | WHEELER RIDGE: Inst 75 MVAR Capacitors |  |  | Kern | Install three 75 Mega Volt-Ampere reactive (MVAR) steps of mechanically switched capacitors, upgrade the 230kV bus to breaker-and-a-half (BAAH), and add an MPAC building at Wheeler Ridge Substation, | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | Reliability | Voltage Support | NERC TPL Standards | 2024-03-06 | 9 | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 10.403 | NA | 230 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5767969 | T.0000662 | WHEELER RIDGE 230kV VOLTAGE SUPPORT | 3 | 61 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-04-15 | 2016-12-01 | 2021-02-01 | Prioritization | FALSE | $25,000 ¦ $40,000 | NA | 36547.9267 | 36547.9267 | 6438.2118 | 22695.7655 | 5707.5285 | 64.7646 | 14.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 36547.9267 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 35822.4888 | 63.5454 | 14.6385 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 501 | Wheeler Ridge: Votlage Support Phase 2 |  |  | Kern | Install three 75 Mega Volt-Ampere reactive (MVAR) steps of mechanically switched capacitors, upgrade the 230kV bus to breaker-and-a-half (BAAH), and add an MPAC building at Wheeler Ridge Substation, | Substation - Voltage Support Equipment | New | NA | Reliability | Voltage Support | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $150 Mil - $175 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5785918 | T.0000662 | WHEELER RIDGE 230kV VOLTAGE SUPPORT | 3 | 61 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-05-03 | 2016-12-01 | 2021-07-02 | Prioritization | TRUE | $25,000 ¦ $40,000 | NA | 2436.3076 | 2436.3076 | 1.1815 | 0.406 | 2138.355 | 55.6184 | 240.7467 | 0 | 0 | 0 | 0 | 0 | 0 | 2436.3076 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1886.2186 | 48.9863 | 212.0392 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 502 | LOS ESTEROS: Install Shunt Reactors |  |  | San Jose, Santa Clara | Install three 85 MVar shunt reactors on the 230kV buses at Los Esteros Substation to help control system voltages. | Substation - Voltage Support Equipment | New | NA | Reliability | Voltage Support | NERC TPL Standards | 2024-03-12 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 230 kV | 1007 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5768542 | T.0001130 | Los Esteros Shunt Reactor Project | 1 | 61 | NA | 2016 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-12-02 | 2020-05-01 | 2021-03-18 | Prioritization | FALSE | $24,000 ¦ $36,000 | NA | 18616.0457 | 18616.0457 | 3655.1542 | 11738.9909 | 1937.364 | 105.8186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18616.0457 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 18510.2306 | 105.8186 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
| 503 | DELEVAN: Install 200 MVAR Shunt Reactor |  |  | Colusa | Install three steps for a total of 202 MVar shunt reactors1 at Delevan 230kV Substation to help control system voltages | Substation - Voltage Support Equipment | New | NA | Reliability | Voltage Support | NERC TPL Standards | 2024-03-07 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.7615 | NA | 230 kV | 1002 | 8. Compliance/Commitments With Low Safety Risk | 22 | NA | NA | 5771160 | T.0001991 | DELEVAN Substation 230kV Shunt Reactor | 1 | 61 | 5768472 | 2016 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-01-27 | 2020-05-01 | 2020-10-08 | NA | FALSE | $19,000 ¦ $28,000 | NA | 16957.2187 | 16957.2187 | 6511.5059 | 8196.2917 | 124.5794 | 37.6812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16957.2187 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 16789.5845 | 124.5369 | 37.6683 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
| 504 | COTTONWOOD: Replace Bank |  |  | Cottonwood CDP, Shasta | Replace Cottonwood Transformer Banks 1 & 4, replacement of six circuit breakers, addition of bus parallel circuit breaker, and upgrade the aging protection and control equipment at the Cottonwood substation. | Substation - Transformer | Upgrade/Retrofit | T.0004659 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-06 | 66 | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 26.1945 | NA | 230 ¦ 115 kV | 1002 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5768471 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 61 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-09-18 | 2022-12-31 | 2026-10-23 | Prioritization | FALSE | 15000 | NA | 973.2381 | 24977.6919 | 188.0115 | 143.9756 | 104.7318 | 62.7034 | 137.8143 | 2329.2543 | 13330.9856 | 1220.2548 | 0 | 0 | 0 | 952.3802 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 505 | San Ardo: Install 60kV Voltage Support |  |  | Monterey | The 60 kV system serving Oil Fields Substation and the large Chevron and Aera Energy oil production facilities in San Ardo, CA, could experience low voltages and a potential voltage collapse under certain outage situations. To strengthen the local 60 kV system a voltage support project has been proposed to install 10 MVAR of shunt capacitors at Oil Fields Substation. The CAISO supports the project and will approve it in their 2017-2018 Transmission Plan. | Substation - Voltage Support Equipment | New | TBD | Reliability | Voltage Support | NERC TPL Standards | 2024-03-04 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.44363 | NA | 60 kV | 76 | 5. Compliance/Commitments With Strong Safety Link | 19 | RBPPF - TBD | Yes | 5790100 | T.0004889 | San Ardo: Oil Fields Voltage Support | 4 | 61 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-01-04 | 2022-05-01 | 2029-06-26 | Prioritization | FALSE | $7,000 ¦ $10,000 | NA | 740.128 | 14709.6621 | 0 | 692.5677 | 47.5603 | 0 | 0 | 103.5395 | 700 | 8000 | 6500 | 700 | 200 | 740.128 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 506 | RMR: TRIMBLE-SAN JOSE B 115KV SERIES REA |  |  | San Jose, Santa Clara | The project proposes to install a 4-ohm series reactor at Trimble Substation on the termination of the Trimble – San Jose B 115 kV Line and upgrade line termination equipment and protection equipment at both Trimble and San Jose B Substations. This project was one of several projects that are needed to eliminate the need to have a reliability must run (RMR) contract with Calpine’s Metcalf Energy Center. | Substation - Voltage Support Equipment | New | NA | Economic | Voltage Support | NERC TPL Standards | 2024-02-06 | NA | Steady State Power Flow System Analysis | Wires - New T-Line Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8982 | NA | 115 kV | 180 | Not Available | NA | NA | NA | 5779919 | T.0003944 | Trimble-San Jose B 115kV Series Reactor | 2 | 61 | NA | 2018 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-26 | 2019-05-01 | 2019-02-25 | NA | FALSE | $6,000 ¦ $9,000 | NA | 3341.1184 | 3341.1184 | 1045.264 | -28.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3341.1184 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 3314.7775 | -28.4004 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 507 | OCEI - Oakland X 115kV Bus Upgrade |  |  | Oakland, Alameda | The project will install one bus-sectionalizing circuit breakers and associated switches on the 115kV bus at Oakland X Substation, which will improve the reliability and operational flexibility of the buses. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-14 | 31 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 1.1294 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | 5 | NA | NA | 5784219 | T.0004590 | OCEI -Oakland X 115kV Bus Upgrade | 1 | 61 | NA | 2017 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-08-03 | TBD | 2022-06-24 | NA | TRUE | $56,000 ¦ $76,000 | NA | 7305.3813 | 7305.3813 | 85.5897 | 496.5365 | 3308.2185 | 3340.2826 | 74.754 | 0 | 0 | 0 | 0 | 0 | 0 | 7305.3813 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 7023.5139 | 72.5163 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $300 Mil - $350 Mil ¦ Over $500 Mil ¦ $300 Mil - $350 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 508 | OCEI - Moraga 115kV Bus Upgrade |  |  | Orinda, Contra Costa | The project will install two bus-sectionalizing circuit breakers and one bus-tie breaker on the 115 kV buses at Moraga Substation, which will improve the reliability and operational flexibility of the buses. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-06 | 61 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 15.8714 | NA | 115 kV | Not Available | 8. Compliance/Commitments With Low Safety Risk | 1 | RBPPF - TBD | Yes | 5783340 | T.0004650 | OCEI-MORAGA 115KV BUS UPGRADE & BK 3 SWI | 2 | 61 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-11-16 | TBD | 2025-05-30 | Project Design | TRUE | $56,000 ¦ $76,000 | NA | 13082.6669 | 18934.6024 | 7.0163 | 162.3306 | 3341.7659 | 5653.5159 | 3720.9188 | 3193.2892 | 2796.2131 | 24.0478 | 0 | 0 | 0 | 12885.5476 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $300 Mil - $350 Mil ¦ Over $500 Mil ¦ $300 Mil - $350 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 509 | OCEI Moraga Bank 3 Switch Repl |  |  | Orinda, Contra Costa | The project will replace Bank 3 115kV switches 771, 773, 777, 779, 791, 793, & 795 which will improve the reliability and operational flexibility of the buses. | Substation - Switch | Upgrade/Retrofit | NA | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-06 | 60 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 15.8714 | NA | 115 kV | Not Available | 8. Compliance/Commitments With Low Safety Risk | 1 | NA | NA | 5789153 | T.0004650 | OCEI-MORAGA 115KV BUS UPGRADE & BK 3 SWI | 2 | 61 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-12-03 | TBD | 2022-06-30 | Prioritization | FALSE | $56,000 ¦ $76,000 | NA | 2211.8949 | 2211.8949 | 0 | 36.6876 | 778.6613 | 1383.4136 | 13.1324 | 0 | 0 | 0 | 0 | 0 | 0 | 2211.8949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1951.8856 | 11.6127 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $300 Mil - $350 Mil ¦ Over $500 Mil ¦ $300 Mil - $350 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 510 | BELLOTA: Install 230 kV Shunt Reactor |  |  | San Joaquin | This project proposes to install a 100 MVAR shunt reactor, extend the 230 kV bus to connect the reactor, and construct a new control building, which will mitigate high voltages in the PG&E’s Stockton Division. | Substation - Voltage Support Equipment | New | NA | Reliability | Voltage Support | NERC TPL Standards | 2024-03-01 | NA | Steady State Power Flow System Analysis | Wires - Voltage Support/Reactive Support Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 14.7513 | NA | 230 kV | 1002 | Not Available | NA | NA | NA | 5768582 | T.0001203 | Bellota 230 kV Shunt Reactor | 1 | 61 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2016 | FALSE | 2016 | NA | https://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-31 | 2020-05-01 | 2019-04-25 | NA | FALSE | $13,000 ¦ $19,000 | NA | 13935.8998 | 13935.8998 | 2476.2158 | 28.1676 | 1.1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13935.8998 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 13937.7234 | 28.1676 | 1.1023 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-Board-Approved2015-2016TransmissionPlan.pdf
| 511 | KERN OIL: Upgrade 115 KV Line |  |  | Oildale CDP, Kern | This project proposes to reconductor approximately 15 miles of 115 kV line from Kern to Kern Oil substations. In addition, the project will upgrade the limiting equipment at the Live Oak, Kern Oil, and Petrol substations. Load and generation balance is difficult in this area as demand increases and more private generation retires. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-03-04 | 62 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.2122 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5776126 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 9 | 61 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-01-08 | 2016-03-01 | 2027-03-31 | Prioritization | FALSE | $40,000 ¦ $65,000 | NA | 51.3909 | 5310.5521 | 41.4271 | 3.5956 | 0 | 0 | 0 | 0 | 25 | 50 | 1000 | 10000 | 1000 | 51.3909 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 512 | LIVE OAK: Upgrade 115 KV Line |  |  | Live Oak, Sutter | This project proposes to reconductor approximately 15 miles of 115 kV line from Kern to Kern Oil substations. In addition, the project will upgrade the limiting equipment at the Live Oak, Kern Oil, and Petrol substations. Load and generation balance is difficult in this area as demand increases and more private generation retires. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Line Termination | NERC TPL Standards | 2024-02-08 | 62 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 0.39793 | NA | 115 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5776125 | T.0002707 | Kern - Kern Oil 115 kV Line Reconductori | 9 | 61 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-01-08 | 2016-03-01 | 2027-03-31 | Prioritization | FALSE | $40,000 ¦ $65,000 | NA | 33.6369 | 1361.8765 | 23.158 | 2.6734 | 0 | 0 | 0 | 0 | 25 | 50 | 1000 | 5000 | 1000 | 33.6369 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 513 | TESLA: 230KV BUS REACTORS D - E |  |  | Alameda | This project proposes to replace the existing bus series reactors (8&16 ohms) in 230kV bus sections C, D & E with 36 ohms reactors and make the necessary connection changes. The proposed project will limit the fault duty to commonly used standard equipment in the industry to 63KA and comply with BES Transmission System Reliability and NERC requirements. | Substation - Voltage Support Equipment | Upgrade/Retrofit | T.0003456 | Reliability | Voltage Support | NERC TPL Standards | 2024-03-15 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | 230 kV | Not Available | 8. Compliance/Commitments With Low Safety Risk | 9 | NA | NA | 5784841 | T.0004673 | Tesla 230 kV Series Reactor Replacement | 2 | 61 | NA | 2019 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-04-19 | 2023-12-31 | 2023-06-14 | NA | TRUE | $24,000 ¦ $29,000 | NA | 16786.7261 | 16809.0357 | 23.9895 | 234.7528 | 1586.1892 | 9991.8688 | 4955.7861 | 16.4494 | 0 | 0 | 0 | 0 | 0 | 16792.5864 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 16023.1518 | 69.9714 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 514 | TESLA: 230KV BUS REACTORS C - D |  |  | Alameda | This project proposes to replace the existing bus series reactors (8&16 ohms) in 230kV bus sections C, D & E with 36 ohms reactors and make the necessary connection changes. The proposed project will limit the fault duty to commonly used standard equipment in the industry to 63KA and comply with BES Transmission System Reliability and NERC requirements. | Substation - Voltage Support Equipment | Upgrade/Retrofit | T.0003456 | Reliability | Voltage Support | NERC TPL Standards | 2024-03-15 | 57 | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5793942 | T.0004673 | Tesla 230 kV Series Reactor Replacement | 2 | 61 | NA | 2019 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-06-15 | 2023-12-31 | 2024-03-22 | NA | TRUE | $24,000 ¦ $29,000 | NA | 8015.8835 | 10278.3521 | 0 | 7.7109 | 22.0468 | 3746.2333 | 3223.6406 | 3278.7205 | 0 | 0 | 0 | 0 | 0 | 6999.6316 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 7836.1021 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 515 | South of Mesa Upgrade - Sub Voltage Sup |  |  | Lompoc, Santa Barbara | This project proposes to upgrade approximately 21.3 miles of conductor on the Sisquoc – Santa Ynez SW STA 115 kV Line, install 20 Mega Volt-ampere reactive (MVAR) shunt capacitors at Cabrillo Substation and install Remedial Action Scheme (RAS) (formerly known as Special Protection Scheme (SPS)) on the Sisquoc – Santa Ynez SW STA 115 kV Line. Completion of this project is needed to improve the electric transmission system reliability and operational flexibility in the Santa Barbara County. This project will be funded under Major Work Category (MWC) 60, Electric Transmission Line Capacity and 61, Electric Transmission Substation Capacity. The project has a Risk Informed Budget Allocation (RIBA) score of 137. The RIBA score is based on the impact and frequency of three risk categories: safety, reliability and environmental. | Substation - Voltage Support Equipment | New | TBD | Reliability | Voltage Support | NERC TPL Standards | 2024-02-07 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.3073 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 14 | RBPPF - TBD | Yes | 5785938 | T.0004832 | South Of Mesa Upgrade Project | 5 | 61 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-08-28 | 2023-12-31 | 2027-03-24 | Prioritization | FALSE | $29,600 ¦ $59,200 | NA | 351.3284 | 14825.0392 | 74.4337 | 277.2289 | -0.3342 | 0 | 0 | 0 | 150 | 1500 | 10000 | 10000 | 10000 | 351.3284 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 516 | BORDEN: Install 230 KV Single Bay BAAH |  |  | Madera | This project will connect two additional 230kV lines to Borden Substation from the Wilson-Gregg 230kV Line, which will improve voltage and service reliability, and provide full deliverability needs for new generation. A new Modular Protection and Automation Control (MPAC) building will also be needed to integrate the new equipment to the protection and control system, as well as upgrade terminal equipment at other substations. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 7.1874 | NA | 230 kV | 20 | Not Available | NA | NA | NA | 5767830 | T.0000924 | BORDEN 230 KV VOLTAGE SUPPORT (SUB) | 6 | 61 | 5747852 | 2010 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-12-11 | 2019-05-01 | 2019-02-06 | NA | FALSE | $15,000 ¦ $20,000 | NA | 16655.2669 | 16655.2669 | 2612.2519 | -45.5156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16655.2669 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 16088.4521 | -43.6666 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 517 | GREGG: Upgr Borden 230 KV Term Equip |  |  | Madera | This project will connect two additional 230kV lines to Borden Substation from the Wilson-Gregg 230kV Line, which will improve voltage and service reliability, and provide full deliverability needs for new generation. A new Modular Protection and Automation Control (MPAC) building will also be needed to integrate the new equipment to the protection and control system, as well as upgrade terminal equipment at other substations. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Line Termination | NERC TPL Standards | 2024-03-01 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 13.266 | NA | 230 kV | 20 | Not Available | NA | NA | NA | 5774008 | T.0000924 | BORDEN 230 KV VOLTAGE SUPPORT (SUB) | 6 | 61 | NA | 2010 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-04-18 | 2019-05-01 | 2019-02-07 | NA | FALSE | $15,000 ¦ $20,000 | NA | 1311.7015 | 1311.7015 | 269.0712 | 0.0976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1311.7015 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1126.9973 | 0.09759 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 518 | STOREY: Upgr Borden 230kV Term Equip |  |  | Madera | This project will connect two additional 230kV lines to Borden Substation from the Wilson-Gregg 230kV Line, which will improve voltage and service reliability, and provide full deliverability needs for new generation. A new Modular Protection and Automation Control (MPAC) building will also be needed to integrate the new equipment to the protection and control system, as well as upgrade terminal equipment at other substations. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Line Termination | NERC TPL Standards | 2024-02-07 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.4318 | NA | 230 kV | 20 | Not Available | NA | NA | NA | 5774009 | T.0000924 | BORDEN 230 KV VOLTAGE SUPPORT (SUB) | 6 | 61 | NA | 2010 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-05-23 | 2019-05-01 | 2019-03-12 | NA | FALSE | $15,000 ¦ $20,000 | NA | 2457.6171 | 2457.6171 | 575.1145 | 0.8067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2457.6171 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 2341.631 | 0.79352 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 519 | WILSON: Upgr Borden 230 KV Term Equip |  |  | Merced, Merced | This project will connect two additional 230kV lines to Borden Substation from the Wilson-Gregg 230kV Line, which will improve voltage and service reliability, and provide full deliverability needs for new generation. A new Modular Protection and Automation Control (MPAC) building will also be needed to integrate the new equipment to the protection and control system, as well as upgrade terminal equipment at other substations. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Line Termination | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 22.8151 | NA | 230 kV | 20 | Not Available | NA | NA | NA | 5774007 | T.0000924 | BORDEN 230 KV VOLTAGE SUPPORT (SUB) | 6 | 61 | NA | 2010 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-01-07 | 2019-05-01 | 2019-04-24 | NA | FALSE | $15,000 ¦ $20,000 | NA | 1032.8677 | 1032.8677 | 731.1498 | 0.2865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1032.8677 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 903.808 | 0.28652 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 520 | Gates:500kV Dynamic Voltage Support |  |  | Fresno | The reactive support study results noted above indicated that a +/- 800 MVAR dynamic reactive device at Gates Substation is required to address the high voltage and to improve dynamic performance. The recommendation is to approve installation of a total of +/-800 MVAR of dynamic reactive support on the Gates 500kV bus. Interconnect new Transmission Owner (TO) LS Power Grid California’s Orchard Substation STATCOM Facility to Gates 500kV Bus The scope of the proposed project is to install a minimum of two equally sized blocks of reactive devices independently connected to the 500kV system at PG&E’s Gates Substation to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power output over the complete range of the capability (unless the facility experiences a planned or forced outage). Sub-synchronous Resonance studies are required to be completed and any identified mitigation shall be implemented as part of this project. The project scope will include connecting two blocks of the STATCOM to two separate bays of Gates 500kV breaker-and-a-half (BAAH) bus. STATCOM connections will require both overhead and high-voltage underground cables. The high-level scope includes the following: • Install two 550kV, 4000 Amp 63KA breakers with associated switches and structures. • Relocate 500kV Bank 12 connection from BAAH Bay 2 to Bay 1 using GIB. • Build two transition stations (one inside the PG&E substation and one outside on PG&E property) to connect LS Power’s two STATCOM connections to PG&E 500kV bus. • Install overhead conductors, underground high-voltage cables and associated structures and switches to connect two STATCOMs • Relocate Bank 12 tertiary reactors controls and protection equipment from the 500kV control building to new Tertiary Reactors control building installed under Gates Bank 11 project. This is needed to create space in the 500kV control building for new breakers. • Install protection, controls, and IT equipment for new 500 kV breakers needed to support LS Power project. • Upgrade ground grid and grading as required. | Substation - Voltage Support Equipment | New | T.0001373 | Reliability | Voltage Support | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 500 kV | Not Available | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5784840 | T.0004672 | Gates:500Kv Dynamic Voltage Support | 5 | 61 | NA | 2019 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2023-04-03 | 2025-07-16 | 2024-11-15 | Workforce | TRUE | $210,000 ¦ $250,000 | NA | 32648.5032 | 43741.3305 | 37.0762 | 119.7151 | 564.8449 | 4474.5306 | 22504.2552 | 14769.9981 | 1270.9102 | 0 | 0 | 0 | 0 | 27700.4222 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 521 | Round Mtn:Modify 500kV Series CAPs 3&4 |  |  | Round Mountain CDP, Shasta | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | Reliability | Voltage Support | NERC TPL Standards | 2024-03-06 | 21 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Extreme Heat |  | NA | 29.1389 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5793954 | T.0006815 | Round Mountain Area 500kV Dynamic React | 5 | 61 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-13 | 2024-12-31 | 2024-12-20 | Workforce | TRUE | $160,000 ¦ $190,000 | NA | 11750.496 | 31566.1191 | 0 | 0 | 287.7999 | 268.3997 | 8809.1949 | 15797.8418 | 6053.0656 | 299.0802 | 6.7931 | 0 | 0 | 9365.3945 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 522 | Table Mtn:Modify 500kV Series Caps 1&2 |  |  | Butte | Interconnect new Transmission Owner (TO) LS Power Grid California’s Fern Road Substation STATCOM Facility to the Round Mountain-Table Mountain 500kV line Study results show that with 500 MVAR injection from Round Mountain dynamic reactive device, the voltage drop after PDCI outage will be only 18kV. The results also show that the voltage in the area ranged between 488kV and 558kV in the existing system, which is outside the acceptable range, especially on the high voltage. After implementing the Round Mountain +/-500 MVAR dynamic voltage support, the voltage in the area ranged between 503kV and 548kV which is within the acceptable range. The reactive device is to be installed in a minimum of two equally sized blocks independently connected to the 500kV to accommodate maintenance and contingencies of the reactive device. The reactive power support is required to provide continuous dynamic reactive power support over the complete range of the capability (unless the facility experienced a planned or forced outage). It can be by one of the following types of devices: Static VAR Compensator (SVC) with Thyristor Switched Capacitors (TSC), Static Synchronous Compensator (STATCOM), or Synchronous Condenser. The proposed project will route both 500kV lines between Round Mountain and Table Mountain to the new 500kV substation and reduce the Round Mountain 500kV Series Capacitor Banks 3 & 4 reactance. The scope will include the following: • Reduce Round Mountain 500kV Series Capacitors Banks 3 & 4 reactance from 18.58 ohms to 5.28 ohms. This will require modifying the equipment on the platform and upgrading protection and controls equipment in the control building. • Increase Table Mountain 500kV Series Capacitor Banks 1 & 2 reactance from 29.58 ohms to 36.32 ohms. This will require adding a new step on a new platform and all associated equipment (e.g., breakers, switches, etc.). Upgrade protection and controls in the control building. • Loop in Round Mountain-Table Mountain 500kV lines 1 & 2 to the new Fern Road Substation installed by LS Power. • Install control room, switches, and all associated equipment to connect Round Mountain-Table Mountain 500kV Lines 1 & 2 to LS Power Fern Road Substation. | Substation - Voltage Support Equipment | Upgrade/Retrofit | NA | Reliability | Voltage Support | NERC TPL Standards | 2024-03-06 | 22 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5793953 | T.0006815 | Round Mountain Area 500kV Dynamic React | 5 | 61 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | TRUE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2023-02-15 | 2024-12-31 | 2024-12-24 | Workforce | TRUE | $160,000 ¦ $190,000 | NA | 39329.32 | 65562.1443 | 0 | 0 | 240.0967 | 13447.4834 | 21073.7509 | 29229.1483 | 824.8295 | 74.9151 | 4.6476 | 0 | 0 | 34761.3311 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% ¦ LS Power | NA | TBD | Granted 100% Abandoned Plant Recovery Incentive | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [TPP Phase 3] Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Voltage Support/Reactive Support Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 523 | Los Esteros-Nortech 115kV Series Reactor |  |  | San Jose, Santa Clara | To address the near-term critical, category P1 contingency driven issues, the ISO is recommending approval of adding series compensation devices on the Los Esteros-Nortech 115 kV line. As part of this scope, 2 Ohms reactor will be added on the Los Esteros-Nortech 115kV Line at Los Esteros Substation. | Substation - Voltage Support Equipment | New | TBD | Reliability | Voltage Support | NERC TPL Standards | 2024-03-12 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5802781 | T.0008698 | Los Esteros-Nortech 115kV Series Reactor | 3 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-06-18 | 2023-06-01 | 2025-12-10 | Prioritization | TRUE | $10,000 ¦ $15,000 | NA | 269.3497 | 9209.9603 | 0 | 0 | 0 | 0 | 172.3946 | 2452.6081 | 6401.8553 | 200 | 0 | 0 | 0 | 172.3946 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 524 | BAKERSFIELD: Upgrade 230 KV BAAH |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Line Termination | Upgrade/Retrofit | T.0000220 ¦ T.0003350 ¦ T.0000980 | Reliability | Line Termination | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.6195 | NA | 230 kV | 764 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5774239 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 61 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2012 | FALSE | 2012 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-10-01 | 2013-05-01 | 2020-02-07 | Prioritization | FALSE | $32,000 ¦ $44,000 | NA | 2379.1395 | 2379.1395 | 1564.1543 | 574.8372 | 14.3856 | 3.2364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2379.1395 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 1647.3056 | 549.4939 | 13.7513 | 3.0937 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 525 | MARYSVILLE: Convert to Ring BUS |  |  | Marysville, Yuba | Upgrade the Marysville 60kV Bus to a five-circuit-breaker ring bus configuration. This project will resolve current configuration issues, address reliability concerns, and replace deteriorating equipment at Marysville Substation. The upgrades will also position the substation for future system reinforcement or interconnection projects, and provide enhanced automation and additional controls of PG&E’s transmission system. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-02-17 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.73781 | NA | 60 kV | 180 | 8. Compliance/Commitments With Low Safety Risk | Not Available | NA | NA | 5767818 | T.0000911 | MARYSVILLE 60kV Bus Upgrade | 2 | 61 | 5766635 | 2006 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-08-01 | 2018-02-08 | 2020-04-29 | Workforce | FALSE | 20340 | NA | 21938.2652 | 21938.2652 | 6654.7536 | 5148.5095 | 241.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21938.2652 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 20772.2202 | 286.7925 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 526 | STOREY SUB, NEW 230KV CIRCUIT BRE |  |  | Madera | Capacity increase at Storey Substation in Yosemite Division. This project proposes to replace Storey Bank 1 transformer with a new 230/12 kV - 60 MVA three-phase transformer with LTC. Install one new 230 kV high-side circuit breaker, extend the existing distribution bus 1/bus 2 structure, and install three new distribution circuit breakers, three new distribution feeder outlets, and three 12 kV overhead distribution circuits from the substation to the customer sites. | Substation - Circuit Breaker | New | TBD | Reliability | Substation Capacity | NA | 2024-02-02 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.27429 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801542 | T.0007270 | Storey Sub, Rep Bank & Install Feeders | 1 | 61 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-11-25 | NA | 2026-08-18 | NA | FALSE | NA | NA | 31.0679 | 31.0679 | 0 | 0 | 0 | 0 | 29.9201 | 0.3661 | 1500 | 0 | 0 | 0 | 0 | 30.7018 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 527 | Henrietta: Henrietta BK 3 Replacement |  |  | Kings | Replace Henrietta 230/115 kV Bank 3 | Substation - Transformer | Replace | TBD | Policy | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-05 | 18 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 7.0079 | NA | 230 ¦ 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806921 | T.0009553 | Henrietta 230/115 kV Bank 3 Replacement | 1 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-01 | 2032-12-31 | 2027-06-01 | NA | FALSE | 20000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 7000 | 3000 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-F-Board-Approved_2022-2023_Transmission-Plan.pdf
| 528 | Cortina: Replace Bank 1 with 2 banks |  |  | Colusa | Replace the Cortina 230/115/60 kV Transformer 1 with one 230/115 kV and one 115/60 kV transformers. Upgrade bus differential relay, as needed. The annual reliability assessment identified thermal overload issues for NERC Category contingencies that involve loss of Cortina 230/115 kV Transformer 4. For an outage of Cortina 230/115 kV Transformer 4, Cortina 230/115/60 kV Transformer 1 will have to serve the Cortina 60 kV load and the Cortina 115 kV load and North Geysers area via Cortina 115/60 kV Transformer 5. The most severe of such contingencies may lead to loading of Cortina 230/115/60 kV Transformer 1 up to 137.5% of its summer emergency rating. Currently, there is an Operating Procedure to radialize the 60 kV and 115 kV loads by opening Cortina 115/60 KV Transformer 5 pre-contingency in order to prevent the Cortina 230/115/60 kV Transformer 1 overload post-contingency. However, planning and real time operating analysis show that opening Cortina 115/60 kV Bank 5 under normal condition could cause loss of generation violations, such as losing Wadham generator could overload Cortina 230/115/60 kV Transformer 1 up to 106.2% of its summer emergency rating. Therefore, this Operating Procedure cannot longer be used as a viable long-term solution under peak loading conditions. | Substation - Transformer | Replace | TBD | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-07 | 54 | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.7436 | NA | 230 ¦ 115 ¦ 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806847 | T.0009531 | Cortina 230/115/60 kV Transformer Bank No. 1 Replacement Project | 1 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-10-01 | 2027-05-01 | 2028-06-01 | Prioritization | FALSE | $21,000 ¦ $42,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 12000 | 8000 | 1000 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 529 | Mesa: 230/115kV Spare Transformer |  |  | Nipomo CDP, San Luis Obispo | This project proposes to install a new 420Mva 230/115kV spare transformer to provide capacity to perform maintenance on existing Transformers 2 and 3, the Morro Bay-Mesa, and the Diablo Canyon PP 230kV lines | Substation - Transformer | New | TBD | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 10.5414 | NA | 230 ¦ 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807200 | T.0009596 | Mesa 230/115kV Spare Transformer | 1 | 61 | EX113238 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | 2023 | NA | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-01-15 | 2032-12-31 | 2028-04-01 | NA | FALSE | 24000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 3000 | 5000 | 3000 | 200 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/Appendix-C-Board-Approved-2022-2023-Transmission-Plan.pdf
| 530 | TRANS_ Sub_WEBER Replace Bank 3 and 4 |  |  | San Joaquin | This project proposes to install one new 60/12 kV, 30 MVA three-phase transformer, one new 12 kV bus 1/bus 2 structure with four breaker bays, one bus-tie breaker and two feeder breakers, and one new Weber distribution circuit outside of the substation by installing new underground lines and tying into existing 12 kV system. This work will eliminate a 1 percent overload of Weber Bank 6, a 55 percent overload of the Weber 1110 circuit. These overloads are forecasted to occur between the summer of 2024 to 2025 and are the result of a new business application of 10.17 MW from Niagara Bottling STK3. | Substation - Circuit Breaker | New | NA | Reliability | Transformer Addition/Replacement | NA | 2024-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 6.1366 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801881 | T.0008215 | WEBER: Repl Bank 3 & 4 and Inst Feeders | 1 | 61 | NA | 2022 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-06-01 | 2026-06-01 | 2026-04-01 | NA | FALSE | 10700 | NA | 0 | 17.3964 | 0 | 0 | 0 | 0 | 0 | 7.805 | 1060.6108 | 453.2413 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 531 | Atlantic: Install 230/60 kV Bank |  |  | Atascadero, San Luis Obispo ¦ San Luis Obispo | This project will install a 200 MVA, 3-phase 230/60 kV transformer with LTC. Below is the high-level scope of this project: 1. Install a 200 MVA, 3-phase 230/60 kV transformer with LTC 2. Connect the new transformer to 230kV BAAH. This will require one new 230kV breaker and relocating other 230kV connections. 3. Install 60kV breaker to connect the new transformer. Modify 60kV bus as necessary to connect the new bank. 4. Modify the protection scheme as necessary to support this project. 5. Upgrade SPCC and the ground grid as necessa This project would mitigate the Atlantic 60 kV system high voltage issue. It will also increase operating flexibility, load serving capability, and customer reliability. | Substation - Transformer | New | TBD | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-27 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | 230 ¦ 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806786 | T.0009529 | Atlantic 230/60 kV transformer voltage regulator | 1 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-03-01 | 2026-01-01 | 2027-12-01 | Prioritization | FALSE | $5,000 ¦ $10,000 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 5000 | 3000 | 500 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 532 | Table Mtn: Install second 500/230kV Bank |  |  | Butte | This project will support installation of the second 500/230kV transformer at Table Mountain substation. The second 500/230kV transformer is needed to address the 230kV high voltage issue in the North-Valley region. The proposed high-level scope of work for this project includes: • Install three single-phase 374MVA transformers and the associated structures. • Relocate terminal connections as necessary to connect both 500kV banks in separate bays. • Install tertiary shunt reactors for the new bank as required. • Install Bus tie breaker in Bus Section E. • Upgrade protection scheme as required to implement the project scope. • Modify RAS scheme if required. Additional studies may be required to determine this. | Substation - Transformer | New | TBD | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | 500 ¦ 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806785 | T.0009530 | Table Mountain Second 500/230 kV Transformer | 1 | 61 | EX112236 | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-07-01 | 2027-01-01 | 2028-06-01 | Prioritization | FALSE | $38,400 ¦ $76,800 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 5000 | 17000 | 16000 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 533 | Gold Hill: Add 230/115 kV Transformer |  |  | Folsom, Sacramento | A Bus section Fault (P2-1) overload on Missouri Flats – Gold Hill Lines 115 kV were identified in last year’s analysis and was addressed by switching load in the area. This year’s result show that given the load growth in the area, the P2-1 overload shows up in the long term. In order to mitigate the issue, the CAISO recommendeds the installation of a third 230/115 kV transformer at Gold Hill Substation | Substation - Transformer | New | TBD | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-28 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 12.8702 | NA | 230 ¦ 115 kV | Not Available | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5787179 | T.0004950 | Gold Hill: Add 230/115 kV Transformer | 1 | 61 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-02-15 | 2022-12-31 | 2028-06-26 | Prioritization | FALSE | 22000 | NA | 7.6996 | 19950.798 | 2.1574 | 3.1218 | 1.3221 | 0.4802 | 0.5281 | 106.4624 | 1720.138 | 1781.8481 | 9700.1953 | 6242.7241 | 0 | 7.6096 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 534 | PEASE: Install BK 5 |  |  | Sutter | Install a second 115/60kV transformer and upgrade the 115kV and 60kV buses at Pease Substation. | Substation - Transformer | New | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-02-08 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.6809 | NA | 115 ¦ 60 kV | 76 | 8. Compliance/Commitments With Low Safety Risk | 14 | NA | NA | 5756140 | T.0000598 | Pease Transformer Add & Bus Upgrade | 3 | 61 | NA | 2013 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-07 | 2016-05-31 | 2020-12-08 | Material | TRUE | $25,000 ¦ $35,000 | NA | 12873.5389 | 12873.5389 | 4898.3724 | 1565.2922 | 885.5154 | 492.6064 | 562.2293 | 0.5274 | 0 | 0 | 0 | 0 | 0 | 12873.0115 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 10516.0833 | 879.0681 | 472.8102 | 539.6354 | 1.2173 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 535 | PEASE: Reconfigure 115 KV Bus to BAAH |  |  | Sutter | Install a second 115/60kV transformer and upgrade the 115kV and 60kV buses at Pease Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NERC TPL Standards | 2024-02-08 | 10 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.6809 | NA | 115 kV | 76 | 8. Compliance/Commitments With Low Safety Risk | 14 | NA | NA | 5768208 | T.0000598 | Pease Transformer Add & Bus Upgrade | 3 | 61 | NA | 2013 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-07-25 | 2016-05-31 | 2020-12-10 | Workforce | TRUE | $25,000 ¦ $35,000 | NA | 31540.4434 | 32105.6895 | 6265.0549 | 5461.4266 | 2322.647 | 1122.319 | 1995.9522 | 642.3045 | 238.1662 | 0 | 0 | 0 | 0 | 31225.2188 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 24826.7644 | 2184.7926 | 1072.9739 | 1908.1959 | 306.5579 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Non-Wires - Large Scale Energy Alternative [Alternative Solutions and Costs - Costs] $50 Mil – $75 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 536 | WILSON: Install 115 KV Transformer |  |  | Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Transformer | New | T.0001381 ¦ T.0002231 | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 22.8151 | NA | 115 kV | 58 | 8. Compliance/Commitments With Low Safety Risk | 7 | RBPPF - TBD | Yes | 5781260 | T.0004116 | WILSON: 115 kV ARP - BAAH | 6 | 61 | NA | 2012 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-05-07 | 2015-05-01 | 2028-01-28 | Prioritization | FALSE | $35,000 ¦ $45,000 | NA | 98.6039 | 8493.3368 | 48.232 | 42.4115 | 3.5219 | 0 | 0 | 204.4072 | 3126.1294 | 3203.267 | 1759.8713 | 24.6437 | 0 | 98.6039 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 537 | GATES BK 12 500/230KV TRANSFORMER |  |  | Fresno | Installing the Gates 500/230 kV Transformer No. 2 is needed to provide deliverability to renewable generation in the Fresno area and additional flexibility for pumping operations at HPSP. The scope of work includes the following: • Install Gates 500/230 kV Transformer No. 2; • Install half-bay (two breakers and disconnect switches) on the existing 500 kV BAAH bus; • Connect transformer to 500 kV and 230 kV BAAH buses; • Upgrade overstressed circuit breakers and terminal equipment, as needed; and install low-side reactors; • Repair collapsed trench and associated work. | Substation - Transformer | New | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 500 ¦ 230 kV | 318 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5787467 | T.0003388 | GATES 500kV Bank 12 Installation | 3 | 61 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-01-31 | 2017-05-01 | 2020-04-22 | Prioritization | FALSE | $75,000 ¦ $85,000 | NA | 45681.9759 | 45681.9759 | 41441.3018 | 4248.9215 | -8.2474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45681.9759 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 45690.2233 | -8.2474 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $250 Mil – $300 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 538 | Gates Bk 12 Conduit/Trench Failure Repl |  |  | Fresno | Installing the Gates 500/230 kV Transformer No. 2 is needed to provide deliverability to renewable generation in the Fresno area and additional flexibility for pumping operations at HPSP. The scope of work includes the following: • Install Gates 500/230 kV Transformer No. 2; • Install half-bay (two breakers and disconnect switches) on the existing 500 kV BAAH bus; • Connect transformer to 500 kV and 230 kV BAAH buses; • Upgrade overstressed circuit breakers and terminal equipment, as needed; and install low-side reactors; • Repair collapsed trench and associated work. | Other - Civil | Replace | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 77.6619 | NA | 500 ¦ 230 kV | 318 | 5. Compliance/Commitments With Strong Safety Link | Not Available | NA | NA | 5787766 | T.0003388 | GATES 500kV Bank 12 Installation | 3 | 61 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-08-10 | 2017-05-01 | 2021-10-14 | Prioritization | FALSE | $75,000 ¦ $85,000 | NA | 10591.4225 | 10591.4225 | 22.4022 | 2361.934 | 7038.343 | 1458.4316 | -289.6883 | 0 | 0 | 0 | 0 | 0 | 0 | 10591.4225 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 8703.3913 | 1342.5637 | -266.6735 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $250 Mil – $300 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 539 | GATES: BK 12 ADDITION 500/230 KV TRANSFO |  |  | Fresno | Installing the Gates 500/230 kV Transformer No. 2 is needed to provide deliverability to renewable generation in the Fresno area and additional flexibility for pumping operations at HPSP. The scope of work includes the following: • Install Gates 500/230 kV Transformer No. 2; • Install half-bay (two breakers and disconnect switches) on the existing 500 kV BAAH bus; • Connect transformer to 500 kV and 230 kV BAAH buses; • Upgrade overstressed circuit breakers and terminal equipment, as needed; and install low-side reactors; • Repair collapsed trench and associated work. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-08 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 ¦ 230 kV | 318 | 5a. Mitigates System Wide Failure Risk | NA | NA | NA | 5768212 | T.0003388 | GATES 500kV Bank 12 Installation | 3 | 61 | 5751202 | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2013 | FALSE | 2013 | NA | https://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-01-31 | 2017-05-01 | 2019-11-13 | Prioritization | FALSE | $75,000 ¦ $85,000 | NA | 4330.3387 | 4330.3387 | -11629.0896 | 2175.6672 | 388.2181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4330.3387 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | -11629.0896 | 2175.6672 | 388.2181 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - New T-Line Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $250 Mil – $300 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2012-2013TransmissionPlan.pdf
| 540 | Carbona Sub, Replace Bank 2 |  |  | San Joaquin | Replace Carbona Transformer Bank 2 with a larger transformer, upgrade 60kV equipment, replace the Carbona Bank 1 foundation, replace the entire 12kV bus with switchgear, and establish a new distribution circuit outside of the substation. The capacity increase is needed to eliminate a 30 percent normal overload of Carbona Bank 1, a 33 percent normal overload of the Carbona 1104 distribution feeder, and a 38 percent normal overload of the Tracy 1102 distribution feeder. These overloads are forecasted to occur by summer 2022 and are the result of several large new business applications including Amazon and Home Depot warehouse-distribution centers. Transmission Substation Work (MWC 61) under this Project – Planning Order 5797580: • Install 60 kV main bus comprised of 2300Al bare conductor. • Install two 60 kV, 1200 A circuit breakers and associated disconnect switches. • Install one 60 kV, 1200 motor-operated air switch (MOAS) to sectionalize the 60 kV bus. • Install current and potential transformers and surge arresters as required for system protection. • Install 60kV control and protection racks inside the new switchgear building. | Substation - Circuit Breaker | New | NA | Reliability | Transformer Addition/Replacement | NA | 2024-03-06 | NA | NA | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.27151 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5797580 | T.0007094 | Carbona Substation Bank 2 Replacement | 4 | 61 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2022-12-05 | 2023-09-30 | 2025-05-06 | Prioritization | TRUE | 32000 | NA | 1697.3018 | 3233.5925 | 0 | 0 | 5.3002 | 435.7673 | 1134.6219 | 756.8171 | 843.3685 | 0 | 0 | 0 | 0 | 1575.6894 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 541 | CASCADE: Install BK 2 Phase 1 |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Transformer | New | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-02-12 | 23 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | NA | 115 ¦ 60 kV | 58 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5777641 | T.0000651 | Cascade Substation Upgrade | 10 | 61 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2019-07-09 | 2014-03-01 | 2024-12-27 | Prioritization | TRUE | $20,000 ¦ $30,000 | NA | 14525.895 | 17457.3735 | 3348.6147 | 2718.3135 | 4609.8332 | 1073.484 | 1173.9983 | 2543.1822 | 604.5961 | 0 | 0 | 0 | 0 | 14305.3071 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 542 | CASCADE: Install BK 2 Phase 2 |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Transformer | New | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-02-12 | NA | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | NA | 115 ¦ 60 kV | 58 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5777642 | T.0000651 | Cascade Substation Upgrade | 10 | 61 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2011 | FALSE | 2011 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-03-03 | 2014-03-01 | 2025-04-18 | Prioritization | TRUE | $20,000 ¦ $30,000 | NA | 2292.698 | 3502.7668 | 311.0568 | 145.5715 | 1236.1694 | 235.5049 | 238.5812 | 287.2744 | 948.653 | 0 | 0 | 0 | 0 | 2266.8394 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 543 | PITTSBURG: Install 230/115KV TRANSFORMER |  |  | Pittsburg, Contra Costa | This project proposes to add a third Pittsburg 230/115 kV Transformer with a rating of 420 MVA. Completion of this project will provide adequate transmission capacity to enable safe and reliable electric service to electric customers served by Pittsburg Substation | Substation - Transformer | New | TBD | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-05 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.72358 | NA | 115 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 14 | RBPPF - TBD | Yes | 5768148 | T.0000946 | PITTSBURG: Install 230/115KV TRANSFORMER | 1 | 61 | 5738798 | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2025-08-20 | 2011-05-01 | 2026-07-17 | Prioritization | FALSE | $10,000 ¦ $20,000 | NA | 3395.0251 | 23996.4848 | 110.113 | 1709.6948 | 975.1644 | 223.7535 | 315.6961 | 1887.8246 | 7199.061 | 1083.4532 | 0 | 0 | 0 | 3352.7453 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 544 | San Miguel Sub Expansion & 70kV Ringbus |  |  | San Miguel CDP, San Luis Obispo | This project proposes to install a second transformer bank at San Miguel Substation to eliminate a forecasted 16 percent overload of San Miguel Transformer Bank 1, a 4 percent overload of the San Miguel 1104 distribution feeder, and a 13 percent overload of the Paso Robles 1107 distribution feeder. These overloads are forecasted to occur under normal conditions (N-0) during the summer months of 2024 and cannot be alleviated by load transfer because of depleted area capacity. Transmission Substation Work (MWC 61): • Expand the yard at San Miguel Substation for an ultimate 70kV six-breaker ring bus to accommodate a third distribution transformer, future 70kV transmission VAR support, and two 70kV line positions. • Modify the San Miguel 70kV bus and 70kV equipment to accommodate a second transformer . • The MWC 61 project will partially fund the yard expansion and creation of an Ultimate General Arrangement Outdoors Plan. | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Load Growth | Bus Upgrade | NA | 2024-02-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.77704 | NA | 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798129 | T.0006955 | San Miguel Install Bank 3 | 1 | 61 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-01-02 | NA | 2025-09-26 | NA | TRUE | NA | NA | 446.2176 | 7737.0804 | 0 | 0 | 0 | 186.4175 | 150.8462 | 671.5172 | 6418.0973 | 1633.633 | 0 | 0 | 0 | 337.2637 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 545 | Green Valley - Install Bank 4 |  |  | Interlaken CDP, Santa Cruz | This project proposes to install one new 115/21 kV, 45 MVA three-phase transformer, one new 21 kV bus 1/bus 2 structure with four breaker bays, one bus-tie breaker and two feeder breakers, two new 21 kV distribution feeder outlets, two new Green Valley distribution circuits outside of the substation by installing new lines, reconductoring existing 21 kV sections and voltage conversion of existing 4 kV circuits. This work will eliminate a 14 percent overload of Green Valley Bank 2 and a 11 percent overload of Green Valley Bank 3. These overloads are forecasted to occur by summer 2024 and are the result of multiple new business applications, including 18 large cannabis cultivation greenhouses to be built on available agricultural land surrounding the City of Watsonville Transmission Substation Work (MWC 61) • Install one 115kV breaker and two switches at existing Bay #2 of the existing Breaker-and-a-Half (BAAH) 115 kV bus at Green Valley Substation to complete the BAAH arrangement | Substation - Circuit Breaker | Upgrade/Retrofit | TBD | Reliability | Transformer Addition/Replacement | NA | 2024-02-14 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.6121 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799591 | T.0007278 | Green Valley_Replace Bank 3 | 1 | 61 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-06-13 | NA | 2025-08-21 | NA | TRUE | NA | NA | 175.4646 | 3565.8109 | 0 | 0 | 0 | 130.177 | 32.2844 | 811.4782 | 2543.734 | 97.7019 | 0 | 0 | 0 | 162.4614 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 546 | Mountain View: Repl SW 157 & 159 w/CBs |  |  | Mountain View, Santa Clara | This project proposes to replace existing substation transformer Bank 1 in order to eliminate a growing deficiency on both Mountain View Bank 1 and Mountain View Bank 3. Replace two existing 115 kV motor-operated switches (157 and 159) with circuit breakers. Presently any bus or bank fault will trip both existing 115 kV breakers CB 112 & CB 122. By adding two additional 115 kV circuit breakers, only the faulted bus or bank would experience an outage. This additional scope will improve the looped bus, provide a logical path to an ultimate five-element 115 kV ring bus, improve bank clearances and increase reliability by reducing momentary outages to the 39,141 existing customers on Mountain View Substation. Transmission Substation Work (MWC 61): • Replace 115 kV circuit switchers 159 and 157 with 115 kV circuit breakers. • Extend existing control building will to accommodate the new relays for the breakers. with 115 kV circuit breakers. • Replace existing CB 112 with new circuit breaker/disconnect switches. | Substation - Circuit Breaker | Upgrade/Retrofit | TBD | Reliability | Substation Capacity | NA | 2024-02-09 | 59 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8224 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798023 | T.0005971 | Mountain View - Replace Bank 1 | 2 | 61 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-09-04 | NA | 2025-11-13 | NA | TRUE | NA | NA | 275.3225 | 4884.5359 | 0 | 0 | 36.571 | 166.6344 | 44.46 | 1449.913 | 3157.2912 | 815.4357 | 8.2331 | 0 | 0 | 247.6654 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 547 | East Marysville: Inst Transformer |  |  | Marysville, Yuba | This project will entail the following: 1.Loop the Pease – Marysville 60 kV Line into E. Marysville Substation. 2.Install a 200MVA, 115/60kV (LTC) transformer at E. Marysville Substation. 3.Upgrade the terminal equipment at E. Marysville Substation. 4.Install 25 MVAR of voltage support at the Pease Substation 115 kV bus. | Substation - Transformer | New | TBD | Economic | Transformer Addition/Replacement | NERC TPL Standards | 2024-02-01 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 1.8811 | NA | 115 ¦ 60 kV | Not Available | 8. Compliance/Commitments With Low Safety Risk | 14 | RBPPF - TBD | Yes | 5785381 | T.0004728 | East Marysville 115/60 kV Project | 2 | 61 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | 2019 | NA | https://www.caiso.com/Documents/ISO_BoardApproved-2018-2019_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-01-04 | 2022-12-31 | 2028-01-17 | Prioritization | FALSE | $26,000 ¦ $32,000 | NA | 325.9514 | 4993.3155 | 0.187 | 253.8941 | 25.3737 | 20.3285 | 22.356 | 30.2553 | 99.8665 | 2351.1296 | 1643.0841 | 318.4138 | 0 | 322.1394 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2018-2019TransmissionPlan.pdf
| 548 | GLENN: Replace BK 1 |  |  | Glenn | This project will replace GLENN Bank 1 with a new 230/60 kV, 200 MVA transformer with a Load Tap Changer (LTC) and parallel scheme under MWC-61 | Substation - Transformer | Upgrade/Retrofit | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-13 | 61 | Steady State Power Flow System Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.7152 | NA | 230 ¦ 60 kV | 45 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5757478 | T.0000817 | Glenn: Replace 230/60kV Bank 1 | 2 | 61 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | 2014 | FALSE | 2014 | NA | https://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2020-04-30 | 2018-03-01 | 2024-05-30 | Workforce | TRUE | $5,000 ¦ $10,000 | NA | 18233.6022 | 20619.29 | 3940.6891 | 7953.9977 | 2151.6674 | 745.3453 | 1038.8603 | 3641.6093 | 0 | 0 | 0 | 0 | 0 | 16977.6807 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 17926.8047 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixCBoardApproved2013-2014TransmissionPlanJuly162014.pdf
| 549 | COOLEY LANDING: Install BK 2 |  |  | East Palo Alto, San Mateo | This project will replace the existing Cooley Landing Transformer No. 2 with a 200 MVA, three-phase transformer. Completion of this project is needed to provide additional transmission capacity and reliability to serve electric customers in southern San Mateo County. This project will be funded under Major Work Category (MWC) 61, Electric Transmission Substation Capacity. The project has a combined Risk Informed Budget Allocation (RIBA) score of 45. The RIBA score is based on the impact and frequency of three risk categories: safety, reliability, and environmental. This project will improve service reliability for the south Peninsula area by allowing the transmission system to be more networked. It will also increase maintenance and operational flexibility. Replacing Table Mountain No. 1 Transformer bank will provide voltage and generation support, and will maintain Pacific AC Intertie Transfer capability. | Substation - Transformer | Upgrade/Retrofit | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-06 | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.1512 | NA | 115 ¦ 60 kV | 45 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5747999 | T.0000249 | COOLEY LANDING 115/60 KV TRANSFORMER #2 | 1 | 61 | NA | 2012 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | 2008 | FALSE | 2008 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-01-05 | 2010-05-31 | 2019-04-08 | Clearances | FALSE | $10,000 ¦ $20,000 | NA | 16168.7539 | 16168.7539 | 4416.3145 | 146.2513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16168.7539 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 14945.2141 | 133.988 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 550 | REPLACE VACA DIXON BANK #5 |  |  | Solano | This project will replace Vaca Dixon Bank 5, existing four single-phase transformers, with one three-phase 115/60 kV, 200 MVA, as well as reconductoring the low-side all the way to the 60 kV bus to support up to 3000 A and installing two 60 kV single-phase station service voltage transformers and removal of 115/60 kV single-phase transformers, lattice structures, 60 kV breakers, and switches. | Substation - Transformer | Upgrade/Retrofit | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-12 | 21 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 115 ¦ 60 kV | 137 | 8. Compliance/Commitments With Low Safety Risk | 4 | NA | NA | 5782080 | T.0005914 | Vaca Dixon - Replace Bank 5 | 1 | 61 | NA | 2012 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-07-26 | 2023-12-01 | 2022-08-11 | NA | TRUE | 15000 | NA | 13919.5802 | 13938.1338 | 198.4064 | 865.0674 | 6781.8064 | 5883.8701 | 129.6684 | 22.9856 | 0 | 0 | 0 | 0 | 0 | 13915.1482 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 13006.3693 | 122.1557 | 9.4224 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 551 | RIO OSO: Install BK 1 and BK 2 |  |  | Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Transformer | Upgrade/Retrofit | NA | Reliability | Transformer Addition/Replacement | NERC TPL Standards | 2024-03-04 | 69 | Steady State Power Flow System Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.3219 | NA | 230 ¦ 115 kV | 318 | 8. Compliance/Commitments With Low Safety Risk | Not Available | RBPPF - TBD | Yes | 5726234 | T.0000614 | Rio Oso Substation Upgrade | 12 | 61 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | 2007 | FALSE | 2007 | NA | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request. | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2022-07-05 | 2009-05-01 | 2025-05-21 | Prioritization | TRUE | $10,000 ¦ $20,000 | NA | 13715.8651 | 18752.9652 | 737.7239 | 672.8212 | 5866.8701 | -2159.2006 | 2104.3251 | 2891.4158 | 2123.7033 | 25.7318 | 0 | 0 | 0 | 13397.9548 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements. [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachments. These are available on request as the CAISO does not not archive Transmission Plans prior to 2013.
| 552 | Metcalf 230/115 kV Transformers Circuit Breaker Addition |  |  | Santa Clara | To address the near-term critical, category P2 contingency driven issues, the ISO is recommending approval of adding parallel breakers to each of the 230/115kV bank 1, 2 & 3 at Metcalf 230kV Substation so that the three Metcalf 230/115 kV transformer banks can connect to both Metcalf 230kV Bus1 and Bus 2. | Substation - Circuit Breaker | New | TBD | Reliability | Substation Capacity | NERC TPL Standards | 2024-03-13 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 230 ¦ 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803919 | T.0008980 | Metcalf 230 / 115 kV Transformers Circuit Breaker Addition | 1 | 61 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | 2022 | NA | https://www.caiso.com/Documents/ISOBoardApproved-2021-2022TransmissionPlan.pdf | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-09-22 | 2026-12-31 | 2026-04-02 | NA | FALSE | $900 ¦ $1,350 | NA | 86.4286 | 3660.2019 | 0 | 0 | 0 | 0 | 15.8875 | 280.9611 | 2000 | 4000 | 1000 | 0 | 0 | 15.8875 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved-2021-2022TransmissionPlan.pdf
| 553 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | Other [See Notes] | NERC CIP Compliance | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 180 | Not Available | NA | NA | NA | 5780178 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | 2014 | 2014 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2019-01-02 | NA | FALSE | NA | NA | 1306.4307 | 1306.4307 | 4.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1306.4307 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 | 1306.4307 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 7 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 554 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | Other [See Notes] | NERC CIP Compliance | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 236 | Not Available | Not Available | NA | NA | 5782699 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | 2014 | 2014 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2020-03-31 | NA | FALSE | 6000 | NA | 6648.5443 | 6648.5443 | 4402.275 | 1918.3597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6648.5443 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 6648.5443 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 7 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 555 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | Other [See Notes] | NERC CIP Compliance | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 1780 | Not Available | Not Available | NA | NA | 5782500 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | 2014 | 2014 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1045.4173 | 1045.4173 | 851.878 | 194.1922 | -0.6528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1045.4173 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 851.878 | 194.1922 | -0.65279 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 7 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 556 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | Other [See Notes] | NERC CIP Compliance | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5788426 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | 2014 | 2014 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 3967.4371 | 3967.4371 | 68.4439 | 3883.6683 | 15.3249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3967.4371 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 3967.4371 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 6 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 557 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | Other [See Notes] | NERC CIP Compliance | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 236 | Not Available | Not Available | NA | NA | 5780172 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | 2014 | 2014 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | 3693 | NA | 5814.5207 | 5814.5207 | 3236.4742 | 421.1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5814.5207 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 5393.4038 | 239.4787 | 181.6382 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 3 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 558 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | Other [See Notes] | NERC CIP Compliance | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 45 | Not Available | Not Available | NA | NA | 5783698 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | 2014 | 2014 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | OAI | NA | FALSE | NA | NA | 1695.1522 | 1695.1522 | 667.6766 | 1022.9307 | 4.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1695.1522 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 1695.1522 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 7 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 559 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Cybersecurity | Upgrade/Retrofit | NA | Other [See Notes] | NERC CIP Compliance | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5786102 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | 2014 | 2014 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-04-28 | 2020-06-12 | 2021-01-06 | Workforce | FALSE | 549 | NA | 1188.3913 | 1188.3913 | 225.2491 | 946.8334 | 16.3089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1188.3913 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 1188.3913 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Cybersecurity [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 2 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 560 | ET PI - Phase 1 |  |  | NA | A data warehouse named ET DW was built as the work output of this Planning Order. The ET DW helps improve Transmission Operations processes to minimize customer outage and to mitigate wildfire risk. It also helps to improve planning and asset strategy processes that ultimately leads to lower cost of operation and reduced wildfire risk. The ET DW also helps with meeting compliance requirements such as FERC Order 881. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5788320 | NA | NA | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-07-19 | NA | TRUE | NA | NA | 1781.0577 | 1781.0577 | 0 | 744.3259 | 758.6595 | 215.6293 | 62.443 | 0 | 0 | 0 | 0 | 0 | 0 | 1781.0577 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1781.0577 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 561 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 975 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5775350 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-03-03 | NA | TRUE | NA | NA | 8142.786 | 8142.786 | 1503.008 | 1818.8639 | 2049.0964 | 1640.1073 | 288.1272 | 0 | 0 | 0 | 0 | 0 | 0 | 8142.786 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1148.9258 | 243.8808 | 6749.9581 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 562 | SynchroPhasor Implementation |  |  | NA | Bucket for SynchroPhasor Implementation. PG&E will be working together with Alstom for the EMS software upgrades, and GE for PMU/PDC firmware upgrades. Since the technology is in the early stages of usage there are risks in obtaining the required functionality within the time frame of the grant; which has a fixed end date. Solano County. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 45 | Not Available | Not Available | NA | NA | 5760306 | NA | NA | NA | 63 | NA | 2013 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | 8850 | NA | 9186.0795 | 9186.0795 | 6.6788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9186.0795 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2024 | 584.9195 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 563 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | EX112100 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 564 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 1 | No | EX112101 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 565 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | EX112102 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 566 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | Ex112750 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 567 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | Ex112758 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 568 | CAISO Tie-Line |  |  | NA | Install PMUs on CAISO tie-lines with other Balancing Authorities (BAs) at approximately fifteen substations to monitor frequency response and facilitate compliance with NERC BAL-003 and other standards. This work is at the direction of the CAISO | Other - Operations Tech | New | NA | Reliability | System Operations | NERC BAL Compliance | NA | NA | Steady State Power Flow System Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | 5. Compliance / Commitments with Strong Safety Link | Not Available | Tier 5 | No | 5792854 | NA | NA | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2020-12-01 | OAI | NA | FALSE | 11000 | NA | 294.0311 | 294.0311 | 0 | 0 | 13.134 | 88.7935 | 132.0563 | 27.9202 | 0 | 0 | 0 | 0 | 0 | 266.111 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC BAL-003 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 569 | EMS Application Projects Cap |  |  | NA | Project for EMS application enhancements needed to enhance the quality of network applications and EMS application functions. This includes enhancements to PG&E's network modeling processes, data mapping enhancements, and data enhancements to improve the quality of state estimator and contingency analysis. Both real-time and study EMS applications will be enhanced through this project. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5801898 | NA | NA | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | NA | NA | 2024-06-30 | NA | TRUE | NA | NA | 1370.3915 | 1370.3915 | 0 | 0 | 0 | 849.3666 | 504.3501 | 16.6748 | 0 | 0 | 0 | 0 | 0 | 1353.7167 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 703.1053 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 570 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Replace | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | Ex112755 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 15000 | 5000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 571 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | Ex112749 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | 2025-01-01 | NA | 2033-12-31 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 572 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | 6 | Lifecycle Replacement Analysis | Non-Wires | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807118 | T.0009554 | Electric Transmission Operations Upgrade | 3 | 63 | NA | 2023 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2028-12-01 | 2024-01-31 | NA | FALSE | 31800 | NA | 2778.5528 | 2778.5528 | 0 | 0 | 0 | 0 | 27.4469 | 2751.106 | 0 | 0 | 0 | 0 | 0 | 27.4468 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 573 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | 6 | Lifecycle Replacement Analysis | Non-Wires | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5808113 | T.0009554 | Electric Transmission Operations Upgrade | 3 | 63 | NA | 2023 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2028-12-01 | 2024-02-29 | NA | FALSE | 31800 | NA | 1027.9586 | 1027.9586 | 0 | 0 | 0 | 0 | 0 | 1027.9586 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 574 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5547904 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | 1200 | NA | 1180.1634 | 1180.1634 | 0 | 0 | 0 | 1161.1628 | 19.0007 | 0 | 0 | 0 | 0 | 0 | 0 | 1180.1634 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 468.1573 | 712.0061 | 0 | 0% | NA | NA | NA | 100% | 0% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 575 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 45 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5504279 | T.0001667 | Electric Transmission Operations Upgrade | 1 | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 4167.4346 | 4167.4346 | 1217.1012 | 644.8363 | 334.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4167.4346 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 16.1598 | 27.6425 | 2702.1497 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 576 | OBI ET - CAP |  |  | NA | Bucket for ET PI Data Analytics | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5792856 | NA | NA | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 9022.7967 | 17864.0471 | 0 | 0 | 674.5554 | 2357.5174 | 4595.1239 | 10236.8503 | 0 | 5500 | 4500 | 4500 | 4500 | 7627.1968 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 577 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | T.0006190 | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 213 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5782618 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | 2019 | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | NA | NA | OAI | NA | TRUE | 2500 | NA | 1900.7272 | 1900.7272 | 681.6633 | 1656.0546 | 398.1719 | -855.9931 | 20.8305 | 0 | 0 | 0 | 0 | 0 | 0 | 1900.7272 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 139.6862 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 578 | Emergent Work |  |  | NA | Bucket for system operations emergent work | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5792857 | NA | NA | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 894.7561 | 1012.0496 | 0 | 0 | 894.7561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 894.7561 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 ¦ 2026 | 0 | 0 | 0 | 894.7561 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 579 | SYNCHROPHASOR SUSTAINMNT AND PI APP PROJ |  |  | NA | Bucket for the Synchrophasor PI Project, which puts into service the next phase of evolution for PG&E’s synchrophasor system to more effectively support the growing needs of PG&E’s Phasor Data community. This project will implement a synchrophasor data archival system leveraging OSIsoft PI, a standard industry software tool which PG&E is already fully licensed. The ability to leverage synchrophasor data has been requested by several PG&E consumers, to be used for multiple business applications relating to compliance and operational integrity, such as: • NERC PRC-002-2 R5 - PMUs fulfill the role of DDRs (Dynamic Data Recorders) for post-event analysis required at specific locations within the transmission grid • NERC MOD-033 – Requires the Transmission Operator to provide transmission system recorded data for post-event analysis upon request • CPUC Advice Letter 5571-E – Requires frequency monitoring and quarterly reporting to determine frequency impacts on operation of inverter-based resources • Asset Performance Center – Provide PMU data for APC use cases such as equipment monitoring for preventive maintenance, big data analytics, and others | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 45 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5780185 | NA | NA | NA | 63 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | 896 | NA | 1335.8018 | 1335.8018 | 113.663 | 409.6875 | 368.6261 | 35.9549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1335.8018 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 1335.8018 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 580 | T-SCADA/Congruitive |  |  | NA | Bucket for Transmission SCADA | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5805507 | NA | NA | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1015.1218 | 1015.1218 | 0 | 0 | 0 | 0 | 901.2399 | 113.8819 | 0 | 0 | 0 | 0 | 0 | 901.2399 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 548.2044 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 581 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5544571 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1196.4973 | 1196.4973 | 0 | 0 | 364.553 | 799.1749 | 32.7694 | 0 | 0 | 0 | 0 | 0 | 0 | 1196.4973 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1196.4972 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 582 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 741 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5752873 | T.0004406 | Electric Transmission Operations Upgrade | 2 | 63 | NA | 2013 | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 17974.9969 | 17974.9969 | 1645.8731 | 1007.6514 | 322.2714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17974.9969 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 14567.8615 | 2471.8649 | 322.2714 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 583 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5795759 | T.0004406 | Electric Transmission Operations Upgrade | 1 | 63 | NA | 2013 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-01 | 2020-12-31 | 2022-01-28 | Project Design | FALSE | 5022 | NA | 7047.2061 | 7047.2061 | 2358.4148 | 2756.4582 | 1511.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7047.2061 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 5936.5689 | 1110.6372 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 584 | PMU_CAISO_ROUND MOUNTAIN |  |  | Round Mountain CDP, Shasta | The scope of the project includes installation of PMUs at Round Mountain for tie lines to external Balancing authorities, testing, validation of data quality and availability at CAISO, and integration of PMU data into the Energy Management System (EMS) to be utilized for situational awareness displays, state estimation, and as backups to existing real-time data. The transmission lines to be monitored include Malin – Round Mountain #1 and Malin - Round Mountain #2 500kV lines. The installation of the PMUs will provide CAISO with improved data that will support system frequency response assessments and their compliance with BAL-003-1.1. In addition, PG&E has objectives to achieve through the implementation of these PMUs. PG&E’s objectives include an improved model validation process as well as enhanced situational awareness data and tools for use in Transmission Operations. | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | System Operations | NERC BAL Compliance | 2024-03-06 | NA | Steady State Power Flow System Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5800680 | T.0008264 | PMU_CAISO_ROUND MOUNTAIN | 1 | 63 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-11-06 | 2020-12-01 | 2025-01-03 | Prioritization | TRUE | 11000 | NA | 102.0822 | 1038.2608 | 0 | 0 | 0 | 19.1905 | 51.2844 | 898.7872 | 68.9987 | 0 | 0 | 0 | 0 | 70.4749 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC BAL-003 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. For Steady State Power Flow System Analysis results, please also refer to annual CAISO Transmission Plan & corresponding attachment: https://www.caiso.com/Documents/AppendixC-BoardApproved2017-2018TransmissionPlan.pdf
| 585 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5795758 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-01 | 2020-12-30 | 2022-03-29 | Project Design | FALSE | 1858 | NA | 1495.9747 | 1495.9747 | 0 | 627.7966 | 781.5098 | 86.6684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1495.9747 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 1495.9747 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 586 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Removal | T.0006261 | Other [See Notes] | System Operations | NA | NA | 14 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.2173 | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5795881 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 3 | 2024-02-01 | 2025-12-31 | 2024-07-17 | NA | TRUE | 182000 | NA | 805.9649 | 1058.2334 | 0 | 0 | 0 | 44.7383 | 722.4976 | 290.9976 | 0 | 0 | 0 | 0 | 0 | 767.2359 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 587 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | T.0006261 | Other [See Notes] | System Operations | NA | 2024-02-08 | 14 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.3205 | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5801822 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-06-25 | 2025-12-31 | 2026-07-16 | Project Design | FALSE | 182000 | NA | 876.6004 | 33638.8462 | 0 | 0 | 0 | 11.3639 | 557.5518 | 14000.5325 | 9271 | 10732 | 128 | 0 | 0 | 568.9157 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 588 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | T.0006261 | Other [See Notes] | System Operations | NA | NA | 14 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5798442 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-04-04 | 2025-12-31 | 2025-10-31 | NA | TRUE | 182000 | NA | 302.256 | 2151.4576 | 0 | 0 | 5.4438 | 190.7815 | 79.529 | 353.9803 | 1429.5539 | 0 | 0 | 0 | 0 | 275.7543 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 589 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | T.0006261 | Other [See Notes] | System Operations | NA | 2024-02-14 | 14 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.96252 | NA | 115 ¦ 60 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5795040 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-12-17 | 2025-12-31 | 2027-07-12 | Project Design | TRUE | 182000 | NA | 458.9286 | 1828.197 | 0 | 0 | 79.9481 | 246.3805 | 121.0231 | 41.3205 | 108 | 0 | 0 | 0 | 0 | 447.3518 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 590 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | T.0006261 | Other [See Notes] | System Operations | NA | NA | 14 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.4936 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5795061 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-12-30 | 2025-12-31 | 2025-12-31 | NA | TRUE | 182000 | NA | 390.6535 | 1782.5314 | 0 | 0 | 104.4802 | 208.7661 | 49.9606 | 117.7769 | 190.4419 | 8 | 0 | 0 | 0 | 363.2068 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 591 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | T.0006261 | Other [See Notes] | System Operations | NA | NA | 14 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5792159 | T.0006190 | Electric Transmission Operations Upgrade | 8 | 63 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2023-04-14 | 2025-12-31 | 2024-04-26 | NA | TRUE | 182000 | NA | 17865.1503 | 20373.0272 | 0 | 140.3507 | 1448.0441 | 4526.0009 | 10215.1634 | 3928.6828 | 114.7853 | 0 | 0 | 0 | 0 | 16329.5591 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Location/Route Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ $125 Mil - $150 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 592 | FERC Order 881 |  |  | NA | This project provides compliance for FERC NOPR 881 and Improved transmission capability due to Ambient-Adjusted ratings based on ambient temperature and other weather related measurements. Improved real-time situational awareness because EMS tools would be utilizing highly accurate, near real-time determined facility ratings, needed for safe and reliable management of the PG&E Transmission Grid | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5800498 | NA | NA | NA | 63 | NA | NA | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 3414.201 | 3414.201 | 0 | 0 | 0 | 4.1093 | 3135.5247 | 274.5672 | 0 | 0 | 0 | 0 | 0 | 3139.6338 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2338.5852 | 942.739 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [NERC/WECC/CAISO Standard/Requirement/Contingency] FERC 881 [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 593 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5548665 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1227.7169 | 1227.7169 | 0 | 0 | 0 | 1006.0584 | 221.6585 | 0 | 0 | 12800 | 3000 | 3300 | 0 | 1227.7169 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1227.7169 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 594 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Relocate | NA | Other [See Notes] | System Operations | NA | NA | 14 | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5791860 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | 2020 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2021-01-01 | 2022-12-31 | 2024-06-30 | Material | TRUE | 2873 | NA | 4987.4416 | 4987.4416 | 0 | 441.8424 | 870.0172 | 940.7095 | 2393.213 | 341.6594 | 0 | 0 | 0 | 0 | 0 | 4645.7822 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 134.2036 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 595 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-03-14 | 26 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.55624 | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5797502 | T.0007421 | Electric Transmission Operations Upgrade | 3 | 63 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2021-09-01 | 2021-12-31 | 2025-10-28 | Project Design | TRUE | 900 | NA | 2286.6339 | 3301.8073 | 0 | 0 | 377.7657 | 1414.029 | 494.8391 | 139.1737 | 848.0673 | 0 | 0 | 0 | 0 | 2286.6339 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 596 | Electric Transmission Operations Upgrade |  |  |  |  | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5799031 | NA | Electric Transmission Operations Upgrade | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2022-01-01 | NA | 2026-12-31 | NA | FALSE | NA | NA | 2492.8559 | 2492.8559 | 0 | 0 | 9.628 | 777.0494 | 1425.399 | 280.7796 | 0 | 2000 | 2000 | 2000 | 2000 | 2212.0763 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 597 | TSRP_NS_SUB_CORTINA |  |  | Colusa | Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS e-terra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, with system-wide migration by December 2029, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover installation of new IT equipment, EMS database development and testing. Scope does not cover removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring change to this premise will require scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-03-07 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.7436 | NA | NA | Not Available | 3. Emergency Preparedness | Not Available | RBPPF - TBD | No | 5786915 | T.0005033 | TSRP_NS _SUB_CORTINA | 1 | 63 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-09-21 | 2024-03-31 | 2024-02-05 | NA | TRUE | 629 | NA | 1161.4274 | 1178.6763 | 0 | 297.8716 | 478.9771 | 85.7174 | 194.1906 | 121.9196 | 0 | 0 | 0 | 0 | 0 | 1056.7567 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 1081.5391 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 598 | TSRP_SV_T-LINE_AUBERRY |  |  | Auberry CDP, Fresno ¦ Fresno | Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS e-terra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, with system-wide migration by December 2029, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover installation of new IT equipment, EMS database development and testing. Scope does not cover removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring change to this premise will require scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-03-19 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5542081 | T.0006703 | TSRP_SV_T-LINE_AUBERRY | 1 | 63 | NA | NA | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-11-07 | 2024-12-01 | 2023-11-07 | NA | TRUE | 965 | NA | 1633.229 | 1633.229 | 0 | 0 | 0 | 12.8575 | 1620.1427 | 0.2289 | 0 | 0 | 0 | 0 | 0 | 1633.0001 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 12.8575 | 1620.1427 | 0.22891 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 599 | TSRP Programmatic Forecast |  |  | NA | Forecast placeholder for Transmission SCADA Replacement Program | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5763261 | NA | NA | NA | 63 | NA | 2016 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33000 | 32000 | 30000 | 20000 | 20000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 600 | TSRP PMO |  |  | NA | Provide program management support for TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5536661 | T.0004903 | TSRP PMO | 1 | 63 | NA | 2016 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2021-12-31 | NA | FALSE | NA | NA | 3742.2077 | 3742.2077 | 218.2391 | 3251.8075 | 3885.7761 | -5137.4379 | 3582.0723 | -2058.2494 | 0 | 0 | 0 | 0 | 0 | 5800.4571 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 109.1196 | 1625.9037 | 1942.8881 | -2568.7197 | 1791.0358 | -907.9204 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 601 | TSRP SV - IT CROSS CONNECTS |  |  | NA | As part of the Transmission SCADA Replacement Program (TSRP) scope, the program needs to assure a secure, reliable, TCP/IP connection from all substations into PG&E’s secure data network. “TSRP SV - IT CROSS CONNECTS” addresses those substations in the South Valley (SV) of PG&E’s service territory (Fresno and Kern Divisions.) Specifically, this order supports those substations within SV that already have TCP/IP communications path including routers and switches installed. TSRP SV - IT CROSS CONNECTS scope includes installing communication cabling and ancillary IT equipment within these substations to assure reliable data flow from the SCADA monitoring/control devices with the substation out to PG&Es secure data network. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5787478 | T.0005137 | Tsrp Sv - It Cross Connects | 1 | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1060.8233 | 1090.6284 | 0 | 26.8172 | 84.2114 | 509.883 | 383.106 | 86.6108 | 0 | 0 | 0 | 0 | 0 | 1004.0176 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 602 | Video Wall Controller Upgrade |  |  | NA | Bucket for Video Wall Controller Upgrade | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5788318 | T.0005299 | TSRP_SV_SUB_KERN OIL | 1 | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2115.8721 | 2115.8721 | 0 | 1695.8307 | 355.9005 | 64.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2115.8721 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 2115.8722 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 603 | TSRP_SV_SUB_MC CALL |  |  | Fresno | Electric Operations (EO) has requested the migration of six Electric Transmission (ET) operating jurisdictions of existing SCADA platform onto the existing EMS – E-Terra to enhance ET operability, efficiency, security, and safety. Initiated October 2014, with system-wide migration by March 2026, this program identified as Transmission SCADA Replacement Program (TSRP) have been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture; prove telecommunication circuits connections to EMS via SCADA RTU, and addition of T-Line switch data and control. Once completed, Electric Transmission OPS will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. South Valley is one of the six operation jurisdictions and is chosen to undergo this TSRP SCADA migration plan. Targeted are various substations that currently possess a form of legacy telecommunication circuit connection to RTSCADA, with transmission equipment assets. Among these targeted substations is Tranquility Switching Station. Targeted are substations with Human – Machine Interface platform (HMI). For these stations, each HMI platform within the station will require the installation of (2) new Eaton SG-4260 devices which will replace the existing DELL servers and successfully migrate all devices to the new Eaton SG-4260. These requirements cover the work associated with TSRP at McCall Substation. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-03-08 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 16.2494 | NA | NA | Not Available | 5a. Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | No | 5788123 | T.0005313 | TSRP_SV_SUB_MC CALL | 1 | 63 | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2022-08-30 | 2022-06-30 | 2024-05-10 | Workforce | TRUE | 743 | NA | 1522.0666 | 1694.907 | 0 | 0 | 108.7374 | 337.8508 | 719.4248 | 528.894 | 0 | 0 | 0 | 0 | 0 | 1166.013 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 604 | TSRP_NS_SUB_COTTONWOOD |  |  | Cottonwood CDP, Shasta | Migrate off of the existing SCADA platform and onto the existing EMS to improve ET operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within ET Transmission System Operators currently use both RTscada and EMS. The use of two control consoles for RTscada and EMS increases unsafe conditions for field personnel and customers because the existing processes and safeguards are inadequate for operation of two independent SCADA control systems. The current interaction between RTscada and EMS requires completely manual processes to ensure that the separate databases are aligned. Alignment between the two databases is critical, as this is the only way to ensure that the correct device operates in the field when a System Operator initiates a SCADA control. Moving to a single system will reduce the risk of inadvertent operation of field devices due to database misalignment. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-03-06 | NA | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 26.1945 | NA | NA | Not Available | 3. Emergency Preparedness | Not Available | RBPPF - TBD | No | 5786934 | T.0005015 | TSRP_NS_SUB_COTTONWOOD | 1 | 63 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-03-01 | 2022-12-31 | 2024-02-15 | Prioritization | TRUE | 1600 | NA | 2072.3424 | 2073.7044 | 0 | 265.4433 | 26.8221 | 85.4558 | 1418.3395 | 277.6438 | 0 | 0 | 0 | 0 | 0 | 1796.0606 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 1919.3525 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 605 | TSRP_NBS_SUB_IGNACIO |  |  | Novato, Marin | TSRP will migrate off of the current Supervisory Control and Data Acquisition (SCADA) system and onto the existing Energy Management System (EMS). Migrate off of the existing SCADA platform and onto the existing EMS to improve ET operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within ET. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-03-14 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.9486 | NA | 230 ¦ 115 ¦ 60 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5788812 | T.0005575 | TSRP_NBS_SUB_IGNACIO | 1 | 63 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-06 | 2020-12-17 | 2020-12-17 | NA | FALSE | 1100 | NA | 1056.1415 | 1061.8587 | 0 | 963.0655 | 77.3 | 8.7959 | 6.2544 | 6.443 | 0 | 0 | 0 | 0 | 0 | 1055.4157 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 953.3274 | 8.0392 | 5.7164 | 1.6767 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 606 | TSRP_NBS_SUB_LAKEVILLE |  |  | Sonoma | TSRP will migrate off of the current Supervisory Control and Data Acquisition (SCADA) system and onto the existing Energy Management System (EMS). Migrate off of the existing SCADA platform and onto the existing EMS to improve ET operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within ET. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-03-11 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 14.7021 | NA | 230 ¦ 115 ¦ 60 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5788814 | T.0005547 | TSRP_NBS_SUB_LAKEVILLE | 1 | 63 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-06 | 2020-12-31 | 2020-12-15 | NA | FALSE | 1600 | NA | 2106.7652 | 2106.7652 | 0 | 2034.4422 | 47.9046 | 24.2084 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 2106.7652 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 1873.8015 | 43.7228 | 22.0845 | 0.19155 | 0 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 607 | TSRP_NBS_SUB_VACA DIXON |  |  | Solano | TSRP will migrate off of the current Supervisory Control and Data Acquisition (SCADA) system and onto the existing Energy Management System (EMS). Migrate off of the existing SCADA platform and onto the existing EMS to improve ET operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within ET. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-03-12 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 42.1076 | NA | 500 ¦ 230 ¦ 115 ¦ 60 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5788839 | T.0005544 | TSRP_NBS_SUB_VACA DIXON | 1 | 63 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-06 | 2020-12-31 | 2021-11-17 | Prioritization | TRUE | 1400 | NA | 1797.5511 | 1822.5369 | 0 | 1389.5551 | 389.1974 | 12.7649 | 5.3078 | 25.7029 | 0 | 0 | 0 | 0 | 0 | 1796.8253 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 1642.9946 | 4.8294 | 1.5545 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 608 | TSRP_NS_SUB_TABLE MOUNTAIN |  |  | Butte | TSRP will migrate off of the current Supervisory Control and Data Acquisition (SCADA) system and onto the existing Energy Management System (EMS). Migrate off of the existing SCADA platform and onto the existing EMS to improve ET operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within ET. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-03-06 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | NA | Not Available | 3. Emergency Preparedness | 5 | NA | NA | 5786910 | T.0005084 | TSRP_NS_SUB_TABLE MOUNTAIN | 1 | 63 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-01-04 | 2024-12-31 | 2023-10-20 | NA | TRUE | 1600 | NA | 1300.4818 | 1309.8191 | 4.425 | 119.14 | 272.8298 | 487.7439 | 308.0108 | 117.6697 | 0 | 0 | 0 | 0 | 0 | 1192.1494 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1119.7021 | 221.1734 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 609 | TSRP_NBS_SUB_BASALT |  |  | Napa | TSRP work on BASALT. Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS e-terra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, with system-wide migration by December 2029, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover installation of new IT equipment, EMS database development and testing. Scope does not cover removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring change to this premise will require scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-02-08 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.63831 | NA | NA | Not Available | 3. Emergency Preparedness | 18 | Tier 5 | No | 5788931 | T.0005607 | TSRP_NBS_SUB_BASALT | 1 | 63 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-06-23 | 2023-03-31 | 2026-01-22 | Prioritization | FALSE | 496 | NA | 499.009 | 2173.7633 | 0 | 80.4835 | 43.5795 | 214.5204 | 149.1707 | 987.0095 | 0 | 0 | 0 | 0 | 0 | 487.7541 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 610 | TSRP_NBS_SUB_HIGHWAY |  |  | American Canyon, Napa | TSRP work on Highway: Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS e-terra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, with system-wide migration by December 2029, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover installation of new IT equipment, EMS database development and testing. Scope does not cover removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring change to this premise will require scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-02-07 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.71048 | NA | NA | Not Available | 3. Emergency Preparedness | 9 | Tier 5 | No | 5788810 | T.0005573 | TSRP_NBS_SUB_HIGHWAY | 1 | 63 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2024-01-15 | 2022-03-31 | 2024-11-18 | Prioritization | TRUE | 312 | NA | 831.7418 | 1019.9843 | 0 | 112.8538 | 104.8009 | 262.2198 | 209.2937 | 328.8751 | 1.941 | 0 | 0 | 0 | 0 | 689.1681 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 611 | TSRP_NS_SUB_MAPLE CREEK |  |  | Humboldt | TSRP work on Maple Creek: Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS e-terra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, with system-wide migration by December 2029, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover installation of new IT equipment, EMS database development and testing. Scope does not cover removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring change to this premise will require scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-03-05 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.27362 | NA | 60 kV | Not Available | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5787009 | T.0004997 | TSRP_NS_SUB_MAPLE CREEK | 1 | 63 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-05-15 | 2022-12-31 | 2025-10-31 | Prioritization | TRUE | 603 | NA | 759.9867 | 1421.7669 | 0 | 226.5478 | 33.8308 | 100.0718 | 372.5871 | 486.4643 | 202.2652 | 0 | 0 | 0 | 0 | 733.0375 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 612 | TSRP_NS_SUB_NEWBURG |  |  | Fortuna, Humboldt | TSRP work on NEWBURG. Electric Operations’ (EO) requested to migrate six Electric Transmission (ET) operating jurisdictions from the existing RTSCADA platform and onto the existing EMS E-Tierra platform to enhance ET operability, efficiency, security, and safety. Initiated in October 2014, with system-wide migration by December 2029, this program, identified as Transmission SCADA Replacement Program (TSRP), has been created to design, procure, and install the necessary communication circuits and paths to eliminate the EMS dependency on the RTSCADA system. This migration program includes revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. Once completed, Electric Transmission Ops will then be able to fully operate EMS exclusively for its supervisory control and data acquisition. Scope items cover installation of new IT equipment, EMS database development and testing. Scope does not cover removal of existing legacy lease circuit connections to RTSCADA; as some circuits will remain in service to provide SCADA visibility to Distribution equipment assets; whereas other circuits will be removed. Any design requiring change to this premise will require scope change request. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | 2024-02-08 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.2161 | NA | 60 kV | Not Available | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5787015 | T.0005102 | TSRP NS _SUB_NEWBURG | 1 | 63 | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2026-02-17 | 2024-03-31 | 2026-10-30 | Prioritization | FALSE | 606 | NA | 703.1801 | 1308.8928 | 22.7718 | 68.2149 | 313.9514 | 209.0384 | 79.766 | 52.236 | 0 | 0 | 0 | 0 | 0 | 693.7425 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 613 | TSRP NBS IT Cross Connects |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5777377 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-06-18 | 2024-01-10 | Workforce | FALSE | 225000 | NA | 1795.867 | 1795.867 | 664.7553 | 202.6884 | 282.8784 | 243.6013 | 200.1293 | 5.5398 | 0 | 0 | 0 | 0 | 0 | 1790.3272 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 1785.4367 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 614 | TSRP NBS IT New MPLS |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5777401 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-07-10 | 2024-01-10 | Workforce | FALSE | 225000 | NA | 4180.146 | 4422.6675 | 1239.2026 | 444.3733 | 313.657 | 333.686 | 319.8999 | 254.7722 | 0 | 0 | 0 | 0 | 0 | 4167.8953 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 4153.3304 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 615 | TSRP NBS IT Other Sites |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5778582 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-07-10 | 2024-01-10 | Workforce | FALSE | 225000 | NA | 4098.261 | 4098.261 | 837.7002 | 447.2139 | 334.92 | 330.4898 | 349.9442 | 23.0773 | 0 | 0 | 0 | 0 | 0 | 4075.1837 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 4085.5343 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 616 | TSRP NBS IT T-Line Switches |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | NA | NA | 5778581 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-07-10 | 2022-03-22 | Workforce | FALSE | 225000 | NA | 2162.2337 | 2162.2337 | 935.2387 | 270.5141 | 169.7272 | 33.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2162.2337 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 2145.7899 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 617 | TSRP NBS IT VSAT |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5777403 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-07-10 | 2024-01-10 | Workforce | TRUE | 225000 | NA | 1633.3884 | 1633.3884 | 692.6902 | 137.3459 | 167.1893 | 151.763 | 123.4326 | 4.784 | 0 | 0 | 0 | 0 | 0 | 1628.6044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 1621.8939 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 618 | TSRP NS - IT NEW MPLS |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | No | 5783802 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-07-10 | 2024-01-11 | Workforce | FALSE | 225000 | NA | 2624.4966 | 2624.4966 | 537.2369 | 817.6208 | 602.8265 | 428.5147 | 227.4815 | 10.8164 | 0 | 0 | 0 | 0 | 0 | 2613.6802 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 2624.4966 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 619 | TSRP NS - IT OTHER SITES |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5782304 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-07-10 | 2024-01-11 | Workforce | FALSE | 225000 | NA | 5615.375 | 5615.375 | 2538.1317 | 800.8572 | 849.2666 | 482.3716 | 500.288 | 16.5632 | 0 | 0 | 0 | 0 | 0 | 5598.8118 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 5615.375 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 620 | TSRP NS - IT VSAT |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | 3. Emergency Preparedness | Not Available | RBPPF - TBD | No | 5783803 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-06-18 | 2024-01-11 | Workforce | FALSE | 225000 | NA | 1055.7362 | 1055.7362 | 437.0288 | 182.3665 | 157.528 | 120.4581 | 152.9266 | 5.4282 | 0 | 0 | 0 | 0 | 0 | 1050.308 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 1055.7362 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 621 | TSRP-NORTH BAY SIERRA ET COMM- |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | NA | NA | 5777404 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-07-10 | 2020-03-27 | Workforce | FALSE | 225000 | NA | 2130.5004 | 2130.5004 | 1833.0425 | -384.6449 | 24.7454 | 2.3067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2130.5004 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 2048.7087 | 24.0363 | 2.2406 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 622 | TSRP-NORTH BAY SIERRA ET MPAC/H |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | NA | NA | 5777402 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-07-10 | 2021-02-01 | Workforce | FALSE | 225000 | NA | 1760.3055 | 1760.3055 | 1762.5973 | -1366.5767 | 16.3922 | 24.2266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1760.3055 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 1672.7002 | 15.8243 | 23.3873 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 623 | TSRP-NORTH BAY SIERRA ET NEW CO |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | NA | NA | 5777398 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-07-10 | 2020-03-27 | Workforce | FALSE | 225000 | NA | 3195.9789 | 3195.9789 | 2844.584 | -2494.359 | 26.0868 | 4.3083 | 1.5511 | 0 | 0 | 0 | 0 | 0 | 0 | 3195.9789 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 3021.3358 | 24.8862 | 4.11 | 1.4797 | 0 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 624 | TSRP-NORTH BAY SIERRA ET NEW CO |  |  | NA | Upgrade communications infrastructure in North State (Humboldt, Round Mtn,Table Mtn jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 2095 | 3. Emergency Preparedness | Not Available | NA | NA | 5777400 | T.0003414 | EMS/SCADA COMMUNICATION SEPERATION | 22 | 63 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-05 | 2019-07-10 | 2020-03-27 | Workforce | FALSE | 225000 | NA | 3503.4937 | 3503.4937 | 3809.5334 | -1680.4582 | 55.6639 | 20.8576 | 10.1885 | 0 | 0 | 0 | 0 | 0 | 0 | 3503.4937 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 3267.2178 | 53.1876 | 19.9297 | 9.7352 | 0 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 625 | TSRP SV - IT NEW MPLS |  |  | NA | Upgrade communications infrastructure in South Valley (Midway, Fresno jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5787479 | T.0005138 | Tsrp Sv - It New Mpls | 1 | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 2 | 2022-01-02 | NA | 2024-12-31 | NA | TRUE | NA | NA | 1557.3219 | 1609.4055 | 0 | 61.4098 | 39.8787 | 959.3022 | 420.3891 | 128.4257 | 0 | 0 | 0 | 0 | 0 | 1480.9798 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 626 | TSRP SV - IT OTHER SITES |  |  | NA | Upgrade communications infrastructure in South Valley (Midway, Fresno jurisdcitions) in support of TSRP. TSRP will transition Transmission Operations (TO) monitoring and control off the existing SCADA platform and onto the EMS platform. This transition improves operability, efficiency, and safety by replacing the antiquated SCADA platform with a more capable, comprehensive platform that is already in use within TO. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | 5a. Mitigates System Wide Failure Risk | Not Available | NA | NA | 5787481 | T.0005140 | TSRP SV - IT OTHER SITES | 1 | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-08-31 | NA | 2023-12-31 | NA | TRUE | NA | NA | 1396.193 | 1492.8939 | 0 | 105.5257 | 558.5454 | 100.5209 | 497.5014 | 187.1784 | 0 | 0 | 0 | 0 | 0 | 1262.0935 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 627 | placeholder for trans. breakers online monitors |  |  | NA | Forecast placeholder for online monitoring on trans. breakers, $50k/unit, 5 units in 2024, 10 units in 2025, 15 units in 2026, 20 units in 2027, 25 units in 2028 | Substation - Circuit Breaker | New | NA | Asset Condition | Age/Condition - Replace Breakers | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | Yes | EX113190 | NA | NA | NA | 64 | NA | NA | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | 5280 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 750 | 1000 | 1250 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 628 | Non-SF6 GIS Pilot Project |  |  | Livermore, Alameda | Installation of a single-bay, non-SF6-gas insulated switchgear (GIS) at PG&E’s Livermore Training Facility as a pilot that evaluates the GE-supplied alternative insulation gas, g3. The g3 gas has a much lower Global Warming Potential (GWP) than SF6. This pilot is part of PG&E’s sustainability initiative to reduce its CO2 footprint by 2050 in support of California’s goal of 80% reduction in greenhouse gas emissions. | Substation - Circuit Breaker | New | NA | Asset Condition | Age/Condition - Replace Breakers | NA | 2024-02-05 | NA | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.60395 | NA | 115 kV | Not Available | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5777410 | T.0003481 | Non-SF6 GIS Pilot Project | 1 | 64 | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-05-24 | 2018-11-30 | 2027-08-25 | Prioritization | FALSE | 800 | NA | 878.876 | 1866.8863 | 19.2218 | 39.01 | 8.1874 | 24.4345 | 772.6239 | 63.7703 | 0 | 0 | 0 | 0 | 0 | 868.5976 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 629 | GATES: Repl BK 3 Trans BRKR & SW |  |  | Fresno | Replace Gates Bank 3 (three single-phase, 1941 General Electric, 115/12kV, 6.25 MVA transformers), as well as Gates Bk 1 (three single-phase, 1951 Westinghouse, 230/115kV, 40 MVA transformers) with one new 230/12kV 45 MVA transformer with LTC. Replace 230kV CB 292 and switches 291 & 293 including the bypass switch 295. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace Breakers | NA | 2024-03-08 | 70 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 77.6619 | NA | 230 kV | 240 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5782222 | T.0000810 | GATES: REPLACE BK3 | 1 | 64 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-10 | 2020-06-30 | 2020-05-26 | NA | FALSE | 7400 | NA | 2455.6928 | 2455.6928 | 1623.5342 | 900.98 | -77.6281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2455.6928 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 2314.9208 | -70.7531 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 630 | SAN LUIS OBISPO: Repl CB 112- 132- 162 |  |  | San Luis Obispo | Replace SAN LUIS OBISPO CB 112, 132, &162 oil circuit breakers under the 2020 transmission breakers replacement program | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace Breakers | NA | 2024-02-01 | 64 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.8969 | NA | 115 kV | 95 | 9. Reliability (Low Safety Risk) | 10 | RBPPF - TBD | Yes | 5770060 | T.0001698 | San Luis Obispo: Repl CB 112, 132, 162 | 1 | 64 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-04-08 | NA | 2027-08-13 | NA | FALSE | NA | NA | 0 | 6421.5815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 631 | Oakland K: Replace CB172 |  |  | Oakland, Alameda | Replacement of the existing 12kV Switchgear at Oakland K (Claremont) Substation | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace Breakers | NA | 2024-03-19 | 58 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 3.9974 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5791478 | T.0000513 | OAKLAND "K" (CLAREMONT): REPLACE 12KV SW | 1 | 64 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2022-03-29 | 2022-05-04 | 2025-09-12 | Project Design | TRUE | 43200 | NA | 1826.396 | 2593.6857 | 0 | 41.3006 | 206.1127 | 1143.1134 | 86.4706 | 646.8392 | 454.4006 | 0 | 0 | 0 | 484.1023 | 1476.9972 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 632 | MOSS LANDING: Replace 500 KV Breakers |  |  | Monterey | This project will resolve current configuration issues and address reliability concerns. This project will rebuild Moss Landing 500kV Substation within the existing substation fence line. The project will replace the existing 500kV breakers and switches in a BAAH configuration, and upgrade the protection schemes. This will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 500 kV Breakers | NA | 2024-03-12 | 32 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 41.3213 | NA | 500 kV | 321 | 9. Reliability (Low Safety Risk) | 10 | NA | NA | 5759485 | T.0000678 | MOSS LANDING 500KV Upgrade | 6 | 64 | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-04 | 2020-03-31 | 2020-06-30 | NA | FALSE | 46400 | NA | 36280.2913 | 36280.2913 | 9381.36 | 9820.206 | 2250.1301 | -66.8208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36280.2913 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 32374.589 | 2127.8324 | -63.189 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 633 | Mobile: Purch 115kV CB and CS w/125VDC |  |  | NA | Emergency Preparedness. Purchase 115 kv mobile circuit breaker | Substation - Circuit Breaker | New | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 115 kV | Not Available | Not Available | Not Available | Tier 4 | Yes | 5542140 | T.0006671 | Electric Asset: Purchase mobile CS | 1 | 64 | NA | NA | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | 2200 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 634 | CEM breakers - purchase four 115kV CBs + |  |  | NA | This project will procure four (4) 115kV and two (2) 230kV circuit breakers (CBs) to increase Capitalized Emergency Material (CEM) inventory. PG&E maintains a stock of CEMs, which is equipment of long lead time and is kept on hand for emergency replacements. PG&E’s Emergency Transmission Substation Replacement Program replaces transmission substation equipment which has failed while in service or is expected to fail in service due to rapidly deteriorating condition. Transmission breakers are among such equipment. The breakers would be taken out of service and replaced under emergency (MWC 65), using breakers from CEM stock. In 2019, an evaluation of the CEM breaker inventory showed a rapid depletion of CEM breakers due to increased number of emergency and just-in-time breaker replacements in recent years—a trend that is anticipated to continue for several years, which would exhaust the CEM breaker inventory. In order to provide emergency support and to improve emergency response time, it is recommended to purchase four 115kV and two 230kV circuit breakers for CEM stock. | Substation - Circuit Breaker | New | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 115 kV | Not Available | Not Available | Not Available | Tier 4 | Yes | 5541690 | T.0006374 | CEM breakers - purchase four 115kV CBs + | 1 | 64 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | NA | 2025-09-02 | 2025-09-02 | NA | TRUE | 842 | NA | 4.5947 | 842.0019 | 0 | 0 | 0 | 0 | 4.5947 | 0 | 837.4072 | 0 | 0 | 0 | 0 | 4.5947 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 635 | Kingsburg: Replace CB 162 |  |  | Fresno | 2021 Transmission Breakers Replacement Program: There are a total of 32 circuit breakers identified for replacement at 13 substations. These breakers have been identified as the highest ranked candidates in the 2021 Transmission Breaker Replacement Program PG&E’s Deteriorated Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria include: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. The “year” a breaker is slated for replacement is based on the individual asset’s rank. The overall strategy dictates the replacement rate. The Circuit Breaker Strategy’s objective is to minimize failures and maximize useful life through an effective maintenance plan and by replacing breakers for which maintenance is either ineffective or uneconomical. The breakers were selected based upon 1-N ranking & the RIBA scores. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-06 | 32 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.3704 | NA | 115 kV | 22 | Not Available | Not Available | RBPPF - TBD | Yes | 5773863 | T.0002635 | Kingsburg: Replace CB 162 | 1 | 64 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-08-12 | NA | 2026-11-03 | NA | FALSE | NA | NA | 0 | 2450.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 636 | CARIBOU PH #1: Repl CB 22,42, 62,92,122 |  |  | Plumas | 2022 Program AA Transmission Circuit Breaker Replacements: This 2022 program proposes to replace transmission circuit breakers at various voltage levels at Cooley, East Nicolaus, Evergreen, Fulton, Melones SW STA, Santa Maria, Smyrna, Trinity, Westwood SW STA, Caribou PH#1, and Herdlyn Substations, to address elevated risk of failure due to age and condition. PG&E’s Transmission Substation Circuit Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria includes: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-14 | 35 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 0.96252 | NA | 115 ¦ 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799688 | T.0007887 | Caribou - Repl CB 22, 42, 62, 92, 122 | 1 | 64 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2026-08-05 | NA | 2026-12-21 | NA | FALSE | 3950 | NA | 49.721 | 3949.6873 | 0 | 0 | 0 | 41.5276 | 7.5215 | 3.6983 | 0 | 0 | 0 | 0 | 0 | 49.049 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 637 | TRINITY: Repl 70 kV CBs 12,22,32 |  |  | Weaverville CDP, Trinity | 2022 Program AA Transmission Circuit Breaker Replacements: This 2022 program proposes to replace transmission circuit breakers at various voltage levels at Cooley, East Nicolaus, Evergreen, Fulton, Melones SW STA, Santa Maria, Smyrna, Trinity, Westwood SW STA, Caribou PH#1, and Herdlyn Substations, to address elevated risk of failure due to age and condition. PG&E’s Transmission Substation Circuit Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria includes: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-14 | 32 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.3227 | NA | 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799685 | T.0007884 | Trinity - Repl 70kv CB 12, 22, 32 | 1 | 64 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2026-08-05 | NA | 2026-12-21 | NA | FALSE | 550 | NA | 57.3292 | 2095.8506 | 0 | 0 | 0 | 49.9689 | 6.6899 | 4.1598 | 0 | 0 | 0 | 0 | 0 | 56.6587 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 638 | WESTWOOD SW STA: Replace CBs 22, 52 |  |  | Westwood CDP, Lassen | 2022 Program AA Transmission Circuit Breaker Replacements: This 2022 program proposes to replace transmission circuit breakers at various voltage levels at Cooley, East Nicolaus, Evergreen, Fulton, Melones SW STA, Santa Maria, Smyrna, Trinity, Westwood SW STA, Caribou PH#1, and Herdlyn Substations, to address elevated risk of failure due to age and condition. PG&E’s Transmission Substation Circuit Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria includes: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-13 | 40 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 0.47411 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799687 | T.0007886 | Westwood - Replace CB 22 & 52 | 1 | 64 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2027-08-04 | NA | 2027-12-20 | NA | FALSE | 450 | NA | 42.0152 | 1481.2931 | 0 | 0 | 0 | 35.9962 | 5.4372 | 3.1391 | 0 | 0 | 0 | 0 | 0 | 41.4333 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 639 | EL PATIO: Replace CB 122 142 |  |  | Campbell, Santa Clara | It is recommended by the project Team to proceed with the replacement of the transmissions breakers CB 122 and CB 142 at El Patio substation due to the RIBA ranking system which place these breakers at higher risk of failure due to the age and type. By planning, scoping, engineering and replacing these breakers at this time the company will have a higher cost savings and shortened clearance outages to perform the work compared to replacing the breakers after failure causing longer outages and higher replacement costs. Replacing these breakers will be in line with current company goals in providing efficient, reliable energy to our customers. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-07 | 64 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.392 | NA | 115 kV | 284 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5769808 | T.0001497 | El Patio CB 122 and 142 Planned Repl. | 1 | 64 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-01-19 | 2021-02-17 | 2021-03-24 | NA | FALSE | 2766 | NA | 3089.6624 | 3089.6624 | 94.5487 | 562.9788 | 2037.4385 | 396.6315 | -4.4125 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.6624 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1957.0459 | 286.4223 | -3.1864 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 640 | EL PATIO: Replace CB 312 332 |  |  | Campbell, Santa Clara | It is recommended by the project Team to proceed with the replacement of the transmissions breakers CB 312 and CB 332 at El Patio substation due to the RIBA ranking system which place these breakers at higher risk of failure due to the age and type. By planning, scoping, engineering and replacing these breakers at this time the company will have a higher cost savings and shortened clearance outages to perform the work compared to replacing the breakers after failure causing longer outages and higher replacement costs. Replacing these breakers will be in line with current company goals in providing efficient, reliable energy to our customers. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-07 | 59 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.392 | NA | 115 kV | 155 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5777172 | T.0003435 | EL PATIO CB312 and CB332 | 1 | 64 | NA | 2017 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-09-08 | 2020-12-31 | 2020-12-17 | NA | FALSE | 1797 | NA | 1395.6222 | 1395.6222 | 97.847 | 1212.822 | 84.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1395.6222 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1156.6409 | 74.7957 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 641 | SAN LEANDRO U: Repl CB 182- 372- 382 |  |  | San Leandro, Alameda | Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. 1. Replace OCBs 182, 372, and 382 with new 115kV, 2000A circuit breakers. 2. Replace OCBs 182, 372, and 382 foundations. 3. Relocate and enlarge switchman platforms. 4. Evaluate and replace conductors as required. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-07 | 59 | Lifecycle Replacement Analysis | Wires - Bus Upgrade Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 10.2372 | NA | 115 kV | 242 | Not Available | NA | NA | NA | 5772691 | T.0002360 | San Leandro U: Replace CB 182, 372, 382 | 1 | 64 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-12-06 | 2019-06-30 | 2019-12-17 | NA | FALSE | 2523 | NA | 5460.3662 | 5460.3662 | 2002.8406 | 1030.443 | 122.0217 | 324.0097 | 68.9456 | 4.9874 | 0 | 0 | 0 | 0 | 0 | 5455.3788 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 3656.5669 | 960.155 | 234.51 | 309.6686 | 65.894 | 4.7666 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 642 | Gold Hill: Repl 115kV CB 142, 172 |  |  | Folsom, Sacramento | Replace 115 kV Circuit Breakers 142 and 172 and associated equipment as required. PG&E’s Deteriorated Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria include: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. The “year” a breaker is slated for replacement is based on the individual asset’s rank. The overall strategy dictates the replacement rate. The Circuit Breaker Strategy’s objective is to minimize failures and maximize useful life through an effective maintenance plan and by replacing breakers for which maintenance is either ineffective or uneconomical. The breakers were selected based upon the vintage, unreliable performance for breaker model types, Percentage of F6 gas leakage, high fault duty, and the critical nature of Gold Hill substation. Gold Hill Substation is located at HFTD zone 1. | Substation - Circuit Breaker | Replace | T.0004920 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-28 | 61 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 12.8702 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541700 | T.0006348 | Gold Hill: Repl 115kV CB 142, 172 | 2 | 64 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-04 | 2025-05-30 | 2025-01-02 | NA | TRUE | 6400 | NA | 1051.3458 | 2815.0696 | 0 | 0 | 102.9063 | 662.7222 | 79.534 | 1611.589 | 1066.9802 | 0 | 0 | 0 | 0 | 845.1624 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 102.9063 | 662.7222 | 4.4042 | 287.4574 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 643 | Gold Hill: Replace CB 142 Project |  |  | Folsom, Sacramento | Replace 115 kV Circuit Breakers 142 and 172 and associated equipment as required. PG&E’s Deteriorated Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria include: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. The “year” a breaker is slated for replacement is based on the individual asset’s rank. The overall strategy dictates the replacement rate. The Circuit Breaker Strategy’s objective is to minimize failures and maximize useful life through an effective maintenance plan and by replacing breakers for which maintenance is either ineffective or uneconomical. The breakers were selected based upon the vintage, unreliable performance for breaker model types, Percentage of F6 gas leakage, high fault duty, and the critical nature of Gold Hill substation. Gold Hill Substation is located at HFTD zone 1. | Substation - Circuit Breaker | Replace | T.0004920 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-28 | 61 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 12.8702 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801228 | T.0006348 | Gold Hill: Repl 115kV CB 142, 172 | 2 | 64 | NA | 2014 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-05-23 | 2025-05-30 | 2024-12-12 | NA | TRUE | 6400 | NA | 528.6752 | 3010.7687 | 0 | 0 | 0 | 65.8871 | 269.5487 | 1395.2791 | 1279.0457 | 81.0876 | 0 | 0 | 0 | 335.4358 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 644 | Swift Sub: Replace CB 142 |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Circuit Breaker | Replace | T.0009169 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-07 | 51 | Lifecycle Replacement Analysis | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.1012 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5772488 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 64 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2028-12-14 | 2023-03-31 | 2029-01-25 | Bundling Dependencies | TRUE | 65600 | NA | 275.7446 | 1378.285 | 0 | 0 | 73.2292 | 182.9051 | 16.9169 | 19.4765 | 0 | 0 | 0 | 0 | 0 | 273.0511 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 645 | BALCH PH #2: Replace CB 232 |  |  | Fresno | Replace BALCH PH #2 CB 232 oil circuit breakers under the 2021 transmission breakers replacement program | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-06 | 66 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.54903 | NA | 230 kV | 168 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5773862 | T.0002634 | Balch PH #2: Replace CB 322 | 1 | 64 | NA | 2016 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-10-28 | 2025-02-01 | 2025-12-30 | Prioritization | TRUE | 3762 | NA | 731.5465 | 2585.1025 | 0 | 0 | 87.1833 | 546.3949 | 88.6394 | 53.2676 | 1647.4457 | 0 | 0 | 0 | 1398.2527 | 722.2176 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $3 Mil -$5 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 646 | DCPP: Replace CB 262 & 282 |  |  | San Luis Obispo | Replace breakers 262 & 282 at Diablo Canyon 230 kV Substation. DCPP CB 262 & 282 are identified for replacement in 2020 as part of the deteriorated transmission breaker replacement program. The prioritization criteria were developed based upon technical assessments of the transmission breaker including: age, condition, high failure rate models, criticality, and overstress. In addition, factors such as recurring maintenance costs, availability of spare parts, and environmental issues are also considered. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-07 | 55 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 35.6227 | NA | 230 kV | 68 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5775227 | T.0000663 | Diablo 230kV CB 262 & 282 Replacement | 1 | 64 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-07-06 | NA | 2027-11-05 | NA | FALSE | NA | NA | 6.5053 | 2814.7792 | 2.1118 | 2.506 | 0.5291 | 0.4057 | 0.4462 | 0.47 | 0 | 0 | 0 | 0 | 0 | 6.4292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 647 | NEWARK: Repl CB 180 |  |  | Fremont, Alameda | Replace Circuit Breaker 180 at Newark substation. PG&E’s Deteriorated Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. The deteriorated breaker replacement program criteria are primarily based on the technical health and risk based assessments of the breakers. The health assessment includes dissolved gas analysis, oil quality data, on-site inspections, vintage, and maintenance costs. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-08 | 56 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 27.7611 | NA | 115 kV | 168 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5772747 | T.0002361 | Newark Sub Replace CB 180 | 1 | 64 | NA | 2016 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-11-02 | 2022-12-23 | 2023-01-05 | NA | TRUE | 2180 | NA | 2507.1663 | 2507.1663 | 0.6521 | 13.658 | 563.5983 | 1425.0019 | 478.536 | 13.43 | 0 | 0 | 0 | 0 | 0 | 2493.7363 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2328.0073 | 14.2508 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $2 Mil - $3 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 648 | COTTONWOOD: Repl CB 152/192 |  |  | Cottonwood CDP, Shasta | Replace Cottonwood Transformer Banks 1 & 4, replacement of six circuit breakers, addition of bus parallel circuit breaker, and upgrade the aging protection and control equipment at the Cottonwood substation. | Substation - Circuit Breaker | Replace | T.0004659 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-06 | 36 | Lifecycle Replacement Analysis | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 26.1945 | NA | 115 kV | 80 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5781697 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 64 | NA | 2014 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-09-11 | 2028-04-30 | 2026-12-08 | NA | FALSE | 51200 | NA | 188.5116 | 3340.2544 | 9.3522 | 58.3155 | 18.2521 | 27.5487 | 66.4447 | 381.9875 | 389.8872 | 0 | 0 | 0 | 0 | 179.9133 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 649 | COTTONWOOD: Replace Various CBs |  |  | Cottonwood CDP, Shasta | Replace Cottonwood Transformer Banks 1 & 4, replacement of six circuit breakers, addition of bus parallel circuit breaker, and upgrade the aging protection and control equipment at the Cottonwood substation. | Substation - Circuit Breaker | Replace | T.0004659 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-06 | 60 | Lifecycle Replacement Analysis | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 26.1945 | NA | 230 kV | 33 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5769042 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 64 | 5758737 | 2014 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-10-08 | 2028-04-30 | 2027-06-25 | NA | FALSE | 51200 | NA | 413.398 | 9966.214 | 82.1189 | 75.6172 | 80.1742 | 35.1657 | 85.6031 | 1304.9743 | 1416.7702 | 0 | 0 | 0 | 0 | 402.3812 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 650 | MCKEE: Repl CB 152- 162 |  |  | San Jose, Santa Clara | Replace McKee CB 152 & 162 oil circuit breakers under the 2020 transmission breakers replacement program | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-07 | 60 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.7627 | NA | 115 kV | 95 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5769809 | T.0001492 | McKee CB 152 and 162 Planned Repl | 1 | 64 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-03-29 | NA | 2027-10-22 | NA | FALSE | NA | NA | 1.4491 | 4358.7773 | 1.071 | 0.0879 | 0.0835 | 0.0904 | 0.0994 | 0.1048 | 0 | 0 | 0 | 0 | 0 | 1.4321 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 651 | MORAGA: Replace CB 612 622 422 712 |  |  | Orinda, Contra Costa | Replace Moraga CB 612, 622, 642 and 712 oil circuit breakers under the 2019 transmission breakers replacement program | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-06 | 61 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 15.8714 | NA | 115 kV | 104 | 9. Reliability (Low Safety Risk) | 1 | RBPPF - TBD | Yes | 5770156 | T.0001635 | MORAGA: REPL CB612, CB622, CB422, CB712 | 1 | 64 | 5761189 | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-03-09 | NA | 2026-12-03 | NA | FALSE | NA | NA | 1190.6311 | 4398.9287 | 70.5654 | 94.5569 | 143.5536 | 1294.412 | -425.4126 | 84.91 | 0 | 0 | 0 | 0 | 0 | 1178.0414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 652 | MORGAN HILL: Replace 115 KV CB 172 |  |  | Morgan Hill, Santa Clara | Replace Morgan Hill 115 kV CB 172 as identified in the 2017-2018 Transmission Deteriorated Breaker Replacement Program. PG&E’s Deteriorated Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. PG&E’s prioritization criteria include: (1) age; (2) failure rate; (3) condition; (4) frequency and costs of maintenance; (5) criticality or impact of failure; and (6) fault current magnitude. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. The “year” a breaker is slated for replacement is based on the individual asset’s rank. The overall strategy dictates the replacement rate. The Circuit Breaker Strategy’s objective is to minimize failures and maximize useful life through an effective maintenance plan and by replacing breakers for which maintenance is either ineffective or uneconomical. The breakers were selected based upon 1-N ranking & the RIBA scores. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-09 | 37 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.8017 | NA | 115 kV | 42 | Not Available | Not Available | RBPPF - TBD | Yes | 5757733 | T.0000802 | MORGAN HILL SUB 115 KV CB 172 | 1 | 64 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-06-07 | NA | 2028-07-11 | NA | FALSE | NA | NA | 0.6419 | 1947.5984 | 0.0185 | 0.0298 | 0.1554 | 0.04 | 0.044 | 0.0464 | 0 | 0 | 0 | 0 | 0 | 0.6344 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 653 | OAKLAND K: CB 172, 322,162,132,152 |  |  | Oakland, Alameda | Replace OAKLAND K CB 162, 132, & 152 oil circuit breakers under the 2023 transmission breakers replacement program | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-19 | 58 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 3.9974 | NA | 230 kV | Not Available | 9. Reliability (Low Safety Risk) | 5 | RBPPF - TBD | Yes | 5777325 | T.0003466 | Oakland K: CB 162,132,152 | 1 | 64 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2025-12-10 | NA | 2026-08-06 | NA | FALSE | NA | NA | 550.4694 | 4968.8989 | 0 | 0 | 75.3195 | 468.2768 | 6.8731 | 0 | 0 | 0 | 0 | 0 | 500 | 550.4694 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 654 | OAKLAND L: Replace CB 312 and 412 |  |  | Oakland, Alameda | Replace OAKLAND L CB 312 and 412 oil circuit breakers under the 2023 transmission breakers replacement program | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-06 | 49 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 1.197 | NA | 230 kV | Not Available | 9. Reliability (Low Safety Risk) | 16 | RBPPF - TBD | Yes | 5777326 | T.0003467 | Oakland L Sub: Repl CB 322, 422,312,412 | 2 | 64 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-04-29 | NA | 2026-12-16 | NA | FALSE | 950 | NA | 228.0866 | 3652.6224 | 0 | 0 | 0 | 205.1682 | 22.9184 | 13.9628 | 0 | 0 | 0 | 0 | 919.3376 | 228.0866 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 655 | VACA DIXON: Replace CB 442 452 462 |  |  | Solano | Replace overstressed 230kV CB 442, 452, 462 with 3000A CC, 63kA IC breakers and add new bus paralleling substitute breaker CB 402 as part of PG&E’s Deteriorated Breakers Replacement Program. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-12 | 35 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | 104 | 9. Reliability (Low Safety Risk) | 4 | RBPPF - TBD | Yes | 5761196 | T.0001609 | Vaca Dixon - Replace CB 442, 452, 462 | 1 | 64 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-04-03 | NA | 2027-03-18 | NA | FALSE | 2000 | NA | 695.6005 | 14271.1138 | 0 | 80.3529 | 157.4981 | 120.8488 | 170.4299 | 671.2525 | 3139.382 | 0 | 0 | 0 | 0 | 529.1297 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 656 | Metcalf: Repl CBs 654,664,674,684 |  |  | Santa Clara | Replace overstressed CB 492, CB 502, & CB 632 at Metcalf 115 kV substation. Replace overstressed CB 492, CB 502, & CB 632 at Metcalf 115 kV substation. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-13 | 26 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5796971 | T.0007291 | Metcalf: Replace Overstressed CBs | 3 | 64 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-07-08 | NA | 2027-01-28 | NA | FALSE | NA | NA | 517.0878 | 5284.9106 | 0 | 0 | 31.3983 | 211.1708 | 259.6756 | 1991.8901 | 1673.0099 | 703.5066 | 0 | 0 | 0 | 502.2448 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 657 | PALERMO: Repl CB 122- 132- 142- 152- 162 |  |  | Palermo CDP, Butte | Replace Palermo CBs 122, 132, 142, 152, & 162 oil circuit breakers under the 2021 transmission breakers replacement program | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-04 | 62 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 8.0464 | NA | 230 kV | 95 | 9. Reliability (Low Safety Risk) | 11 | RBPPF - TBD | Yes | 5777331 | T.0003476 | Palermo Repl CBs 122, 132, 142, 152, 162 | 1 | 64 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-09-27 | NA | 2027-11-11 | NA | FALSE | NA | NA | 0 | 1625.6192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 658 | RAVENSWOOD: Replace CB 152 162 312 322 |  |  | Menlo Park, San Mateo | Replace RAVENSWOOD CB 152, 162, 312, & 322 oil circuit breakers under the 2019 transmission breakers replacement program | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-06 | 54 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | NA | 115 kV | 120 | 9. Reliability (Low Safety Risk) | 11 | RBPPF - TBD | Yes | 5761192 | T.0001608 | RAVENSWOOD SUB CB 152,162,312,322 | 1 | 64 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-08-14 | NA | 2027-03-03 | NA | FALSE | 300 | NA | 142.7072 | 3670.3322 | 0 | 15.0723 | 31.3585 | 83.6734 | 10.934 | 10.3547 | 0 | 0 | 0 | 0 | 0 | 141.0382 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 659 | Salinas Sub: Repl 60kV CB 2, 32 |  |  | Salinas, Monterey | Replace SALINAS 60KV CB 2 & 32 oil circuit breakers under the 2023 transmission breakers replacement program | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-12 | 56 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.4966 | NA | 60 kV | Not Available | 9. Reliability (Low Safety Risk) | 10 | RBPPF - TBD | Yes | 5777323 | T.0003464 | Salinas Sub: Repl 60kV CB 2, 32 | 1 | 64 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2025-02-14 | NA | 2025-07-02 | NA | TRUE | NA | NA | 668.35 | 3186.5095 | 0 | 0 | 160.7486 | 503.3578 | 4.2436 | 41.9504 | 2455.7949 | 0 | 0 | 0 | 2068.8649 | 668.35 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 660 | SONOMA: Replace 115kV CB 132 & 142 |  |  | Sonoma, Sonoma | Replace SONOMA 115KV CB 132 & 142 oil circuit breakers under the 2021 transmission breakers replacement program | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-06 | 49 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.5781 | NA | 115 kV | 80 | 9. Reliability (Low Safety Risk) | 8 | RBPPF - TBD | Yes | 5777332 | T.0003477 | Sonoma Sub Repl 115kV CB 132, 142 | 1 | 64 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-12-30 | NA | 2029-03-07 | NA | FALSE | NA | NA | 0 | 4073.2001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 661 | CASCADE: Repl 60 KV Phase 2 CBS |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-12 | 61 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | NA | 60 kV | 95 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5777643 | T.0000651 | Cascade Substation Upgrade | 10 | 64 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-03-15 | 2022-01-31 | 2025-04-23 | Prioritization | TRUE | 35800 | NA | 2052.1216 | 3470.9058 | 277.2937 | 569.6944 | 767.5361 | 292.6927 | 101.2361 | 156.6918 | 1283.4037 | 0 | 0 | 0 | 0 | 2030.8103 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 662 | CASCADE: Replace 60 KV CB 42 52 62 72 |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-12 | 60 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | NA | 60 kV | 58 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5757727 | T.0000651 | Cascade Substation Upgrade | 10 | 64 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2020-03-10 | 2022-01-31 | 2025-01-31 | Prioritization | TRUE | 35800 | NA | 5563.0133 | 7931.2774 | 1445.3926 | 1582.3203 | 834.2092 | 626.9971 | 466.0654 | 1981.3903 | 453.3298 | 0 | 0 | 0 | 0 | 5492.4401 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 663 | TIDEWATER: Replace CB 212 & 232 |  |  | Contra Costa | Replace TIDEWATER CB 212 & 232 oil circuit breakers under the 2021 transmission breakers replacement program | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-05 | 38 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.2848 | NA | 230 kV | 30 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5772484 | T.0002323 | Tidewater Sub: Replace CB 202, 212, 232 | 1 | 64 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-08-19 | NA | 2028-02-22 | NA | FALSE | NA | NA | 10.3182 | 5414.06 | 0.3846 | 0.6194 | 0.5942 | 0.6435 | 0.7077 | 0.7456 | 0 | 0 | 0 | 0 | 0 | 10.1975 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 664 | PITTSBURG: Replace CB 352 362 |  |  | Pittsburg, Contra Costa | Replacement of the deteriorated 115kV circuit breakers 352 and 362 at Pittsburg Switching Center. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-06 | 46 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 28.8512 | NA | 115 kV | 15 | Not Available | Not Available | NA | NA | 5769806 | T.0001495 | Pittsburg PP CB 352 Repl. | 1 | 64 | NA | 2016 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-07-02 | 2018-06-18 | 2020-01-13 | Workforce | FALSE | 1377 | NA | 2968.7067 | 2968.7067 | 1617.5156 | 158.2163 | 0.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2968.7067 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 2608.438 | 0.80494 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 665 | MONTAGUE: Replace 115 KV CB 132 142 |  |  | San Jose, Santa Clara | The Montague Substation Bundle and Remote End projects will replace Circuit Breaker (CB) 132, CB 142, Circuit Switcher (CSW) 176, CSW 186, replace protection relays for Bank 1, Bank 2, Bank 3, line and bus protection relays, install Distribution SCADA on CB 2100, CB 2200 and CB 2300. In addition, the line and bus protection relays at the Remote End Substations Los Esteros and Trimble will be replaced. The Montague Substation Bundle and Remote Ends are comprised of multiple projects that contribute to the betterment of the PG&E Electric System. CB132 and CB142 are being replaced as part of the Deteriorated Breakers Replacement Program to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. The replacement of the old Protection relays at Montague Substation, as well as the Remote Ends will improve system reliability, whereas installing SCADA on all the distribution equipment in Montague Substation will provide system visibility for low side devices at Montague Substation. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-07 | 58 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.2309 | NA | 115 kV | 95 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5761188 | T.0000706 | MONTAGUE SUB 115 KV CB 132, 142 | 4 | 64 | NA | 2014 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-01-04 | 2023-02-01 | 2023-01-31 | NA | TRUE | 9841 | NA | 4286.1631 | 4345.0404 | 9.2056 | 124.4869 | 817.4434 | 2069.7231 | 1182.3746 | 59.0696 | 3.5574 | 0 | 0 | 0 | 0 | 4282.4135 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 3789.0813 | 4.7568 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 666 | PALO ALTO: Convert 115 KV Bus to BAAH |  |  | Palo Alto, Santa Clara | The Palo Alto switching station is already set-up for BAAH. However, it is operated as a nonstandard variant of Bus 1& 2 with six breakers installed for six lines. Presently it is required to trip the entire bus in order to protect SVP equipment. This project will replace the six breakers, install three additional breakers, and convert the bus to BAAH.Install modular protection, automation, and control (MPAC) panels in MPAC building for the 115 kV bus to replace the existing control building | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-05 | 50 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.0138 | NA | 115 kV | 472 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5769807 | T.0001493 | PALO ALTO SS: Convert 115kV Bus to BAAH | 2 | 64 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2029-04-06 | NA | 2031-10-08 | NA | FALSE | NA | NA | 2142.8015 | 31726.4688 | 306.0083 | 100.6823 | 1112.3765 | 546.0706 | -261.1413 | 131.3451 | 690.1515 | 7363.8693 | 17406.3063 | 313.0807 | 0 | 2142.8015 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 667 | Los Banos: Replace 70 kV_ CB 12, 22, 32, 52, 92 |  |  | Merced | This planned project will replace Los Banos CBs 12, 22, 32, 52, and 92 with new 70 kV CBs. This project is needed to support the Gonzaga Wind Farm Generation Interconnection project (Q1378). The Gonzaga Wind project will add a new bay with (2) Breakers and a new control enclosure to Los Banos substation. This project will also convert the 70 kV Main & Aux to Double Bus Single Breaker (DBSB). This breaker replacement funded under MWC 64 will replace the five additional 70kV CBs at Los Banos. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-06 | 58 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 70 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799749 | T.0007906 | Los Banos_Replace 70 kV_ 5 CBs | 1 | 64 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-03 | 2025-02-01 | 2025-12-31 | Prioritization | TRUE | 3750.908 | NA | 936.8777 | 3216.2054 | 0 | 0 | 0 | 156.2183 | 175.4163 | 1938.9931 | 945.5777 | 0 | 0 | 0 | 0 | 331.6345 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 668 | Vacaville: Replace 115 kV CBs 132 & 142 |  |  | Vacaville, Solano | This planned project will replace Vacaville 115 kV CBs 132 & 142 with new 115 kV CBs to improve electric reliability and operational flexibility. Vacaville 115 kV CBs 132 & 142 have been targeted for replacement as part of the PG&E Breaker Replacement Program. The Circuit Breaker Strategy’s objective is to minimize failures and maximum useful life through an effective maintenance plan and by replacing breakers for which maintenance is either ineffective or uneconomical. Refer to TD-8103 – “Substation Asset Management Plan” for more details. PG&E’s Deteriorated Transmission Circuit Breakers Replacement Program was developed to identify transmission circuit breakers most at risk of failure and proactively replace them to minimize customer-minutes of outage time. The benefits associated with replacing transmission circuit breakers on a planned basis as opposed to emergency replacements are numerous and listed out in TD-8103. The transmission circuit breaker replacement is divided into three groupings, overstressed, oil, and age. Below is description of each groupings: 1. Overstressed breakers are ranked based the ratio (in percent) of the fault duty at the breaker’s physical location to the breaker’s nameplate interrupting rating. The most overstressed breakers are targeted first. 2. Oil breakers are ranked based on high failure rate makes/models, Accumulative Critical Current (ACC) count and Breaker Oil Analysis (BOA). 3. Age - breakers are ranked based on oldest to newest. Whenever possible, circuit breakers planned for replacement within a substation for implementation in the same year are grouped together and titled as one project to capture efficiency. The “year” a breaker is slated for replacement is based on the individual asset’s rank. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-01 | 34 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.725 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5800138 | T.0008074 | Vacaville: Replace 115 kV CBs 132 & 142 | 1 | 64 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-11-03 | NA | 2028-01-18 | NA | FALSE | NA | NA | 5.0503 | 5558.9437 | 0 | 0 | 0 | 4.4416 | 0.5491 | 0.3653 | 0 | 0 | 0 | 0 | 0 | 4.9908 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 669 | MERCED: Replace SW with Circuit Breaker |  |  | Merced | This project proposes to replace 115kV switch 185 with a new circuit breaker, associated dead-end suport structures, disconnect switches and relays upgrades on a planned basis PG&E’s substation transmission and distribution buses are aging and many existing bus designs do not meet current switching, operating, protection and maintenance needs to support the highest level of reliable service or meet regulatory expectations. As a result, the Bus Reliability Program was introduced to identify buses that can be modified and reconfigured. The strategic objective of this project are:•To improve reliable operation of the bus and service to our customers•To support compliance of regulatory requirements •To ease operational and maintenance constraints | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-02 | 36 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7481 | NA | 115 kV | 3 | 9. Reliability (Low Safety Risk) | 10 | RBPPF - TBD | Yes | 5761858 | T.0001159 | MERCED: REPL SW 185 WITH CIRCUIT BREAKER | 1 | 64 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-01-02 | 2019-07-30 | 2026-01-15 | Prioritization | TRUE | 4522 | NA | 1463.2563 | 3997.5091 | 30.3095 | 628.026 | 97.7443 | 194.2665 | 104.3222 | 105.4743 | 0 | 0 | 0 | 0 | 2208.7321 | 1446.8417 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 670 | Mountain View CB 112 & 122 Planned Repl |  |  | Mountain View, Santa Clara | This project proposes to replace existing substation transformer Bank 1 in order to eliminate a growing deficiency on both Mountain View Bank 1 and Mountain View Bank 3. Replace two existing 115 kV motor-operated switches (157 and 159) with circuit breakers. Presently any bus or bank fault will trip both existing 115 kV breakers CB 112 & CB 122. By adding two additional 115 kV circuit breakers, only the faulted bus or bank would experience an outage. This additional scope will improve the looped bus, provide a logical path to an ultimate five-element 115 kV ring bus, improve bank clearances and increase reliability by reducing momentary outages to the 39,141 existing customers on Mountain View Substation. Transmission Substation Work (MWC 61): • Replace 115 kV circuit switchers 159 and 157 with 115 kV circuit breakers. • Extend existing control building will to accommodate the new relays for the breakers. with 115 kV circuit breakers. • Replace existing CB 112 with new circuit breaker/disconnect switches. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-09 | 65 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8224 | NA | 115 kV | 290 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5769810 | T.0005971 | Mountain View - Replace Bank 1 | 2 | 64 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2025-08-07 | NA | 2026-08-03 | NA | FALSE | 1000 | NA | 215.7232 | 5485.3067 | 0 | 0 | 6.7853 | 145.7536 | 36.8407 | 783.5347 | 2067.4291 | 1750.062 | 177.9545 | 8.1431 | 0 | 189.3796 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 671 | GOLD HILL: 230kV: Repl CB 242, 712 |  |  | Folsom, Sacramento | This project will replace 230kV circuit breakers 212, 222, 242, 252, 712 and associated equipment at Gold Hill Substation. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-28 | 60 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 12.8702 | NA | 230 kV | Not Available | NA | Not Available | NA | NA | 5784367 | T.0000466 | GOLD HILL: REPL CBS 252,212,222,242,712 | 5 | 64 | NA | 2011 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-15 | 2020-12-18 | 2022-03-23 | Prioritization | FALSE | 10585 | NA | 2958.166 | 2958.166 | 347.7068 | 1130.4864 | 469.8719 | 978.8802 | 31.2206 | 0 | 0 | 0 | 0 | 0 | 0 | 2958.166 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2926.9454 | 31.2206 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 672 | GOLD HILL: 230kV: Repl CB 252, 212 |  |  | Folsom, Sacramento | This project will replace 230kV circuit breakers 212, 222, 242, 252, 712 and associated equipment at Gold Hill Substation. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-28 | 58 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 12.8702 | NA | 230 kV | 80 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5756856 | T.0000466 | GOLD HILL: REPL CBS 252,212,222,242,712 | 5 | 64 | NA | 2011 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-15 | 2019-05-01 | 2019-02-13 | NA | FALSE | 10585 | NA | 7182.0536 | 7182.0536 | 2777.7072 | -502.2762 | 27.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7182.0536 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 6746.2411 | -441.2141 | 23.9724 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 673 | GOLD HILL: Replace CB 12 112 142 |  |  | Folsom, Sacramento | This project will replace 60kV and 115kV circuit breakers 12, 122, 142 and associated equipment at Gold Hill Substation as part of PG&E’s Deteriorated Breakers Replacement Program. | Substation - Circuit Breaker | Replace | T.0004920 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-28 | 61 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 12.8702 | NA | 115 ¦ 60 kV | 130 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5761184 | T.0001157 | Gold Hill: Replace 60kV CB 12 | 1 | 64 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-03-31 | 2020-05-01 | 2026-07-02 | Prioritization | FALSE | 4500 | NA | 478.1615 | 3416.6843 | 14.5836 | 25.686 | 27.0157 | 62.3101 | 41.1742 | 34.7973 | 0 | 0 | 0 | 0 | 0 | 472.467 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $5 Mil - $10 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 674 | LODI: Replace CB 12 22 32 |  |  | Lodi, San Joaquin | This project will replace all 60kV circuit breakers, 60kV Main and Auxiliary bus structure and the associated equipment at Lodi Substation.The replacement criteria were developed based on technical assessments of the switches including design characteristics, system criticality, historical failure rates, onsite inspections, vintage, environmental factors, and operating conditions. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-03 | 63 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.93622 | NA | 60 kV | 48 | 9. Reliability (Low Safety Risk) | 20 | NA | NA | 5756866 | T.0000303 | LODI SUB: REPL CB 12, 22 AND 32 | 2 | 64 | NA | 2013 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-08-04 | 2019-10-17 | 2022-05-20 | Project Design | TRUE | 7215 | NA | 14583.1644 | 14636.3011 | 1042.0651 | 1666.3604 | 4415.7357 | 3857.8096 | 1330.7626 | 136.0886 | 0 | 0 | 0 | 0 | 0 | 14500.2125 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2023 ¦ 2024 | 2775.6387 | -2775.6387 | 0 | 12454.5549 | 1252.4945 | 152.4228 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 675 | SANTA ROSA A: Repl CB 142 |  |  | Santa Rosa, Sonoma | This project will replace deteriorating oil filled circuit breakers 132, 142 and 162 with non-SF6 breakers at Santa Rosa A Substation. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-08 | 49 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.91804 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5793879 | T.0002317 | Santa Rosa A: Replace CB 132,142,162 | 3 | 64 | NA | 2016 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-03-03 | 2023-05-31 | 2026-05-22 | Prioritization | TRUE | 7690 | NA | 780.5655 | 2530.118 | 0 | 107.0347 | 344.8882 | 102.911 | 215.2111 | 58.0289 | 0 | 0 | 0 | 0 | 1484.1851 | 770.0449 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 676 | SANTA ROSA A: Repl CB 162 |  |  | Santa Rosa, Sonoma | This project will replace deteriorating oil filled circuit breakers 132, 142 and 162 with non-SF6 breakers at Santa Rosa A Substation. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-08 | 49 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.91804 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5793839 | T.0002317 | Santa Rosa A: Replace CB 132,142,162 | 3 | 64 | NA | 2016 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-04-01 | 2023-05-31 | 2026-06-22 | Prioritization | TRUE | 7690 | NA | 732.5773 | 2215.2751 | 0 | 108.5637 | 309.6608 | 49.6461 | 254.4931 | 54.8011 | 0 | 0 | 0 | 0 | 1085.8021 | 722.3637 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 677 | SANTA ROSA A: Replace CB 132 |  |  | Santa Rosa, Sonoma | This project will replace deteriorating oil filled circuit breakers 132, 142 and 162 with non-SF6 breakers at Santa Rosa A Substation. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-08 | 51 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.91804 | NA | 115 kV | 30 | 9. Reliability (Low Safety Risk) | 12 | RBPPF - TBD | Yes | 5772481 | T.0002317 | Santa Rosa A: Replace CB 132,142,162 | 3 | 64 | NA | 2016 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-01-16 | 2023-05-31 | 2026-03-11 | Prioritization | TRUE | 7690 | NA | 1436.7532 | 2385.5086 | 1.2964 | 198.1449 | 676.9747 | 216.6911 | 317.1441 | 107.9933 | 0 | 0 | 0 | 0 | 985.9198 | 1416.2064 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 678 | HENRIETTA: Repl CB 77- 22- 12 |  |  | Kings | This project will replace four (4) 70 kV oil circuit breakers on bus section “E” with new SF6 units - the switches and structures for these breakers will also be replaced. Bus section “E” is currently set up in main-aux configuration, and in order to enhance reliability the new bus section “E” will be configured as a double bus – single breaker. The 230 kV bus protection will migrate from the existing control building to a new MPAC building. The plan is to use the existing control building’s vacated space to accommodate the new 70kV protection relays. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-05 | 62 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 7.0079 | NA | 70 kV | 227 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5777328 | T.0002651 | Henrietta: Repl CB 72,22,12 | 2 | 64 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-06-20 | NA | 2026-12-14 | NA | FALSE | NA | NA | 418.8329 | 6159.679 | 53.8695 | 18.8644 | 118.7054 | 185.1693 | 29.3113 | 457.6147 | 2348.1181 | 2293.2565 | 98.6933 | 0 | 0 | 409.5643 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 679 | WEEDPATCH: Repl 70 KV CB 42- 52- 62 |  |  | Kern | This project will replace four transmission class breakers 32, 42, 52 and 62 including disconnects. | Substation - Circuit Breaker | Replace | T.0000144 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-02-07 | 54 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.2535 | NA | 70 kV | 137 | Not Available | NA | NA | NA | 5757198 | T.0001604 | WEEDPATCH 70 KV CB 42 52 62 | 2 | 64 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-12 | 2018-01-10 | 2019-03-29 | Project Design | FALSE | 3715 | NA | 5949.4847 | 5949.4847 | 1676.6698 | 157.1762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5949.4847 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 5472.1115 | 148.1764 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 680 | WESTPARK: Replace 115KV CB 112 |  |  | Bakersfield, Kern | This project will replace one transmission class 115 kV breaker (CB 112). Westpark CB 112 is identified for replacement in 2019 as part of the deteriorated transmission breaker replacement program. The prioritization criteria were developed based upon technical assessments of the transmission breaker including: age, condition, high failure rate models, criticality, and overstress. In addition, factors such as recurring maintenance costs, availability of spare parts, and environmental issues are also considered. | Substation - Circuit Breaker | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-05 | 35 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7259 | NA | 115 kV | 42 | 9. Reliability (Low Safety Risk) | 12 | RBPPF - TBD | Yes | 5757736 | T.0000740 | WESTPARK SUB 115KV CB 112 | 1 | 64 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-10-01 | 2019-04-30 | 2027-04-30 | Prioritization | FALSE | 1310 | NA | 636.3618 | 2107.4309 | 36.4607 | 172.1544 | 4.6302 | 0 | 0 | 39.4745 | 0 | 0 | 0 | 0 | 50.0615 | 636.3618 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 681 | OAKLAND D: Replace 115 KV CB 112 132 152 |  |  | Oakland, Alameda | This project will replace the 115kV Circuit Breakers 122, 132, and 152 at Oakland D substation . PG&E’s Deteriorated Breakers Replacement Program was developed to realize the savings that is associated with replacing breakers on a planned basis as opposed to emergency replacements. Planned replacements avoid the risk of outages and the higher costs that can be associated with emergency replacements due to overtime labor charges, schedule delays for other projects, and possible oil discharge clean-up from a failure. Breakers being replaced under this project are 1960s and 1970s vintage oil circuit breakers. These breakers are in deteriorated condition. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-12 | 53 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 0.54348 | NA | 115 kV | 80 | 9. Reliability (Low Safety Risk) | 1 | NA | NA | 5758808 | T.0000024 | Oakland D Replace Sub CB112, CB132 | 1 | 64 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-06-01 | 2019-03-21 | 2021-03-28 | Prioritization | FALSE | 3626 | NA | 5014.007 | 5014.007 | 256.0421 | 2918.0671 | 1415.3289 | 10.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5014.007 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 4585.9205 | 9.9127 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 682 | NEWARK: Replace 60 KV CB 30 50 & 60 |  |  | Fremont, Alameda | This project will replace the deteriorated 60 kV Circuit Breakers 30, 50, and 60 and associated disconnect and bypass switches and associated support structures. Newark Substation 60 kV Circuit Breakers (CBs) 30, 50, and 60 are of vintage 1965 General Electric. All circuit breakers have been nominated for replacement due to their deteriorated condition. Each has a RIBA score of 77 and RIBA Delta of 54. They are ranked #60 on the system 1-n replacement list. There are no plans at this time to add or remove elements on the 60kV bus. | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Breakers | NA | 2024-03-08 | 55 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 27.7611 | NA | 60 kV | 77 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5761191 | T.0001161 | NEWARK SUB 60 KV CB 30 50 60 | 1 | 64 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-07-31 | 2019-02-21 | 2019-11-01 | Prioritization | FALSE | 2397 | NA | 2974.9861 | 2974.9861 | 1744.4258 | 84.8873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2974.9861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1982.6675 | 58.6128 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 683 | Helm:Replace Bank 1 |  |  | Fresno | Emergency replacement of failed Helm 230/70 kV Bank 1 | Substation - Transformer | Replace | TBD | Emergency Event | Replace Transformer | NA | 2024-03-05 | 59 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 6.7555 | NA | 230 ¦ 70 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5808685 | T.0009930 | HELM: TXFR BK1 REP ETS51 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2024-01-22 | NA | 2024-04-15 | NA | FALSE | 3676 | NA | 894.3283 | 2249.8192 | 0 | 0 | 0 | 0 | 0 | 2249.8192 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 684 | PALERMO: JIT REPL BK 1 w/ 2 BANKS |  |  | Palermo CDP, Butte | 230/115x60kV Bank 1 has developed a leak and will be replaced on JIT Emergency project. | Substation - Transformer | Replace | TBD | Emergency Event | Replace Transformer | NA | 2024-03-04 | 58 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 8.0464 | NA | 230 ¦ 115 ¦ 60 kV | Not Available | Not Available | Not Available | NA | NA | 5796018 | T.0007127 | Palermo: Em Repl Bk 1 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-07-15 | NA | 2023-05-29 | NA | TRUE | 261 | NA | 27560.974 | 27800.4246 | 0 | 0 | 3954.5664 | 14472.4221 | 9112.2772 | 261.1589 | 0 | 0 | 0 | 0 | 0 | 27539.2657 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 27539.2657 | 19.7556 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 685 | KASSON: EM Replace BK 1 |  |  | San Joaquin | Due to the aThis project proposes to replace the deteriorated 115/60kV Transformer Bank 1, 60kV three-phase regulator, and associated equipment at Kasson Substation. | Substation - Transformer | Replace | NA | Emergency Event | Replace Transformer | NA | 2024-03-05 | 58 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.1988 | NA | 115 ¦ 60 kV | 638 | 3. Emergency Preparedness | NA | NA | NA | 5773301 | T.0002471 | Kasson: Replace Bank 1 | 1 | 65 | NA | NA | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-05-01 | 2019-08-05 | 2019-05-17 | NA | FALSE | 6944 | NA | 9735.4988 | 9735.4988 | 2959.5729 | 465.1161 | 72.4066 | 5.6129 | 11.2134 | 0 | 0 | 0 | 0 | 0 | 0 | 9735.4988 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 9011.1943 | 448.2536 | 69.7361 | 5.4059 | 10.5926 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 686 | Midway: Replace Bk 13 Spare Phase |  |  | Buttonwillow CDP, Kern | Emergency replacement of Miday Bank 13 spare transformer. | Substation - Transformer | Replace | TBD | Emergency Event | Replace Transformer | NA | 2024-03-15 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | 500 ¦ 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5807277 | T.0009605 | Midway: Replace Bk 13 Spare Phase | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-11-13 | NA | 2024-03-12 | NA | TRUE | 9468 | NA | 1712.2133 | 10251.0446 | 0 | 0 | 0 | 0 | 681.2392 | 2250.773 | 36.3245 | 0 | 0 | 0 | 0 | 681.2393 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 1860.6798 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 687 | Rio Oso: Replace Bank 1 Project |  |  | Sutter | In late December 2020, Rio Oso 230/115 kV Bank 1 A Phase saw an internal fault and failed. Install 3 single phase mobile transformers rated at 40MVA each to replace Transformer Bank 1 at Rio Oso until the new 3 phase 420mva transformer is installed. Current plan is 12/23. The Mobiles do not have an emergency rating (same as normal rating). In addition during this period, Bank 2 will be limited to normal rating of 134.4 MVA three phase. | Substation - Transformer | Replace | TBD | Emergency Event | Replace Transformer | NA | 2024-03-04 | 70 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 9.3219 | NA | 230 ¦ 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5794995 | T.0006954 | Rio Oso: EM Repl Bank 1 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2022-07-05 | NA | 2024-12-13 | NA | TRUE | 2000 | NA | 33070.7993 | 39042.2061 | 0 | 8.5572 | 19855.5313 | 8717.3048 | 3798.7523 | 4988.2437 | 1529.7737 | 0 | 0 | 0 | 0 | 32380.1455 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 688 | Vaca Dixon: Replace Bank 2 and 2A |  |  | Solano | Replace transmission bank 2/2A to one three-phase, 230/115 kV, 420 MVA, transformer bank with LTC at Vaca Dixon Substation. Due to concerns with the deteriorated transformer Westinghouse type, history of oil leaks, SAM recommends expediting the replacement of Vaca Dixon Bank 2/2A on emergency. The recommendation to expedite the bank under emergency had the review and concurrence of Substation Maintenance, Equipment Specialist, and Asset Strategy. | Substation - Transformer | Replace | NA | Emergency Event | Replace Transformer | NA | 2024-03-12 | 71 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 ¦ 115 kV | Not Available | 3. Emergency Preparedness | 4 | NA | NA | 5788181 | T.0005466 | Vaca Dixon - Replace Bank 2 & 2A | 1 | 65 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-06-16 | 2021-06-03 | 2021-12-17 | Clearances | TRUE | 11850 | NA | 12072.0601 | 12347.8468 | 0 | 3274.8763 | 8621.3037 | 174.5732 | 0.9319 | 0.375 | 275.7867 | 0 | 0 | 0 | 0 | 12071.6851 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 11502.5788 | 168.5381 | 0.89968 | 0.36204 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 689 | IGNACIO: EM REP BK 1 |  |  | Novato, Marin | This project will replace the Ignacio Substation Bank 1 with a 200MVA, 115/60kV LTC transformer.. This bank is expected to fail while in service, therefore, it is being replaced as an emergency project. The costs are based on an AACE Class 4 estimate. The funding authorization will support design, procurement and construction. | Substation - Transformer | Replace | NA | Emergency Event | Replace Transformer | NA | 2024-03-14 | 14 | NA | Wires - Minimum Required Scope (spot repair) Alternative | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 11.9486 | NA | 115 ¦ 60 kV | Not Available | 3. Emergency Preparedness | 5 | NA | NA | 5786429 | T.0004883 | IGNACIO: EM REP BK 1 | 1 | 65 | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-01-21 | 2020-01-28 | 2020-04-20 | NA | FALSE | 6800 | NA | 5867.1233 | 5867.1233 | 1244.0941 | 2768.1352 | 1854.8941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5867.1233 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 4012.2292 | 1562.3149 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 690 | Moraga Sub-EM Replace Reg 3 |  |  | Orinda, Contra Costa | Emergency Replacement of 115kV Bank #3 Regulator at Moraga sub | Substation - Other Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-06 | 19 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 15.8714 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5796162 | T.0007197 | Moraga Bank #3 Regulator | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-09-19 | NA | 2024-01-19 | NA | TRUE | 6005 | NA | 5741.9288 | 6124.103 | 0 | 0 | 71.5321 | 871.6504 | 4791.0436 | 273.7526 | 116.1243 | 0 | 0 | 0 | 0 | 5734.226 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 5218.0419 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 691 | EL DORADO PH: EM Replace CB 320 |  |  | El Dorado | This is a Just-in-time emergency replacement of 115kV CB 320. The breaker has had several issues and repairs over the years and the unit has been deemed too expensive to maintain. Substation Asset Management has concurred with the emergency replacement of the breaker, which remains in service and is being monitored by Maintenance. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-02-02 | 31 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.43336 | NA | 115 kV | Not Available | 3. Emergency Preparedness | NA | NA | NA | 5528580 | T.0003614 | El Dorado PH: Em Replace CB 320 | 1 | 65 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-11-04 | 2019-12-20 | 2019-12-20 | NA | FALSE | 1654 | NA | 1682.5038 | 1682.5038 | 1187.5152 | 121.097 | 74.5299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1682.5038 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1068.7636 | 161.9159 | 69.5302 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 692 | OAKLAND K REPLACE 115KV CB162 |  |  | Oakland, Alameda | During the inspection of CB162 at Oakland K (Claremont), it was found that the compressor would not hold air. Therefore, the existing oil circuit breaker must be replaced under an emergency replacement project. Additionally, a new CCVT on the line side (C-phase) needs to be installed to provide potentials to protection relays. CB162 was scheduled to be replaced under a planned project in 2023. Due to this emergency, CB162 will be replaced under this emergency project, and the breaker switches, structures, and the by-pass switches will be replaced on the planned project. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-19 | 51 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 3.9974 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5802458 | T.0008628 | Oak K: EM Repl CB 162 115kV | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-09-06 | NA | 2022-11-07 | NA | FALSE | 750 | NA | 1007.5796 | 1007.5796 | 0 | 0 | 0 | 788.9766 | 214.5834 | 4.0196 | 0 | 0 | 0 | 0 | 0 | 1003.56 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 710.7725 | 193.1249 | 3.6176 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 693 | Famoso: Emerg Repl CB 22 |  |  | Kern | Based on the ageing factor, non-standard wooden pole installations & maintenance challenges, replace existing CB 22 and associated switches, structures and PT's with a new CB 22, switches & PT's to match standards. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Age/Condition - Replace Breakers | NA | 2024-02-02 | 63 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.8913 | NA | 70 kV | Not Available | Not Available | Not Available | NA | NA | 5545884 | T.0007371 | FAMOSO: EM REPL CB 22 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-02-01 | NA | 2023-02-06 | NA | TRUE | NA | NA | 1562.276 | 1623.7995 | 0 | 0 | 74.7791 | 1117.2302 | 367.3786 | 40.9245 | 0 | 0 | 0 | 0 | 0 | 1559.3879 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 37.3896 | 558.6142 | 183.6892 | 3.174 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 694 | COCO PP: EM REPL CB 410 |  |  | Antioch, Contra Costa | During the CB410 test at Contra Costa PP, It was found that it had expelled oil from the breather. Further testing of the oil indicated flammability levels of +400%. In addition to the internal inspection, pre- insertion resistor values were tested and found to be out of spec per the manufacturers' guidance @ 13.8 ohms (Req. 1.4 ohms +/- 20%). Therefore, SAI concurred to the emergency replacement of CB410. In addition, the project entails installing 3 new CCVTs on A/B/C phase line side and 1 new CCVT on C phase bus side. Also, due to the foundation's existing condition, Civil recommended replacing the breaker foundation. Civil scope also includes installation of new operating platform for the circuit breaker, foundations for the CCVT support structures, and verhicle guard posts. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Age/Condition - Replace Breakers | NA | 2024-03-06 | 37 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence, Corrosion |  | NA | 19.1042 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5550544 | T.0008580 | CoCo PP: EM Repl CB 410 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-08-16 | NA | 2022-12-12 | NA | FALSE | NA | NA | 969.291 | 1169.6328 | 0 | 0 | 0 | 849.1281 | 120.1629 | 200.3417 | 0 | 0 | 0 | 0 | 0 | 969.291 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 764.2155 | 108.1466 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 695 | Oakland L: Replace CB322 & CB422 |  |  | Oakland, Alameda | Emergency replacement failed 115 kV oil HVCB 322 and 422 at Oakland L sub. Install 3 CCVTs and pull all new control cables. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-06 | 82 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 1.197 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5796720 | T.0007256 | Oak L: EM Repl CB322 & CB422 | 1 | 65 | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-28 | 2021-06-15 | 2021-06-15 | NA | FALSE | 1827 | NA | 1791.0014 | 1791.0014 | 0 | 0 | 1762.7601 | 28.2413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1791.0014 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1762.7601 | -92.2891 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 696 | Newark: Replace CB 994 |  |  | Fremont, Alameda | Emergency replacement of 230kV CB 974 & 994 at Newark Sub | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-08 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 27.7611 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5540555 | T.0006049 | NEWARK: REPL CAP BREAKER 994 EMER | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-03-04 | NA | 2021-07-06 | NA | FALSE | NA | NA | 1362.5843 | 1362.5843 | 0 | 277.8884 | 1026.7653 | 57.9305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1362.5843 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1304.6537 | -17.6425 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 697 | WOODWARD: EM Repl CB 122 |  |  | Fresno, Fresno | Emergency replacement of 115 KV HVCB 122 Woodward. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-06 | 32 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.9838 | NA | 115 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5531795 | T.0004262 | WOODWARD: REPL CB 122 (JIT) | 1 | 65 | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-11-04 | 2020-12-17 | 2020-12-17 | NA | FALSE | 1253 | NA | 1252.7464 | 1252.7464 | 189.0862 | 706.9601 | 329.9357 | 3.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.7464 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 189.0862 | 572.6032 | 281.6908 | 11.6348 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 698 | Lakeville: EM REPL CB262 |  |  | Sonoma | Emergency replacement of CB 222 and 262 at Lakeville substation. Both circuit breaker failed service testing and deemed unable to place back into service due to the possibility of catastrophic failure. CB 222 needed to be put into service first, followed by CB 262. CB 222 foundation was reused but new beam was used to support the new breaker, 2 CCVT foundations were placed on the high side for 3 phase line potential and a new bus transfer switch was installed inside the 230kv MPAC building. For CB 262, new foundation was installed for the new breaker, 2 new CCVT foundation on the line side and a bus potential was installed inside the 230kv MPAC building. Existing wires were used for both breakers. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-11 | 39 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 14.7021 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5545284 | T.0007237 | Lakeville: Repl CB 222 and 262 | 1 | 65 | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-05-03 | 2021-07-12 | 2021-05-17 | NA | FALSE | 1403 | NA | 1381.2497 | 1381.2497 | 0 | 0 | 1351.9651 | 29.2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1381.2497 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1216.7684 | -6.5025 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $1 Mil - $2 Mil ¦ NA
| 699 | Clayton: Replace CB 112 |  |  | Concord, Contra Costa | Emergency replacement of circuit breakers at EM Clayton Sub. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-06 | 48 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.9731 | NA | 115 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5532804 | T.0004363 | Clayton Sub CB 112 | 1 | 65 | NA | NA | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-30 | 2020-12-07 | 2020-12-07 | NA | FALSE | 2150 | NA | 2134.1988 | 2134.1988 | 711.504 | 554.6731 | 158.9284 | 43.9252 | 4.4658 | 0 | 0 | 0 | 0 | 0 | 0 | 2134.1988 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1372.2062 | 554.6731 | 6.7085 | 40.7196 | -175.1107 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 700 | Kern PP: Emerg Repl CB 112 |  |  | Bakersfield, Kern | Emergency replacement of failed Kern PP 115 kV CB 112 | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-04-12 | 59 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | 37.7504 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5543274 | T.0006913 | KERN PP: EM CB 112 FAIL | 1 | 65 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-03-08 | 2021-04-30 | 2021-05-10 | NA | FALSE | 912 | NA | 1070.2221 | 1070.2221 | 0 | 7.8221 | 1016.3154 | 46.0845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070.2221 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 950.6198 | -46.0403 | 58.6204 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 701 | Jefferson: Replace 230kV CB2712 |  |  | San Mateo | Emergency replacement of Jefferson 230 kV CB 2712 and 2612, along with the Protection relays for the CBs and shunt reactors. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-06 | 18 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.7091 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5798806 | T.0007616 | JEFFERSON SUB: EM REPL CB2712 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-10-09 | NA | 2024-02-27 | NA | TRUE | 894 | NA | 4360.0957 | 4363.4078 | 0 | 0 | 49.2371 | 893.3985 | 2704.1866 | 716.5856 | 0 | 0 | 0 | 0 | 0 | 3646.8222 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 4126.7832 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 702 | Morro Bay: Emerg Repl CB 532 |  |  | Morro Bay, San Luis Obispo | Emergency replacement of Morro Bay 230 kV CB 532 (Diablo 230 kV line) due to a SF6 leak. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-04 | 61 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion, Flooding |  | NA | 12.614 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5543273 | T.0006917 | MORRO BAY: EM REP CB 532 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-10-01 | NA | 2021-12-06 | NA | FALSE | NA | NA | 1280.6957 | 1280.6957 | 0 | 1.3523 | 1175.7949 | 103.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1280.6957 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 1.2171 | 1058.2155 | 93.1936 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 703 | FAMOSO: EM Repl CB 132- 152 |  |  | Kern | Famoso Substation is located in the vicinity of the City of McFarland, within Kern County, California. Circuit breakers 132 and 152 were installed in 1963. These need to be replaced for improved quality and efficiency. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-02-02 | 60 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.8913 | NA | 115 kV | 638 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5781324 | T.0004147 | Famoso: Rep EM CB 132_152 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2020-02-10 | NA | 2024-09-29 | NA | TRUE | 736 | NA | 5200.4075 | 5695.5965 | 551.3611 | 3049.8763 | 443.8714 | 616.7108 | 413.9792 | 552.6482 | 0 | 0 | 0 | 0 | 0 | 5142.9482 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 704 | GRAND ISLAND: EM repl CB 172- 182 |  |  | Sacramento | Having already been completed, this project immediately replaced failing 115kV OCB 172 using a breaker from emergency stock and then replaced identical OCB 182 the following year, to allow time for adequate design and material to be issued. The replacement of these end-of-life, oil-filled circuit breakers greatly increases the reliability of the substation and associated 115kV lines as well as improve personnel and public safety from events that could arise from catastrophic failure of said oil-filled equipment. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-06 | 44 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.9111 | NA | 115 kV | 638 | 3. Emergency Preparedness | NA | NA | NA | 5782263 | T.0004293 | Grand Island: Em Repl CB 172 & 182 | 1 | 65 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-10-15 | 2019-12-19 | 2019-12-19 | NA | FALSE | 1453 | NA | 1430.5983 | 1430.5983 | 900.0955 | 132.9291 | 2.0359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1430.5983 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1169.47 | 177.3501 | 1.916 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 705 | Kerman: REP EM SW 41 |  |  | Fresno | Install 1200AMPS center side break (V Type) switches for 41, 43 and 45 on existing northern structure at Kerman sub | Substation - Switch | Replace | NA | Emergency Event | Age/Condition - Replace Other Substation Equipment | NA | 2024-02-08 | 77 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.2852 | NA | 70 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5540141 | T.0005924 | KERMAN:REP EM SW 41 | 2 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-01 | NA | 2024-12-31 | NA | TRUE | NA | NA | 194.6037 | 1630.4091 | 0 | 31.3606 | 7.0544 | 116.0787 | 4.8268 | 1295.4519 | 175.6368 | 0 | 0 | 0 | 0 | 159.3204 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 38.4149 | 116.0787 | 4.8268 | 41.5056 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 706 | Gold Hill: Replace CB 202 Project |  |  | Folsom, Sacramento | On 12/10/2020, during switching for new Gold Hill CB 242 Test Program, the Gold Hill 230kV Bus-Tie CB 202 failed and was determined irrepairable after an immediate investigation. Substation Asset Implementation concurred to the emergency replacement of the failed circuit breaker on 12/14/2020. After performing the walkdown meeting, it was determined that the breaker foundation should be replaced due to age and that 2 sets of CCVT's would need to be installed for 230kV Bus 1 & 2 since the existing bus PT's were internal to the failed CB 202. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-28 | 56 | NA | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 12.8702 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5794387 | T.0006912 | Gold Hill: Em Replace CB 202 | 1 | 65 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-01-06 | 2021-03-31 | 2021-03-31 | NA | FALSE | 1380 | NA | 1398.5308 | 1398.5308 | 0 | 119.9998 | 1278.4557 | 0.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1398.5308 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1322.4145 | 0.07114 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 707 | Rossmoor: Install 230kV Bus Tie Breaker |  |  | Walnut Creek, Contra Costa | Phase 1 of the project was to replace Rossmoor failed transformer 2 under emergency conditions to have in service by 9/11/2019. Phase 2 of this project is to remove the temp transformer protection and replace with the final SMP design. The project will also add a 230kV Bus Sectionalizing Circuit Breaker for increased reliability and operational flexibility that is much needed in the sensitive Rossmoor/Lafayette area | Substation - Circuit Breaker | New | NA | Emergency Event | Replace Breakers | NA | 2024-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.0542 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5804086 | T.0004810 | Rossmoor: EM Replace Bank 2 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-05-02 | NA | 2025-08-14 | NA | TRUE | 2152 | NA | 28.5497 | 2152.0462 | 0 | 0 | 0 | 0 | 24.2681 | 402.1568 | 1725.6213 | 0 | 0 | 0 | 0 | 24.2681 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 708 | Humboldt: Repl CB102 & Instl Synch Scope |  |  | Humboldt | Replace 115kV Oil Circuit Breakers with new SF6 Circuit Breakers for breaker 172, 182, and 112, relocate circuit breaker 102, replace switches 111, 113, 115, 181, 183, 185, add new switches 175 & 101, add new 115kV line CCVTs, add new 115kV wave trap and CCVT with carrier accessories. 112, relocate circuit breaker 102, replace switches 111, 113, 115, 181, 183, 185, add new switches 175 & 101, add new 115kV line CCVTs, add new 115kV wave trap and CCVT with carrier accessories. Humboldt Substation. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-08 | 59 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.569 | NA | 115 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5790276 | T.0005831 | Humboldt - EM Replace CB 102,112,172,182 | 4 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-18 | NA | 2020-06-29 | NA | FALSE | 1549 | NA | 1549.1994 | 1549.1994 | 0 | 1546.2049 | 1.8473 | 1.1473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1549.1994 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 1546.2049 | -167.095 | 1.0215 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 709 | Humboldt: Repl CBs 112, 172, 182 |  |  | Humboldt | Replace 115kV Oil Circuit Breakers with new SF6 Circuit Breakers for breaker 172, 182, and 112, relocate circuit breaker 102, replace switches 111, 113, 115, 181, 183, 185, add new switches 175 & 101, add new 115kV line CCVTs, add new 115kV wave trap and CCVT with carrier accessories. 112, relocate circuit breaker 102, replace switches 111, 113, 115, 181, 183, 185, add new switches 175 & 101, add new 115kV line CCVTs, add new 115kV wave trap and CCVT with carrier accessories. Humboldt Substation. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-08 | 62 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.569 | NA | 115 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5791020 | T.0005831 | Humboldt - EM Replace CB 102,112,172,182 | 4 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-04-04 | NA | 2023-07-11 | NA | TRUE | 4548 | NA | 5058.5431 | 5074.3213 | 0 | 581.3565 | 1237.0789 | 2504.3902 | 744.2222 | 7.2735 | 0 | 0 | 0 | 0 | 0 | 5067.0479 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 5067.0478 | -27.2769 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 710 | Metcalf: Replace CB 694 |  |  | Santa Clara | Replace 230kV Cap Bank Step 5 High Voltage Circuit Breaker 694. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-13 | 24 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5540301 | T.0005958 | METCALF: EM Replace CB 694 74033781 | 1 | 65 | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-01-04 | 2021-10-01 | 2021-10-15 | NA | FALSE | 1490 | NA | 1447.2547 | 1447.2547 | 0 | 246.5046 | 1194.8846 | 5.8654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1447.2547 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 221.8542 | 1075.3965 | -65.7141 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 711 | CORCORAN: EM Repl CB 152 |  |  | Kings | Replace circuit breaker 152 at Corcoran Substation under a just-in-time emergency project. This project was a like for like replacement of existing 115kV Bus Tie Circuit Breaker 152 due to the failure on some of the tests performed by maintenance. Multiple attempts were performed to repair various leaks, but PG&E Substation Asset Management decided to replace the circuit breaker as an emergency project to maintain the system reliability at Corcoran Substation. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-05 | 28 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.8529 | NA | 115 kV | 638 | 3. Emergency Preparedness | Not Available | NA | NA | 5782000 | T.0004259 | Corcoran: Replace CB 152 (JIT) | 1 | 65 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-12-10 | 2020-03-13 | 2020-02-17 | NA | FALSE | 1147 | NA | 1058.8647 | 1058.8647 | 550.7596 | 462.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058.8647 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 954.2008 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 712 | MILPITAS: EM Replace CB 342 115KV |  |  | Milpitas, Santa Clara | Replace existing failed CB342 with new breaker from CEM Stock, If breaker is equipped with dual trip coils, Jumper Trip Coils 1 and 2 at the breaker cabinet. The cap bank breaker 694 tripped due to internal fault on C phase. Since step 2 cap bank breaker 664 already failed, it is important to replace 694 immediately as two of the five steps are currently out of service. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-02-08 | 30 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.3452 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5792842 | T.0006430 | MILPITAS EM Replace CB 342 74035988 | 1 | 65 | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-11-09 | 2021-10-22 | 2021-11-30 | NA | FALSE | 1321 | NA | 1306.6932 | 1306.6932 | 0 | 993.8864 | 279.0253 | 30.781 | 3.0005 | 0 | 0 | 0 | 0 | 0 | 0 | 1306.6932 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1135.9015 | 2.5877 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 713 | LAKEVILLE: EM Rep CB 232 and SWes |  |  | Sonoma | Replace HVCB 232 and associated SW's. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-11 | 40 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 14.7021 | NA | 230 kV | 638 | 3. Emergency Preparedness | Not Available | NA | NA | 5526881 | T.0003355 | LAKEVILLE: EM Replace CB 232 | 1 | 65 | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-10-04 | 2022-01-13 | 2022-01-13 | NA | TRUE | 2370 | NA | 2347.9913 | 2347.9913 | 120.4243 | 533.9982 | 1149.9823 | 505.0385 | 35.8353 | 0 | 0 | 0 | 0 | 0 | 0 | 2347.9913 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 108.1106 | 480.5984 | 1034.9841 | 367.3514 | 30.9005 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 714 | MORRO BAY: EM Repl CB 622 |  |  | Morro Bay, San Luis Obispo | Replacement of 230KV HVCB 622. Existing 50+ year old 230KV OCB 622 to be replaced along with 230kV SW 621. relocated on new foundations. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-04 | 59 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion, Flooding |  | NA | 12.614 | NA | 230 kV | 638 | 3. Emergency Preparedness | Not Available | NA | NA | 5532305 | T.0004257 | MORRO BAY EM REP CB 622 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-03-10 | NA | 2020-08-06 | NA | FALSE | NA | NA | 2006.1188 | 2006.1188 | 454.3052 | 1490.5108 | 12.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2006.1188 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 454.3052 | 1490.5108 | 12.5507 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 715 | Newark: Repl CB 470 |  |  | Fremont, Alameda | The emergency replacement of circuit breaker 470 at Newark substation | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-08 | 20 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 27.7611 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5802984 | T.0008739 | NEWARK: EM Replace CB 470 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-03-03 | NA | 2023-04-07 | NA | TRUE | 800 | NA | 1215.0099 | 1221.6341 | 0 | 0 | 0 | 82.8052 | 1126.4502 | 12.3787 | 0 | 0 | 0 | 0 | 0 | 1209.2554 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1089.2671 | 5.179 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 716 | Moraga: Repl OCBs 612 & 622 |  |  | Orinda, Contra Costa | The emergency replacement of oil circuit breakers 612 and 622 at Newark substation | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-06 | 61 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 15.8714 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5804045 | T.0009053 | Moraga: Repl OCBs 612 & 622 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-10-10 | NA | 2024-02-18 | NA | TRUE | 2000 | NA | 3276.6043 | 3849.1623 | 0 | 0 | 0 | 0 | 2139.8883 | 1686.62 | 22.654 | 0 | 0 | 0 | 0 | 2139.8883 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 3408.7569 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 717 | Evergreen EM Repl CB 152 |  |  | San Jose, Santa Clara | The existing 115KV Breaker CB 152 at Evergreen Substation is leaking gas out and recommended for replaceemnt. This project will replace the existing breaker CB 152 with a new 115kV breaker with associated switches & Structure | Substation - Circuit Breaker | Replace | NA | Emergency Event | Age/Condition - Replace Breakers | NA | 2024-02-02 | 38 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.3776 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5800379 | T.0008197 | Evergreen EM Repl CB 152 74046522 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-06-14 | NA | 2023-09-15 | NA | TRUE | 900 | NA | 2215.1319 | 2218.1728 | 0 | 0 | 0 | 324.5107 | 2073.3494 | -179.6873 | 0 | 0 | 0 | 0 | 0 | 2397.8601 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2162.203 | -162.3618 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 718 | El Cerrito G: Replace 115KV CB112 |  |  | El Cerrito, Contra Costa | The oil filled 115 kV CB 112 at El Cerrito G substation on the 115 kV Sobrante No 1 line will be replaced with a MEPPI, 40 kA, 2000 AMP HVCB. The oil filled breaker was found with bad CTs and had to be taken out of service during the prechecks leading up to the Test Program and release to operations of BAAH Bay 5 & 6 and Bank 2. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-20 | 70 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 8.2538 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5799318 | T.0007744 | El Cerrito G: EM Repl 115kV CB 112 | 1 | 65 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-02-03 | NA | 2022-03-31 | NA | FALSE | 912 | NA | 1088.5335 | 1088.5335 | 0 | 0 | 360.9026 | 726.1845 | 1.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.5335 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 911.1466 | 1.2095 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 719 | HERNDON: EM Replace CB 242 |  |  | Fresno, Fresno | This emergency project replaces Herndon CBs 242 & 262 with new SF6 230kV, 2000 A breakers including new switches and structures. The civil group recommended the replacement of the lattice structures because they were inadequate for new switches and their foundations were severely cracked. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-08 | 41 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 13.3414 | NA | 230 kV | 638 | 3. Emergency Preparedness | NA | NA | NA | 5773451 | T.0002504 | EM HERNDON REP CB 262 &SWS | 2 | 65 | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-01-04 | 2018-11-30 | 2019-04-26 | NA | FALSE | 4000 | NA | 2740.1787 | 2740.1787 | 1177.5364 | 19.9628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2740.1787 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 2720.2159 | -96.1406 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 720 | SARATOGA: EM REP: CB232 230KV 74020947 |  |  | Saratoga, Santa Clara | This project proposes to replace CB 232, Air Switch 233, and supporting equipment. Saratoga Bank 1 failed in May of 2018 due to corrosive sulfur corrosion. The transformer is being replaced under emergency order 74019563. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-02-06 | 34 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.4212 | NA | 230 kV | 638 | 3. Emergency Preparedness | Not Available | NA | NA | 5783358 | T.0004264 | SARATOGA: EM REP: CB232 230KV 74020947 | 1 | 65 | NA | NA | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-01-27 | 2020-08-31 | 2020-06-24 | NA | FALSE | 4900 | NA | 2349.4057 | 2349.4057 | 893.3564 | 1399.1661 | -12.5088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2349.4057 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | -69.3919 | 2173.9722 | -11.4848 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 721 | Clayton: Replace CB 122 |  |  | Concord, Contra Costa | This project replaced the failed 115 kV oil breaker 122 with a new 3000 Amps SF6 breaker at Clayton Substation. In an effort to support PG&E top-level initiatives to improve safety, this project replaced failed breaker at Clayton Substation. This improved 115 kV system in Concord area. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Breakers | NA | 2024-03-06 | 58 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.9731 | NA | 115 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5537239 | T.0004975 | CLAYTON EM REPLACE CB122 74028644 | 1 | 65 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-04-01 | 2020-04-26 | 2020-04-26 | NA | FALSE | 1500 | NA | 1522.3661 | 1522.3661 | 142.7397 | 1382.7003 | -3.0739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1522.3661 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1426.2958 | -1.1535 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 722 | Purchase bushings for COTA replacements |  |  | San Jose, Santa Clara | Emergency replacement of bushings for CEM stock. | Substation - Other Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-02-02 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.68753 | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5555844 | T.0009938 | COTA Bushings Order-EM Stock | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | NA | NA | 2024-11-13 | NA | FALSE | NA | NA | 65.5403 | 2579.6143 | 0 | 0 | 0 | 0 | 0 | 2579.6144 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 723 | Metcalf: Repl Bk 11B & 11C |  |  | Santa Clara | Emergency replacement of failed Bk 11B & 11C at Metcalf substation; | Substation - Transformer | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-13 | 56 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 500 ¦ 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5806639 | T.0009586 | Metcalf: EM Repl Bk 11B & 11C | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-09-17 | NA | 2026-03-27 | NA | FALSE | 25000 | NA | 187.5346 | 4198.5849 | 0 | 0 | 0 | 0 | 122.343 | 424.9437 | 0 | 0 | 0 | 0 | 0 | 122.343 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 724 | Midway: Replace Midway BK13 A Bushings |  |  | Buttonwillow CDP, Kern | Emergency replacement of failed BK13 A Bushings at Midway substation; | Substation - Other Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-15 | 22 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | 500 ¦ 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5554008 | T.0009471 | MIDWAY: EM BK 13 A PHASE BUSHING REPLC | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-09-06 | NA | 2024-11-01 | NA | FALSE | NA | NA | 171.8433 | 1209.4938 | 0 | 0 | 0 | 0 | 7.7653 | 1201.7285 | 0 | 0 | 0 | 0 | 0 | 7.7652 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 561.1491 | 0% | NA | TBD | NA | 100% | 0%
| 725 | Placer: EM Replace Batteries |  |  | Placer | Emergency replacement of failed station batteries at Placer sub | Substation - Other Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5555366 | T.0009798 | PLACER: EM REPLACE BATTERIES | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-07-31 | NA | 2024-09-25 | NA | FALSE | NA | NA | 189.9051 | 2106.0309 | 0 | 0 | 0 | 0 | 163.9331 | 1942.0978 | 0 | 0 | 0 | 0 | 0 | 163.9331 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 726 | Bellota: EM Replace SW 233 |  |  | San Joaquin | Emergency replacement of failed SW 233 at Bellota substation | Substation - Switch | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-01 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5551341 | T.0008848 | Bellota: EM Replace SW 233 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-04-29 | NA | 2024-07-31 | NA | TRUE | NA | NA | 235.6888 | 1143.3842 | 0 | 0 | 0 | 8.2782 | 219.0414 | 916.0645 | 0 | 0 | 0 | 0 | 0 | 227.3197 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 7.4504 | 197.1372 | 139.897 | 0% | NA | TBD | NA | 100% | 0%
| 727 | Brighton: EM Replace Sub fence |  |  | Sacramento, Sacramento | Emergency replacement of fence at Brighton substation. | Substation - Structure | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-01 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 6.4413 | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5804686 | T.0009142 | BRIGHTON: EM REPLACE FENCE | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-09-20 | NA | 2024-12-23 | NA | TRUE | 1900 | NA | 359.5354 | 1652.8167 | 0 | 0 | 0 | 0 | 292.098 | 1333.3364 | 27.3823 | 0 | 0 | 0 | 0 | 292.098 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 728 | GARBERVILLE: EM Mitigate Sliding Hill |  |  | Garberville CDP, Humboldt | Emergency replacement of the Battery Charger at GARBERVILLE SUBSTATION. The Battery Charger at GARBERVILLE SUBSTATION was found in a failed state during a WSIP audit. The Battery Charger at GARBERVILLE SUBSTATION was replaced and placed back into service. | Substation - Structure | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.3065 | NA | 60 kV | 638 | 3. Emergency Preparedness | NA | NA | NA | 5525759 | T.0002876 | GARBERVILLE: Mitigate Sliding Hillside | 1 | 65 | NA | NA | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-24 | 2019-08-16 | 2019-08-16 | NA | FALSE | 1688.07 | NA | 1671.1642 | 1671.1642 | 342.2548 | -62.1866 | 1.8077 | 0 | 2.2169 | 0.877 | 0 | 0 | 0 | 0 | 0 | 1670.2872 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2023 ¦ 2024 | 342.2548 | -62.1866 | -17.7786 | 0 | 2.1909 | 0.86669 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 729 | Bellota: Replace SW 243 |  |  | San Joaquin | Replace Rancho Seco-Bellota 230kV line 2 SW 243. Substation maintenance has not had success in making repairs to gear box or adjustments to fully open switch resulting in its replacement. Existing switch is underhung 6 pole gang operated and will be replaced with SW 241 and SW 243 for CB 240. | Substation - Switch | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-01 | 60 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5547159 | T.0007630 | BELLOTA REPLACE SWITCH 243 | 1 | 65 | NA | NA | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-04-04 | 2023-07-19 | 2023-07-19 | NA | TRUE | 1203.907 | NA | 1193.4403 | 1194.6609 | 0 | 0 | 25.2959 | 473.8872 | 687.1174 | 8.3603 | 0 | 0 | 0 | 0 | 0 | 1186.3006 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 22.7663 | 426.4987 | 618.4057 | -111.2541 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 730 | KERCKHOFF: EM Replace SW 113 and CB 112 |  |  | Fresno | The project objective is to replace existing 115kV breaker 112 with a new breaker; Replace existing switch 111 and 113 with new switches and replace existing CB 112 dead end structure with a new structure | Substation - Circuit Breaker | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-02-07 | 36 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.0825 | NA | 115 kV | 638 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5776919 | T.0003366 | EM KERCKHOFF REP SW 113 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-05-28 | NA | 2024-07-09 | NA | TRUE | 1022 | NA | 992.9682 | 1021.9401 | 54.6296 | 54.1162 | 154.9724 | 86.7045 | 37.4342 | 41.1567 | 0 | 0 | 0 | 0 | 0 | 980.7833 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 731 | Round Mountain: Em Repl Rear Gate-WSIP |  |  | Round Mountain CDP, Shasta | Back in 2016, as part of substation security upgrade program (Tier 2/3), the old substation fence was replaced with 10’ high pre-cast walls on the west side only, and with 10’ high non-visibility fence (with vertical vinyl slats) along all other sides. Later, during WSIP (wildfire) inspections, it was determined that on the north side of the substation, the fencing with vinyl slats is too close to energized equipment, and approximately for 1400 linear feet of fencing, the non-visibility vinyl slats were removed. This included one double swing gate as well. Corporate security has determined that the visibility into the substation for the sections with removed vinyl slats is unacceptable, and measures should be taken to install new fencing per Corporate Security Standard SEC-2010S Rev 0, to prevent visibility into the substation. This area is Highlighted in the attached drawing 3015615_R2. For this replacement of 1400 feet, Corporate Security has determined that Shakespeare fence (manufactured by Safefence) is an acceptable replacement. After consulting with Shakespeare manufacturing, we have determined that we can salvage, and re-use the existing 6” diameter fence posts, and pier foundations (at a very large saving, especially since the existing fencing is less than 6 years old). Shakespeare will provide clips, that can be bolted into the existing fence posts, and Shakespeare fence panels can be secured into these clips. Therefore, there will not be any foundation work, or fence post installation. | Substation - Structure | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-06 | 6 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Extreme Heat |  | NA | 29.1389 | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5540303 | T.0005956 | ROUND MOUNTAIN: EM REPL FENCE | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2024-01-22 | NA | 2024-04-15 | NA | TRUE | NA | NA | 639.0287 | 1124.2065 | 0 | 6.1088 | 27.5553 | 43.7046 | 65.4257 | 981.412 | 0 | 0 | 0 | 0 | 0 | 142.7945 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 31.9809 | 41.5192 | 62.1543 | 703.7635 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 732 | Emergency Replacement , Overall Budget |  |  | NA | Bucket for Substation Emergency replacement | Substation - Multiple | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 638 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5506263 | NA | NA | NA | 65 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1338.2663 | 59110.9936 | 0 | 0 | 0 | 0 | 0 | 32772.7273 | 25000 | 80000 | 80000 | 80000 | 80000 | 1338.2663 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 733 | Colusa: Rebuild 60 kV |  |  | Colusa, Colusa | Due to the recent catastrophic failure of Bank 2 A-phase transformer, Substation Asset Management has concurred to emergency replace Bank 2 with a 3-phase transformer (JO# 74031330). This project will be performed in conjunction with the Colusa Emergency Replace Distribution Equipment (JO# 74017764) to allow extensive remediation to be performed. A third JO was issued to replace Bank 1 on a just-in-time emergency basis (JO# 74032102). In addition, a fourth JO has been issued to replace the 60kV equipment under emergency (JO# 74035560). When all work is completed, the station will be fully rebuilt and remediated. | Substation - Structure | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-04-02 | 19 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 0.25267 | NA | 60 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5792278 | T.0006254 | Colusa: Replace 60kV Equipment | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-06-28 | NA | 2024-03-22 | NA | TRUE | 208 | NA | 2007.1113 | 2121.7855 | 0 | 42.3415 | 1129.7171 | 556.906 | 236.8871 | 155.9337 | 0 | 0 | 0 | 0 | 0 | 1965.8518 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 2164.5501 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 734 | PITTSBURG PP: EM REPL CB822 & SWITCH 823 |  |  | Pittsburg, Contra Costa | During a regular maintenance inspection of the 230KV double bus single breaker section of the Pittsburg Power Plant Substation found that the Switch 823 mechanical arms failed and deemed to be unrepairable. This Switch 823 is a part of the section tie breaker that connects Bus Section E and Bus Section D Main Bus 2. Civil Engineering determined that re-using the current latctice structure would fail under peak wind loads and the existing pile/pilecap connection is not sufficient for seismic load transfter. Due to this analysis, The Switches on the current lattice structure would be removed and a new switch structures and will be installed for the new switches. In addition during the walkdown, it was found that the current CB 822 and its structure is deteriorating and in need of replacement. This project will also include replacing the deteriorating CB 822 with a 230KV 3000A 63KA High voltage breaker. | Substation - Circuit Breaker | Replace | NA | Emergency Event | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-06 | 31 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 28.8512 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5547227 | T.0007657 | Pittsburg PP SWitch 823 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-09-25 | NA | 2024-01-31 | NA | TRUE | NA | NA | 2740.0702 | 2868.9835 | 0 | 0 | 29.8556 | 289.3786 | 2008.7564 | 540.9931 | 0 | 0 | 0 | 0 | 0 | 2327.9905 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 319.2341 | 1797.1206 | 369.5088 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 735 | Oakland J: Replace 115kV PTs & Structure |  |  | Oakland, Alameda | Emergency project to replace failed 115kV bus PTs & associated structures. The failed PTs caused outages to 50,000 customers as well as failure of other equipment. | Substation - Structure | Replace | NA | Emergency Event | Age/Condition - Replace Other Substation Equipment | NA | 2024-02-28 | 64 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 2.5059 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5552205 | T.0009033 | Oak J: EM Repl 115kV Bus PTs & Structure | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-02-20 | NA | 2023-04-19 | NA | TRUE | NA | NA | 2983.1329 | 2990.8356 | 0 | 0 | 0 | 0 | 2927.8293 | 63.0063 | 0 | 0 | 0 | 0 | 0 | 2927.8293 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2635.0461 | 49.9834 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 736 | GARBERVILLE: EM Repl 33,35,43,45 |  |  | Garberville CDP, Humboldt | Emergency replacement of 60kV SW 33, 35, 43, & 45 at Garberville Sub | Substation - Switch | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-05 | 76 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.3065 | NA | 60 kV | Not Available | Not Available | Not Available | NA | NA | 5544620 | T.0007086 | GARBERVILE:EMRPL SW33,35,43,45, 74038748 | 1 | 65 | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-05-02 | 2022-05-14 | 2022-05-14 | NA | FALSE | 2950 | NA | 2935.3454 | 2935.3454 | 0 | 0 | 146.3048 | 2788.8737 | 0.1669 | 0 | 0 | 0 | 0 | 0 | 0 | 2935.3454 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 129.3263 | 2551.058 | 0.15244 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 737 | Vaca Dixon: Replace 230 kV Shunt Caps |  |  | Solano | Emergency replacement of 230 kV Shunt Caps at Vaca-Dixon substation | Substation - Reactive Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-12 | 39 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5792199 | T.0006308 | Vaca Dixon: Em Repl 230kV Shunt Caps | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-05-10 | NA | 2023-11-06 | NA | TRUE | 250 | NA | 9947.3643 | 9969.2626 | 0 | 399.6031 | 3212.9739 | 1469.5746 | 4838.5301 | 48.581 | 0 | 0 | 0 | 0 | 0 | 9920.6816 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 9010.2817 | 58.9181 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 738 | IGNACIO: EM Repl SW 183 & 185 |  |  | Novato, Marin | Emergency replacement of deteriorating 115 kV SW 183,185 at Ignacio substation | Substation - Switch | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-14 | 62 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.9486 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5796093 | T.0007170 | Ignacio: Repl Sw 183 & 185 | 1 | 65 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-26 | 2021-04-30 | 2021-04-30 | NA | FALSE | 1538 | NA | 1449.3761 | 1449.3761 | 0 | 0 | 1449.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1449.3761 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 1414.6534 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $2 Mil - $3 Mil ¦ NA
| 739 | METCALF: EM Replace AC Panel BK 11 |  |  | Santa Clara | Emergency replacement of Metcalf AC Panel BK 11 | Substation - Other Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-13 | 55 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 37.8815 | NA | 500 ¦ 230 kV | 638 | 3. Emergency Preparedness | Not Available | NA | NA | 5522282 | T.0001870 | METCALF BK11 AC PANEL 74005700 EM | 1 | 65 | NA | NA | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-01 | 2022-09-07 | 2022-09-07 | NA | FALSE | 1265 | NA | 1219.896 | 1219.896 | 32.4042 | 192.3672 | 582.6065 | 123.5888 | 6.279 | 0 | 0 | 0 | 0 | 0 | 0 | 1219.896 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 29.1637 | 173.1304 | 524.3459 | 111.2299 | -27.8079 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 740 | Midway: Repl 500kV Bk Tert Insul |  |  | Buttonwillow CDP, Kern | Emergency replacement of Midway 500 kV Bank 11 Tertiary Reactor | Substation - Reactive Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-15 | 18 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5544579 | T.0007084 | MIDWAY: EM BK 11 TERT REACTOR FDN-INSUL | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 3 | 2024-03-01 | NA | 2024-07-31 | NA | TRUE | NA | NA | 3133.872 | 3483.37 | 0 | 0 | 42.982 | 415.5387 | 2400.2051 | 624.6442 | 0 | 0 | 0 | 0 | 0 | 2858.7257 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 39.9927 | 386.639 | 2233.2768 | 376.3955 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 741 | Pittsburg Sub: Replace SW 419 |  |  | Pittsburg, Contra Costa | Emergency replacement of Pittsburg PP 230 kV SW 419. Switch 419 failed during normal maintenance interval. This 230kV switch is a part of two bus selector switches located at bus section D. Civil engineering determined that the existing switch support structure does not meet current seismic standard. Complete replacement of the switch support structure, its foundations, and two bus selector switches is recommended. | Substation - Switch | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-06 | 24 | NA | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 28.8512 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5543039 | T.0006821 | Pittsburg PP - Switch 419 | 1 | 65 | NA | NA | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-04-12 | 2022-06-02 | 2022-06-02 | NA | FALSE | 1480 | NA | 1461.605 | 1461.605 | 0 | 23.1456 | 622.9428 | 823.1462 | -7.6296 | 0 | 0 | 0 | 0 | 0 | 0 | 1461.605 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1322.3114 | -153.0274 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 742 | VACA DIXON: EM REPLACE 1306 ABC REACTORS |  |  | Solano | Emergency replacement of Shunt Reactor 1306 reactor at Vaca-Dixon substation due to failure | Substation - Reactive Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-12 | 16 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | Not Available | Not Available | Not Available | NA | NA | 5550552 | T.0008591 | Vaca Dixon: Em Repl 1306 Reactors | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-06-13 | NA | 2023-10-12 | NA | FALSE | NA | NA | 1398.9109 | 1402.6437 | 0 | 0 | 0 | 52.2795 | 1341.8107 | 8.5535 | 0 | 0 | 0 | 0 | 0 | 1394.0902 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 47.0516 | 1207.6296 | 4.3387 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 743 | ROUND MOUNT: EM Repl MOAS 821- 823- 825 |  |  | Round Mountain CDP, Shasta | Install approximately 300ft of 30" trench North of MOAS's 821, 825, 831, and 835 to route MOAS's 821, 825, 831, and 835 control, power, alarm and fiber conductors. | Substation - Switch | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-06 | 23 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Extreme Heat |  | NA | 29.1389 | NA | 500 kV | 638 | 3. Emergency Preparedness | Not Available | NA | NA | 5782104 | T.0004266 | ROUND MOUNTAIN: EM Rep MOAS 821,823,825, | 2 | 65 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-07-01 | 2019-12-09 | 2020-02-25 | NA | FALSE | 7129 | NA | 6755.0939 | 6755.0939 | 4589.5785 | 1525.9189 | -30.4008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6755.0939 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 6388.5628 | -28.5588 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 744 | Morro Bay: Flood Mitigation Transmission |  |  | Morro Bay, San Luis Obispo | Minimize or reduce impact of flooding on the Transmission Switching Station. | Substation - Structure | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 12.614 | NA | 230 ¦ 115 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5536006 | T.0004816 | MORRO BAY SWSTA: EM FLOOD MITIGATION TRN | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-10-01 | NA | 2021-10-05 | NA | FALSE | NA | NA | 2623.2058 | 2623.2058 | 140.0475 | 1007.8998 | 1445.8825 | 28.9268 | 0.4492 | 0 | 0 | 0 | 0 | 0 | 0 | 2623.2058 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 140.0475 | 1007.8998 | 1445.8825 | 28.9268 | 0.44917 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 745 | Vaca Dixon: Replace 1301 Shunt Reactors |  |  | Solano | On 2/12/2021, one of the Vaca Dixon CB 1301 tertiary reactors became over-heated and caught fire, causing the 500/230kV Bank 11 and associated 1301/1302/1303/1304 tertiary reactors to be cleared until the fire burned out. On 2/22/2021, Substation Asset Implementation concurred to the emergency replacement of all three 1301 tertiary reactors using new equipment recently ordered for a similar job at Table Mountain Substation that was cancelled. Upon performing the walkdown meeting on 4/14/2021, it was determined that the new reactors would not match the existing, non-standard footings and that the foundations and support insulators would need to be replaced as well. This project will replace the TB 11 Tertiary reactors 1301 ABC phases, including the foundations and support insulators | Substation - Reactive Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-12 | 32 | NA | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 ¦ 230 kV | Not Available | Not Available | Not Available | NA | NA | 5544723 | T.0007114 | Vaca Dixon: Em Repl 1301 Reactors | 1 | 65 | NA | NA | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-10-18 | 2022-01-28 | 2022-01-28 | NA | FALSE | 1430 | NA | 1408.4625 | 1408.4625 | 0 | 0 | 945.7677 | 445.9902 | 16.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 1408.4625 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 851.191 | 401.391 | 83.986 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 746 | Trinity Sub: Em Repl Fence-WSIP |  |  | Weaverville CDP, Trinity | PG&E proposes to replace the entire existing fence with both chain link and non-conductive fencing at the Trinity Substation | Substation - Structure | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-02-14 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | 1.3227 | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5541291 | T.0006200 | Trinity Sub: Em Repl Fence-WSIP | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-10-16 | NA | 2024-01-19 | NA | TRUE | NA | NA | 1638.6429 | 1643.3089 | 0 | 5.8148 | 37.8933 | 85.8829 | 1425.9464 | 87.7715 | 0 | 0 | 0 | 0 | 0 | 1555.5374 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 39.3373 | 77.2943 | 1283.3516 | 79.5318 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 747 | Placer: Repair/Refurbish Bank 1_WSIP |  |  | Placer | Refurbish bank #1 bushings at Placer sub | Substation - Other Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-12 | 69 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 ¦ 60 kV | Not Available | Not Available | Not Available | NA | NA | 5539564 | T.0005806 | Placer: Replace BK1 Bushings - WSIP | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-03-23 | NA | 2021-05-14 | NA | TRUE | NA | NA | 1137.426 | 1142.092 | 0 | 51.9184 | 964.6152 | 20.8092 | 53.7582 | 50.991 | 0 | 0 | 0 | 0 | 0 | 1091.101 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 46.7266 | 868.1535 | 18.7283 | 48.3825 | 42.8498 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 748 | Drum PH 1:Replace SW363 Structure-WSIP |  |  | Placer | Replace 115kV SW 363’s (2), 357, 353’s (2), 347, 343’s (2) and related structures. | Substation - Switch | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-02-09 | 114 | NA | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 2.2491 | NA | 115 kV | Not Available | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5785879 | T.0004814 | Drum PH 1: Replace SW 333 Structure-WSIP | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2020-04-14 | NA | 2024-10-17 | NA | TRUE | 200 | NA | 5909.7274 | 8470.0786 | 85.9725 | 4788.8193 | 454.0676 | 389.4896 | 131.2555 | 2606.2034 | 14.2706 | 0 | 0 | 0 | 0 | 5849.6046 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 749 | TESLA: EM Replace Station Service BK 4 |  |  | Alameda | Replace the existing station service transformer #4, #5 and #6. Install a new station service transformer by CB 522. Replace the outdoor AC panels for station service transformer #4 and #5. | Substation - Voltage Support Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-15 | 19 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 69.382 | NA | 500 ¦ 230 ¦ 115 kV | 638 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5522385 | T.0001996 | TESLA: EM REPL STATION SERVICE BANK #4 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-10-21 | NA | 2024-01-24 | NA | TRUE | NA | NA | 5053.1411 | 5183.3851 | 502.0906 | 386.4993 | 37.0763 | 958.6231 | 2469.4271 | 262.6127 | 0 | 0 | 0 | 0 | 0 | 4920.7723 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 395.1757 | 347.8493 | 33.3687 | 862.7607 | 2222.4842 | 156.4686 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 750 | ROUND MOUNTAIN: Repl Backup Generator |  |  | Round Mountain CDP, Shasta | Replace under sized backup generator with larger backup generator with minimum size of 450VA. | Substation - Other Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-06 | 24 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Extreme Heat |  | NA | 29.1389 | NA | 500 ¦ 230 kV | 638 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5531647 | T.0004226 | ROUND MTN: EM REPL BACKUP GEN 74020803 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 3 | 2024-03-04 | NA | 2024-06-06 | NA | TRUE | NA | NA | 1156.9734 | 1409.1565 | 77.4743 | 272.4095 | 381.3576 | 247.2962 | 161.7761 | 255.5502 | 0 | 0 | 0 | 0 | 0 | 1153.6064 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 69.727 | 245.1687 | 343.2219 | 222.5667 | 145.5986 | 5.426 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 751 | VACA DIXON: EM Install Station Lighting |  |  | Solano | Substation Maintenance brought up a safety issue at Vaca Dixon Substation that existed due to insufficient lighting within the station that made the station difficult and dangerous to navigate for any personnel driving in the station at night. This project will install standard lighting, including new conduit runs and lighting panels, in all required areas of the 60kV, 230kV and 500kV yards at Vaca Dixon Substation. While Project Engineering support is being provided by internal Substation Engineering, design has been contracted to HDR since they are also designing several other projects at the station and the construction will be performed by Station Construction. | Substation - Other Equipment | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 ¦ 115 kV | 638 | 3. Emergency Preparedness | NA | NA | NA | 5774677 | T.0002896 | Vaca Dixon: JIT Install Station Lighting | 1 | 65 | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-11-28 | 2018-01-16 | 2019-06-05 | Project Design | FALSE | 3200 | NA | 3636.0062 | 3636.0062 | 822.0173 | 18.4973 | 12.8089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3636.0062 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 3604.7 | 18.4973 | -8.3285 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 752 | MORAGA: EM REPL SINKHOLE & DRAIN PIPE |  |  | Orinda, Contra Costa | There are three areas of repair needed which are related to drainage and erosion for the substation. 1. Failed culvert from SPCC pond #2 to water outlet has caused a massive sinkhole just outside the West corner of the sub. Phase 1 of this item is to replace the portion of the failed culvert and fill up the sinkhole. Phase II is to replace the rest of the culvert which has showed signs of damage, but will require a lengthy permitting process and environmental reviews. 2. Repair erosion damages caused by clogged Grizzly(the inlet of the 48" culvert pass under the Sub) near the precast security walls. 3. Repair the V-ditch near bank 3 and replace the crashed pipe between two catch basins. | Substation - Structure | Replace | NA | Emergency Event | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-06 | 74 | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 15.8714 | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5549230 | T.0008251 | Moraga: Em Repl Sinkhole & Drain Pipe | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-10-26 | NA | 2023-11-22 | NA | TRUE | NA | NA | 1227.3905 | 1219.8145 | 0 | 0 | 0 | 737.4873 | 469.3016 | 13.0257 | 0 | 0 | 0 | 0 | 0 | 1206.7889 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1206.7889 | 6.4142 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 753 | EM: Wheeler Ridge ErosionDrainage Fence |  |  | Kern | This project is needed to maintain safe and reliable power to electric customers served from Wheeler Ridge Substation and provides the following benefits: • Improve public and employee safety by eliminating weaknesses in the present substation fence • Decrease costs associated with recurring break-ins to the substation and subsequent theft of equipment and materials. | Substation - Structure | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.403 | NA | 115 ¦ 70 kV | Not Available | 3. Emergency Preparedness | Not Available | NA | NA | 5535601 | T.0004729 | WHEELER RIDGE: EM EROSION DRAINAGE FENCE | 1 | 65 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-30 | 2020-03-27 | 2020-04-19 | NA | FALSE | 1524 | NA | 1333.8332 | 1333.8332 | 979.8291 | 353.6127 | 0.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1333.8332 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 979.8291 | 261.1433 | -4.274 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 754 | Bellota: Replace Switch 433 & 43530KV |  |  | San Joaquin | This project proposal is for Bellota Substation, located in San Joaquin County. Due to 230 kV switch failure of breaker disconnecting switch SW433 and probable failure of SW435, SW423 & SW425 in the future, these switches shall be replaced. | Substation - Switch | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-01 | 13 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | 638 | 3. Emergency Preparedness | Not Available | NA | NA | 5533824 | T.0004480 | BELLOTA: EM Replace Switch 433 & 435 | 1 | 65 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-10-01 | NA | 2020-06-04 | NA | FALSE | NA | NA | 1769.801 | 1769.801 | 441.6772 | 1318.8127 | 2.9755 | 1.3976 | 2.3006 | 0.3155 | 0 | 0 | 0 | 0 | 0 | 1769.4855 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 397.2772 | 1186.9314 | 2.6779 | 1.2579 | 2.0705 | 0.28395 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 755 | Monta Vista-Replace 230kV SW Stru/Slope |  |  | Cupertino, Santa Clara | To better serve nearby Santa Clara County residents and businesses, PG&E proposes to upgrade substation equipment foundations and stabilize the northern substation slope. Located in Santa Clara County, the Monta Vista Substation is bounded by grassland to the north, a wooded area to the east, a railroad to the south and southeast, and maintenance roads to the west and is located within the community of Cupertino. Specifically, PG&E will stabilize the slope outside of the PG&E fence to the north of the substation. The work will extend from the substation fence for approximately 150 feet adjacent to the existing fence line and 12 feet down the embankment. All vegetation will be cleared off the slope. The slope vegetation consists of ruderal plants such as thistles and common weeds. The slope will be compacted, and galvanized metal spikes that are 10 to 20 feet in length will be driven into the ground which will hold the metal mesh on the slope. Anchors will also be placed 10-15 feet below grade level to secure the mesh. Jute netting will be placed under the metal mesh as a first layer of soil stabilization. DrillTech will broadcast seed the area after the jute netting is placed. Work will occur outside of the fence with a small excavator on the flat area adjacent to the fence. The bottom of the embankment has an open metal culvert which extends the entire 150-foot length, with a small portion enclosed (approximately 10 feet). No work or equipment will occur within or beyond the culvert. Additionally, PG&E will install new foundations for a new bus structure, circuit breaker, and current transformer inside of the substation fence | Substation - Structure | Replace | NA | Emergency Event | Replace Other Substation Equipment | NA | 2024-03-11 | 64 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8314 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5796394 | T.0007213 | MONTA VISTA Rep 230kV Structure 74039803 | 1 | 65 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-04-08 | NA | 2024-08-21 | NA | TRUE | 1000 | NA | 2432.973 | 4508.8788 | 0 | 0 | 473.9633 | 1499.7621 | 183.6898 | 2351.2015 | 0.2622 | 0 | 0 | 0 | 0 | 2157.4151 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 756 | Misc Replacements |  |  | NA | Forecast placeholder for misc. substation replacements | Substation - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5506318 | NA | NA | NA | 66 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 312.1091 | 312.1091 | 0 | 0 | 0 | 0 | 312.1091 | 0 | 0 | 0 | 0 | 0 | 4000 | 312.1091 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 757 | MAT 66A - ET Sub Repl Miscellaneous Civil Assets |  |  | NA | Forecast placeholder for replacement of miscellaneous civil assets | Substation - Structure | Replace | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | Ex112796 | NA | NA | NA | 66 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 758 | Humboldt SVC Mach 2 Controller Replacement |  |  | Humboldt | This equipment "Static Var Compensator (SVC) is critical to the safe operation of the substation and help control the operation of the SVC (essentially the brains of the system). These controllers are considered a 15-year asset and need to be replaced | Substation - Other Equipment | Replace | TBD | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-08 | 14 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.569 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | No | EX111032 | TBD | TBD | TBD | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-12-01 | NA | 2031-12-31 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 759 | CORDELIA: Remove Control Building |  |  | Fairfield, Solano | Removal of the control building at Cordelia Substation. Cordelia Substation is located in the vicinity of the City of Fairfield, within Solano County, California. The old control building located at Cordelia Substation in PG&E’s property has experience many intrusions since the building was decommissioned. Although, the building was boarded up, and recently had the metal doors welded and shut to prevent break-ins, over the years the building has been vacant and has been vandalized several times. In 2015, an emergency project was approved to temporarily seal all entrances with concrete due to the vandalism and continuous break-ins. The concrete building was built in the early 1900s, and has many glass windows and Spanish roof tiles. Due to the building’s vintage it is no longer seismically safe, and it is not cost effective to continually make repairs. We believe the building may also be a historic item that may need to confirm prior to removing the building. | Substation - Modular Protection and Automation Control Building | Removal | TBD | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-04-01 | 71 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.9782 | NA | 115 ¦ 60 kV | 20 | 9. Reliability (Low Safety Risk) | 20 | Tier 2 | No | 5769863 | T.0001516 | Cordelia: Remove Control Building | 1 | 66 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2025-07-31 | NA | 2026-05-05 | NA | FALSE | NA | NA | 549.6238 | 6468.4714 | 0.5157 | 0.744 | 157.7779 | 378.599 | 3.3371 | 33.4523 | 0 | 0 | 0 | 0 | 0 | 549.6238 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 760 | VACA DIXON: REP 500 KV Series CAP BK 1 |  |  | Solano | Replace the existing 500kV Series Capacitor Bank 1 and associated circuit breakers, and upgrade the associated protection and control systems at Vaca Dixon Substation to support the power transfer on three major transmission paths. | Substation - Reactive Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-12 | 35 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | 1797 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5768878 | T.0001165 | Vaca Dixon 500Kv Replace Bank 1 | 1 | 66 | 5763138 | 2015 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-08 | 2020-03-31 | 2019-12-13 | NA | FALSE | 26231 | NA | 26677.8491 | 26677.8491 | 10416.6281 | 3262.7339 | 41.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26677.8491 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 21435.1604 | 2995.7712 | 38.0055 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 761 | TESLA: Replace 500 KV Series CAP BK 2 |  |  | Alameda | Replace the existing 500kV Series Capacitor Bank 2 (Tesla SC#2) at Tesla Substation and associated equipment to support the power transfer on three major transmission paths. | Substation - Reactive Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-15 | 50 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 69.382 | NA | 500 kV | 1797 | 9. Reliability (Low Safety Risk) | 9 | NA | NA | 5760991 | T.0001451 | TESLA REPLACE 500KV SERIES Cap BANK 2 | 1 | 66 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-10-26 | 2020-05-21 | 2021-06-21 | Workforce | FALSE | 36564 | NA | 39554.0305 | 39952.7178 | 1338.5059 | 18803.6538 | 19288.8361 | 82.9707 | 10.7113 | 398.6874 | 0 | 0 | 0 | 0 | 0 | 39554.0305 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 35417.077 | 74.1174 | 9.5683 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 762 | VACA DIXON: REP 500 KV Series CAP BK 2 |  |  | Solano | Replace the existing 500kV Series Capacitor Bank 2 at Vaca Dixon Substation and associated circuit breakers, and upgrade the associated protection and control systems to support the power transfer on three major transmission paths | Substation - Reactive Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-12 | 35 | Lifecycle Replacement Analysis | Wires - Voltage Support/Reactive Support Alternative | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | 581 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5759161 | T.0001606 | Vaca Dixon 500kV Replace Bank 2 | 1 | 66 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-06 | 2018-12-27 | 2019-05-31 | NA | FALSE | 28306 | NA | 29046.7523 | 29046.7523 | 6782.1863 | 975.4795 | 8.9379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29046.7523 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 26344.2269 | 914.5165 | 8.3654 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 763 | TABLE MOUNTAIN: Repl 500 KV CAP on BK 3 |  |  | Butte | Replace the existing 500kV Series Capacitor Bank 3 (Table Mountain SC#3) at Table Mountain Substation and associated equipment to support the power transfer on three major transmission paths | Substation - Reactive Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-06 | 39 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | 500 kV | 1797 | 9. Reliability (Low Safety Risk) | 5 | NA | NA | 5767919 | T.0000677 | Table Mountain Cap Bank No. 3 | 1 | 66 | NA | 2015 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-11-29 | 2022-12-14 | 2022-08-31 | NA | TRUE | 28500 | NA | 35013.3428 | 35434.5162 | 249.4337 | 5285.4651 | 10669.387 | 18599.7415 | 24.0489 | 408.2768 | 20.6363 | 0 | 0 | 0 | 0 | 35005.603 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 31159.7609 | 21.2575 | 13.8153 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 764 | POTRERO: Replace SVC Controller |  |  | San Francisco, San Francisco | The average lifespan of SVC systems is 30-35 years, and the PC based controls have a lifespan of 15-17 years. The strategy is to replace the SVC controls on a planned basis as opposed to emergency replacements. The SVC controller replacement project will replace both MACH 2 computers (System A & B), and OWS computer of the SVC controller at Potrero Substation. | Substation - Voltage Support Equipment | Replace | TBD | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-28 | 19 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 230 kV | 1797 | 9. Reliability (Low Safety Risk) | 5 | Tier 5 | No | 5773178 | T.0002438 | POTRERO SUB: REPLACE SVC CONTROLLER | 1 | 66 | NA | 2016 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-01-03 | 2023-03-31 | 2025-02-27 | Prioritization | TRUE | 5656 | NA | 4724.6116 | 6268.4595 | 60.2443 | 95.2339 | 171.2375 | 2658.0319 | 321.0718 | 616.54 | 1256.2891 | 0 | 0 | 0 | 1800 | 4395.6303 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 765 | PAUL SWEET: Replace Statcom |  |  | Live Oak CDP, Santa Cruz | The project scope of work includes following: • Replace the existing 1998 vintage StatCom with a modern StatCom • Re-use existing 115 kV interconnection equipment and shunt capacitors • Replace StatCom transformers | Substation - Voltage Support Equipment | Replace | TBD | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-02-13 | 26 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.5678 | NA | 115 kV | 186 | 9. Reliability (Low Safety Risk) | 12 | Tier 3 | No | 5777261 | T.0003455 | PAUL SWEET SUB: Replace STATCOM | 1 | 66 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-04-08 | NA | 2028-02-17 | NA | FALSE | 11648 | NA | 87.6024 | 11648.3794 | 36.5834 | 7.9707 | 11.1307 | 19.2184 | 6.0984 | 6.3453 | 0 | 0 | 0 | 0 | 0 | 86.5779 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 766 | GATES BUS ""E"" SECURITY |  |  | Fresno | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Other - Physical Security | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-08 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 77.6619 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5790590 | T.0006452 | GATES BUS SECTION ""E"" | 9 | 66 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-04-18 | 2023-04-30 | 2022-10-05 | NA | TRUE | 58600 | NA | 1680.8237 | 1680.8237 | 0 | 0 | 15.1034 | 1612.5533 | 53.167 | 0 | 0 | 0 | 0 | 0 | 0 | 1680.8237 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1574.8922 | 51.3979 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA
| 767 | Geysers 3 & 4: Decommission sub |  |  | Sonoma | This planned project will convert Eagle Rock 115 kV bus to DBSB, decommission Geysers 3 & 4, and build 1.5 miles between Eagle Rock and Cloverdale Substations | Substation - Multiple | Removal | TBD | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-01 | 52 | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.31702 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799858 | T.0007732 | Eagle Rock: Convert 115 kV Bus | 3 | 66 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-09-27 | NA | 2028-02-04 | NA | FALSE | NA | NA | 4.1993 | 1537.3863 | 0 | 0 | 0 | 4.1993 | 0 | 0.2636 | 0 | 0 | 0 | 0 | 206.4167 | 4.1993 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 768 | McCall: Repl Synch Condensers #2 |  |  | Fresno | This project proposes to replace the existing Synchronous Condener #2 at McCall Substation with similar size (40 MVAR) unit to improve the electric transmission system reliability, and safety, and help improve the transmission grid reliability, and efficiency to serve electric customers in Fresno and Madera Counties. | Substation - Reactive Equipment | Replace | TBD | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-08 | 29 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 16.2494 | NA | 230 kV | Not Available | 9. Reliability (Low Safety Risk) | Not Available | Tier 5 | No | 5773867 | T.0002639 | McCall: Repl Synch Condensers #2 | 1 | 66 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-09-05 | NA | 2025-10-17 | NA | TRUE | NA | NA | 123.7811 | 1975.5191 | 0.0347 | 0.0571 | 8.0676 | 105.0255 | 8.4898 | 8.9461 | 1844.2395 | 0 | 0 | 0 | 1000 | 122.3335 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 769 | Martin Sub. - Hunters Point 115 kV MPAC |  |  | Brisbane, San Mateo | This proposed project will rebuild the entire Hunters Point Substation about 2,000 feet from its current location but is still within the existing PG&E parcel. Rebuilding at a new site has many benefits based on lessons learned from other substation rebuild projects. Specific scope of work includes: • A new 115 kV bus using gas-insulated switchgear (GIS) in a breaker-and-a-half (BAAH) configuration, • 115 kV modular protection, automation, and control (MPAC) panels, • New 12 kV switchgear in a double-bus-double-breaker configuration, • Two new 115/12 kV substation transformers, • Spill prevention control and countermeasure (SPCC) facilities, and • Relocation and potentially undergrounding of the 115 kV transmission and 12 kV outlets. | Substation - Modular Protection and Automation Control Building | New | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-20 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5795304 | T.0000590 | Hunters Point Substation | 4 | 66 | NA | 2013 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2030-06-28 | 2017-12-15 | 2031-05-29 | Prioritization | FALSE | 190398 | NA | 72.2387 | 4475.891 | 0 | 0 | 15.2999 | 43.2159 | 12.0606 | 22.3932 | 0 | 0 | 0 | 0 | 842.2507 | 70.5765 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $200 Mil - $250 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 770 | Mission Sub. - Hunters Point 115 kV MPAC |  |  | San Francisco, San Francisco | This proposed project will rebuild the entire Hunters Point Substation about 2,000 feet from its current location but is still within the existing PG&E parcel. Rebuilding at a new site has many benefits based on lessons learned from other substation rebuild projects. Specific scope of work includes: • A new 115 kV bus using gas-insulated switchgear (GIS) in a breaker-and-a-half (BAAH) configuration, • 115 kV modular protection, automation, and control (MPAC) panels, • New 12 kV switchgear in a double-bus-double-breaker configuration, • Two new 115/12 kV substation transformers, • Spill prevention control and countermeasure (SPCC) facilities, and • Relocation and potentially undergrounding of the 115 kV transmission and 12 kV outlets. | Substation - Modular Protection and Automation Control Building | New | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-02-09 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.83366 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5795305 | T.0000590 | Hunters Point Substation | 4 | 66 | NA | 2013 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2028-06-22 | 2017-12-15 | 2031-04-09 | Prioritization | FALSE | 190398 | NA | 71.1552 | 3333.9844 | 0 | 0 | 13.784 | 37.2303 | 18.4913 | 33.4127 | 0 | 0 | 0 | 0 | 559.9422 | 69.5057 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $200 Mil - $250 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 771 | Potrero Sub. - Hunters Point 115 kV MPAC |  |  | San Francisco, San Francisco | This proposed project will rebuild the entire Hunters Point Substation about 2,000 feet from its current location but is still within the existing PG&E parcel. Rebuilding at a new site has many benefits based on lessons learned from other substation rebuild projects. Specific scope of work includes: • A new 115 kV bus using gas-insulated switchgear (GIS) in a breaker-and-a-half (BAAH) configuration, • 115 kV modular protection, automation, and control (MPAC) panels, • New 12 kV switchgear in a double-bus-double-breaker configuration, • Two new 115/12 kV substation transformers, • Spill prevention control and countermeasure (SPCC) facilities, and • Relocation and potentially undergrounding of the 115 kV transmission and 12 kV outlets. | Substation - Modular Protection and Automation Control Building | New | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | 2024-03-28 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5795306 | T.0000590 | Hunters Point Substation | 4 | 66 | NA | 2013 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-12-17 | 2017-12-15 | 2031-02-19 | Prioritization | FALSE | 190398 | NA | 65.6436 | 2324.3067 | 0 | 0 | 12.5324 | 38.6462 | 13.1872 | 45.7173 | 0 | 0 | 0 | 0 | 294.418 | 64.3658 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $200 Mil - $250 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 772 | Atlantic: Replace 60 kV SWs 47, 49, 71 |  |  | Roseville, Placer | Atlantic (6) 60kV SWs 47, 49, 61, 65, 71 and 73 have been targeted for replacement as part of the PG&E Transmission Proactive Disconnect Air Swithches Replacement Program. The prioritization criteria for this program is primarily based on maintenence condition assessment. The predominant factors include operating condition, age, safety, and impact of consequence of an in-service failure, availability of spare parts. | Substation - Switch | Replace | TBD | Asset Condition | Age/Condition - Replace Switches | NA | 2024-03-01 | 72 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 10.6984 | NA | 60 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5547540 | T.0007687 | Atlantic: Replace 60 kV SWs 47, 49, 71 | 1 | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-10-01 | NA | 2030-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 773 | Bellota: Repl 230 kV SWs 417,419,477,479 |  |  | San Joaquin | Bellota (4) 230kV SWs have been targeted for replacement as part of the PG&E Transmission Proactive Disconnect Air Swithches Replacement Program. The prioritization criteria for this program is primarily based on maintenence condition assessment. The predominant factors include operating condition, age, safety, and impact of consequence of an in-service failure, availability of spare parts. | Substation - Switch | Replace | TBD | Asset Condition | Age/Condition - Replace Switches | NA | 2024-03-01 | 80 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 14.7513 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5799119 | T.0007689 | Bellota: Repl 230 kV SWs 417,419,477,479 | 1 | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2029-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 774 | Kelso: Replace 230 kV SWs 217,237,257 |  |  | Alameda | Kelso (4) 230kV SWs 237, 217, 231, 257 have been targeted for replacement as part of the PG&E Transmission Proactive Disconnect Air Swithches Replacement Program. The prioritization criteria for this program is primarily based on maintenence condition assessment. The predominant factors include operating condition, age, safety, and impact of consequence of an in-service failure, availability of spare parts. | Substation - Switch | Replace | TBD | Asset Condition | Age/Condition - Replace Switches | NA | 2024-03-06 | 80 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Heat Wave |  | NA | 2.4538 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5799120 | T.0007691 | Kelso: Replace 230 kV SWs 217,237,257 | 1 | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-03-01 | NA | 2029-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 775 | Stagg sub - repl (14) 60 kV vintage SWs 11, 13, 15, 23, 25, 31, 33, 35, 41, 42, 45, 51, 52 and 55 |  |  | Stockton, San Joaquin | Stagg sub (14) 60kV SWs have been targeted for replacement as part of the PG&E Transmission Proactive Disconnect Air Swithches Replacement Program. The prioritization criteria for this program is primarily based on maintenence condition assessment. The predominant factors include operating condition, age, safety, and impact of consequence of an in-service failure, availability of spare parts. | Substation - Switch | Replace | TBD | Asset Condition | Age/Condition - Replace Switches | NA | 2024-03-01 | 80 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.5909 | NA | 60 kV | Not Available | Not Available | Not Available | Tier 3 | No | EX112115 | TBD | TBD | TBD | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-03-01 | NA | 2030-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 776 | EAST PORTAL SUB - REPL 115KV MOAS 117 |  |  | Orinda, Contra Costa | The project scope of work includes the following: • Replace the 115kV MOAS 117 on the Sobrante-Claremont line • Replace the 115kV MOAS 119 on the Sobrante-Claremont line • Upgrade associated equipment if required East Portal is a single customer distribution substation and it is in Contra Costa County in the Concord Division. The Motor Operated Air Switch (MOAS) 117 & 119 at East Portal are in service for the last 50 years and are at the end of their useful life. Both serve as 115kVline switching to Sobrante and Claremont. Based on the age and performance, it was recommended by Asset Strategy to replace the MOAS 117 & 119 at East Portal. The Sobrante-Grizzly-Claremont #1 115 kV line associated with the switches is rated less than 1200 Amps. CB 172 maximum load is only 125 A as it supplies only the Bart Bank rated 25 MVA. The new SWs 117 and 119 will be rated for 1200 A like the existing ones. | Substation - Switch | Replace | TBD | Asset Condition | Age/Condition - Replace Switches | NA | 2024-03-04 | 52 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 0.37448 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5793673 | T.0006778 | East Portal Sub - Repl 115kV MOAS 117 | 1 | 66 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-01-06 | NA | 2026-03-02 | NA | FALSE | NA | NA | 112.6506 | 1194.4749 | 0 | 0 | 70.5678 | 31.7848 | 8.9806 | 8.1414 | 0 | 0 | 0 | 0 | 200 | 111.3332 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 777 | LAS POSITAS: 230KV RING CONV & BLDG INST |  |  | Livermore, Alameda | This planned project will replace Las Positas Substation’s failed CKT SW 286 and Motor Operated Air Switch (MOAS) 289 with four (4) 230 kV circuit breakers (CBs) that will be interconnected in a “Ring” bus configuration, install one (1) new control building to be installed near the 60 kV yard, install new relays on all new 230 kV CBs (Nos. 222, 232, 262, 272). This planned project is needed to maintain safe and reliable power to the East Bay area and will support PG&E top-level initiatives such as improved service reliability, improved operational flexibility, and reducing operating costs. | Substation - Switch | Replace | NA | Asset Condition | Age/Condition - Replace Switches | NA | 2024-03-05 | 32 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.2184 | NA | 230 kV | Not Available | 9. Reliability (Low Safety Risk) | 6 | NA | NA | 5785643 | T.0000185 | LAS POSITAS: REPL CKT SWS 286 & 289 | 5 | 66 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-11-01 | 2023-06-30 | 2023-06-30 | NA | TRUE | 7851 | NA | 10663.1025 | 10663.1025 | 112.2012 | 684.0717 | 2937.8898 | 3932.6052 | 2923.8638 | 59.8536 | 0 | 0 | 0 | 0 | 0 | 10603.2489 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2023 ¦ 2024 | 101.8216 | 615.6645 | -728.0504 | 0 | 9928.1768 | 82.3881 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 778 | LAS POSITAS: 230KV RING CONV Phase 2 |  |  | Livermore, Alameda | This planned project will replace Las Positas Substation’s failed CKT SW 286 and Motor Operated Air Switch (MOAS) 289 with four (4) 230 kV circuit breakers (CBs) that will be interconnected in a “Ring” bus configuration, install one (1) new control building to be installed near the 60 kV yard, install new relays on all new 230 kV CBs (Nos. 222, 232, 262, 272). This planned project is needed to maintain safe and reliable power to the East Bay area and will support PG&E top-level initiatives such as improved service reliability, improved operational flexibility, and reducing operating costs. | Substation - Switch | Replace | NA | Asset Condition | Age/Condition - Replace Switches | NA | 2024-03-05 | 32 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.2184 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798813 | T.0000185 | LAS POSITAS: REPL CKT SWS 286 & 289 | 5 | 66 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2024-01-02 | 2023-06-30 | 2024-06-24 | Project Design | TRUE | 7851 | NA | 729.0998 | 2596.5527 | 0 | 0 | 0 | 6.01 | 26.2161 | 2564.3266 | 0 | 0 | 0 | 0 | 0 | 32.2261 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 779 | Cottonwood Sub repl 115kV SW133,135,163 |  |  | Cottonwood CDP, Shasta | This project will replace 115kV switches 131, 133, 135, 161, 163, 165 and associated equipment as required at Cottonwood Substation. Maintenance has identified 115kV switches 131, 133, 135, 161, 163 and 165 to be ergonomically unsafe, old, and difficult to operate. The replacement of these switches will make their operation safe and reliable while the relocation of HVCB 132 will ensure the switches an extended life expectancy. The completion of this project is essential to maintain safe and reliable power to electric customers served from Cottonwood substation. | Substation - Switch | Replace | TBD | Asset Condition | Age/Condition - Replace Switches | NA | 2024-03-06 | 19 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 26.1945 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5792847 | T.0006463 | COTTONWOOD SUB REPL 115kV SW133,135,163 | 1 | 66 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-10-31 | 2022-11-04 | 2022-12-22 | NA | TRUE | 3800 | NA | 1753.3812 | 1753.3812 | 0 | 2.4197 | 137.1829 | 1517.9465 | 95.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 1753.3812 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1496.7646 | -85.6982 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 780 | New Pad for CEM Banks |  |  | Alameda | Extend the existing CEM transformer foundation at the southwest corner of the sub | Substation - Transformer | New | TBD | Asset Condition | Age/Condition - Replace Civil Structures | NA | 2024-03-15 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5546164 | T.0007412 | New Pad for CEM Banks | 1 | 66 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | NA | 2023-06-12 | NA | TRUE | NA | NA | 1222.0881 | 1222.0881 | 0 | 0 | 0 | 67.6576 | 1153.9997 | 0.4308 | 0 | 0 | 0 | 0 | 0 | 1221.6573 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 60.8918 | 1038.5997 | 0.38771 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 781 | EO-SYSPLN 66E - ET Sub Repl Other Equip |  |  | NA | Forecast placeholder for replacement of civil structures | Substation - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5533277 | NA | NA | NA | 66 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2900 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 782 | Ravenswood-S-Prot-Agst-Climate-Chg-Flood |  |  | Menlo Park, San Mateo | This project proposes to protect against Flooding from Climate Change rising water plus provide levee heights to protect against last 100-year flood levels, restores the surrounding ponds, and protects part of the Dumbarton Bridge along Hwy SR84. • To provide protection against sea level rise (flooding) of Ravenswood Substation assets, serving the electric customers in the San Mateo County and other surrounding counties. • To address Climate Change normal deficiency projected for futures years. • To improve the Levee system will help with electric transmission and distribution system sustainability and help maintain the transmission grid reliability. | Substation - Structure | New | TBD | Asset Condition | Age/Condition - Replace Civil Structures | NA | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5793758 | T.0006761 | Ravenswood-S-Prot-Agst-Climate-Chg-Flood | 1 | 66 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-07-03 | NA | 2027-04-06 | NA | FALSE | NA | NA | 225.3645 | 281.1966 | 0 | 0 | 0 | 216 | 3.2712 | 16.352 | 2000 | 3000 | 0 | 0 | 0 | 222.7289 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 783 | Biola New Structures&Switches: CB12 & 22 |  |  | Fresno | This equipment is nominated for replacement based on an assessment study performed by PG&E’s Civil Engineering team on transmission class structures in substations. | Substation - Structure | Replace | TBD | Asset Condition | Age/Condition - Replace Civil Structures | NA | 2024-02-08 | 26 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | 0.87974 | NA | 70 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5759178 | T.0000910 | BIOLA: INSTALL T-SCADA ON CB12 & 22 | 1 | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-12-23 | NA | 2027-02-19 | NA | FALSE | 100 | NA | 14.1224 | 72.5091 | 0 | 0 | 0 | 0 | 14.1224 | 1.0202 | 0 | 0 | 0 | 0 | 500 | 13.9572 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 784 | Kingsburg:Repl CB122,142&115kV Str & FDN |  |  | Fresno | This equipment is nominated for replacement based on an assessment study performed by PG&E’s Civil Engineering team on transmission class structures in substations. | Substation - Structure | Replace | TBD | Asset Condition | Age/Condition - Replace Civil Structures | NA | 2024-02-06 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.3704 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5799067 | T.0007707 | Kingsburg:Repl CB122.142.115kV Str FDN | 1 | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-03-01 | NA | 2030-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 785 | Oakland K: Replace 115kV Lattice Structure |  |  | Oakland, Alameda | In 2015, a temporary solution of adding cross bars to address buckling of the 115kV lattice structures was completed. This was only a temporary solution to a permanent fix. | Substation - Structure | Replace | TBD | Asset Condition | Age/Condition - Replace Civil Structures | NA | 2024-03-19 | 104 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 3.9974 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | No | Ex112785 | TBD | TBD | TBD | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-12-01 | NA | 2032-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 786 | HERNDON SUB INST EQP TO CONTROL BLD |  |  | Fresno, Fresno | This project installed relocated equipment at Herndon yard in Fresno. Once the building is removed the yard will be graded and cleared out. Scope OUTDOOR WORK: Relocate all wiring from old building Install new phone connection to New building Remove abandoned battery, charger and associated wiring EQUIPMENT TO BE REMOVED:Remove abandoned battery, charger and associated wiring Remove old communication wires Remove old building. | Substation - Structure | Replace | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | 2024-03-08 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 13.3414 | NA | 230 ¦ 115 kV | 309 | Not Available | Not Available | NA | NA | 5519684 | P.05032 | HERNDON SUB INST EQP TO CONTROL BLD | 1 | 66 | NA | NA | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2010-12-16 | 2019-06-15 | 2020-06-26 | Workforce | FALSE | 1667 | NA | 1079.2601 | 1079.2601 | 38.7336 | 2.9897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1079.2601 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 30.523 | 2.3559 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 787 | MARTIN: Retrofit 230 KV Bus |  |  | Brisbane, San Mateo | This project provides seismic upgrade of the Martin Substation 230kV System. The scope will include the following activities•Seismic retrofit of 230kV Bus components per IEEE 693•Replace switches and insulators with seismic qualified equipment•Provide flexible connections to allow for lateral movement during earthquakes Under this AA, the team will:•Finalize the scope of work•Perform preliminary engineering•Evaluate Construction bids•Develop construction sequence•Develop job estimate & schedule. | Substation - Structure | Replace | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | 2024-03-20 | NA | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 230 kV | 470 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5764038 | T.0000028 | Martin Sub: 230kV Bus Retrofit | 1 | 66 | NA | 2015 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-26 | 2019-07-09 | 2019-05-18 | NA | FALSE | 8393 | NA | 9047.7609 | 9047.7609 | 6659.3341 | 793.4919 | 24.5981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9047.7609 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 7705.8813 | 742.5129 | 23.0115 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 788 | OAKLAND K: Replace OB Insulators |  |  | Oakland, Alameda | This project improves the reliability in Oakland area by replacing failure prone 1960s & 1970s vintage 20” Ohio Brass insulators. These Ohio Brass 20” insulators have history of catastrophic failure. Replacing these insulators improves reliability as well as safety of the personnel working near these insulators. | Substation - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Insulators | NA | 2024-03-19 | 51 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 3.9974 | NA | 115 ¦ 60 kV | 445 | 5. Compliance/Commitments With Strong Safety Link | Not Available | NA | NA | 5770523 | T.0001818 | Oakland K Sub Repl OB Insulator | 1 | 66 | NA | 2016 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-06-07 | 2019-06-12 | 2020-02-24 | Scope Change | FALSE | 2400 | NA | 1161.394 | 1161.394 | 685.1155 | 313.1099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1161.394 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 1118.5433 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 789 | Brighton: Replace OB Insulators |  |  | Sacramento, Sacramento | This project is intended to replace the targeted 20” cap and pin insulators manufactured by Ohio Brass (Catalog # 35126) that were installed at Brighton Substation. Brighton substation was identified as having the targeted 115kV OB insulators and will be replaced under the program. By completing this project, the Company will be diligently addressing known reliability issues attributed to the existing equipment. | Substation - Other Equipment | Replace | TBD | Asset Condition | Age/Condition - Replace Insulators | NA | 2024-03-01 | 58 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 6.4413 | NA | 115 kV | 445 | 5. Compliance/Commitments With Strong Safety Link | Not Available | NA | NA | 5784147 | T.0004198 | Brighton: Replace OB insulators | 1 | 66 | NA | 2016 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-01-14 | 2021-09-21 | 2022-02-23 | NA | FALSE | 3706 | NA | 3512.7219 | 3512.7219 | 528.2798 | 1570.4762 | 1074.7532 | 324.7567 | 3.9181 | 0 | 0 | 0 | 0 | 0 | 0 | 3512.7219 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2855.0867 | 3.1274 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 790 | SAN ARDO: EM Replace 60 KV OB Insulators |  |  | Monterey | This project is intended to replace the targeted 20” cap and pin insulators manufactured by Ohio Brass at the San Ardo Substation | Substation - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Insulators | NA | 2024-03-04 | 51 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.44363 | NA | 60 kV | 197 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5522356 | T.0001767 | San Ardo Sub: Replace OB Insulators | 1 | 66 | NA | 2016 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-12-02 | 2019-07-31 | 2019-12-11 | NA | FALSE | 2492 | NA | 1412.5377 | 1412.5377 | 619.5101 | 520.2207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1412.5377 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 513.8117 | 442.6939 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 791 | North Tower Sub: Replace OB Insulators |  |  | Vallejo, Solano | This project will replace the 115kV OB insulators at North Tower Substation. Improve safety and human performance. Improves employee safety by eliminating aging and deteriorated equipment that have high risk of catastrophic failure. | Substation - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Insulators | NA | 2024-03-11 | 67 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 5.8111 | NA | 115 kV | 445 | 5. Compliance/Commitments With Strong Safety Link | Not Available | NA | NA | 5770522 | T.0001823 | North Tower Sub: Replace OB Insulators | 1 | 66 | NA | 2016 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-16 | 2020-12-31 | 2022-11-10 | Prioritization | TRUE | 1100 | NA | 1640.81 | 1640.81 | 265.3225 | 47.3705 | 690.2532 | 615.4883 | -6.1656 | 0 | 0 | 0 | 0 | 0 | 0 | 1640.81 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1620.5193 | -6.055 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 792 | MWC 66 Fire Protection Upgrades |  |  | NA | Forecast placeholder for substation fire protection upgrades | Other - Physical Security | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - Replace Civil Structures | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5513328 | NA | NA | NA | 66 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 793 | Purchase 2 sets CEM Shunt Reactors |  |  | NA | Purchase 2 sets of 13.4kV 15 MVAR CEM Shunt Reactors. 500kV Tertiary Shunt Reactor Replacement Program addresses high risk of failure 15MVAR shunt reactors connected to the tertiary of 500kV banks to supply reactance and reduce overvoltage. Due to high failure and lack of proactive replacement CEM equipment needs to be procured. | Substation - Reactive Equipment | New | NA | Asset Condition | Age/Condition - Replace Reactors | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 kV | Not Available | Not Available | Not Available | Tier 4 | No | 5547495 | T.0007699 | Purchase 2 sets CEM Shunt Reactors | 1 | 66 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | 500 | NA | 2.8596 | 2.8596 | 0 | 0 | 0 | 0 | 2.6628 | 0.1968 | 1300 | 100 | 0 | 0 | 0 | 2.6628 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 794 | Tesla: Rep Ter 1301,1302,1303,1304 |  |  | Alameda | 500kV Tertiary Shunt Reactor Replacement Program addresses high risk of failure 15MVAR shunt reactors connected to the tertiary of 500kV banks to supply reactance and reduce overvoltage. | Substation - Reactive Equipment | Replace | T.0004673 | Asset Condition | Age/Condition - Replace Reactors | NA | 2024-03-15 | 28 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Heat Wave |  | NA | 69.382 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5799539 | T.0007854 | Tesla: Rep Ter 1301,1302,1303,1304 | 1 | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-01-01 | NA | 2031-04-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 795 | Vaca Dixon Sub: repl insulators @500kV Bk 11 Tert Reactor #1302 |  |  | Solano | Vaca Dixon Reactor & Insulator have been targeted for replacement as part of the PG&E Transmission Reactors & Insulators Replacement Program. The prioritization criteria for this program is primarily based on maintenence condition assessment. The predominant factors include weathered, age, safety, and impact of consequence of an in-service failure, availability of spare parts. | Substation - Reactive Equipment | Replace | TBD | Asset Condition | Age/Condition - Replace Insulators | NA | 2024-03-12 | 31 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 3 | No | Tx001556 | TBD | TBD | TBD | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-01-15 | NA | 2029-12-15 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 796 | Vaca Dixon Sub: repl insulators @500kV Bk 11 Tert Reactor #1303 |  |  | Solano | Vaca Dixon Reactor & Insulator have been targeted for replacement as part of the PG&E Transmission Reactors & Insulators Replacement Program. The prioritization criteria for this program is primarily based on maintenence condition assessment. The predominant factors include weathered, age, safety, and impact of consequence of an in-service failure, availability of spare parts. | Substation - Reactive Equipment | Replace | TBD | Asset Condition | Age/Condition - Replace Insulators | NA | 2024-03-12 | 31 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 5 | No | Tx001557 | TBD | TBD | TBD | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-01-15 | NA | 2030-12-15 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 797 | SF MARTIN: Repl Shunt Reactor HZ2 |  |  | Brisbane, San Mateo | Replace existing 230kV three (3) single phase reactors on HZ-2 line with three (3) new 230 kV reactors and make provisions for a spare in the future. | Substation - Reactive Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Reactors | NA | 2024-03-20 | 48 | Lifecycle Replacement Analysis | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 230 kV | 18 | 9. Reliability (Low Safety Risk) | 4 | NA | NA | 5779901 | T.0000894 | SF H (MARTIN)-REPL SHUNT REACTOR BK HZ-2 | 1 | 66 | NA | 2013 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-19 | 2020-11-13 | 2021-04-10 | NA | FALSE | 11190 | NA | 8077.3588 | 8077.3588 | 2523.2171 | 2342.6831 | 3013.0043 | 11.9233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8077.3588 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 7143.5416 | 10.4875 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 798 | Los Banos: Replace Tertiary Reactors |  |  | Merced | The 500kV Air Core tertiary reactor insulators have been identified, by the Substation Standards group, as having a high rate of failure. The cause of the failure of the insulator is mechanical stress on the aging glass of the cap and pin insulator. There are 4 tertiary reactors at Los Banos 500kV bank1 and currently reactor 1302 is offline due to NG insulators. It has been determined that it is best to replace all four reactors (1301, 1302, 1303 & 1304). The fence will be replaced by nonconductive fence. Depending on the size of the new reactors, the fenced area may be increased to keep clearances and safe working distances. The existing animal abatement on the equipment will be reused. If the new reactor placement allows, the conductors and insulator support structures will be reused | Substation - Reactive Equipment | Replace | TBD | Asset Condition | Age/Condition - Replace Reactors | NA | 2024-03-06 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 53.2803 | NA | 500 kV | Not Available | Not Available | Not Available | NA | NA | 5796645 | T.0007249 | Los Banos Replace Tertiary Reactors | 1 | 66 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-06-20 | 2022-11-30 | 2022-11-04 | NA | TRUE | 3910 | NA | 5214.6265 | 5214.6265 | 0 | 0 | 211.7312 | 4587.5226 | 406.7182 | 8.6545 | 0 | 0 | 0 | 0 | 0 | 5205.972 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 4101.9532 | 345.9948 | 8.2156 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 799 | MARTIN: Replace 230 KV Shunt Reactor 1 |  |  | Brisbane, San Mateo | This project is part of Substation Asset Strategy’s Shunt Reactor replacement plan at Martin Substation. This project proposes to replace four single phase shunt reactors, including the spare phase. | Substation - Reactive Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Reactors | NA | 2024-03-20 | 46 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 18.2105 | NA | 230 kV | 19 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5768952 | T.0001362 | MARTIN SUB: REPL 230KV SHNT RCTR1 | 1 | 66 | NA | 2011 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-29 | 2018-02-01 | 2019-04-08 | Bundling Dependencies | FALSE | 7195 | NA | 4246.1297 | 4246.1297 | -971.9898 | 112.9882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4246.1297 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 4032.255 | 109.9132 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 800 | Round Mtn: Rep Ter Shnt Reac 1301&1303 |  |  | Round Mountain CDP, Shasta | This project proposes to replace Round Mountain tertiary shunt reactors 1301, and 1303 to address elevated risk of failure due to age and condition. PG&E has 40 in-service shunt reactors on 13.8kV tertiary buses of 500/230kV transformers. Since 2012 PG&E has four reactor failures causing fires and heavy smoke. Failures of reactors can remove 500kV/230kV transformers out of service from the electric transmission grid for an extended period. Procurement of Shunt Reactor can take more than 6 months. | Substation - Reactive Equipment | Replace | TBD | Asset Condition | Age/Condition - Replace Reactors | NA | 2024-03-06 | 37 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Extreme Heat |  | NA | 29.1389 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799660 | T.0007862 | Round Mtn: Rep Ter Shnt Reac 1301&1303 | 1 | 66 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-02-09 | NA | 2027-06-24 | NA | FALSE | NA | NA | 4.1629 | 2613.5697 | 0 | 0 | 0 | 2.6366 | 0.4145 | 1.3652 | 0 | 0 | 0 | 0 | 259.7716 | 3.0511 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 801 | Placer: Repl Perimeter Fence & Grading |  |  | Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801703 | T.0010002 | Placer: Repl Fence & Grading | 1 | 66 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-18 | 2024-12-30 | 2025-05-27 | NA | TRUE | 17200 | NA | 440.998 | 4249.146 | 0 | 0 | 0 | 75.1135 | 334.5051 | 1272.7958 | 2307.0436 | 202.2282 | 0 | 0 | 0 | 409.6187 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 802 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807544 | T.0009659 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-04-23 | NA | 2026-09-04 | NA | FALSE | NA | NA | 27.2775 | 2297.4295 | 0 | 0 | 0 | 0 | 21.4622 | 112.7634 | 0 | 0 | 0 | 0 | 0 | 21.4622 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
| 803 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-13 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807546 | T.0009661 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-09-18 | NA | 2027-02-05 | NA | FALSE | NA | NA | 82.2772 | 5147.006 | 0 | 0 | 0 | 0 | 31.5908 | 1137.1643 | 0 | 0 | 0 | 0 | 0 | 31.5908 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
| 804 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-13 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807583 | T.0009669 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-08-13 | NA | 2026-12-30 | NA | FALSE | 197 | NA | 4.6721 | 2714.6695 | 0 | 0 | 0 | 0 | 2.1645 | 199.5509 | 0 | 0 | 0 | 0 | 0 | 2.1645 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
| 805 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-13 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807591 | T.0009676 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-09-16 | NA | 2027-02-03 | NA | FALSE | 95 | NA | 5.4643 | 2485.386 | 0 | 0 | 0 | 0 | 1.6685 | 98.3179 | 0 | 0 | 0 | 0 | 0 | 1.6686 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
| 806 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-15 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807543 | T.0009658 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-04-08 | NA | 2026-08-20 | NA | FALSE | NA | NA | 26.546 | 2393.8002 | 0 | 0 | 0 | 0 | 19.8342 | 127.1347 | 0 | 0 | 0 | 0 | 0 | 19.8343 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
| 807 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-14 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807545 | T.0009660 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-05-15 | NA | 2026-08-18 | NA | FALSE | NA | NA | 58.5382 | 3786.0215 | 0 | 0 | 0 | 0 | 24.1187 | 1146.1523 | 0 | 0 | 0 | 0 | 0 | 24.1188 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
| 808 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-14 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807582 | T.0009668 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-08-27 | NA | 2027-01-14 | NA | FALSE | 198 | NA | 5.8462 | 2646.544 | 0 | 0 | 0 | 0 | 1.9165 | 200.0032 | 0 | 0 | 0 | 0 | 0 | 1.9165 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
| 809 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-14 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807590 | T.0009675 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-14 | NA | 2027-03-04 | NA | FALSE | 96 | NA | 5.3061 | 2492.7192 | 0 | 0 | 0 | 0 | 1.7925 | 96.6555 | 0 | 0 | 0 | 0 | 0 | 1.7926 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
| 810 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 47.516 | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807540 | T.0009655 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-02-28 | NA | 2025-10-01 | NA | TRUE | NA | NA | 22.4034 | 2110.3494 | 0 | 0 | 0 | 0 | 0 | 1327.1596 | 757.7115 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14
| 811 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-01 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.5909 | NA | NA | Not Available | Not Available | Not Available | Tier 3 | No | Ex112772 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-03-01 | NA | 2029-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 812 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-12 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.8539 | NA | NA | Not Available | Not Available | Not Available | Tier 1 | No | Ex112764 | TBD | Electric Transmission Substation Security Upgrade | TBD | 66 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2025-03-01 | NA | 2025-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 813 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-06 | NA | NA | Wires - Replacement Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 26.1945 | NA | 230 ¦ 115 ¦ 60 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | 1 | NA | NA | 5773524 | T.0002572 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-16 | 2020-03-30 | 2020-08-31 | NA | FALSE | 10388 | NA | 11511.6611 | 11511.6611 | 3026.0028 | 6856.2708 | 1128.7467 | 236.3895 | 1.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 11511.6611 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 9819.1719 | 1091.3126 | 228.5498 | 1.8331 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 814 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 335 | Not Available | Not Available | Tier 3 | No | 5533282 | NA | Electric Transmission Substation Security Upgrade | NA | 66 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 25477.2727 | 0 | 0 | 0 | 0 | 0 | 25477.2727 | 0 | 3000 | 3000 | 3000 | 3000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 815 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Replace | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-08 | NA | NA | Other - Deferral | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.851 | NA | NA | Not Available | Not Available | Not Available | Tier 3 | No | 5793672 | T.0006889 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2020 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-01 | 2024-09-26 | 2024-10-23 | NA | TRUE | 960 | NA | 331.5894 | 1344.1423 | 0 | 0 | 149.4215 | 131.4721 | 29.366 | 1031.8176 | 2.065 | 0 | 0 | 0 | 0 | 310.2596 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 816 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-04-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.7504 | NA | 230 ¦ 115 ¦ 70 kV | 445 | 8. Compliance/Commitments With Low Safety Risk | 19 | RBPPF - TBD | Yes | 5776721 | T.0003350 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2022-01-03 | 2021-12-31 | 2024-12-30 | Prioritization | TRUE | 7500 | NA | 7172.9984 | 9045.9891 | 174.0205 | 123.4342 | 2095.3141 | 4582.9214 | 68.5882 | 1872.9907 | 0 | 0 | 0 | 0 | 0 | 7172.9984 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 817 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-07 | NA | NA | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.1779 | NA | NA | Not Available | Not Available | Not Available | Tier 3 | No | 5793671 | T.0006787 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2020 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-05-13 | 2024-05-21 | 2024-10-11 | NA | TRUE | 2198 | NA | 359.8 | 2380.31 | 0 | 0 | 188.8318 | 112.4012 | 29.0939 | 2049.9832 | 0 | 0 | 0 | 0 | 0 | 330.3268 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 818 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-01 | NA | NA | Wires - Replacement Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 14.7513 | NA | 230 ¦ 115 kV | 197 | Not Available | NA | NA | NA | 5773979 | T.0002578 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-08-13 | 2018-05-07 | 2019-06-07 | Project Design | FALSE | 5025 | NA | 5285.8631 | 5285.8631 | 884.5621 | 14.6534 | 0.2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5285.8631 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 5271.0088 | 14.6534 | 0.20091 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 819 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-07 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.7615 | NA | 230 kV | 197 | 8. Compliance/Commitments With Low Safety Risk | 22 | NA | NA | 5773980 | T.0002584 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-01-04 | 2020-07-16 | 2021-03-08 | Workforce | FALSE | 4313 | NA | 3196.0945 | 3196.2404 | 123.8632 | 1562.2742 | 1247.7604 | 9.3775 | 0 | 0.1459 | 0 | 0 | 0 | 0 | 0 | 3196.0945 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 3106.282 | 9.1314 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 820 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-05 | NA | NA | Wires - Replacement Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.4076 | NA | 230 ¦ 115 ¦ 60 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | 2 | NA | NA | 5773528 | T.0002590 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-03-31 | 2020-01-31 | 2020-06-30 | NA | FALSE | 3597 | NA | 3351.3124 | 3351.3124 | 729.8066 | 2604.4952 | -190.1749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3351.3124 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 3392.5341 | -181.9562 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 821 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-28 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 12.8702 | NA | 230 ¦ 115 ¦ 60 kV | 197 | 8. Compliance/Commitments With Low Safety Risk | 13 | NA | NA | 5773531 | T.0002580 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-02-22 | 2021-02-10 | 2021-08-06 | NA | FALSE | 4990 | NA | 4766.0764 | 4766.0764 | 208.2146 | 244.2356 | 3852.9363 | 118.7668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4766.0764 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 4581.9378 | 117.0205 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 822 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-14 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.9486 | NA | 230 ¦ 115 ¦ 60 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | 5 | NA | NA | 5773537 | T.0002589 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-07 | 2019-12-31 | 2020-11-16 | Prioritization | FALSE | 4461 | NA | 5383.2247 | 5383.2247 | 3241.2593 | 1784.2228 | 45.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5383.2247 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 5235.3156 | 44.5375 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 823 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-06 | NA | NA | Wires - Replacement Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 7.7091 | NA | 230 ¦ 60 kV | 197 | 8. Compliance/Commitments With Low Safety Risk | 4 | NA | NA | 5773539 | T.0002591 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-07-15 | 2018-08-06 | 2020-03-26 | Prioritization | FALSE | 2478 | NA | 3050.3881 | 3050.3881 | 1463.9425 | 1253.9425 | 11.4187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3050.3881 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 2932.1118 | 11.0051 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 824 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-11 | NA | NA | Wires - Replacement Alternative | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 14.7021 | NA | 230 ¦ 115 ¦ 60 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | 6 | NA | NA | 5773541 | T.0002579 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-03-02 | 2020-01-31 | 2020-03-05 | NA | FALSE | 3555 | NA | 3268.1794 | 3268.1794 | 1206.4562 | 2017.7274 | -158.2948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3268.1794 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 3247.5677 | -149.8677 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 825 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-11 | NA | NA | Wires - Replacement Alternative | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8314 | NA | 230 ¦ 115 ¦ 60 kV | 197 | 8. Compliance/Commitments With Low Safety Risk | 6 | NA | NA | 5773545 | T.0002574 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-08-30 | 2021-11-30 | 2022-03-08 | NA | FALSE | 4989 | NA | 3371.1736 | 3371.1736 | 76.0338 | 89.0588 | 2401.8993 | 504.609 | 1.3711 | 0 | 0 | 0 | 0 | 0 | 0 | 3371.1736 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 3369.8025 | 1.3711 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 826 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.3472 | NA | 230 ¦ 115 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5773548 | T.0002573 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-15 | 2018-08-10 | 2019-12-03 | Prioritization | FALSE | 2525 | NA | 3290.7618 | 3290.7618 | 2909.2544 | 89.1908 | -0.4734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3290.7618 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 2963.6762 | 83.9054 | -0.43729 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 827 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-07 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 11.0767 | NA | 230 ¦ 115 kV | 335 | 8. Compliance/Commitments With Low Safety Risk | 3 | NA | NA | 5773554 | T.0002592 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-03-08 | 2020-09-30 | 2022-06-13 | Prioritization | FALSE | 3692 | NA | 3986.8661 | 3986.8661 | 85.0492 | 2066.5101 | 1229.1681 | 175.3528 | 0.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 3986.8661 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 3986.1174 | 0.7487 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 828 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 10.5414 | NA | 230 ¦ 115 kV | 197 | 8. Compliance/Commitments With Low Safety Risk | NA | NA | NA | 5773543 | T.0002586 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-06-10 | 2018-06-29 | 2019-11-21 | Workforce | FALSE | 2681 | NA | 2628.7186 | 2628.7186 | 2146.5868 | 176.2985 | 31.8091 | 7.4502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2628.7186 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 2275.8415 | 166.6513 | 29.9589 | 7.0168 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 829 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 77.6619 | NA | 500 ¦ 230 ¦ 700 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5799103 | T.0007757 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-05-27 | NA | 2025-09-02 | NA | TRUE | NA | NA | 85.9874 | 3242.9856 | 0 | 0 | 0 | 0 | 61.2022 | 549.2314 | 2607.6175 | 0 | 0 | 0 | 0 | 61.2022 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 830 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 53.2803 | NA | 500 ¦ 230 ¦ 700 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5799101 | T.0007755 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2024-04-26 | NA | 2025-04-08 | NA | TRUE | NA | NA | 241.0993 | 8077.8199 | 0 | 0 | 0 | 0 | 204.6607 | 230.9336 | 3209.4296 | 500 | 0 | 0 | 0 | 204.6607 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 831 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-13 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 500 ¦ 230 ¦ 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5799105 | T.0007759 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-04-28 | NA | 2025-11-06 | NA | TRUE | NA | NA | 213.4523 | 3547.2706 | 0 | 0 | 0 | 0 | 166.61 | 605.3803 | 2763.5995 | 500 | 0 | 0 | 0 | 166.61 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 832 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-15 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 500 ¦ 230 ¦ 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5799102 | T.0007756 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-07-30 | NA | 2025-10-31 | NA | TRUE | NA | NA | 109.9947 | 3330.0476 | 0 | 0 | 0 | 0 | 66.633 | 276.4744 | 2817.0273 | 7.2252 | 0 | 0 | 0 | 66.633 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 833 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-14 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 17.354 | NA | 230 ¦ 115 ¦ 60 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5799104 | T.0007758 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-04-28 | NA | 2025-11-14 | NA | TRUE | NA | NA | 228.359 | 17100.9236 | 0 | 0 | 0 | 0 | 174.0853 | 652.4083 | 16237.6825 | 500 | 0 | 0 | 0 | 174.0853 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 834 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 47.516 | NA | 500 ¦ 230 ¦ 115 ¦ 60 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5799099 | T.0007753 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-11-18 | NA | 2025-06-25 | NA | TRUE | NA | NA | 233.0982 | 1834.1655 | 0 | 0 | 0 | 4.8832 | 187.4474 | 1038.6339 | 589.59 | 18.6958 | 0 | 0 | 0 | 192.3306 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 835 | Electric Transmission Substation Security Upgrade |  |  |  |  | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NERC CIP Compliance | 2024-03-15 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 500 ¦ 230 ¦ 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5799100 | T.0007754 | Electric Transmission Substation Security Upgrade | 1 | 66 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-11-12 | NA | 2026-01-13 | NA | FALSE | NA | NA | 230.7136 | 20090.3471 | 0 | 0 | 0 | 0 | 209.5013 | 729.0782 | 2000 | 500 | 0 | 0 | 0 | 209.5013 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] NERC CIP 14 [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 836 | EO-SYSPLN 66X - ET Sub Repl Other Equip |  |  | NA | Forecast placeholder for animal abatement | Substation - Structure | New | NA | Asset Condition | Animal Abatement | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 3 | No | 5533283 | NA | NA | NA | 66 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 837 | McCall (T) Sub - Inst Animal Abatement |  |  | Fresno | This project proposes to Install Animal Abatement at McCall Substation to improve the electric transmission system reliability and safety and help improve the transmission grid reliability, additional transmission capacity and efficiency to serve electric customers in Fresno County. | Substation - Structure | New | TBD | Asset Condition | Animal Abatement | NA | 2024-03-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 16.2494 | NA | NA | 65 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5768394 | T.0001020 | McCall (T) Sub - Inst Animal Abatement | 1 | 66 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-07-10 | NA | 2026-07-10 | NA | TRUE | 20 | NA | 763.3994 | 1007.5545 | 13.332 | 46.0042 | 522.2494 | 119.7883 | 52.3593 | 55.3915 | 0 | 0 | 0 | 0 | 0 | 754.4715 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 838 | HERNDON: Install Animal Abatement |  |  | Fresno, Fresno | This project proposes to Install Animal Abatement at Herndon Substation to improve the electric transmission system reliability and safety and help improve the transmission grid reliability, additional transmission capacity and efficiency to serve electric customers in Fresno County. The animal abatement program mitigates the risks to safety and reliability at substations prone to outages resulted from animal contacts. Animal contact analysis shows that most animal contacts at substations result in sustained power outages as well as damage to substation equipment. Substation Animal Abatement Program Projects were ranked according to criticality, based on the number of customers or transmission and generation facilities potentially impacted. Consideration was also given to contact history and observed animal activity within the substation. Therefore, based on the criticality and probability of future animal contact, Substation Asset Management has identified Herndon Substation. Herndon Substation is located at HFTD zone 1. | Substation - Structure | New | TBD | Asset Condition | Animal Abatement | NA | 2024-03-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 13.3414 | NA | 230 ¦ 115 kV | 65 | 9. Reliability (Low Safety Risk) | Not Available | Tier 2 | No | 5768367 | T.0001006 | Herndon Sub - Inst Animal Abatement | 1 | 66 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2025-12-25 | NA | 2026-02-19 | NA | TRUE | NA | NA | 772.6803 | 1092.2593 | 5.1293 | 23.7997 | 18.9658 | 693.7368 | 9.2728 | 47.0284 | 0 | 0 | 0 | 0 | 0 | 772.6803 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 839 | CCCSD_IMHOFF: Upgrade Pitts MPAC Remote |  |  | Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-04 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.21496 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5791519 | T.0004581 | Pittsburg PP MPAC Installation | 20 | 67 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-03-13 | 2025-08-31 | 2028-01-06 | Bundling Dependencies | FALSE | 29600 | NA | 102.9934 | 775.6958 | 0 | 33.3257 | 16.1302 | 23.6973 | 5.808 | 79.3402 | 302.2499 | 431.0502 | 94.7827 | 11.3358 | 0 | 94.0835 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 840 | TASSAJARA: Upgrade Pitts MPAC Remote En |  |  | Blackhawk CDP, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.1384 | NA | 230 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5790831 | T.0004581 | Pittsburg PP MPAC Installation | 20 | 67 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-08-15 | 2025-08-31 | 2026-11-25 | Bundling Dependencies | FALSE | 64600 | NA | 233.167 | 988.21 | 0 | 23.5638 | 17.7314 | 13.0666 | 57.1714 | 122.6023 | 635.9153 | 112.5298 | 23.6228 | 0 | 0 | 219.8083 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 841 | Tesla - Bellota: 230kV Remote End |  |  | San Joaquin | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | T.0004673 ¦ T.0007288 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 14.7513 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5795705 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-10-05 | 2026-12-01 | 2027-10-18 | Prioritization | FALSE | 36500 | NA | 18.6591 | 1042.2993 | 0 | 0 | 2.7468 | 15.8026 | 0 | 141.0618 | 44.7683 | 45.318 | 600 | 10 | 0 | 18.5493 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 842 | LOCKEFORD: INSTALL 115KV MPAC |  |  | Lockeford CDP, San Joaquin | This project proposes to reconfigure the Lockeford 115 kV bus into a Breaker-And-A-Half (BAAH) bus configuration starting in June 2022 and completing it by December 2027. This project will improve operational flexibility and electric service reliability for the customers in San Joaquin County. Upon completion of this project, the frequency and duration of electric service interruption will be significantly reduced, and the aging protection, automation, and control assets of the Lockeford 115 kV system will be replaced with Modular Protection Automation & Control enclosure (MPAC) under MWC 67. In addition, this project is also needed to support the installation of a new 115/21 kV distribution bank, which is aimed to go operational under MWC 46 in 2027. Completion of this project will facilitate the removal of the 75-year-old, deteriorated and idle 115/60 kV Lockeford bank1 that is currently being used for distribution bank 4 back up. The project scope of work includes the following: • Demolish existing 115 kV OCBs and associated switches • Convert Lockeford 115 kV Bus to Breaker-And-A-Half (BAAH) configuration • Install 8 Circuit Breakers; Three (3) BAAH bays • Install Breaker/Line disconnect Switches • Install CCVT as required • Install Bank Disconnect Switches, install necessary conduits and pull new wires as required | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2719 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5801426 | T.0008354 | Lockeford: Convert 115 kV Bus to BAAH | 2 | 67 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-04-01 | NA | 2033-06-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 843 | MONTA VISTA: Inst Metcalf Remote End |  |  | Cupertino, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Other - Operations Tech | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-11 | NA | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.8314 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5775340 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-04-30 | 2020-08-07 | 2024-08-02 | Prioritization | TRUE | 39600 | NA | 500.0638 | 926.781 | 51.0489 | 53.6994 | 64.2362 | 91.2292 | 108 | 438.7727 | 5.1694 | 0 | 0 | 0 | 0 | 482.8387 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 844 | SMARTVILLE SUB: INSTALL 60KV MPAC |  |  | Smartsville CDP, Yuba | Install protection, automation, and control equipment on the 60kV system at Smartville Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to execute concurrently with the bus conversion project from existing MaiNAux to DBSB in 94D. Smartville 60kV has lots of EM relays and makes sense to deploy MPAC solution and align with the bus work schedule. 60kV Bus Diff = KAB installed in Y1996. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-11 | NA | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.2017 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5792886 | T.0006510 | SMARTVILLE SUB_INSTALL 60KV MPAC | 1 | 67 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-04-01 | NA | 2033-06-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 845 | PLACER: Install 115/60kV MPAC |  |  | Placer | Deploy 115 kV MPAC and Upgrade 60 kV protective relaying equipment in the existing control building. The driver of the new MPAC building enclosure is to support the concurrent Placer 115 kV Bus Conversion Project in the same substation (MWC 61 & MWC 94) and various Placer substation Bus Protection Upgrade projects (MWC 3F), and Placer Transformer Addition Project (MWC 61). | Substation - Modular Protection and Automation Control Building | New | T.0005697 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.9734 | NA | 115 kV | 439 | 5. Compliance/Commitments With Strong Safety Link | Not Available | Tier 4 | No | 5733505 | T.0006004 | Placer: Install 115/60kV MPAC | 1 | 67 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-08-11 | 2024-06-30 | 2027-03-03 | Prioritization | FALSE | 12200 | NA | 3417.0036 | 15478.6588 | 0 | 35.0849 | 154.1883 | 180.1054 | 2973.3098 | 282.2876 | 0 | 0 | 0 | 0 | 3782.4443 | 3342.6885 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 846 | UKIAH SUB: INSTALL 115KV MPAC |  |  | Mendocino | Deploy 115 kV MPAC at Ukiah Substation to support the concurrent 115 kV bus conversion reliability project funded under MWC 94. This project scope describes the scope of a generic MPAC project for furnishing and installing one or more MPAC buildings as part of a substation aging asset replacement project. For the Ukiah 115 kV MPAC Automation project, the existing protection assets are deficient, namely relaying and automation equipment, control wires, conduits, cable tray, etc. Ukiah Substation serves Humboldt county at the 115 kV voltage level and a major substation in the North Coast area. Installing new protection and automation equipment at the Ukiah 115 kV system will improve the service reliability to our customers and increase system visibility for Operations. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.92364 | NA | 115 kV | 439 | Not Available | Not Available | RBPPF - TBD | Yes | 5792230 | T.0001467 | Ukiah Sub 115 kV Reliability Project | 2 | 67 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-02-03 | NA | 2028-05-29 | NA | FALSE | NA | NA | 0 | 6857.2691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 847 | Monta Vista: Upgrade Mt View MPAC Remote |  |  | Cupertino, Santa Clara | Install 115 kV MPAC at Mountain View substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 kV system and non-standard bus differential scheme that reduce the reliability of the station. This project proposes to deploy a new 115 kV MPAC enclosure to support the concurrent, 115 kV Bus Conversion, Transformer #1 Replacement, and Feeder Circuit Breaker Replacement projects. Mountain View is one of the key substations in the Central Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 115 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Mountain View Substation, and the interconnected stations at the remote-end. | Other - Operations Tech | Upgrade/Retrofit | T.0005971 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-11 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 15.8314 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799751 | T.0007709 | MT VIEW SUB - INSTALL 115KV MPAC | 2 | 67 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-04-27 | NA | 2027-06-23 | NA | FALSE | NA | NA | 162.1945 | 2268.6988 | 0 | 0 | 0 | 135.192 | 21.512 | 835.6958 | 350 | 206.9004 | 462.1193 | 0 | 0 | 156.704 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 848 | MT VIEW SUB - INSTALL 115KV MPAC |  |  | Mountain View, Santa Clara | Install 115 kV MPAC at Mountain View substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 kV system and non-standard bus differential scheme that reduce the reliability of the station. This project proposes to deploy a new 115 kV MPAC enclosure to support the concurrent, 115 kV Bus Conversion, Transformer #1 Replacement, and Feeder Circuit Breaker Replacement projects. Mountain View is one of the key substations in the Central Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 115 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Mountain View Substation, and the interconnected stations at the remote-end. | Substation - Modular Protection and Automation Control Building | New | T.0005971 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-09 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.8224 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799139 | T.0007709 | MT VIEW SUB - INSTALL 115KV MPAC | 2 | 67 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-06-25 | NA | 2025-12-29 | NA | TRUE | NA | NA | 1888.0155 | 9147.6595 | 0 | 0 | 1.3816 | 411.8691 | 1417.6325 | 1843.0833 | 3272.2457 | 11 | 0 | 0 | 0 | 1830.8832 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 849 | FULTON SUB: INSTALL 60KV MPAC |  |  | Fulton CDP, Sonoma | Install 60 kV MPAC at Fulton substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 60 kV system and non-standard bus differential scheme that reduce the reliability of the station. This project proposes to deploy a new 60 kV MPAC enclosure to support the concurrent, 230 kV and 115 kV MPAC Projects. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 60 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation, and the interconnected stations at the remote-end. | Substation - Modular Protection and Automation Control Building | New | T.0007811 ¦ T.0005942 ¦ T.0005942 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.4076 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798447 | T.0007660 | FULTON SUB - INSTALL 60KV MPAC | 1 | 67 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2028-02-04 | NA | 2030-04-26 | NA | FALSE | NA | NA | 113.1533 | 17445.3999 | 0 | 0 | 13.6996 | 83.0211 | 15.1094 | 9160.2732 | 0 | 0 | 0 | 0 | 0 | 111.83 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 850 | SANGER: Install 115 KV MPAC |  |  | Fresno | Install a new seven bay 115 kV BAAH bus, two MPAC buildings, and relocate all associated 115 kV lines at Sanger Substation. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-07 | NA | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.0513 | NA | 115 kV | 225 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5756775 | T.0000601 | Sanger Substation 115kV Bus Replacement | 4 | 67 | NA | 2014 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2017-07-13 | IS/MND | NA | CPUC | NA | PTC: A.15-09-012 | 2015-09-30 | Approved | 2017 | Operational | 2 | 2019-05-02 | 2019-12-31 | 2020-11-02 | Prioritization | FALSE | 55300 | NA | 12147.1528 | 12147.1528 | 2916.6458 | 2184.4459 | 747.1901 | 101.3005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12147.1528 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 11298.141 | 747.1901 | 101.3005 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
| 851 | Cottonwood MPAC_Remote End Delevan |  |  | Colusa | Install MPAC bulding on the 230 kV system at Cottonwood Substation Bus Sect. E and F. The driver of the new MPAC building is to support the concurrent Cottonwood Transformer Replacement Projects, replacement of six circuit breakers, addition of bus parallel circuit breaker, and upgrade the aging protection and control equipment at the Cottonwood substation. | Other - Operations Tech | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-07 | NA | NA | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.7615 | NA | 230 kV | Not Available | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5784661 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 67 | NA | 2018 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-10-08 | 2028-04-30 | 2027-01-06 | NA | FALSE | 51200 | NA | 64.0171 | 1042.6905 | 9.7022 | 3.8157 | 6.2519 | 11.8011 | 26.9912 | 161.7328 | 350 | 750 | 500 | 0 | 0 | 58.5622 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 852 | Cottonwood MPAC_Remote End Glenn |  |  | Glenn | Install MPAC bulding on the 230 kV system at Cottonwood Substation Bus Sect. E and F. The driver of the new MPAC building is to support the concurrent Cottonwood Transformer Replacement Projects, replacement of six circuit breakers, addition of bus parallel circuit breaker, and upgrade the aging protection and control equipment at the Cottonwood substation. | Other - Operations Tech | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-13 | NA | NA | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 5.7152 | NA | 230 kV | Not Available | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5784662 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 67 | NA | 2018 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-10-08 | 2028-04-30 | 2026-11-19 | NA | FALSE | 51200 | NA | 52.216 | 1133.8026 | 8.3367 | 3.8937 | 3.4816 | 5.4325 | 25.553 | 177.4318 | 200 | 638.9316 | 1415.5477 | 0 | 0 | 46.6975 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 853 | Cottonwood MPAC_Remote End Round Mtn |  |  | Round Mountain CDP, Shasta | Install MPAC bulding on the 230 kV system at Cottonwood Substation Bus Sect. E and F. The driver of the new MPAC building is to support the concurrent Cottonwood Transformer Replacement Projects, replacement of six circuit breakers, addition of bus parallel circuit breaker, and upgrade the aging protection and control equipment at the Cottonwood substation. | Other - Operations Tech | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | NA | NA | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 29.1389 | NA | 230 kV | Not Available | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5784659 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 67 | NA | 2018 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-10-08 | 2028-04-30 | 2027-01-06 | NA | FALSE | 51200 | NA | 84.7512 | 1102.8099 | 8.8635 | 3.8582 | 7.1716 | 20.6934 | 36.6272 | 170.889 | 200 | 645.1655 | 1228.4101 | 10.1143 | 0 | 77.2139 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 854 | Cottonwood Sub: Install 230kV MPAC |  |  | Cottonwood CDP, Shasta | Install MPAC bulding on the 230 kV system at Cottonwood Substation Bus Sect. E and F. The driver of the new MPAC building is to support the concurrent Cottonwood Transformer Replacement Projects, replacement of six circuit breakers, addition of bus parallel circuit breaker, and upgrade the aging protection and control equipment at the Cottonwood substation. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | NA | NA | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 26.1945 | NA | 230 kV | 1002 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5783341 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 67 | NA | 2018 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-03-20 | 2028-04-30 | 2028-05-18 | NA | FALSE | 51200 | NA | 464.8516 | 27114.6882 | 80.7389 | 82.4527 | 63.4035 | 70.7023 | 137.3583 | 2799.1005 | 750 | 3500 | 6000 | 3500 | 1000 | 434.6558 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 855 | COTTONWOOD SUB_INSTALL 230KV MPAC BUS G |  |  | Cottonwood CDP, Shasta | Install MPAC bulding on the 230 kV system at Cottonwood Substation Bus Sect. E and F. The driver of the new MPAC building is to support the concurrent Cottonwood Transformer Replacement Projects, replacement of six circuit breakers, addition of bus parallel circuit breaker, and upgrade the aging protection and control equipment at the Cottonwood substation. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | NA | NA | Wires - Voltage Support/Reactive Support Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 26.1945 | NA | 230 kV | 472 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5791155 | T.0001129 | Cottonwood Install Bank Replacements | 13 | 67 | NA | 2018 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2025-12-18 | 2028-04-30 | 2026-09-28 | NA | FALSE | 51200 | NA | 153.4734 | 2098.3153 | 0 | 3.9432 | 16.8901 | 37.0881 | 76.0423 | 68.4204 | 750 | 3000 | 4000 | 2500 | 750 | 133.9637 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 856 | WILSON: Install 115 KV MPAC |  |  | Merced, Merced | Install new 115 kV and 230 kV Breaker-and-a-half (BAAH) Bus Arrangements, two Modular Protection and Automation Control (MPAC) Buildings, and two new 230/115 kV Transformers. Installing the Wilson 115 kV Area Reinforcement project will improve grid reliability, improve operational and maintenance flexibility, mitigate potential voltage issues that could increase fire ignition risks, system-wide outages and increase load serving capability in the Merced Area. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 22.8151 | NA | 115 kV | 58 | 5a.Mitigates System Wide Failure Risk | 7 | RBPPF - TBD | Yes | 5781261 | T.0004116 | WILSON: 115 kV ARP - BAAH | 6 | 67 | NA | 2012 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-10-13 | 2022-08-12 | 2027-09-07 | Prioritization | FALSE | 66700 | NA | 93.2785 | 11390.7035 | 48.6191 | 35.4913 | 3.429 | 0 | 0 | 5.8548 | 232.7929 | 3147.5227 | 7427.9083 | 20.0227 | 0 | 93.2785 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - New Substation Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $50 Mil – $75 Mil
| 857 | ORO LOMA: Install 115 KV MPAC |  |  | Fresno | install protection, automation and control equipment at on the 115 kV bus at Oro Loma Substation. Installation of automation, protection and control equipment will increase the operational visibility and provide remote control capabilities that will help PG&E become the leading utility in the United States. | Substation - Modular Protection and Automation Control Building | New | T.0003408 ¦ T.0001473 ¦ T.0000891 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-16 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.8637 | NA | 115 kV | 235 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5744220 | T.0000563 | ORO LOMA: INSTALL 115 KV MPAC | 1 | 67 | NA | 2011 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-04 | 2019-02-28 | 2019-11-06 | Workforce | FALSE | 9038 | NA | 12433.7647 | 12433.7647 | 3025.7369 | 791.9846 | 446.253 | 0 | 0.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 12433.7647 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2023 ¦ 2024 | 11229.4622 | 791.9846 | 446.253 | 0 | 0.04581 | 0 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 858 | RAVENSWOOD SUB: INSTALL 115KV MPAC |  |  | Menlo Park, San Mateo | Install protection, automation, and control equipment on the 115 kV & 230 kV systems at Ravenswood Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 & 230 kV systems and non-standard bus differential scheme that reduce the reliability of the station.The 115 kV & 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Ravenswood Substation. | Substation - Modular Protection and Automation Control Building | New | T.0007874 ¦ T.0001608 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.3472 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5797793 | T.0006509 | RAVENSWOOD SUB_INSTALL 230KV MPAC | 2 | 67 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-04-16 | NA | 2028-03-10 | NA | FALSE | NA | NA | 139.8924 | 7757.3929 | 0 | 0 | 3.2776 | 136.8022 | -0.1875 | 8.5144 | 1250 | 3000 | 6000 | 3000 | 2500 | 139.8924 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 859 | RAVENSWOOD SUB: INSTALL 230KV MPAC |  |  | Menlo Park, San Mateo | Install protection, automation, and control equipment on the 115 kV & 230 kV systems at Ravenswood Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 & 230 kV systems and non-standard bus differential scheme that reduce the reliability of the station.The 115 kV & 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Ravenswood Substation. | Substation - Modular Protection and Automation Control Building | New | T.0007874 ¦ T.0001608 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.3472 | NA | 230 kV | 184 | Not Available | Not Available | RBPPF - TBD | Yes | 5792885 | T.0006509 | RAVENSWOOD SUB_INSTALL 230KV MPAC | 2 | 67 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-06-04 | NA | 2028-08-03 | NA | FALSE | NA | NA | 387.6936 | 19162.3172 | 0 | 0 | 76.9524 | 310.7713 | -0.0301 | 23.5966 | 1250 | 3500 | 6500 | 6000 | 1500 | 387.6936 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 860 | CLAYTON: Repl 115 KV MPAC |  |  | Concord, Contra Costa | Install protection, automation, and control equipment on the 115 kV system at Clayton substation. The driver of the new 115 kV MPAC building is to support the Clayton 115 kV Bus Reliability Project (MWC 94), which PG&E will be sectionalizing the existing 115 kV bus configuration and install dedicated circuit breaker for each distribution transformer bank to increase reliability. The 115 kV MPAC building will provide the necessary automation and remote control capabilities protective relays, and modular control building at Clayton Substation. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.9731 | NA | 115 kV | 472 | 5a.Mitigates System Wide Failure Risk | 11 | RBPPF - TBD | Yes | 5757527 | T.0001640 | CLAYTON: 2SECT-BRK & MPAC | 2 | 67 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-03-18 | NA | 2027-08-02 | NA | FALSE | NA | NA | 72.5268 | 10822.1716 | 13.6935 | 28.864 | 5.1216 | 4.5571 | 4.9608 | 5.4575 | 0 | 0 | 0 | 0 | 5.2332 | 71.4835 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 861 | Fulton: Install 115kV MPAC |  |  | Fulton CDP, Sonoma | Install protection, automation, and control equipment on the 115 kV system at Fulton Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 115 kV system and non-standard bus differential scheme that reduce the reliability of the station. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 20 years. The 115 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation. | Substation - Modular Protection and Automation Control Building | New | T.0007811 ¦ T.0007660 ¦ T.0005940 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.4076 | NA | 230 kV | 166 | 5. Compliance/Commitments With Strong Safety Link | 2 | RBPPF - TBD | Yes | 5790906 | T.0005942 | Fulton_Install 115kV MPAC | 2 | 67 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-10-07 | NA | 2028-06-30 | NA | FALSE | NA | NA | 245.6671 | 15733.8447 | 0 | 0 | 155.953 | 62.6707 | 24.1705 | 17.7943 | 0 | 0 | 0 | 0 | 100 | 242.794 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 862 | Lawrence: Install 115kV MPAC |  |  | Sunnyvale, Santa Clara | Install protection, automation, and control equipment on the 115 kV system at Lawrence Substation. The driver of the new MPAC building enclosure is to support the concurrent Lawrence 115 kV Ring Bus Conversion Project in the same substation (MWC 94). The Lawrence MPAC project will also address the “Fault Protection Scheme Deficiency” concerns at Lawrence substation. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-01 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.8829 | NA | 115 kV | 133 | Not Available | Not Available | RBPPF - TBD | Yes | 5791858 | T.0006096 | Lawrence_Install 115kV MPAC | 1 | 67 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-07-07 | NA | 2028-11-16 | NA | FALSE | NA | NA | 110.5708 | 9754.1081 | 0 | 0 | 94.798 | 6.8959 | 7.5837 | 7.9893 | 0 | 0 | 0 | 0 | 0 | 109.2777 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 863 | CLAYTON: Upgrade Pitts MPAC Remote End |  |  | Concord, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.9731 | NA | 230 ¦ 115 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | 11 | RBPPF - TBD | Yes | 5790834 | T.0004581 | Pittsburg PP MPAC Installation | 20 | 67 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-05-28 | 2024-10-31 | 2027-08-25 | Bundling Dependencies | FALSE | 64600 | NA | 125.5379 | 3048.7892 | 0 | 34.9772 | 27.5026 | 30.0953 | 13.9577 | 417.3979 | 1043.6109 | 1356.4029 | 90.4857 | 11.3358 | 0 | 106.5329 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 864 | LAKEWOOD: Upgrade Pitts MPAC Remote End |  |  | Walnut Creek, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-07 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.1281 | NA | 230 ¦ 115 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | 8 | RBPPF - TBD | Yes | 5790835 | T.0004581 | Pittsburg PP MPAC Installation | 20 | 67 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-02-07 | 2024-10-31 | 2027-10-28 | Bundling Dependencies | FALSE | 64600 | NA | 1080.5248 | 2677.2223 | 0 | 28.9008 | 63.4473 | 652.1539 | 296.1396 | 353.2179 | 406.1192 | 753.1761 | 84.8758 | 11.3358 | 0 | 1040.6416 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 865 | Pittsburg PP: Install 115kV MPAC |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Substation - Modular Protection and Automation Control Building | New | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | 22 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 28.8512 | NA | 115 kV | 137 | 5a.Mitigates System Wide Failure Risk | 14 | Tier 4 | No | 5784149 | T.0004581 | Pittsburg PP MPAC Installation | 20 | 67 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-10-07 | 2025-08-31 | 2028-09-25 | Bundling Dependencies | FALSE | 64600 | NA | 1028.9556 | 28056.1208 | 33.5847 | 154.0823 | 148.5932 | 144.2491 | 410.3866 | 7618.9453 | 7187.3014 | 4024.3101 | 1636.6442 | 192.5184 | 0 | 890.8958 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 866 | PITTSBURG PP: INSTALL 230KV Bus F MPAC |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Substation - Modular Protection and Automation Control Building | New | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 28.8512 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 4 | No | 5801381 | T.0004581 | Pittsburg PP MPAC Installation | 20 | 67 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-12-27 | 2025-08-31 | 2028-05-02 | Bundling Dependencies | FALSE | 64600 | NA | 31.8665 | 3142.3675 | 0 | 0 | 0 | 5.6333 | 21.7628 | 1747.6907 | 1287 | 649 | 219 | 201 | 0 | 27.396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 867 | Pittsburg PP: Install 230kV MPAC |  |  | Pittsburg, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Substation - Modular Protection and Automation Control Building | New | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | 22 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 28.8512 | NA | 230 kV | 137 | 5a.Mitigates System Wide Failure Risk | 14 | Tier 4 | No | 5784148 | T.0004581 | Pittsburg PP MPAC Installation | 20 | 67 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-07-03 | 2025-08-31 | 2027-03-17 | Bundling Dependencies | FALSE | 64600 | NA | 6545.9695 | 28882.0637 | 20.4883 | 612.1683 | 705.4687 | 240.9185 | 1533.5323 | 11321.3174 | 6832.283 | 3572.3965 | 1871.5392 | 1194.3741 | 0 | 3112.576 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 868 | SAN RAMON: Upgrade Pitts MPAC Remote End |  |  | San Ramon, Contra Costa | Install protection, automation, and control equipment on the 230 & 115 kV system at Pittsburg PP Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. The driver of the new MPAC building enclosure is to support the concurrent Pittsburg 230/115 kV Transformer Capacity Increase Project and 3rd Party Energy Storage Project. | Other - Operations Tech | Upgrade/Retrofit | T.0000946 ¦ T.0009189 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-04 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.3628 | NA | 230 ¦ 115 kV | 137 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | Yes | 5790830 | T.0004581 | Pittsburg PP MPAC Installation | 20 | 67 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-02-10 | 2024-10-31 | 2026-09-22 | Bundling Dependencies | FALSE | 64600 | NA | 222.0542 | 1482.0515 | 0 | 25.819 | 17.7646 | 25.0331 | 141.2079 | 172.2621 | 1028.8207 | 141.5841 | 15.4161 | 0 | 0 | 209.8246 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 869 | Tesla - Eight Mile Road: 230kV Remote En |  |  | Alameda | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | T.0004673 ¦ T.0007288 | Asset Condition | Modular Protection and Automation Control | NA | 2024-03-15 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 2 | No | 5793901 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-12-30 | 2026-12-01 | 2028-02-28 | Prioritization | FALSE | 113900 | NA | 62.503 | 4020.4691 | 0 | 0 | 41.1083 | 17.2395 | 0.8414 | 252.0394 | 150 | 50 | 634.6815 | 0 | 0 | 59.1892 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 870 | Tesla - Install 230kv MPAC (Section D) |  |  | Alameda | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | T.0004673 ¦ T.0007288 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-15 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 288 | Not Available | Not Available | RBPPF - TBD | Yes | 5795887 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-11-19 | 2026-12-01 | 2028-01-07 | Prioritization | FALSE | 113900 | NA | 48.3679 | 9826.1526 | 0 | 0 | 11.0918 | 11.819 | 24.8915 | 3.5096 | 3500 | 6000 | 4500 | 1000 | 0 | 47.8022 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 871 | Tesla - Install 230kv MPAC (Section E) |  |  | Alameda | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | T.0004673 ¦ T.0007288 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-15 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 288 | Not Available | Not Available | RBPPF - TBD | Yes | 5795886 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-08-21 | 2026-12-01 | 2027-03-30 | NA | FALSE | 113900 | NA | 49.3889 | 43648.27 | 0 | 0 | 4.2051 | 20.7825 | 23.468 | 2367.5654 | 0 | 0 | 0 | 0 | 0 | 48.4556 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 872 | Tesla - Kelso: 230kV Remote End |  |  | Alameda | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | T.0004673 ¦ T.0007288 | Asset Condition | Modular Protection and Automation Control | NA | 2024-03-15 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 2 | No | 5793940 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-05-18 | 2026-12-01 | 2026-07-14 | NA | FALSE | 113900 | NA | 61.4144 | 3435.047 | 0 | 0 | 35.7249 | 23.4664 | 0.8414 | 222.5132 | 130.0778 | 645.0222 | 0 | 0 | 0 | 60.0327 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 873 | Tesla - Newark: 230kV Remote End |  |  | Alameda | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | T.0004673 ¦ T.0007288 | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | 2024-03-15 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 2 | No | 5793938 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-05-28 | 2026-12-01 | 2026-07-24 | NA | FALSE | 113900 | NA | 70.7553 | 2033.2906 | 0 | 0 | 40.6865 | 27.7173 | 1.0518 | 217.002 | 300 | 75 | 0 | 0 | 0 | 69.4556 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 874 | Tesla - Ravenswood: 230kV Remote End |  |  | Alameda | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | T.0004673 ¦ T.0007288 | Asset Condition | Modular Protection and Automation Control | NA | 2024-03-15 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 2 | No | 5793900 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-03-31 | 2026-12-01 | 2027-05-25 | NA | FALSE | 113900 | NA | 76.5093 | 1845.0813 | 0 | 0 | 52.1957 | 22.9714 | 0.8923 | 144.923 | 150 | 60.3685 | 600 | 0 | 0 | 76.0593 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 875 | Tesla - Stag: 230kV Remote End |  |  | Alameda | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | T.0004673 ¦ T.0007288 | Asset Condition | Modular Protection and Automation Control | NA | 2024-03-15 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 2 | No | 5793902 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-12-09 | 2026-12-01 | 2028-02-07 | Prioritization | FALSE | 113900 | NA | 100.6774 | 3823.8982 | 0 | 0 | 63.0865 | 34.9163 | 1.0518 | 225.1441 | 50 | 70.0237 | 600 | 0 | 0 | 99.0545 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 876 | Tesla - Tracy: 230kV Remote End |  |  | Alameda | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | T.0004673 ¦ T.0007288 | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | 2024-03-15 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 2 | No | 5793899 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-03-17 | 2026-12-01 | 2027-05-11 | NA | FALSE | 113900 | NA | 38.1258 | 1417.6409 | 0 | 0 | 20.8534 | 16.2067 | 0.8414 | 72.2934 | 211.2036 | 96.6153 | 783.271 | 0 | 0 | 37.9015 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 877 | Tesla - Weber: 230kV Remote End |  |  | San Joaquin | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Other - Operations Tech | Upgrade/Retrofit | T.0004673 ¦ T.0007288 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | NA | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.1366 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5795704 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-11-05 | 2026-12-01 | 2028-01-06 | Prioritization | FALSE | 113900 | NA | 42.7632 | 1903.0398 | 0 | 0 | 30.1353 | 12.2746 | 0.1017 | 150.5127 | 49.5604 | 50 | 600 | 0 | 0 | 42.5117 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 878 | TESLA: Install 230 KV MPAC |  |  | Alameda | Install protection, automation, and control equipment on the 230 kV and 115 kV system at Tesla Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | T.0004673 ¦ T.0007288 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-15 | 39 | NA | Other - Deferral | $100 Mil – $125 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 69.382 | NA | 230 kV | 288 | 5. Compliance/Commitments With Strong Safety Link | 9 | RBPPF - TBD | Yes | 5776770 | T.0003456 | Tesla 230kV MPAC | 18 | 67 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-12-12 | 2026-12-01 | 2026-06-08 | NA | FALSE | 113900 | NA | 891.7413 | 33219.7379 | 0 | 138.15 | 194.5451 | 181.5405 | 313.4306 | 3561.4609 | 3500 | 6000 | 4500 | 2500 | 0 | 827.6661 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 879 | Fulton: Install 230kV MPAC |  |  | Fulton CDP, Sonoma | Install protection, automation, and control equipment on the 230 kV system at Fulton Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 230 kV system and non-standard bus differential scheme that reduce the reliability of the station. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation. | Substation - Modular Protection and Automation Control Building | New | T.0007811 ¦ T.0007660 ¦ T.0005942 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.4076 | NA | 230 kV | 672 | 5. Compliance/Commitments With Strong Safety Link | 2 | RBPPF - TBD | Yes | 5790905 | T.0005940 | Fulton_Install 230kV MPAC | 4 | 67 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2027-10-13 | NA | 2028-12-08 | NA | FALSE | NA | NA | 320.9169 | 13502.879 | 0 | 0 | 200.5668 | 87.1648 | 29.4322 | 368.1359 | 0 | 0 | 0 | 0 | 50 | 317.1638 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 880 | Relay Repl 230kV Fulton - Ignacio Line |  |  | Novato, Marin | Install protection, automation, and control equipment on the 230 kV system at Fulton Substation. The driver of the new MPAC building enclosure is to address various protection deficiencies on the 230 kV system and non-standard bus differential scheme that reduce the reliability of the station. Fulton is one of the key substations in the North Coast area and it has had relatively few relay upgrade projects in the last 15-20 years. The 230 kV MPAC enclosure will incorporate various protection relaying replacement scopes and provide the necessary automation and remote control capabilities (SCADA) and upgrade the aging protective relays at Fulton Substation. | Substation - Protection Relay | Upgrade/Retrofit | T.0007811 ¦ T.0007660 ¦ T.0005942 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-14 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 11.9486 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5797640 | T.0005940 | Fulton_Install 230kV MPAC | 4 | 67 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-10-05 | NA | 2028-02-23 | NA | FALSE | NA | NA | 27.9972 | 1355.1416 | 0 | 0 | 6.5457 | 11.8189 | 9.3051 | 30.0064 | 0 | 0 | 0 | 0 | 0 | 27.6698 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement
| 881 | GOLD HILL: Install 115/60kV MPAC |  |  | Folsom, Sacramento | Install protection, automation, and control equipment on the 230 kV, 115 kV and 60 kV system at Gold Hill Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | T.0004950 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-28 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 12.8702 | NA | 115 kV | 472 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 4 | No | 5786799 | T.0004920 | Gold Hill: Install 115/60kV MPAC | 2 | 67 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-06-07 | 2023-11-30 | 2025-06-09 | Prioritization | TRUE | 12200 | NA | 8950.8444 | 19637.7086 | 0 | 15.0745 | 117.4837 | 213.6133 | 7510.7253 | 6668.0229 | 4944.4327 | 0 | 0 | 0 | 0 | 7856.8968 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 882 | GOLD HILL: Install 230kV MPAC |  |  | Folsom, Sacramento | Install protection, automation, and control equipment on the 230 kV, 115 kV and 60 kV system at Gold Hill Substation. Installation of automation and control equipment will increase the operational visibility, provide remote control capabilities that improve system reliability, and upgrade the aging protection and control equipment in the existing control buildings. | Substation - Modular Protection and Automation Control Building | New | T.0004950 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-28 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 12.8702 | NA | 230 kV | 472 | 5. Compliance/Commitments With Strong Safety Link | Not Available | Tier 4 | No | 5789535 | T.0004920 | Gold Hill: Install 115/60kV MPAC | 2 | 67 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-03-23 | 2023-11-30 | 2028-01-31 | Prioritization | FALSE | 12200 | NA | 21.3459 | 8190.6567 | 0 | 2.7167 | 15.5843 | 1.3312 | 1.464 | 1.5423 | 2375.1658 | 3464.1056 | 1114.5063 | 0 | 0 | 21.0963 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 883 | MIDWAY SUB: INSTALL 230kV MPAC |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-15 | 55 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 230 kV | 705 | 5a.Mitigates System Wide Failure Risk | 9 | RBPPF - TBD | Yes | 5782562 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 67 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 3 | 2021-06-14 | 2022-04-01 | 2025-10-07 | Prioritization | TRUE | 105100 | NA | 11357.3358 | 13451.8694 | 4902.7192 | 880.6445 | 2693.0623 | 2509.8357 | 367.9386 | 1358.9766 | 735.5569 | 0 | 0 | 0 | 0 | 11357.3358 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 884 | HOWLAND: Upgrade Vierra MPAC Remote End |  |  | Lathrop, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | NA | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.29009 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 21 | RBPPF - TBD | Yes | 5777419 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 13 | 67 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 4 | 2025-07-28 | 2023-01-24 | 2026-07-14 | Prioritization | TRUE | 41500 | NA | 1763.0345 | 3069.0921 | 30.591 | 94.3009 | 615.0809 | 435.1811 | 531.1778 | 524.3531 | 11.5063 | 0 | 0 | 0 | 0 | 1738.913 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
| 885 | KASSON: Upgrade Vierra MPAC Remote End |  |  | San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | 14 | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.1988 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 10 | RBPPF - TBD | Yes | 5777396 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 13 | 67 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 4 | 2024-09-03 | 2023-01-24 | 2026-01-13 | Prioritization | TRUE | 41500 | NA | 450.9121 | 1547.9379 | 34.4698 | 119.4249 | 34.7818 | 35.4488 | 165.5054 | 875.3819 | 82.5342 | 0 | 0 | 0 | 0 | 436.0944 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
| 886 | MANTECA: Upgrade Vierra MPAC Remote End |  |  | Manteca, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-12 | NA | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.8539 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 14 | RBPPF - TBD | Yes | 5777418 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 13 | 67 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 4 | 2024-10-17 | 2023-01-24 | 2026-11-05 | Prioritization | FALSE | 41500 | NA | 479.8065 | 1529.2119 | 37.1001 | 105.1484 | 27.7332 | 43.1306 | 207.7897 | 779.5272 | 76.4822 | 21.621 | 0 | 0 | 0 | 461.7217 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
| 887 | TRACY: Upgrade Vierra MPAC Remote End |  |  | Tracy, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | 14 | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.7469 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 13 | RBPPF - TBD | Yes | 5777397 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 13 | 67 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 4 | 2025-01-29 | 2023-01-24 | 2025-06-20 | Prioritization | TRUE | 41500 | NA | 497.9649 | 1737.7585 | 30.609 | 163.2872 | 41.8877 | 31.2087 | 150.8307 | 1031.8119 | 237.4891 | 17.9251 | 0 | 0 | 0 | 461.3107 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
| 888 | Vierra MPAC |  |  | Lathrop, San Joaquin | Loop the Tesla-Stockton Co-Gen Junction 115kV Line into Vierra Substation, convert the Vierra 115kV bus into a 4-bay breaker-and-a-half (BAAH) bus configuration, add a Howland Road Co-Gen Radial Feed, install a 115kV Sustainable Modular Protection (SMP) / Modular Protection Automation and Controls (MPAC), and install battery buildings. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-06 | NA | NA | Wires - Reconductor/Line Rebuild Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.355 | NA | 115 kV | 102 | 5a.Mitigates System Wide Failure Risk | 12 | RBPPF - TBD | Yes | 5777394 | T.0000597 | VIERRA 115 KV REINFORCEMENT | 13 | 67 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-02-01 | IS/MND | NA | CPUC | NA | PTC: A.18-06-004 | 2018-06-15 | Approved | 2021 | Engineering more than 50% complete | 4 | 2024-05-30 | 2023-01-24 | 2025-05-01 | Prioritization | TRUE | 41500 | NA | 4892.2442 | 13687.7686 | 49.5992 | 347.1672 | 248.2162 | 106.2447 | 2217.2928 | 6818.884 | 3344.1379 | 35.089 | 0 | 0 | 0 | 3232.18 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement
| 889 | COYOTE: Upgrade CB 212- 412 Relay |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-08 | 20 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.5453 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 4 | No | 5780955 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 67 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-16 | 2023-03-31 | 2024-12-18 | Bundling Dependencies | TRUE | 78700 | NA | 440.4343 | 2044.9774 | 17.5636 | 18.2867 | 113.581 | 211.9408 | 32.1176 | 1564.3582 | 67.5553 | 0 | 0 | 0 | 0 | 413.0639 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 890 | EDENVALE: Upgrade CB 122 Relay |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-08 | 7 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3853 | NA | 115 kV | 288 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5781018 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 67 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-06-11 | 2023-03-31 | 2026-07-10 | Bundling Dependencies | TRUE | 78700 | NA | 309.8576 | 1029.3507 | 13.9303 | 8.9552 | 126.9099 | 116.6297 | 19.8431 | 22.2755 | 16.8153 | 0 | 0 | 0 | 0 | 306.4413 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 891 | EL PATIO: Upgrade CB 212 & 152 Relay |  |  | Campbell, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-07 | 11 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.392 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 4 | No | 5780956 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 67 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-07-13 | 2023-03-31 | 2026-09-10 | Bundling Dependencies | TRUE | 65600 | NA | 283.9872 | 1242.3915 | 9.225 | 19.9351 | 22.2872 | 190.5947 | 18.6375 | 20.4405 | 3.372 | 0 | 0 | 0 | 0 | 280.8313 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 892 | LOS ESTEROS: Upgrade CB 362- 462 Relay |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-12 | 25 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.1703 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 4 | No | 5780953 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 67 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-11-02 | 2023-03-31 | 2026-12-04 | Bundling Dependencies | TRUE | 65600 | NA | 353.8139 | 1290.4065 | 13.8134 | 29.0318 | 17.8543 | 243.6211 | 23.4386 | 25.4818 | 6.8023 | 0 | 0 | 0 | 0 | 349.8666 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 893 | METCALF: Install 115 KV MPAC |  |  | Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Modular Protection and Automation Control Building | New | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-13 | 28 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 115 kV | 288 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 4 | No | 5776763 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 67 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-08-12 | 2023-03-31 | 2026-04-15 | Bundling Dependencies | FALSE | 65600 | NA | 17843.2068 | 47604.3694 | 109.1006 | 247.85 | 6306.0685 | 3929.447 | 6223.7657 | 5873.7535 | 3517.3438 | 2261.2644 | 330.1861 | 0 | 0 | 17020.5572 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 894 | METCALF: Install 230 KV MPAC |  |  | Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Modular Protection and Automation Control Building | New | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-13 | 28 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.8815 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 4 | No | 5776764 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 67 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-05-09 | 2023-03-31 | 2024-02-20 | Bundling Dependencies | TRUE | 65600 | NA | 43843.6101 | 67532.6843 | 152.2145 | 2483.1166 | 11177.8794 | 17581.8405 | 10416.3042 | 9275.5676 | 6610.4912 | 1819.2333 | 2292.316 | 99.5511 | 0 | 41986.1102 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 39417.6244 | 0% | NA | NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 895 | MOSS LANDING: Relay Work - Metcalf MPAC |  |  | Monterey | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-12 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 41.3213 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | 10 | Tier 4 | No | 5781029 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 67 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-05-28 | 2023-03-31 | 2024-10-14 | Bundling Dependencies | TRUE | 65600 | NA | 636.3255 | 2587.0322 | 12.9884 | 3.6669 | 103.8679 | 419.8455 | 45.4972 | 1882.7036 | 95.5886 | 0 | 0 | 0 | 0 | 608.74 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 896 | PIERCY: Upgrade CB 122 Relay |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-05 | 24 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.3509 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 4 | No | 5781019 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 67 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2028-11-01 | 2023-03-31 | 2028-12-13 | Bundling Dependencies | FALSE | 65600 | NA | 588.9525 | 3959.0545 | 21.1718 | 28.6847 | 101.286 | 262.0768 | 112.0357 | 42.6334 | 1177.4 | 39.5132 | 0 | 0 | 0 | 582.1651 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 897 | SWIFT: Upgrade Metcalf MPAC Remote End |  |  | San Jose, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Other - Operations Tech | Upgrade/Retrofit | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-07 | NA | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.1012 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5792225 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 67 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2028-11-14 | 2023-03-31 | 2029-01-25 | Bundling Dependencies | TRUE | 65600 | NA | 592.8268 | 3044.3544 | 0 | 0 | 18.4958 | 492.7942 | 72.672 | 44.9467 | 417.5155 | 31.8947 | 0 | 0 | 0 | 583.9619 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 898 | VASONA: Upgrade CB 252 Relay |  |  | Los Gatos, Santa Clara | Replace and upgrade the existing MPAC buildings and equipment on the 230kV and 115kV system at Metcalf Substation and associated remote terminals | Substation - Protection Relay | Upgrade/Retrofit | T.0009169 | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-05 | 25 | NA | Other - Deferral | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.5367 | NA | 230 kV | 288 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 4 | No | 5780954 | T.0003803 | Metcalf 230kV & 115kV MPACs | 15 | 67 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-06-16 | 2023-03-31 | 2026-08-31 | Bundling Dependencies | TRUE | 65600 | NA | 1141.3472 | 4664.9349 | 22.3203 | 27.1918 | 113.9815 | 770.7405 | 136.7045 | 82.6398 | 30.8443 | 0 | 0 | 0 | 0 | 1128.1744 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 899 | CASCADE: Install MPAC |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.021098 | NA | 115 kV | 58 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5766588 | T.0000651 | Cascade Substation Upgrade | 10 | 67 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2020-08-03 | 2022-01-31 | 2024-12-27 | Prioritization | TRUE | 35800 | NA | 11136.3699 | 13979.1794 | 6227.0703 | 1458.5343 | 990.8437 | 853.1336 | 1004.5579 | 2503.9011 | 472.3265 | 0 | 0 | 0 | 0 | 11002.9518 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil
| 900 | CASCADE: Repl PACI RAS @ SFCC |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Other - Remedial Action Scheme/Special Protection Scheme | Replace | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.021098 | NA | NA | 58 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5775778 | T.0000651 | Cascade Substation Upgrade | 10 | 67 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-12-30 | 2022-01-31 | 2025-03-18 | Prioritization | TRUE | 35800 | NA | 314.1313 | 1469.6671 | 104.1586 | 35.4717 | 35.3174 | 27.066 | 22.6596 | 22.5228 | 1136.4165 | 0 | 0 | 0 | 0 | 310.7278 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil
| 901 | California Flats Sw. Station |  |  | Morro Bay, San Luis Obispo | Replace the protection and automation equipment with a new Morro Bay 230 kV MPAC building enclosure and at the interconnected stations at the remote-end. The driver of the new MPAC building enclosure will address the reliability concerns of the equipment in the existing control building with flooding risk and concurrently executing various capital projects in the same substation: 1)Relocate all the Protective relaying and Automation equipment from the deteriorated control building into the MPAC building enclosure. 2)Incorporate the failed Morro Bay 230 kV Bus Differential Replacement project in the project scope. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | 8 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.6079 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5797121 | T.0000588 | MORRO BAY 230 KV MPAC | 6 | 67 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2028-02-01 | NA | 2028-05-15 | NA | FALSE | NA | NA | 35.5075 | 1134.6106 | 0 | 0 | 19.1231 | 16.8685 | -0.4841 | 2.2683 | 100 | 100 | 100 | 100 | 0 | 35.5075 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 902 | DIABLO CANYON 230KV SWITCHYARD |  |  | Morro Bay, San Luis Obispo | Replace the protection and automation equipment with a new Morro Bay 230 kV MPAC building enclosure and at the interconnected stations at the remote-end. The driver of the new MPAC building enclosure will address the reliability concerns of the equipment in the existing control building with flooding risk and concurrently executing various capital projects in the same substation: 1)Relocate all the Protective relaying and Automation equipment from the deteriorated control building into the MPAC building enclosure. 2)Incorporate the failed Morro Bay 230 kV Bus Differential Replacement project in the project scope. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.6079 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5797119 | T.0000588 | MORRO BAY 230 KV MPAC | 6 | 67 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2029-01-01 | NA | 2029-06-15 | NA | FALSE | NA | NA | 52.1365 | 1616.5865 | 0 | 0 | 22.9908 | 29.6304 | -0.4847 | 3.3307 | 100 | 100 | 100 | 100 | 0 | 52.1365 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 903 | MESA: Upgrade 230 KV GIS BAAH Relay |  |  | Nipomo CDP, San Luis Obispo | Replace the protection and automation equipment with a new Morro Bay 230 kV MPAC building enclosure and at the interconnected stations at the remote-end. The driver of the new MPAC building enclosure will address the reliability concerns of the equipment in the existing control building with flooding risk and concurrently executing various capital projects in the same substation: 1)Relocate all the Protective relaying and Automation equipment from the deteriorated control building into the MPAC building enclosure. 2)Incorporate the failed Morro Bay 230 kV Bus Differential Replacement project in the project scope. | Substation - Protection Relay | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | 28 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.5414 | NA | 230 kV | 787 | 3. Emergency Preparedness | 11 | RBPPF - TBD | Yes | 5767769 | T.0000588 | MORRO BAY 230 KV MPAC | 6 | 67 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2028-01-03 | NA | 2028-08-31 | NA | FALSE | NA | NA | 250.1514 | 3199.9518 | 0 | 0 | 25.2417 | 50.9344 | 0 | 15.9806 | 123.8682 | 348.7191 | 100 | 100 | 0 | 250.1514 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 904 | MORRO BAY: Install 230 KV MPAC |  |  | Morro Bay, San Luis Obispo | Replace the protection and automation equipment with a new Morro Bay 230 kV MPAC building enclosure and at the interconnected stations at the remote-end. The driver of the new MPAC building enclosure will address the reliability concerns of the equipment in the existing control building with flooding risk and concurrently executing various capital projects in the same substation: 1)Relocate all the Protective relaying and Automation equipment from the deteriorated control building into the MPAC building enclosure. 2)Incorporate the failed Morro Bay 230 kV Bus Differential Replacement project in the project scope. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.6079 | NA | 230 kV | 787 | NA | 10 | RBPPF - TBD | Yes | 5757485 | T.0000588 | MORRO BAY 230 KV MPAC | 6 | 67 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-12-30 | NA | 2029-05-25 | NA | FALSE | NA | NA | 1300.1437 | 37769.1595 | 0 | 45.7743 | 350.0442 | 360.6052 | 2.3665 | 0.0021 | 350 | 2750 | 5000 | 8000 | 6000 | 1300.1437 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 905 | Solar Sw. Station |  |  | Morro Bay, San Luis Obispo | Replace the protection and automation equipment with a new Morro Bay 230 kV MPAC building enclosure and at the interconnected stations at the remote-end. The driver of the new MPAC building enclosure will address the reliability concerns of the equipment in the existing control building with flooding risk and concurrently executing various capital projects in the same substation: 1)Relocate all the Protective relaying and Automation equipment from the deteriorated control building into the MPAC building enclosure. 2)Incorporate the failed Morro Bay 230 kV Bus Differential Replacement project in the project scope. | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | 12 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.6079 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5797120 | T.0000588 | MORRO BAY 230 KV MPAC | 6 | 67 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2028-08-01 | NA | 2029-04-13 | NA | FALSE | NA | NA | 51.0395 | 2053.1645 | 0 | 0 | 20.8294 | 30.6948 | -0.4847 | 3.2606 | 100 | 100 | 100 | 100 | 0 | 51.0395 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 906 | San Ardo: Install 60kV MPAC |  |  | Monterey | The 60 kV system serving Oil Fields Substation and the large Chevron and Aera Energy oil production facilities in San Ardo, CA, could experience low voltages and a potential voltage collapse under certain outage situations. To strengthen the local 60 kV system a voltage support project has been proposed to install 10 MVAR of shunt capacitors at Oil Fields Substation. The CAISO supports the project and will approve it in their 2017-2018 Transmission Plan. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-04 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.44363 | NA | 60 kV | Not Available | 5. Compliance/Commitments With Strong Safety Link | 19 | RBPPF - TBD | Yes | 5790904 | T.0004889 | San Ardo: Oil Fields Voltage Support | 4 | 67 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2028-05-25 | NA | 2029-01-15 | NA | FALSE | NA | NA | 26.026 | 25483.9926 | 0 | 6.8003 | 19.2258 | 0 | 0 | 17.6763 | 1000 | 8000 | 6500 | 700 | 200 | 26.026 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 907 | PALO ALTO SS: Install MPAC |  |  | Palo Alto, Santa Clara | The Palo Alto switching station is already set-up for BAAH. However, it is operated as a nonstandard variant of Bus 1& 2 with six breakers installed for six lines. Presently it is required to trip the entire bus in order to protect SVP equipment. This project will replace the six breakers, install three additional breakers, and convert the bus to BAAH.Install modular protection, automation, and control (MPAC) panels in MPAC building for the 115 kV bus to replace the existing control building | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.0138 | NA | 115 kV | 472 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5774085 | T.0001493 | PALO ALTO SS: Convert 115kV Bus to BAAH | 2 | 67 | NA | 2010 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2028-12-01 | NA | 2029-06-07 | NA | FALSE | NA | NA | 394.9732 | 11213.9671 | 61.5581 | 81.3408 | 51.9568 | 140.2299 | 0 | 24.2103 | 1336.2888 | 4667.704 | 5003.4461 | 137.469 | 0 | 394.9732 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 908 | TEMPLETON: Replace 230/70 KV MPAC |  |  | San Luis Obispo | This project proposes to install one modular protection, automation and control (MPAC) equipment enclosure at 230 / 70 kV Templeton substation | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-19 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.6839 | NA | 230 ¦ 70 kV | 617 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5758359 | T.0000089 | Templeton 230kV and 70kV MPAC-Pulli | 3 | 67 | 5759808 | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-01-08 | 2019-12-01 | 2019-09-18 | NA | FALSE | 9780 | NA | 9623.763 | 9623.763 | 4586.6583 | 1246.4871 | 665.6183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9623.763 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 7363.1259 | 1190.2411 | 634.5173 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 909 | Templeton Sub: Remote End Work Morro Bay |  |  | Morro Bay, San Luis Obispo | This project proposes to install one modular protection, automation and control (MPAC) equipment enclosure at 230 / 70 kV Templeton substation | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.6079 | NA | 230 ¦ 70 kV | 617 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5781860 | T.0000089 | Templeton 230kV and 70kV MPAC-Pulli | 3 | 67 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-06-17 | 2019-12-01 | 2019-09-18 | NA | FALSE | 9780 | NA | 1375.718 | 1375.718 | 1298.0228 | -12.0814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1375.718 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1357.9713 | -11.7714 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 910 | Banta 115kV Conversion - MPAC Building |  |  | San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-12 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.54319 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806221 | T.0006962 | Banta: Repl 60/12kV Bank 1 | 6 | 67 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-06-25 | NA | 2026-12-23 | NA | FALSE | NA | NA | 0 | 5149.2362 | 0 | 0 | 0 | 0 | 0 | 737.2128 | 2750 | 750 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 911 | Kasson Sub, Replace Banta Bank 1 |  |  | San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.1988 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5552802 | T.0006962 | Banta: Repl 60/12kV Bank 1 | 6 | 67 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-07-17 | NA | 2027-01-21 | NA | FALSE | NA | NA | 12.883 | 1938.2241 | 0 | 0 | 0 | 0 | 5.833 | 298.8776 | 1142.4263 | 0 | 0 | 0 | 0 | 5.833 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 912 | Vierra Sub, Replace Banta Bank 1 |  |  | Lathrop, San Joaquin | This project proposes to: - Expand the yard at Banta Substation. Bring 3-115kV lines into the substation. - Install 4-CB 115kV RB (6-CB design) - Install a 115/12kV 60 MVA bank with 12kV switchgear and move Banta 1101, 1102, 1103 feeders to new switchgear. - Remove 60kV line & CB; remove Bk 1 & existing 12kV bus, regulator and CBs | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.355 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5552804 | T.0006962 | Banta: Repl 60/12kV Bank 1 | 6 | 67 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-07-18 | NA | 2027-01-27 | NA | FALSE | NA | NA | 3.7608 | 1178.7637 | 0 | 0 | 0 | 0 | 3.1428 | 114.3637 | 729.2118 | 0 | 0 | 0 | 0 | 3.1429 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 913 | BORDEN: Install MPAC |  |  | Madera | This project will connect two additional 230kV lines to Borden Substation from the Wilson-Gregg 230kV Line, which will improve voltage and service reliability, and provide full deliverability needs for new generation. A new Modular Protection and Automation Control (MPAC) building will also be needed to integrate the new equipment to the protection and control system, as well as upgrade terminal equipment at other substations. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.1874 | NA | 230 kV | 20 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5774698 | T.0000924 | BORDEN 230 KV VOLTAGE SUPPORT (SUB) | 6 | 67 | NA | 2010 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-09-18 | 2018-04-09 | 2019-01-30 | Bundling Dependencies | FALSE | 30400 | NA | 5459.4109 | 5459.4109 | 478.6939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5459.4109 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2024 | 5459.4109 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - New T-Line Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $30 Mil - $40 Mil
| 914 | ATLANTIC: Inst Rio Oso 230KV Remote End |  |  | Roseville, Placer | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Other - Operations Tech | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.6984 | NA | 230 kV | 462 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5770425 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-02-19 | 2019-12-02 | 2025-08-15 | Prioritization | TRUE | 264900 | NA | 628.2494 | 3568.8447 | 0.3916 | 97.9455 | 47.2216 | 65.7425 | 120.8302 | 113.3343 | 2697.696 | 0 | 0 | 0 | 0 | 616.335 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil
| 915 | BRIGHTON: Inst Rio Oso 230KV Remote End |  |  | Sacramento, Sacramento | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Other - Operations Tech | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 6.4413 | NA | 230 kV | 462 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5770426 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-11-17 | 2019-12-02 | 2025-12-12 | Prioritization | TRUE | 264900 | NA | 648.9589 | 1832.7924 | 7.1232 | 124.9581 | 64.9086 | 66.736 | 97.9379 | 144.3238 | 954.1662 | 22.2799 | 0 | 0 | 0 | 636.8837 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil
| 916 | DRUM PH 1: Inst Rio Oso 115KV Remote End |  |  | Placer | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Other - Operations Tech | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-09 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.2491 | NA | 115 kV | 462 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5770430 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-16 | 2019-12-02 | 2025-06-06 | Prioritization | TRUE | 264900 | NA | 1310.0349 | 4473.5293 | 10.0358 | 54.9821 | 91.4002 | 337.4881 | 325.1157 | 934.6469 | 2253.1013 | 0 | 0 | 0 | 0 | 1272.6125 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil
| 917 | RIO OSO: Install 115 KV MPAC |  |  | Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-04 | 16 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.3219 | NA | 115 kV | 462 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5739019 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2023-03-20 | 2019-12-02 | 2024-12-13 | Prioritization | TRUE | 264900 | NA | 17926.799 | 26056.386 | 667.3462 | 1027.6164 | 2463.4675 | 3075.3223 | 2831.3786 | 5257.655 | 2674.8782 | 55.4515 | 0 | 0 | 0 | 17571.8689 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil
| 918 | RIO OSO: Install 230 KV MPAC |  |  | Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-04 | 16 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.3219 | NA | 230 kV | 462 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5732693 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2022-12-06 | 2019-12-02 | 2024-12-13 | Prioritization | TRUE | 264900 | NA | 21153.8458 | 30455.1093 | 922.7551 | 1390.3152 | 2761.3431 | 3455.5779 | 3583.9785 | 5708.2881 | 2840.7498 | 21.1171 | 0 | 0 | 0 | 20486.2877 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil
| 919 | TABLE MOUNTAIN: Inst Rio Oso Remote End |  |  | Butte | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Other - Operations Tech | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 47.516 | NA | 230 kV | 462 | 5a.Mitigates System Wide Failure Risk | 5 | RBPPF - TBD | Yes | 5770422 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-02-18 | 2019-12-02 | 2025-05-21 | Prioritization | TRUE | 264900 | NA | 837.2606 | 2766.2164 | -37.6071 | 144.7401 | 53.2716 | 78.5212 | 207.273 | 128.3855 | 1810.2211 | 19.7358 | 0 | 0 | 0 | 822.97 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil
| 920 | WOODLAND: Inst Rio Oso 115 KV Remote End |  |  | Woodland, Yolo | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Other - Operations Tech | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-04 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.8386 | NA | 115 kV | 462 | 5a.Mitigates System Wide Failure Risk | 12 | NA | NA | 5770427 | T.0000614 | Rio Oso Substation Upgrade | 12 | 67 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-01-06 | 2019-12-02 | 2023-03-08 | Prioritization | TRUE | 264900 | NA | 3071.8108 | 3079.0317 | 621.3932 | 531.8215 | 658.1475 | 516.3038 | 599.7831 | 27.1501 | 0 | 0 | 0 | 0 | 0 | 3051.8816 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 3030.6132 | 19.6623 | 0% | NA | NA | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil
| 921 | ASHLAN: Install MPAC Building & OPGW |  |  | Fresno, Fresno | This project will upgrade the existing 230kV bus from looped design to a ring bus design as well as install an MPAC building and upgrade protection at Ashlan, Herndon, Gregg, and Figarden substations. These upgrades will improve reliability, safety, and maintenance at Ashlan substation and the 230kV protection in the local area. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.6505 | NA | 230 kV | 764 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5766581 | T.0002362 | Ashlan Ave 230kV Bus Reliability | 7 | 67 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5310-E | 2018-06-13 | Approved | 2018 | Operational | 2 | 2019-04-09 | 2020-12-04 | 2020-02-20 | NA | FALSE | 40900 | NA | 8611.1701 | 8611.1701 | 3355.356 | 2201.9122 | 570.3361 | -0.3453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8611.1701 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 7741.2705 | 547.9919 | -0.33183 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement
| 922 | FIGARDEN: Repl CB 252- 262 Relays |  |  | Fresno, Fresno | This project will upgrade the existing 230kV bus from looped design to a ring bus design as well as install an MPAC building and upgrade protection at Ashlan, Herndon, Gregg, and Figarden substations. These upgrades will improve reliability, safety, and maintenance at Ashlan substation and the 230kV protection in the local area. | Substation - Protection Relay | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | 23 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.4543 | NA | 230 kV | 472 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5774143 | T.0002362 | Ashlan Ave 230kV Bus Reliability | 7 | 67 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-17 | 2020-03-03 | 2020-02-20 | NA | FALSE | 40900 | NA | 2583.5413 | 2583.5413 | 1444.1001 | 852.9764 | 2.0704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2583.5413 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 2536.3951 | 2.0328 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 923 | GREGG: Repl CB 552 Relays |  |  | Madera | This project will upgrade the existing 230kV bus from looped design to a ring bus design as well as install an MPAC building and upgrade protection at Ashlan, Herndon, Gregg, and Figarden substations. These upgrades will improve reliability, safety, and maintenance at Ashlan substation and the 230kV protection in the local area. | Substation - Protection Relay | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-01 | 31 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.266 | NA | 230 kV | 472 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5774142 | T.0002362 | Ashlan Ave 230kV Bus Reliability | 7 | 67 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-30 | 2019-11-01 | 2020-02-20 | NA | FALSE | 40900 | NA | 1403.7675 | 1403.7675 | 632.4061 | 369.6208 | 1.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1403.7675 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1375.3682 | 1.1208 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 924 | HICKS: Install 230 KV MPAC |  |  | San Jose, Santa Clara | To reduce customer interruptions at Hicks Substation, it is recommended to re-connect existing T-Line and distribution bank connections and install four new 230kV circuit breakers to build a six-breaker ring bus in conjunction with a new MPAC building. This will reduce System Average Interruption Duration Index (SAIDI) impacts affecting these 44,000 customers. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-08 | NA | NA | Wires - Bus Upgrade Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.8635 | NA | 230 kV | 84 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5742960 | T.0001600 | HICKS SUB: 230 KV BUS REL IMPROV | 3 | 67 | NA | 2011 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-10-02 | 2017-08-29 | 2021-04-27 | Material | FALSE | 21300 | NA | 8658.858 | 8658.858 | 1794.893 | 1925.2683 | 1784.7187 | 390.1742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8658.858 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 8269.8069 | 390.1742 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 925 | MONTA VISTA: Inst Jefferson Remote End |  |  | San Mateo | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Other - Operations Tech | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | NA | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.7091 | NA | 230 kV | 472 | 3. Emergency Preparedness | 4 | RBPPF - TBD | Yes | 5775342 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-04-08 | 2020-08-07 | 2024-09-12 | Prioritization | TRUE | 39600 | NA | 873.2059 | 1764.7746 | 188.7291 | 119.1833 | 230.5593 | 74.9192 | 60.9927 | 983.5471 | 8.6049 | 0 | 0 | 0 | 0 | 772.6226 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 926 | MONTA VISTA: Install 230KV MPAC |  |  | Cupertino, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-11 | 19 | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.8314 | NA | 230 kV | 472 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5774084 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2020-08-25 | 2020-08-07 | 2024-09-26 | Prioritization | TRUE | 39600 | NA | 23457.4892 | 25931.3037 | 6042.0909 | 5366.0284 | 5269.3587 | 2536.1474 | 1712.9285 | 2777.279 | 215.3526 | 25.722 | 0 | 0 | 0 | 22889.267 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 ¦ 2026 | 0 | 0 | 18198.6061 | -18198.6061 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 927 | MONTA VISTA: Repl Coyote RE RLY |  |  | San Jose, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Protection Relay | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-08 | NA | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.5453 | NA | 230 kV | 472 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5775341 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-25 | 2020-08-07 | 2024-12-23 | Prioritization | TRUE | 39600 | NA | 726.7758 | 1585.5919 | 214.4132 | 114.0054 | 94.7651 | 82.8406 | 74.0654 | 875.9646 | 13.8356 | 0 | 0 | 0 | 0 | 695.7917 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 928 | MONTA VISTA: Repl Saratoga RE RLY |  |  | Saratoga, Santa Clara | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Protection Relay | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-02-06 | NA | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.4212 | NA | 230 kV | 472 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5775339 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-07-21 | 2020-08-07 | 2023-01-05 | Prioritization | TRUE | 39600 | NA | 2848.8493 | 2854.5858 | 62.8241 | 262.4463 | 681.8812 | 1594.7464 | 133.4626 | 35.2306 | 0 | 0 | 0 | 0 | 0 | 2819.3553 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2789.1269 | 8.3561 | 0% | NA | NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 929 | MONTA VISTA: Upgd SLAC RE RLY |  |  | San Mateo | Upgrade the 230kV transmission bus configuration at Monta Vista Substation in Cupertino to improve electric system resiliency. This project will replace 230/60 kV No. 5 Transformer with a new 115/60 kV transformer located in the lower Monta Vista switchyard and Install new 230 kV bus-sectionalizing and bus-parallel breakers. | Substation - Protection Relay | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-06 | 19 | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 7.7091 | NA | 60 kV | 472 | 5a.Mitigates System Wide Failure Risk | Not Available | RBPPF - TBD | Yes | 5776918 | T.0000675 | MONTA VISTA 230 KV BUS UPGRADE | 9 | 67 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2019-10-28 | 2020-08-07 | 2024-06-24 | Prioritization | TRUE | 39600 | NA | 1880.6468 | 1959.9693 | 989.5191 | 266.2088 | 125.0277 | 150.7264 | 130.5817 | 102.8611 | 0 | 0 | 0 | 0 | 0 | 1857.1081 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 930 | KERN PP: INSTALL 115KV MPAC BLDG |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-04-12 | 34 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.7504 | NA | 115 kV | 705 | 5a.Mitigates System Wide Failure Risk | 10 | RBPPF - TBD | Yes | 5759901 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 67 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2021-08-23 | 2022-10-12 | 2024-11-08 | Prioritization | TRUE | 77400 | NA | 14988.2704 | 17345.9338 | 1760.046 | 3186.4187 | 3603.2933 | 3065.5833 | 94.7055 | 3037.9517 | 0.389 | 0 | 0 | 0 | 0 | 14307.5931 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil
| 931 | WESTPARK: INSTALL MPAC BUILDING |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-05 | 23 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.7259 | NA | 115 kV | 705 | 5a.Mitigates System Wide Failure Risk | 12 | RBPPF - TBD | Yes | 5773025 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 67 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 3 | 2023-08-21 | 2022-10-12 | 2026-04-30 | Prioritization | FALSE | 77400 | NA | 8955.7827 | 24010.8837 | 807.7716 | 401.1719 | 241.2329 | 1879.2739 | 2926.0904 | 1844.7001 | 1611.4928 | 1895.6062 | 0 | 0 | 0 | 7672.2001 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil
| 932 | KERN: Inst 230 KV MPAC Building |  |  | Bakersfield, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Modular Protection and Automation Control Building | New | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-04-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 37.7504 | NA | 230 kV | 764 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5767884 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 67 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-05-02 | 2019-10-12 | 2019-03-07 | NA | FALSE | 74400 | NA | 11502.4232 | 11502.4232 | 1706.8317 | 833.7359 | 610.4325 | 17.2441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11502.4232 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 10041.03 | 833.7359 | 610.4325 | 17.2441 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil
| 933 | MIDWAY-KERN: Upgrade Relay |  |  | Buttonwillow CDP, Kern | Upgrade the existing Kern Substation 230kV bus to a BAAH configuration, add an MPAC building, and add relay and telecom upgrades. The project expects to improve service reliability in core operations by converting the Kern 230kV bus to current BAAH configuration and operational standards that will improve system performance and reliability, which will reduce outages. | Substation - Protection Relay | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | 2024-03-15 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 94.5324 | NA | 230 kV | 764 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5779615 | T.0000204 | Kern 230kV Bus Upgrade | 16 | 67 | NA | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-18 | 2018-10-01 | 2020-05-08 | Bundling Dependencies | FALSE | 74400 | NA | 1488.8671 | 1488.8671 | 408.536 | 646.6593 | 0.9014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1488.8671 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1391.1848 | 0.83967 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Bus Upgrade Alternative [Alternative Solutions and Costs - Costs] $75 Mil – $100 Mil ¦ $150 Mil - $175 Mil
| 934 | Manteca Sub: Replace T-RTU & Rewire |  |  | Manteca, San Joaquin | Replace existing D20ME RTU and peripheral RTU boards (A,S,& K) with new Eaton SMP SG-4260 RTU & GE IO boards per PG&E standards. Install new Cisco Switch IE4010 and Ruggedcom terminal servers replacing existing SEL 2020/2031 and RFL 9660. This project will also eliminate daisy chaining issues and rewire per current standards. | Other - Operations Tech | Replace | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | 2024-03-12 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.8539 | NA | 115 kV | 236 | Not Available | Not Available | Tier 2 | No | 5796825 | T.0007258 | Manteca: Replace T-RTU & Rewire | 1 | 67 | NA | 2021 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2024-03-29 | 2024-12-31 | 2024-05-09 | NA | TRUE | 1800 | NA | 534.218 | 1460.3578 | 0 | 0 | 68.7425 | 342.8407 | 87.8867 | 960.888 | 0 | 0 | 0 | 0 | 0 | 499.4698 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 935 | LAMBIE SW STA: REPLACE RTU & SEL321 |  |  | Solano | This project will replace the RTU, including peripheral equipment, and SCADA system/equipment (TSRP), including installing ODN via VSAT, at Lambie Switching Station. Transmission Automation strategies aim to enhance O&M efficiency, safety, and compliance. Having a fully automated and integrated electric transmission and distribution grid will support value-added response capabilities and applications. To improve the quality and efficiency of our electric transmission system it is recommended to provide increased visibility at Lambie 230kV Switching Station. The scope of work will replace the legacy RTU and peripheral boards to maintain a reliable monitoring and control system for Grid Operations and replacing equipment to provide full SCADA monitoring and control to all breakers and switches (TSRP). While providing SCADA functionality is the driver, there may be additional justification to modernize the aging protection assets concurrently. The level of automation has been determined by the project team and approved by the System Automation department to include replacing the existing legacy D20++ RTU with an EATON 4260 and upgrading all SCADA peripheral as necessary. This includes installing ODN to the station control building through VSAT and replacing the SEL-321 relay on 230kV Line-1 to allow remote communication. | Other - Operations Tech | Replace | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | 2024-02-07 | 22 | Lifecycle Replacement Analysis | Other - Deferral | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3686 | NA | 230 kV | 236 | Not Available | Not Available | Tier 2 | No | 5791840 | T.0007427 | Lambie SW Sta_Replace RTU & SEL321 | 1 | 67 | NA | 2021 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-04-16 | 2024-05-28 | 2024-06-11 | NA | TRUE | 800 | NA | 531.2527 | 1220.9679 | 0 | 0 | 0.5014 | 168.7351 | 279.9224 | 771.809 | 0 | 0 | 0 | 0 | 0 | 449.1589 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 936 | Trans SCADA Replacement Bucket |  |  | NA | Bucket for SCADA/RTU replacements | Other - Operations Tech | Replace | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 236 | 9. Reliability (Low Safety Risk) | Not Available | Tier 2 | No | 5507180 | NA | NA | NA | 67 | NA | 2015 | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 11019.6999 | 17019.6999 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 0 | 0 | 0 | 4000 | 11019.6999 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 937 | ELK: Replace T-RTU |  |  | Mendocino | Replace T-RTU, automatic feature cutouts for Circuit Breaker 12, 22 and 32 with new building and replace D-RTU and IPAC for Circuit Breaker 1101, Bank 1 meter and regulator, and replace the station service transformer at Elk Substation. This job includes replacing meters and switches with those capable of being SCADA operated. This job will also provide visibility of station annunciation. | Other - Operations Tech | Replace | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | 2024-02-12 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 1.0338 | NA | 60 kV | 236 | 3. Emergency Preparedness | 15 | NA | NA | 5765186 | T.0001189 | ELK: REPL T-RTU | 1 | 67 | NA | 2015 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-08-25 | 2021-12-31 | 2021-12-16 | NA | FALSE | 2210 | NA | 1887.6837 | 1887.6837 | 20.7201 | 408.8261 | 1311.2695 | 146.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1887.6837 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1689.4647 | 142.3443 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 938 | Los Esteros Sub: Replace RTU with D20MX |  |  | San Jose, Santa Clara | The project scope of work includes replacing the existing D20ME RTU with an D20MX RTU, retain all the peripheral boards and DNP devices, move critical alarms from D20S boards to the new C30 relays, migrate the AVC to the new RTU. This SCADA project is necessary to maintain the electric transmission system visibility and control and help improve the distribution grid reliability and efficiency | Other - Operations Tech | Replace | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | 2024-03-12 | 22 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 13.1703 | NA | 230 ¦ 115 kV | 236 | Not Available | Not Available | NA | NA | 5792890 | T.0006775 | Los Esteros Sub: Replace RTU with D20MX | 1 | 67 | NA | 2020 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-10-03 | 2023-12-13 | 2023-12-04 | NA | TRUE | 1395.84 | NA | 1032.6209 | 1097.7701 | 0 | 0 | 10.9444 | 425.0366 | 550.1559 | 111.6333 | 0 | 0 | 0 | 0 | 0 | 986.1369 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 976.4809 | 70.3196 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 939 | Millbrae: Replace T-RTU & FCOs |  |  | Millbrae, San Mateo | This job is to install SCADA on all the distribution equipment in Millbrae Substation. The project is necessary to improve the electric transmission system visibility and control, and help improve the distribution grid reliability and efficiency. | Other - Operations Tech | Replace | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | 2024-03-12 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.0501 | NA | 60 kV | 236 | 9. Reliability (Low Safety Risk) | 14 | NA | NA | 5785894 | T.0004846 | Millbrae: Replace D-Rtu & 4 Ipac | 1 | 67 | NA | 2019 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-06-08 | 2021-09-18 | 2022-06-28 | Workforce | FALSE | 2878 | NA | 1284.0794 | 1284.0794 | 16.2829 | 52.5138 | 980.5915 | 234.6912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1284.0794 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 1284.0794 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 940 | BIG RIVER: Replace T-RTU |  |  | Mendocino CDP, Mendocino | This job is to install SCADA on all the transmission equipment in Big River Substation. Big River Substation currently has SCADA visibility, but the performing equipment has reached its end of life. This project will bring the station up to date with current standards. | Other - Operations Tech | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | 2024-03-05 | 10 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.73337 | NA | 60 kV | 236 | 3. Emergency Preparedness | Not Available | Tier 2 | No | 5761804 | T.0001172 | BIG RIVER: REPLACE T-RTU | 1 | 67 | NA | 2014 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-30 | 2022-08-31 | 2025-01-27 | Scope Change | TRUE | 3090 | NA | 1161.9743 | 2418.6175 | 11.1378 | 39.9302 | 34.3661 | 185.9412 | 830.5341 | 1280.9621 | 22.5933 | 0 | 0 | 0 | 0 | 1115.0621 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 1046.0467 | 63.4852 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 941 | OAKLAND D: Replace T-RTU |  |  | Oakland, Alameda | This job is to replace the SCADA RTU for the T&D equipment in Oakland D Substation. The project is necessary to improve the electric transmission system visibility and control, and help improve the distribution grid reliability and efficiency. | Other - Operations Tech | Replace | NA | Asset Condition | Age/Condition - Replace SCADA/RTU | NA | 2024-03-12 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.54348 | NA | 115 kV | 236 | 9. Reliability (Low Safety Risk) | 1 | NA | NA | 5781845 | T.0000010 | Oakland_D_D-RTU Replacement - concurrent | 1 | 67 | NA | 2018 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-02-01 | 2019-04-03 | 2022-11-04 | Prioritization | FALSE | 693 | NA | 1615.8121 | 1615.8121 | 93.3268 | 68.2367 | 497.4576 | 927.5613 | 2.5478 | 0.5918 | 0 | 0 | 0 | 0 | 0 | 1615.2203 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1509.0141 | 2.3724 | 0.52428 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 942 | 2015 T-SCADA IT Decoupling |  |  | NA | Bucket for 2015 T-SCADA IT Decoupling | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 236 | 5a. Mitigates System Wide Failure Risk | Not Available | NA | NA | 5516256 | NA | NA | NA | 67 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 5957.4201 | 5957.4201 | 503.9976 | 143.9792 | 12.5049 | 1.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5957.4201 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 869.3968 | 143.9792 | 12.5049 | 1.962 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 943 | Trans SCADA Installation Bucket |  |  | NA | Bucket for Transmission SCADA installation | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 236 | 9. Reliability (Low Safety Risk) | Not Available | Tier 2 | No | 5507179 | NA | NA | NA | 67 | NA | 2014 | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 16720.6851 | 17720.6852 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 389 | 16720.6851 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 944 | CYMRIC: Install MRTU |  |  | Kern | This job is to install SCADA and protection on all the transmission equipment at Cymric Substation. | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | 2024-03-01 | 34 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.68557 | NA | 115 kV | 236 | 9. Reliability (Low Safety Risk) | 18 | Tier 3 | No | 5772693 | T.0002375 | CYMRIC SUB | 2 | 67 | NA | 2011 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-02-05 | 2017-12-26 | 2025-07-02 | Clearances | TRUE | 2145 | NA | 2163.8492 | 3042.314 | 125.7926 | 270.1952 | 73.1843 | 71.4273 | 48.9204 | 401.1977 | 486.9744 | 0 | 0 | 0 | 0 | 2154.1418 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 945 | RESERVATION RD: Install T-SCADA |  |  | Monterey | Install new RTU & SCADA on SW37 & SW 39. Add motor operator to SW37 at Reservation Road Substation. This job includes replacing meters and switches with those capable of being SCADA operated. This job will also provide visibility of station annunciation. | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | 2024-02-14 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.59657 | NA | 60 kV | 236 | 3. Emergency Preparedness | 16 | NA | NA | 5757521 | T.0000191 | Reservation Road_Install T-SCADA SW39 | 1 | 67 | 5767672 | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-11 | 2020-11-30 | 2020-11-15 | NA | FALSE | 2575 | NA | 1830.3044 | 1830.3044 | 207.9789 | 632.4204 | 870.6339 | 0.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1830.3044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 924.7214 | 837.3171 | 0.81264 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 946 | OLEMA: Install T-SCADA on SW 27 & 29 |  |  | Marin | Install SCADA at Olema Substation on SW27 & 29, replace reclosing relay and add 60kV PT. This job includes replacing meters and switches with those capable of being SCADA operated. This job will also provide visibility of station annunciation. | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | 2024-02-13 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.26483 | NA | 60 kV | 236 | 3. Emergency Preparedness | 17 | NA | NA | 5757520 | T.0000819 | OLEMA: INSTALL T-SCADA SW 27 & 29 | 1 | 67 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-06-11 | 2019-12-31 | 2021-04-27 | Prioritization | FALSE | 1621 | NA | 1866.6616 | 1866.6616 | 70.7976 | 223.3507 | 645.6538 | 102.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1866.6616 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1724.3299 | 100.3335 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 947 | HERDLYN: Install T-SCADA |  |  | Contra Costa | Install T-SCADA at Herdlyn Substation on CB 32, CB 62, MOAS 79, & TB 2 w/ new building, & battery upgrade. This job includes replacing meters and switches with those capable of being SCADA operated. This job will also provide visibility of station annunciation | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | 2024-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.81884 | NA | 60 kV | 236 | 9. Reliability (Low Safety Risk) | 17 | NA | NA | 5755313 | T.0003772 | HERDLYN SUB: INSTALL: T-SCADA | 1 | 67 | NA | 2011 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-06-10 | 2021-04-30 | 2022-04-01 | Permitting | TRUE | 2213 | NA | 2025.2425 | 2025.2425 | 191.9786 | 373.3785 | 482.2944 | 697.3246 | 16.3389 | 0 | 0 | 0 | 0 | 0 | 0 | 2025.2425 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2010.3481 | 16.3389 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 948 | TEJON: Install T-SCADA on CB 12 22 32 |  |  | Kern | Install T-SCADA on CB 12, 22, & 32 at the Tejon Substation. This project’s scope is to install SCADA on circuit breaker 12, circuit breaker 22 and circuit breaker 32 to enhance efficiency, safety, and reliability. A Shoofly will be installed to obtain the required clearances and upon completion of the relay replacements, the old control building will be removed. | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | 2024-03-08 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.0602 | NA | 70 kV | 236 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5755447 | T.0000160 | Tejon - Install SCADA on CB 12, 22, 32 | 1 | 67 | NA | 2012 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-23 | 2019-06-07 | 2019-10-29 | NA | FALSE | 3723 | NA | 1220.2178 | 1220.2178 | 829.0037 | 269.3767 | 8.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.2178 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 841.6723 | 233.4298 | 7.1484 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 949 | OROVILLE: INSTALL SCADA ON CB12-CB22 |  |  | Oroville, Butte | The scope of work will include adding full SCADA monitoring and control to Circuit Breakers 12, 22, and 32. This project will address the deficiency of transmission SCADA at this substation, installing the necessary equipment for remote status and operation of all transmission equipment that currently do not have SCADA.. The TSRP migration work is included in this project and involves revision of EMS SCADA architecture and provide telecommunication circuits connections to EMS via SCADA RTU. | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | 2024-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.75208 | NA | 60 kV | 236 | 9. Reliability (Low Safety Risk) | 10 | Tier 2 | No | 5738700 | T.0000324 | OROVILLE: T-SCADA CBs 12,22,32 &TSRP | 1 | 67 | 5769051 | 2012 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-02-16 | 2022-07-31 | 2027-05-26 | Bundling Dependencies | TRUE | 1815 | NA | 1179.2414 | 3437.6462 | 37.8019 | 97.9762 | 211.2356 | 337.953 | 75.4545 | 72.0281 | 0 | 0 | 0 | 0 | 1542 | 1179.2414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 950 | CARIBOU PH: Upgrade T-SCADA |  |  | Plumas | This job is to install SCADA on all the transmission equipment in Caribou 1 PH Substation. • The project is necessary to improve the electric transmission system visibility and control, and help improve the distribution grid reliability and efficiency. | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | 2024-02-14 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.96252 | NA | 115 ¦ 60 kV | 236 | 3. Emergency Preparedness | 19 | NA | NA | 5779206 | T.0003784 | Caribou PH - TSCADA Upgrade | 1 | 67 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-06-10 | 2019-12-31 | 2020-10-06 | Prioritization | FALSE | 1536 | NA | 1041.8277 | 1041.8277 | 174.5144 | 710.9765 | 63.1422 | 16.9857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1041.8277 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 902.1983 | 59.082 | 15.8934 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 951 | CUYAMA: Install T-SCADA |  |  | Cuyama CDP, Santa Barbara | This job is to install SCADA on all the transmission equipment in Cuyama | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | 2024-02-05 | 62 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.69685 | NA | 70 kV | 236 | 9. Reliability (Low Safety Risk) | 17 | NA | NA | 5755546 | T.0000771 | INSTALL SCADA @ CUYAMA | 1 | 67 | NA | 2011 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-04 | 2019-02-27 | 2022-11-03 | Scope Change | TRUE | 1330 | NA | 1631.7702 | 1631.7702 | 282.0242 | 175.1026 | 107.2602 | 190.079 | 92.9763 | 0 | 0 | 0 | 0 | 0 | 0 | 1631.7702 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1524.2902 | 91.6719 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 952 | HYAMPOM JCT: Install T-SCADA CB 62 |  |  | Trinity | This job is to install SCADA on all the transmission equipment in Hyampom Jct Substation. | Other - Operations Tech | Upgrade/Retrofit | NA | Reliability | Install SCADA/RTU | NA | 2024-03-14 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.319 | NA | 60 kV | 236 | 3. Emergency Preparedness | NA | NA | NA | 5757493 | T.0000813 | HYAMPOM JCT: INSTALL T-SCADA CB 62 | 1 | 67 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-15 | 2020-10-07 | 2019-03-22 | NA | FALSE | 2606 | NA | 1634.32 | 1634.32 | 309.0395 | 68.8064 | 24.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1634.32 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1466.8887 | 65.4143 | 23.7296 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 953 | Trans SCADA Emergency Replacement Bucket |  |  | NA | Bucket for Emergency Transmission SCADA replacement | Other - Operations Tech | Replace | NA | Emergency Event | Age/Condition - Replace SCADA/RTU | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 ¦ 115 ¦ 70 ¦ 60 kV | 236 | 5a.Mitigates System Wide Failure Risk | Not Available | Tier 5 | No | 5506316 | NA | NA | NA | 67 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 16750.0599 | 17250.0598 | 0 | 0.2745 | 0 | 0 | 0 | 0 | 250 | 500 | 500 | 500 | 500 | 16750.0599 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0.24702 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 954 | Purchase new CEM inventory, Transmission Transformer 100 MVA, 115/(60X70) kV, 100 MVA |  |  | NA | Purchase new CEM Inventory, three-phase cross wound Transmission transformer | Substation - Transformer | New | NA | Asset Condition | Replace Transformer | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | Ex112798 | NA | NA | NA | 68 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 600 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 955 | 500/230kV 374MVA 1-ph CEM transformer |  |  | NA | This project is for emergency preparedness, increasing CEM inventory with purchasing 1-ph 500/230kV 374MVA transformer. | Substation - Transformer | New | NA | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | NA | NA | NA | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 500 ¦ 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX113191 | NA | NA | NA | 68 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2000 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 956 | TABLE MOUNTAIN: Replace 500 KV BK 1 |  |  | Butte | PG&E is designing this project to minimize clearance requirements and impacts to the Pacific AC Intertie by installing the new 500/230kV transformer at a new location within the substation footprint, leaving the existing equipment in service during project construction. The new transformer connection will require swapping one of the 500kV transmission lines and installing an additional 500kV circuit breaker to connect. Installing the new Transformer first will minimize the clearance requirements to support the Pacific AC Intertie path. In addition, the project will upgrade the controls and protection scheme of the new transformer. | Substation - Transformer | Replace | T.0002458 ¦ T.0002459 | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | 2024-03-06 | 56 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Subsidence |  | NA | 47.516 | NA | 500 ¦ 230 kV | 362 | 9. Reliability (Low Safety Risk) | 5 | NA | NA | 5747877 | T.0000250 | Table Mountain 500/230kV Transformer Rep | 1 | 68 | 5767179 | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-08-31 | 2018-11-09 | 2021-11-17 | Prioritization | TRUE | 54100 | NA | 47849.2858 | 49483.9276 | 15574.0627 | 9765.945 | 18581.2151 | 2540.3746 | -85.32 | 57.4612 | 1396.5074 | 0 | 0 | 0 | 0 | 47846.1707 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 42897.7655 | 2719.5788 | -80.847 | 5.0478 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 957 | GATES: Replace BK 11 500/230 KV |  |  | Fresno | Replace three single-phase 500kV Gates Transformers Bank No. 11 (Bank 11) and associated equipment. This project will replace the deteriorated 500kV transmission transformer bank, which is at the end of its useful life. The loss of this transformer bank will require generation curtailment and impact service area reliability. Also, this transformer supports the Pacific 500kV AC Intertie, with connections to DCPP and North-to-South power flow, which is critical for grid stability. | Substation - Transformer | Replace | T.0006452 | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | 2024-03-08 | 63 | Lifecycle Replacement Analysis | Other - Deferral | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 ¦ 230 kV | 319 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5761816 | T.0001373 | Gates 500kV Bank 11 Replacement | 1 | 68 | NA | 2015 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-09-07 | 2023-03-31 | 2023-06-05 | NA | TRUE | 31500 | NA | 43296.5692 | 43296.5692 | 181.1822 | 411.8062 | 12462.5072 | 25171.2671 | 5092.2432 | -22.4367 | 0 | 0 | 0 | 0 | 0 | 43319.0059 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 41892.9791 | -18.9601 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 958 | MOSS LANDING: Replace 500kV Bank 9 |  |  | Monterey | This project proposes to replace all four (4) phases of Moss Landing Bank 9 with four (4) new 500/230kV single-phase 374 MVA transformers under the Deteriorated Transformer Replacement Program. Moss Landing Bank 9 is composed of three (3) 1978-vintage 373MVA McGraw Edison single-phase transformers and one (1) 1997-vintage Pauwels unit of the same size. All four transformers will be replaced with a new bank of four (4) single-phase transformers. Bank 9 has a rank of #3 on the replacement list as of 2019. This bank has a RIBA score of 1,899, and RIBA Delta of 1,339. | Substation - Transformer | Replace | TBD | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | 2024-03-12 | 46 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 41.3213 | NA | 500 ¦ 230 kV | Not Available | 9. Reliability (Low Safety Risk) | 10 | RBPPF - TBD | Yes | 5788362 | T.0005464 | Moss Landing-Replace 500kV Bank 9 | 1 | 68 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-09-09 | NA | 2027-03-19 | NA | FALSE | NA | NA | 579.6235 | 44441.5543 | 0.4685 | 13.674 | 135.4685 | 287.3746 | 127.4444 | 106.7925 | 0 | 0 | 0 | 0 | 1200 | 564.4301 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 959 | Metcalf: Replace Bank 11 Phase B and C |  |  | Santa Clara | This project proposes to replace phases B and C of Metcalf Bank 11 with two (2) new 500/230kV single-phase 374 MVA transformers under the Deteriorated Transformer Replacement Program. Metcalf Bank 11 is composed of three (3) single-phase transformers and one (1) spare transformer, which is shared with Bank 12. | Substation - Transformer | Replace | TBD | Asset Condition | Age/Condition - Replace 500 kV Transformers | NA | 2024-03-13 | 56 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 500 ¦ 230 kV | 362 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5790318 | T.0005835 | Metcalf: Replace Bank 11 Phase B and C | 1 | 68 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-11-29 | NA | 2028-11-24 | NA | FALSE | NA | NA | 18.6836 | 21243.3645 | 0 | 0 | 10.3736 | 6.81 | 1.2814 | 1.35 | 0 | 0 | 0 | 0 | 0 | 18.4651 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 960 | CEM: Purch 115-60/70 KV 30MVA 1-Ph Mob |  |  | NA | This project will add a new single-phasetransmission mobile transformer 115-70/60 kV 30 MVA in our mobile fleet | Substation - Transformer | New | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 115 ¦ 70 ¦ 60 kV | 76 | 3. Emergency Preparedness | Not Available | NA | NA | 5516564 | T.0001727 | MOBILE PROGRAM 2017-2018 | 1 | 68 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2019-10-30 | 2022-03-31 | Material | FALSE | 2000 | NA | 1221.6037 | 1221.6037 | 134.8799 | 352.2163 | 692.7443 | 14.6227 | 0.7904 | 0 | 0 | 0 | 0 | 0 | 0 | 1221.6037 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 134.8799 | 352.2163 | 692.7443 | 14.6227 | 0.79038 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 961 | Cascade - Repl 115/60kV Bk1 |  |  | Shasta | Replace the 115/60kV Bank 1, add a second 115/60kV bank (Bank 2), upgrade the 115kV bus to breaker-and-a-half (BAAH), install a modular control building (MPAC), and replace four 60kV circuit breakers at Cascade Substation. | Substation - Transformer | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-02-12 | 62 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.021098 | NA | 115 ¦ 60 kV | 240 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5777640 | T.0000651 | Cascade Substation Upgrade | 10 | 68 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-03-19 | 2022-01-31 | 2025-06-30 | Prioritization | TRUE | 35800 | NA | 4919.6488 | 7636.8583 | 610.1149 | 200.5995 | 1419.3423 | 2154.4417 | 358.604 | 375.4656 | 2369.7346 | 0 | 0 | 0 | 0 | 4861.1272 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 962 | PIT PH 1: Repl 230 KV BK 2 |  |  | Shasta | Replace the 230/11kV Banks 1 and 2 at Pit PH No. 1 Substation | Substation - Transformer | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-07 | 93 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | 2.7679 | NA | 230 kV | 240 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5777260 | T.0002123 | Pit Powerhouse No1 Substation Replace Ba | 4 | 68 | NA | 2013 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-09-07 | 2021-08-31 | 2022-04-30 | Prioritization | TRUE | 31400 | NA | 14213.7408 | 14213.7408 | 450.118 | 435.1405 | 6476.4453 | 5923.0639 | 419.01 | 2.676 | 0 | 0 | 0 | 0 | 0 | 14211.0648 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 12115.3484 | 365.9303 | 2.337 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Replacement Alternative ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 963 | PIT PH 1: Replace 230 KV BK 1 |  |  | Shasta | Replace the 230/11kV Banks 1 and 2 at Pit PH No. 1 Substation | Substation - Transformer | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-07 | 93 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | 2.7679 | NA | 230 kV | 240 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5767974 | T.0002123 | Pit Powerhouse No1 Substation Replace Ba | 4 | 68 | NA | 2013 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-09-07 | 2021-08-31 | 2022-12-07 | Prioritization | TRUE | 31400 | NA | 25912.2184 | 25912.384 | 1283.2019 | 687.5419 | 13457.422 | 8339.9315 | 729.8509 | 3.3894 | 0 | 0 | 0 | 0 | 0 | 25908.9946 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 22975.2975 | 659.7578 | 9.3345 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Replacement Alternative ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 964 | MARTIN: Replace 230/115 KV BK 7 |  |  | Brisbane, San Mateo | Replacement of the 230/115 kV Bank 7 spare at Martin Substation.This project proposes to replace the spare phase. | Substation - Transformer | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-20 | 51 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 18.2105 | NA | 230 ¦ 115 kV | 227 | 9. Reliability (Low Safety Risk) | 4 | NA | NA | 5745519 | T.0000025 | SF H (Martin)-Replace 230/115KV Bank 7 | 1 | 68 | NA | 2011 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-26 | 2021-02-01 | 2020-12-30 | NA | TRUE | 11700 | NA | 16508.6502 | 16508.6502 | 3414.9278 | 9699.1712 | 2088.6989 | 444.2234 | 348.1036 | 0 | 0 | 0 | 0 | 0 | 0 | 16508.6502 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 12497.044 | 1906.7614 | 405.4976 | 317.7571 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Replacement Alternative ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $20 Mil - $30 Mil ¦ $15 Mil - $20 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 965 | TAFT: Replace BK 2 |  |  | Taft, Kern | Replacement of the deteriorated 115/70kV Transformer Bank #2 at Taft Substation. Taft Substation is located in the vicinity of the City of Taft, within Kern County, California. Bank #2 is comprised of three single-phase 1955-vintage 20 MVA 115/70 kV Westinghouse transformers. Due to the age and condition of this bank, it was added to the “Deteriorated Transformer Replacement Program” and was planned for replacement in 2026. Continuing to operate this transformer will lead to an increasingly high probability of transformer failure in service. The RIBA score for this bank is 227. | Substation - Transformer | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-01 | 69 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 5.2046 | NA | 115 ¦ 70 kV | 240 | 9. Reliability (Low Safety Risk) | 10 | RBPPF - TBD | Yes | 5777284 | T.0003469 | Taft Repl Bk 2 | 1 | 68 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-09-15 | NA | 2029-09-20 | NA | FALSE | NA | NA | 0 | 9216.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 966 | Haas PH: Replace Bk 1 (13.8/230 kV) |  |  | Fresno | Replacement of the deteriorated 13.8/230 kV Transformer Bank #1 at Haas PH. Haas Substation is located in the vicinity of the City of Auberry, within Fresno County, California. Bank #1 is comprised of four single-phase 1940-vintage 50 MVA 13.8/230 kV GSU Westinghouse transformers. Due to the age and condition of this bank, it was added to the “Deteriorated Transformer Replacement Program” and was planned for replacement in 2024. Continuing to operate this transformer will lead to an increasingly high probability of transformer failure in service. The RIBA score for this bank is 227. | Substation - Transformer | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-05 | 84 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.6839 | NA | 230 ¦ 13.8 kV | 227 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5773861 | T.0002633 | Haas PH: Replace Bk 1 (230/13.8 kV) | 1 | 68 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-06-05 | NA | 2028-12-15 | NA | FALSE | NA | NA | 387.7393 | 5807.046 | 0 | 5.6413 | 15.8216 | 4556.5167 | -4194.775 | 28.134 | 0 | 0 | 0 | 0 | 0 | 383.2047 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 967 | Helm Sub: Repl Bk 1 (230/70 kV) |  |  | Fresno | Replacement of the deteriorated 230/70kV Transformer Bank #1 at Helm Substation. Helm Substation is located in the vicinity of the City of Fresno, within Fresno County, California. Bank #1 is comprised of four single-phase 1964-vintage 44 MVA 230/70 kV Westinghouse transformers. Due to the age and condition of this bank, it was added to the “Deteriorated Transformer Replacement Program” and was planned for replacement in 2023. Continuing to operate this transformer will lead to an increasingly high probability of transformer failure in service. The RIBA score for this bank is 319. | Substation - Transformer | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-05 | 59 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 6.7555 | NA | 230 ¦ 70 kV | 319 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5769943 | T.0001589 | Helm Sub: Repl Bk 1 (230/70 kV) | 1 | 68 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-11-09 | NA | 2028-06-06 | NA | FALSE | NA | NA | 141.3283 | 8753.0999 | 0 | 87.919 | 11.6104 | 8.7064 | 9.9207 | 31.7737 | 0 | 0 | 0 | 0 | 0 | 118.1564 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 968 | Reedley: Repl Bk 2 (115/70 kV) |  |  | Fresno | This planned project will replace Reedley Transformer #2 with one new 115/70 kV, 200 MVA transformer. This planned project is needed to maintain safe and reliable power to the greater Dinuba, Reedley and South Fresno area, and will provide the following benefits: Increase the existing transformer capacity from 90 MVA to 200 MVA and allow accommodation for future load growth. Provide a firm station (two T-banks banks in total) Improve employee safety by eliminating a possible catastrophic transformer failure due to equipment condition. Potential decrease in annual recurring maintenance costs by replacing the existing transformer and switches with newer equipment. | Substation - Transformer | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-01 | 60 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.5939 | NA | 115 kV | 240 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5769944 | T.0001590 | Reedley: Repl Bk 2 (115/70 kV) | 1 | 68 | NA | 2016 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-11-01 | 2021-12-04 | 2022-03-31 | NA | TRUE | 5784 | NA | 7614.9521 | 7614.9521 | 103.6887 | 745.6513 | 4464.3355 | 1849.9598 | 451.3168 | 0 | 0 | 0 | 0 | 0 | 0 | 7614.9521 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 6747.6623 | 424.1875 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 969 | ORO LOMA: Replace BK 2 115/70 KV |  |  | Fresno | This project is part of Substation Asset Strategy’s Transmission Transformer Replacement Program for the 115/70 kV transmission Bank 2 at Oro Loma Substation (MWC 68). | Substation - Transformer | Replace | T.0003408 ¦ T.0001473 ¦ T.0000563 | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-02-16 | 70 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.8637 | NA | 115 ¦ 70 kV | 240 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5757748 | T.0000891 | ORO LOMA SUB: REPLACE BK2 115/70 KV | 2 | 68 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-07-26 | 2019-10-21 | 2019-12-17 | NA | FALSE | 7203 | NA | 8713.1079 | 8713.1079 | 2985.4909 | 1916.2985 | 3.7376 | 1.8201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8713.1079 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 6537.7958 | 1843.4348 | 3.5954 | 1.7508 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 970 | Placer: Install 115/60 kV Bank 4 |  |  | Placer | This project proposes to install Transformer 4 (1-3 phase with LTC, 200 MVA) and replace Bank 1 (1-3 phase with LTC, 200 MVA) at Placer Substation. Placer Bank 1 (3-1 phase, Westinghouse, 1962, 22.7 MVA/phase) was installed in 1962. Placer Bank 1 has been targeted for replacement as part of the PG&E Transmission Transformer Proactive Replacement Program. The prioritization criteria for this program is primarily based on technical assessments of the transmission transformer banks. The predominant factors include transformer condition per Dissolved Gas Analysis (DGA), age, and impact of consequence of an In-Service failure. In addition, recurring maintenance costs, availability of spare parts, and environmental issues are also taken into consideration. Specifically, Placer Bank 1 C, B, and A are ranked #57, #167, and #244 on 2021 Transmission Transformer Replacement List. Installation of the second Placer 115/60 kV transformer improves reliability and operational flexibility for customers in the area. Currently, with only one Placer 115/60 kV transformer, recommended clearance window for the bank 1 is limited to April to mid-May. An outage outside of this window could result in customers at risk. In addition, an outage of Placer 115/60 kV bank 1, could result in a sustained outage to customers served from Penryn, Auburn, Mountain Quarries and Halsey Substations (approximately 18,608 customers). | Substation - Transformer | New | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 ¦ 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5797892 | T.0005697 | Placer: Rebuild Substation | 9 | 68 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-11-04 | 2024-12-30 | 2026-07-31 | Prioritization | FALSE | 17200 | NA | 3722.4181 | 10518.2292 | 0 | 0 | 18.0752 | 132.731 | 3521.9433 | 1915.0073 | 0 | 0 | 0 | 0 | 4046.0715 | 3672.7495 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 971 | Placer: Replace 115/60 kV Bank 1 |  |  | Placer | This project proposes to install Transformer 4 (1-3 phase with LTC, 200 MVA) and replace Bank 1 (1-3 phase with LTC, 200 MVA) at Placer Substation. Placer Bank 1 (3-1 phase, Westinghouse, 1962, 22.7 MVA/phase) was installed in 1962. Placer Bank 1 has been targeted for replacement as part of the PG&E Transmission Transformer Proactive Replacement Program. The prioritization criteria for this program is primarily based on technical assessments of the transmission transformer banks. The predominant factors include transformer condition per Dissolved Gas Analysis (DGA), age, and impact of consequence of an In-Service failure. In addition, recurring maintenance costs, availability of spare parts, and environmental issues are also taken into consideration. Specifically, Placer Bank 1 C, B, and A are ranked #57, #167, and #244 on 2021 Transmission Transformer Replacement List. Installation of the second Placer 115/60 kV transformer improves reliability and operational flexibility for customers in the area. Currently, with only one Placer 115/60 kV transformer, recommended clearance window for the bank 1 is limited to April to mid-May. An outage outside of this window could result in customers at risk. In addition, an outage of Placer 115/60 kV bank 1, could result in a sustained outage to customers served from Penryn, Auburn, Mountain Quarries and Halsey Substations (approximately 18,608 customers). | Substation - Transformer | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-12 | 62 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 ¦ 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5797893 | T.0005697 | Placer: Rebuild Substation | 9 | 68 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-07-08 | 2024-12-30 | 2026-12-31 | Prioritization | FALSE | 17200 | NA | 3597.1262 | 10493.8347 | 0 | 0 | 14.7575 | 117.1233 | 3416.308 | 1938.6325 | 0 | 0 | 0 | 0 | 2047.291 | 3548.1887 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 972 | Newark Repl. Bk9 |  |  | Fremont, Alameda | This project proposes to replace Newark 230/115 kV Banks 7 and 9 under the Deteriorated Transformer Replacement Program. | Substation - Transformer | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-08 | 38 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 27.7611 | NA | 230 ¦ 115 kV | 498 | Not Available | Not Available | RBPPF - TBD | Yes | 5777177 | T.0003446 | Newark Repl. Bk 7 and Bk 9 | 2 | 68 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-02-05 | NA | 2029-06-20 | NA | FALSE | NA | NA | 0 | 8486.4343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 973 | Replace Sobrante Bank 1 (230/115 kV) |  |  | Orinda, Contra Costa | This project proposes to replace Sobrante Bank 1 (230/115 kV, 403MVA)with a new bank as part of the "Deteriorated Transmission Transformer Replaement Program". | Substation - Transformer | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-07 | 59 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.0767 | NA | 115 kV | 240 | 9. Reliability (Low Safety Risk) | 3 | RBPPF - TBD | Yes | 5760326 | T.0002845 | Sobrante: Replace Bank 1 | 1 | 68 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-04-20 | NA | 2028-01-19 | NA | FALSE | NA | NA | 337.9679 | 8013.7612 | 45.3921 | 20.299 | 19.4636 | 21.0779 | 23.1802 | 24.42 | 0 | 0 | 0 | 0 | 0 | 334.0154 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 974 | GOLD HILL: Repl BK 5- 115/60 KV |  |  | Folsom, Sacramento | This project proposes to replace the deteriorated Gold Hill Transformer # 5 (three (3) single phase, 115/60 kV, 26.6 MVA, General Electric vintage 1951 autotransformers) with four (4), single-phase, 30 MVA, 115/60 kV transformers to make this a firm autotransformer installation | Substation - Transformer | Replace | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-28 | 73 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 12.8702 | NA | 115 kV | 472 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5768178 | T.0000952 | Gold Hill: Replace 115/60kV Bank 5 | 1 | 68 | 5734628 | 2011 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-04-02 | NA | 2025-12-11 | NA | TRUE | NA | NA | 6451.3747 | 13424.5487 | 19.054 | 45.5622 | 290.2292 | 1071.3858 | 4329.7045 | 1298.0933 | 3892.2701 | 0 | 0 | 0 | 0 | 5987.3766 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 975 | Tesla: Purchase Three-Phase Trans Mobile |  |  | Tracy, San Joaquin | This project will add a new 115/60x70 kV 90MVA three-phase transmission mobile to our mobile fleet. The new mobile transformer will be the first transmission 3-phase mobile transformer in the fleet. The existing three 115-60/70 kV 30 MVA single-phase mobiles can support loss of three single phase transformers or a whole 115-60/70kV bank. The loss of a three-phase bank would require all three of these mobile transformers, leaving 153 transmission transformers without backup for many months, or more than a year. The addition of this three-phase mobile transformer will greatly enhance our ability to recover from transmission transformer outages. | Substation - Transformer | New | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | 115 ¦ 70 ¦ 60 kV | Not Available | Not Available | Not Available | Tier 4 | Yes | 5540940 | T.0006112 | Tesla_Purchase Three-Phase Trans Mobile | 1 | 68 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-04-22 | 2022-12-31 | 2024-05-17 | Material | TRUE | 3800 | NA | 3733.1695 | 5203.0213 | 0 | 0 | 0 | 70.2671 | 2348.2586 | 2784.4956 | 0 | 0 | 0 | 0 | 0 | 2418.5257 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 70.2671 | 2348.2586 | 1314.9928 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 976 | 230/115kV 420MVA New CEM Bank 1 |  |  | NA | This project will procure three (3) 230/115 kV 420 MVA three-phase transformers with load tap changer (LTC) | Substation - Transformer | New | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 kV | Not Available | Not Available | Not Available | NA | NA | 5546160 | T.0007411 | 230/115kV 420MVA New CEM Bank 1 | 1 | 68 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-09-06 | 2022-12-31 | 2023-10-03 | Material | TRUE | 4500 | NA | 6612.5087 | 6612.5087 | 0 | 0 | 1.1183 | 2405.6018 | 3986.9486 | 218.8401 | 0 | 0 | 0 | 0 | 0 | 6393.6686 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2406.7201 | 3986.9486 | 218.8401 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 977 | 230/115kV 420MVA New CEM Bank 3 |  |  | NA | This project will procure three 230/115kV, 420MVA 3-phase transformer with LTC to support failure of existing three phase 230/115kV transmission transformers. | Substation - Transformer | New | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5546162 | T.0007409 | 230 115kV 420MVA New CEM Bank 3 | 1 | 68 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-12-04 | 2024-05-15 | 2024-01-19 | NA | TRUE | 4270 | NA | 5642.8643 | 5642.8643 | 0 | 0 | 2.0738 | 804.4868 | 4621.1496 | 215.1541 | 0 | 0 | 0 | 0 | 0 | 5427.7102 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 806.5606 | 4621.1496 | 215.1541 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 978 | 230/115kV 420MVA New CEM Bank 2 |  |  | NA | This project will procure three 230/115kV, 420MVA 3-phase transformers with LTC to support failure of existing three phase 230/115kV transmission transformers. | Substation - Transformer | New | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | 230 ¦ 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5546161 | T.0007410 | 230 115kV 420MVA New CEM Bank 2 | 1 | 68 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-12-04 | 2023-05-15 | 2024-01-19 | Workforce | TRUE | 4270 | NA | 5700.571 | 5700.571 | 0 | 0 | 0 | 807.0041 | 4657.0679 | 236.499 | 0 | 0 | 0 | 0 | 0 | 5464.072 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 807.0041 | 4657.0679 | 236.9855 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 979 | LOCKEFORD: Remove BK 1 |  |  | Lockeford CDP, San Joaquin | This project will remove the deteriorated 115/60 kV Transformer Bank 1 at Lockeford Substation | Substation - Transformer | Removal | TBD | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-01 | 77 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 10.2719 | NA | 115 ¦ 60 kV | 227 | Not Available | Not Available | RBPPF - TBD | Yes | 5546019 | T.0002193 | LOCKEFORD SUB: REPLACE BANK 1 | 1 | 68 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-10-27 | NA | 2027-11-23 | NA | TRUE | NA | NA | 106.9731 | 1297.5737 | 0.4981 | 47.0179 | 49.6584 | 9.7986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9731 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2027 ¦ 2028 | 0 | 0 | 4.0877 | 0.01954 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 980 | HOPLAND: REPLACE BK 2 |  |  | Mendocino | This project will replace the 115/60kV Bank 2 at Hopland Substation with a new three-phase, 100MVA, 115/60kV transformer bank with load tap-changer (LTC) | Substation - Transformer | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-02-12 | 72 | Lifecycle Replacement Analysis | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.63377 | NA | 115 ¦ 60 kV | 202 | 9. Reliability (Low Safety Risk) | 11 | RBPPF - TBD | Yes | 5748000 | T.0000830 | HOPLAND: REPL 115/60 KV BANK 2 | 1 | 68 | NA | 2012 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-09-30 | 2018-08-14 | 2026-03-27 | Clearances | FALSE | 4575 | NA | 4468.1734 | 7288.0491 | 205.8399 | 210.3056 | -1326.8534 | 413.3536 | 1636.2494 | 1096.1085 | 2879.2522 | 53.1777 | 0 | 0 | 0 | 4384.5234 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 981 | PEASE: Repl BK 2 |  |  | Sutter | This project will replace the 115/60kV Bank 2 at Pease Substation with a three-phase, 200 MVA, 115/60kV transformer bank with load tap-changer (LTC). | Substation - Transformer | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-02-08 | 63 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.6809 | NA | 115 ¦ 60 kV | 240 | 9. Reliability (Low Safety Risk) | 14 | NA | NA | 5770141 | T.0001649 | PEASE: REPLACE 115/60KV BK2 | 1 | 68 | 5760984 | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-03-01 | 2020-03-17 | 2022-04-07 | Clearances | FALSE | 7958 | NA | 9716.4414 | 9716.4414 | 897.3896 | 3096.1859 | 2457.9578 | 2645.9138 | -337.993 | 1.5099 | 0 | 0 | 0 | 0 | 0 | 9714.9315 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 9515.9439 | -318.1003 | 2.7659 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 982 | PIT PH 1: Add BK 5 |  |  | Shasta | This project will replace the aging and deteriorated Bank 3 with a new transformer, as well as add a Bank 5 for redundancy and additional operational flexibility. The Load-Tap-Changer (LTC) built into Bank 3 will also provide flexibility in regulating voltage. The oil from the existing transformer banks will be disposed of per standard PG&E process; PSC, a contractor, will remove the oil from site and either recycle it (if low polychlorinated biphenyl (PCBs) count) or dispose of it at a hazardous waste facility (if high PCBs count). The project scope of work includes the following:  Install a new 30MVA, 60/11kV three-phase transformer with LTC, as replacement for Bank 3.  Install a new 70MVA, 230/60kV Bank 5.  Remove the existing Bank 3 and structures.  Install or upgrade spill prevention control and countermeasure (SPCC) as needed.  Install a new control building, protection package, and SCADA. | Substation - Transformer | New | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-07 | NA | NA | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | 2.7679 | NA | 230 ¦ 60 kV | 202 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5768953 | T.0000623 | Pit No. 1 PH Transformer Upgrade | 3 | 68 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-12-03 | 2018-10-16 | 2020-01-13 | Bundling Dependencies | FALSE | 27000 | NA | 26577.3006 | 26577.3006 | 11209.1261 | 5434.0029 | 90.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26577.3006 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 25969.0737 | 88.206 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 983 | PIT PH 1: Replace BK 3 |  |  | Shasta | This project will replace the aging and deteriorated Bank 3 with a new transformer, as well as add a Bank 5 for redundancy and additional operational flexibility. The Load-Tap-Changer (LTC) built into Bank 3 will also provide flexibility in regulating voltage. The oil from the existing transformer banks will be disposed of per standard PG&E process; PSC, a contractor, will remove the oil from site and either recycle it (if low polychlorinated biphenyl (PCBs) count) or dispose of it at a hazardous waste facility (if high PCBs count). The project scope of work includes the following:  Install a new 30MVA, 60/11kV three-phase transformer with LTC, as replacement for Bank 3.  Install a new 70MVA, 230/60kV Bank 5.  Remove the existing Bank 3 and structures.  Install or upgrade spill prevention control and countermeasure (SPCC) as needed.  Install a new control building, protection package, and SCADA. | Substation - Transformer | Replace | NA | Asset Condition | Age/Condition - Replace 230/115/70/60 kV Transformers | NA | 2024-03-07 | 74 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $20 Mil - $30 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | 2.7679 | NA | 60 ¦ 11 kV | 202 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5776406 | T.0000623 | Pit No. 1 PH Transformer Upgrade | 3 | 68 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-01-14 | 2020-05-29 | 2020-10-29 | NA | FALSE | 27000 | NA | 5756.8174 | 5756.8174 | 539.2337 | 4469.9503 | -93.6014 | -12.2627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5756.8174 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 5250.8409 | -83.2186 | -10.9024 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 984 | placeholder for trans. transformers online monitors |  |  | NA | Forecast placeholder for online monitoring on trans. xfmrs, $60k/unit, 15 units in 2024, 20 units in 2025, 30 units in 2026, 40 units in 2027, 50 units in 2028 | Substation - Transformer | New | NA | Asset Condition | Replace Transformer | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | Yes | EX113192 | NA | NA | NA | 68 | 5543622 | NA | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | 11800 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 1800 | 2400 | 3000 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 985 | WMP - T Line Repl Steel Structures |  |  | NA | Bucket for replacement of t-line steel structures in support of Wildfire Mitigation Plan. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5547686 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1007.7212 | 1007.7212 | 307.2128 | 617.0702 | 61.4988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1007.7212 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 307.2662 | 617.0674 | 22.3172 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 986 | Fiber Replacement/Support |  |  | NA | Forecast placeholder for Replacement of structures as required to support fiber asset replacement. Allows for reliability of telecom assets by facilitating degraded asset replacement by replacement of supporting structures | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | Ex112916 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 10000 | 10000 | 10000 | 10000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 987 | Pole Replacement Engineered |  |  | NA | Bucket for Pole Replacements | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 31 | Not Available | 1367 | NA | NA | 5515926 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 7299.6362 | 7299.6362 | 12396.889 | -12433.6867 | 5.0077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7299.6362 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 5.0077 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 988 | System-Wide Generator Support - 70P |  |  | NA | Bucket for replacement of steel towers and wood poles for gen tie lines | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 81 | 9. Reliability (Low Safety Risk) | 151 | NA | NA | 5523002 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 3249.34 | 3249.34 | 0.2305 | 1.6225 | 10.8863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3249.34 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 0.23046 | 1.5841 | 9.7151 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 989 | RAVENSWOOD-AMES #1 115 KV: SALT POND |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Mountain View, Santa Clara ¦ Palo Alto, Santa Clara ¦ Santa Clara | The California State Coastal Conservancy (SCC) has a project to breach the levee for Salt Pond A2W. That will increase the water levels around the 18 towers in that area. Their plan is to breach the levee in 2023. Engineering has determined that adding cathodic protection, tower coating, and grouting on the towers will address that issue. | Transmission Line - Pole/Tower | Upgrade/Retrofit | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-09 | 74 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5800218 | T.0008192 | RAVENSWOOD-COOLEY-NEWARK-AMES SALT POND | 4 | 70 | NA | 2016 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-12-19 | 2023-03-20 | 2023-10-26 | Prioritization | TRUE | 6362 | NA | 6307.0341 | 6327.5583 | 0 | 0 | 0 | 695.4606 | 5583.5908 | 48.5069 | 0 | 0 | 0 | 0 | 0 | 6279.0514 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 6279.0514 | 35.3264 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $5 Mil - $10 Mil ¦ $75 Mil – $100 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 990 | Ravenswood - San Mateo 230kV 01/011 Rpr |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The project scope of work includes following: • Complete necessary immediate foundation replacement on Tower 001/011. • Replace Tower 001/011. • Replace old insulators, hardware, and equipment on Tower 001/011. • Coordinate transmission outages with T-line Operations, Grid Control, and impacted local stakeholders. • Manage any supporting purchase orders such as vegetation management and engineering. In January 2020, Maintenance and Construction (M&C) crews doing a site walk observed the legs of Tower 001/007 showing deterioration, and the tower required immediate attention. An emergency fix was done, and the tower was then replaced in late 2020. In June 2022, during a planned inspection on this line, a field crew observed significant degradation of the wooden piles and concrete foundation supporting structure 001/011 during a low-tide event. The conditions were reported, and T-Line engineering reviewed the situation and determined that the foundation was in need of immediate and urgent reinforcement, and that the structure as a whole needs to be replaced in order to permanently improve conditions at this location and offset future maintenance and repair costs. This project addresses the Electric Operations risk of Failure of Transmission Overhead Assets. This project will replace a structure with poor asset health to mitigate any potential safety incidents or unplanned outages to serve the electric customers of San Mateo County safely and reliably. Completion of this project will reduce the risk of losing these critical lines that help deliver power to customers in the northern San Francisco Peninsula area. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-27 | 60 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5550228 | T.0008449 | Ravenswood-SanMateo 230kV 01/011 TRP RPR | 2 | 70 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-07-25 | NA | 2022-08-27 | NA | FALSE | NA | NA | 2335.0269 | 2335.0269 | 0 | 0 | 0 | 2318.0327 | 16.9943 | 0 | 0 | 0 | 0 | 0 | 0 | 2335.0269 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2318.0327 | 16.9943 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 991 | Ignacio - Alto - Sausalito 60kV Twr Repl |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | This project proposes to replace at least three aging deteriorated steel structures and/or foundations on the Ignacio-Alto-Sausalito #1 and #2 60kV double circuit towers in order to maintain reliable service. Engineering evaluations will be performed to determine the level of upgrades required for each structure. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-09 | 84 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 598 | 1. Work that prevents fire ignition | 93 | RBPPF - TBD | Yes | 5777901 | T.0003580 | Ignacio - Alto - Sausalito 60kV | 1 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | PTC | TBD | TBD | TBD | On Hold | 5 | 2031-11-19 | NA | 2032-11-16 | NA | FALSE | 950 | NA | 3228.6628 | 373463.137 | 283.5868 | 491.1024 | 597.6651 | 1054.789 | 499.3379 | 199.0915 | 0 | 0 | 0 | 0 | 1000 | 3228.6628 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 992 | West Sac Brighton 115kV Twr Repl |  |  | Arden-Arcade CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento ¦ West Sacramento, Yolo | This project proposes to replace at least two aging deteriorated steel structure and/or foundation on the Pittsburg – San Mateo and Eastshore – San Mateo 230kV double circuit towers in order to maintain reliable service. This project will address the Bay Waters towers on the Pittsburg – San Mateo and Eastshore – San Mateo 230kV lines located in San Mateo County. These lines were built in 1952. These transmission lines share steel structure in this area. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-14 | 55 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 598 | 2. Overhead With Strong Safety Link | 574 | RBPPF - TBD | Yes | 5777913 | T.0003593 | West Sac - Brighton 115kV Twr Repl | 1 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-02-16 | NA | 2028-03-07 | NA | FALSE | NA | NA | 1368.7088 | 5538.7191 | 261.3261 | 243.7678 | 227.889 | 209.0221 | 130.2058 | 84.5092 | 0 | 0 | 0 | 0 | 947 | 1368.7088 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 993 | IGNACIO - MARE ISLAND TWR REPL PHASE 4 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 34 deteriorated towers along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 34 towers in the scope of this project will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. Since the time of the initial Advance Authorization, the cage extensions and 14 miles of reconductoring have been removed from the scope. | Transmission Line - Pole/Tower | Replace | T.0000415 | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-14 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801467 | T.0007072 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) | 6 | 70 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-12-04 | 2027-01-15 | 2025-12-04 | NA | TRUE | 46500 | NA | 0 | 96453.2782 | 0 | 0 | 0 | 0 | 0 | 201.2 | 95052.0782 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 994 | IGNACIO - MARE ISLAND TWR REPL PHASE 5 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 34 deteriorated towers along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 34 towers in the scope of this project will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. Since the time of the initial Advance Authorization, the cage extensions and 14 miles of reconductoring have been removed from the scope. | Transmission Line - Pole/Tower | Replace | T.0000415 | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-14 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806102 | T.0007072 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) | 6 | 70 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-10-26 | 2027-01-15 | 2026-11-06 | NA | FALSE | 46500 | NA | 0 | 60645.8003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54501.4221 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 995 | IGNACIO - MARE ISLAND TWR REPL PHASE 6 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 34 deteriorated towers along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 34 towers in the scope of this project will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. Since the time of the initial Advance Authorization, the cage extensions and 14 miles of reconductoring have been removed from the scope. | Transmission Line - Pole/Tower | Replace | T.0000415 | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-14 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5806103 | T.0007072 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) | 6 | 70 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-11-30 | 2027-01-15 | 2027-12-09 | Clearances | FALSE | 46500 | NA | 0 | 86270.1405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54501.4221 | 54501.4221 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 996 | Colusa Jct No1 60kV Mast Twr |  |  | Colusa ¦ Grimes CDP, Colusa ¦ Meridian CDP, Sutter ¦ Sutter | This project proposes to replace 10 mast towers and/or their anchors in the Yuba Area in order to maintain reliable service. 3 transmission lines are impacted: Almendra Jct 60kV line, District 1500 60kV Tap, and the Colusa Jct #1 60kV line. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-09-30 | 80 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5779006 | T.0003735 | Yuba Area 60kV Mast Twr Repl | 3 | 70 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-05-27 | NA | 2025-07-16 | NA | TRUE | NA | NA | 555.3564 | 968.0046 | 80.0488 | 147.1067 | 77.3202 | 124.3882 | 83 | 34.6004 | 378.0475 | 0 | 0 | 0 | 890.0594 | 555.3564 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 997 | 2.6-mile section of the San Mateo-Bay Meadows Lines from San Mateo to Tower 002/018 |  |  | Foster City, San Mateo ¦ San Mateo, San Mateo | The 2.6-mile section of the San Mateo-Bay Meadows Lines in the main transmission corridor heading up to San Mateo was originally constructed more than 90 years ago. (Many of the 18 structures in that section may be the original structures.) • The 4/0 CU conductor on that section of the lines is over 85 years old. • With summer peak loads of over 110 MW at the substation, an [L-1] outage would result in the remaining line being over the 4 fps SE rating. And the load would still be about 94 MW at 7 PM on a hot day – when the 4/0 CU conductor ratings go back to the 2 fps SE rating of 93.6 MVA • These lines are the only source of power to Bay Meadows Substation. A reconductoring project was initiated over 10 years ago, but was placed on hold. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-22 | 87 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion, Weather |  | 2.6 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | Ex112917 | TBD | TBD | TBD | 70 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2034-12-01 | NA | 2036-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 998 | Sap - 40594850 Twr (003/028) Martin Millbrae #1 |  |  | Brisbane, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ South San Francisco, San Mateo | Replace Tower 003/028 on the Martin-Millbrae #1 line due to degraded condition. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-28 | 87 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion, Weather |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | Ex112920 | TBD | TBD | TBD | 70 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-01-01 | NA | 2031-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 999 | SAP-40758132: 002/014 – Martin-Daly City #1- |  |  | Brisbane, San Mateo ¦ Daly City, San Mateo ¦ San Mateo | Replace Tower 002/014 on the Martin-Daly CIty #1 line due to degraded condition. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2020-10-21 | 87 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion, Weather |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | Ex112922 | TBD | TBD | TBD | 70 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-01-01 | NA | 2031-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1000 | Trans Replace Steel Structure - North |  |  | NA | Bucket for replacement of steel structures (North) | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 212 | 2. Overhead With Strong Safety Link | 39 | RBPPF - TBD | Yes | 5510399 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 12643.3043 | 143122.7435 | 557.5192 | 912.7629 | 670.0788 | 1723.9128 | 973.6073 | 563.139 | 0.0011 | 0 | 0 | 0 | 10000 | 12559.6034 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 547.6361 | 909.9859 | 548.154 | 1435.3342 | 875.2463 | 74.8164 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1001 | Trans Replace Steel Structure - South |  |  | NA | Bucket for replacement of steel structures (South) | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | 77 | RBPPF - TBD | Yes | 5504679 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 6010.364 | 6010.364 | 0 | 70.5111 | -9.076 | 8.5389 | 18.425 | 28.1598 | 0 | 0 | 0 | 0 | 0 | 5982.2042 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 70.5111 | -30.2247 | 0.87921 | 0 | 6.3724 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1002 | WMP - T Line Repl Steel Structures |  |  | NA | Bucket for replacement of transmission steel structures in support of WSIP | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | 4 | NA | NA | 5535225 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1236.1047 | 1236.1047 | 437.7168 | 475.5912 | 309.0334 | 12.6868 | 1.0764 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.1047 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 427.7044 | 398.1557 | 309.6673 | 37.5544 | 1.0764 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1003 | Gold Hill-Bellota-Lockeford 115kV |  |  | Clay CDP, Sacramento ¦ Dogtown CDP, San Joaquin ¦ Folsom, Sacramento ¦ Lockeford CDP, San Joaquin ¦ Sacramento ¦ San Joaquin | Gold Hill-Bellota-Lockeford 115kV Replacement Project, which plans to replace 13 deteriorated transmission line lattice-steel towers. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2020-10-12 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 | NA | 214 | 2. Overhead With Strong Safety Link | 652 | RBPPF - TBD | Yes | 5781562 | T.0004173 | Gold Hill-Bellota-Lockeford 115kV | 1 | 70 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-02-18 | NA | 2028-09-27 | NA | FALSE | NA | NA | 942.7244 | 7322.3371 | 154.004 | 202.7244 | 400.8196 | 38.6771 | 92.7768 | 0 | 0 | 0 | 0 | 0 | 250 | 942.7244 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1004 | Ignacio - Mare Island 115kV Twr Repl |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Ignacio-Mare Island 115 kV Priority Towers Replacement project. This project proposes to replace three transmission structures, Towers 013/093, 013/094, and 014/105 on the Ignacio – Mare Island 115 kV Lines, which have deteriorated steel components. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-14 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $30 Mil - $40 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 1142 | 2. Overhead With Strong Safety Link | 295 | NA | NA | 5777902 | T.0002886 | IGNACIO-MARE ISL 115KV - Priority Towers | 2 | 70 | NA | 2017 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-11-09 | 2021-04-21 | 2021-05-21 | NA | TRUE | 56500 | NA | 62783.7265 | 62783.7265 | 481.0246 | 19403.175 | 42674.091 | 30.667 | 112.6981 | 0 | 0 | 0 | 0 | 0 | 0 | 62783.7265 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 62640.9781 | 30.667 | 112.6981 | 0.16858 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1005 | Vaca-Vacaville-Jameson-North Tower 115kV |  |  | Benicia, Solano ¦ Fairfield, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | In an effort to support PG&E top-level initiatives to manage asset risk for the benefit of public and employee safety, service reliability, operational flexibility, and cost reduction, the proposed Accelerated Obsolete and Deteriorated Tower Replacement projects will proactively replace approximately 150 towers across entire PG&E Transmission grid. This project is a subset identified for replacement to kick start the Tower Replacement Program. Additional towers besides the 150 will be identified and nominated for replacement based on results from Asset Strategy’s Risk Analytics Model, which prioritizes risk based on asset health and consequences. Typically towers with the highest risks from this model are in high atmospheric corrosion areas for which permits take a while to obtain. As such, it is proposed to start the program with high to medium risk assets where permits are less cumbersome to obtain. The replacement of approximately 150 towers will minimize the program implementation risk. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-08 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | 214 | 1. Work that prevents fire ignition | 11 | RBPPF - TBD | Yes | 5781559 | T.0004170 | Vaca-Vacaville-Jameson-North Tower 115kV | 1 | 70 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2026-01-14 | NA | 2026-06-18 | NA | FALSE | NA | NA | 1884.2522 | 15426.7426 | 177.293 | 502.8174 | 226.9576 | 367.9295 | 560.9261 | 116.6603 | 0 | 0 | 0 | 0 | 10000 | 1884.2522 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1006 | IGNACIO - SOBRANTE 230KV TWR RPL |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | In an effort to support PG&E top-level initiatives to manage asset risk for the benefit of public and employee safety, service reliability, operational flexibility, and cost reduction, the proposed Ignacio - Sobrante 230 kV Towers Replacement Project will proactively replace four towers on the line. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-03 | 43 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Heat Wave |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5795020 | T.0007002 | IGNACIO - SOBRANTE 230KV TWR RPL | 2 | 70 | NA | 2021 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-03-01 | 2022-04-13 | 2022-04-18 | NA | TRUE | 5583 | NA | 7687.9187 | 7687.9187 | 0 | 0 | 1670.8381 | 5903.9565 | 105.9001 | 7.224 | 0 | 0 | 0 | 0 | 0 | 7680.6947 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 6897.7577 | 96.3109 | 8.337 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1007 | Ignacio-Sobrante Twr 29/133 Replacement |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | In an effort to support PG&E top-level initiatives to manage asset risk for the benefit of public and employee safety, service reliability, operational flexibility, and cost reduction, the proposed Ignacio - Sobrante 230 kV Towers Replacement Project will proactively replace four towers on the line. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-03 | 42 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5549227 | T.0007002 | IGNACIO - SOBRANTE 230KV TWR RPL | 2 | 70 | NA | 2021 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-10-04 | 2022-04-13 | 2023-11-14 | Prioritization | TRUE | 5583 | NA | 2311.4183 | 2316.2183 | 0 | 0 | 0 | 210.603 | 2061.0302 | 44.5851 | 0 | 0 | 0 | 0 | 0 | 2271.6332 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 210.603 | 1797.1659 | 18.5382 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1008 | Martin-Millbrae #1 Tower Replacements |  |  | Brisbane, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ South San Francisco, San Mateo | In March 2022, transmission line maintenance crews identified severe corrosion on Martin-Millbrae No. 1 115 kV Towers 002/020 and 002/021. The crews made repairs, but were not able to address all of the deterioration. Given the severity of the corrosion on these structures, Asset Strategy and T-Line Civil Engineering has recommended these towers be replaced. These tower replacements have been assigned to the 70S Tower Replacement Program because they are beyond repair and a current safety and reliability concern. The project scope of work includes the following: • Replacement of Martin – Millbrae No. 1 115 kV Towers 002/020 and 002/021 and associated foundations; • Replacement of old insulators, hardware, and equipment; • Construction will require a temporary shoofly to keep the existing circuits in service during installation of the new structures. This work will be completed under a single line or dual line clearance based on consultation with Transmission Operations | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-28 | 34 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5548880 | T.0008193 | Martin-Millbrae #1 Tower Replacements | 1 | 70 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6683-E | 2022-08-18 | Approved | 2022 | Operational | 2 | 2022-11-14 | 2022-12-31 | 2022-11-23 | NA | TRUE | 4300 | NA | 3114.7964 | 3114.7964 | 0 | 0 | 0 | 2838.3075 | 276.4889 | 0 | 0 | 0 | 0 | 0 | 0 | 3114.7964 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2668.8619 | 259.9826 | 0 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1009 | Ignacio-Alto-Sausalito 115 kV 13/94 TRP |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | It has been determined by recent field inspections and confirmed by the Transmission and Civil Engineering group that Tower 013/094 on the Ignacio - Alto – Sausalito 60 kV circuit must be replaced due to the current condition and structural integrity of the structure. The Ignacio - Alto – Sausalito 60 kV Line is located in the North Coast region. It is 17.36 miles long, with 127 structures. The line was constructed in 1930 and is the only source of power to Sausalito Substation, which serves over 7,400 customers. In order to prevent the risk of structure failure, asset components on the line are being proposed to be replaced with the following scope of work: • Replacement of tower 013/094 and its foundation on the Ignacio - Alto – Sausalito 60 kV circuit; and • Replacement of old insulators, hardware, and equipment on the structure. | Transmission Line - Pole/Tower | Replace | T.0008733 I T.0007460 | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-09 | 94 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804688 | T.0009146 | Ignacio-Alto-Sausalito 60 kV 13/94 TRP | 1 | 70 | NA | 2023 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-10-04 | 2024-03-31 | 2025-01-13 | Prioritization | TRUE | 2900 | NA | 1049.1928 | 3139.7983 | 0 | 0 | 0 | 0 | 572.0826 | 2382.1116 | 185.6042 | 0 | 0 | 0 | 1000 | 572.0825 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1010 | Potter Valley-Mendocino 60 KV TWR RPL |  |  | Mendocino ¦ Potter Valley CDP, Mendocino | Rebuild approximately 2.5 miles out of 11 miles of the Potter Valley-Mendocino 60kV transmission line. The scope of work includes replacing 22 old, failing transmission structures (mostly Lattice Steel Poles and some wood poles) with new Engineered Direct Embedded Poles and Tubular steel Poles. This will include repositioning the distribution circuit from the guest position to the underbuild position on the transmission poles as well as the addition of 17 distribution only-wood pole interests. The project will also replace approximately 2.5 miles of 3/0 7 strand Copper conductor with new 397.5 19 Strand All aluminum conductor. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-10 | 87 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | Not Available | 1. Work that prevents fire ignition | 301 | RBPPF - TBD | Yes | 5541160 | T.0006100 | Potter Valley - Mendocino 60 KV TWR RPL | 1 | 70 | NA | 2021 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-09-01 | 2024-10-31 | 2025-09-30 | Prioritization | TRUE | 10381 | NA | 1014.0988 | 7984.4381 | 0 | 158.2506 | 49.2709 | 579.9888 | 197.4649 | 97.1905 | 6887.2725 | 0 | 0 | 0 | 7200 | 984.9751 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 207.5215 | 579.9951 | 197.4649 | 53.4759 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1011 | IGNACIO - MARE ISLAND TWR REPL PHASE 2 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 34 deteriorated towers along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 34 towers in the scope of this project will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. Since the time of the initial Advance Authorization, the cage extensions and 14 miles of reconductoring have been removed from the scope. | Transmission Line - Pole/Tower | Replace | T.0000415 | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-14 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5798400 | T.0007072 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) | 4 | 70 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-11-27 | 2027-01-15 | 2023-12-20 | NA | FALSE | 238200 | NA | 19876.7531 | 20283.4401 | 0 | 0 | 0 | 0 | 19005.5176 | 1277.9225 | 0 | 0 | 0 | 0 | 0 | 19005.5176 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 19005.5176 | 302.8934 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1012 | IGNACIO - MARE ISLAND TWR REPL PHASE 3 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 34 deteriorated towers along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 34 towers in the scope of this project will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. Since the time of the initial Advance Authorization, the cage extensions and 14 miles of reconductoring have been removed from the scope. | Transmission Line - Pole/Tower | Replace | T.0000415 | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-14 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801466 | T.0007072 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) | 4 | 70 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2024-12-03 | 2027-01-15 | 2024-12-12 | NA | TRUE | 238200 | NA | 189.2117 | 17969.311 | 0 | 0 | 0 | 0 | 58.7959 | 15510.4158 | 2400.0993 | 0 | 0 | 0 | 0 | 58.7959 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1013 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace 34 deteriorated towers along the Ignacio-Mare Island #1 and #2 115 kV transmission line. The replacement of the 34 towers in the scope of this project will address NERC non-compliances from Ignacio Substation to Highway Substation and improve the overall safety and reliability of the system due to the condition of these towers. Since the time of the initial Advance Authorization, the cage extensions and 14 miles of reconductoring have been removed from the scope. | Transmission Line - Pole/Tower | Replace | T.0000415 | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-14 | 97 | Lifecycle Replacement Analysis | Other - Deferral | $400 Mil - $500 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5792138 | T.0007072 | IGNACIO-MARE ISL 115KV (IGN SUB/HWY SUB) | 4 | 70 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-02-28 | 2027-01-15 | 2023-03-29 | NA | TRUE | 238200 | NA | 17657.3583 | 17742.8583 | 500.4583 | 1207.9095 | -34.4686 | 6348.9479 | 9925.7336 | -822.7177 | 0 | 0 | 0 | 0 | 0 | 18565.576 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 17496.1508 | -837.3777 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1014 | BRIGHTON - GRAND ISLAND #1 115kV TWR RPL |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | The Brighton – Grand Island #1 115 kV Line is is located in the North Valley region. It is 24.99 miles long, with 205 structures. The following scope of work is proposed to mitigate structure and foundation issues identified in the field: Replacement of 5 structures and their foundations on the Brighton – Grand Island #1 115 kV circuit; Replacement of insulators, hardware, and equipment on these structures; and Replacement of conductor and splices around the (5) structure replacement locations. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-14 | 71 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 | NA | Not Available | 2. Overhead With Strong Safety Link | 388 | NA | NA | 5541336 | T.0006155 | BRIGHTON - GRAND ISLAND #1 115kV TWR RPL | 1 | 70 | NA | 2020 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-11-30 | 2021-02-20 | 2021-02-25 | NA | FALSE | 1130 | NA | 2717.821 | 2717.821 | 0 | 1183.999 | 1533.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2717.821 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 2717.8211 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1015 | Ignacio-Alto-Sausalito-Tower Replacement |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | The Ignacio - Alto – Sausalito 60 kV Line is is located in the North Coast region. It is 17.36 miles long, with 127 structures. In order to prevent the risk of structure failure, asset components on the line are being proposed to be replaced with the following scope of work: • Replacement of tower 009/064 and its foundation on the Ignacio - Alto – Sausalito 60 kV circuit; and • Replacement of old insulators, hardware, and equipment on the structure; | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-09 | 113 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | NA | NA | 5544414 | T.0007060 | Ignacio-Alto-Sausalito-Tower Replacement | 1 | 70 | NA | 2021 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-05-31 | 2021-11-19 | 2022-06-10 | Project Design | TRUE | 5315 | NA | 2987.559 | 2987.559 | 0 | 0 | 392.7716 | 2544.516 | 50.2715 | 0 | 0 | 0 | 0 | 0 | 0 | 2987.559 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 379.8169 | 2460.5908 | 48.6134 | -1e-05 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1016 | Kearney-Biola Pole Replacement |  |  | Biola CDP, Fresno ¦ Fresno ¦ Fresno, Fresno | The Kearney-Biola 70 kV Line located in Fresno County, is approximately 19 miles long and supported by 348 overhead structures. Structure 018/016 is one of the Lattice Steel Poles (LSP) supporting this line located within the Biola Substation fence. The structure was assessed due to a bent distribution underbuild cross-arm at which point the entire pole was found to be in poor condition due to lack of a reinforced foundation, direct embeded along with limited documentation on the asset. After reviewing possible repair options, the project team recommended to replace the existing LSP with Tubular Steel Pole (TSP), due to relatively high foundation retro-fit and corresponding repair costs. The project will also address possible touch-potential issues due to the existing metallic substation fence beng in close proximity to the existing metallic structure. This work is needed to maintain reliable electric service for the customers in Fresno County who are experiencing outages due to circuit unrealiability. In addition, substation clearance issues will reduce safety concerns related to touch potential. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-09-13 | 55 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | Not Available | Not Available | Not Available | NA | NA | 5549361 | T.0008283 | Kearney-Biola Pole Replacement | 1 | 70 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-09-19 | 2023-10-31 | 2023-11-22 | NA | TRUE | 1341 | NA | 1073.6819 | 1077.4319 | 0 | 0 | 0 | 172.1001 | 871.9043 | 33.4275 | 0 | 0 | 0 | 0 | 0 | 1044.0044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 149.8551 | 856.3056 | 36.8917 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1017 | Pittsburg - San Mateo 230kV Twr Repl |  |  | Alameda ¦ Blackhawk CDP, Contra Costa ¦ Castro Valley CDP, Alameda ¦ Contra Costa ¦ Danville, Contra Costa ¦ Fairview CDP, Alameda ¦ Foster City, San Mateo ¦ Hayward, Alameda ¦ Pittsburg, Contra Costa ¦ San Mateo, San Mateo ¦ San Ramon, Contra Costa | The Pittsburg-San Mateo and Eastshore-San Mateo 230 kV Lines are supported by 47 lattice steel towers, with 29 of those towers in the Bay Waters. The current scope of the Pittsburg-San Mateo 230 kV Tower Replacement Project (the “Project”) includes the replacement of most of the towers in the Bay Waters. There is significant corrosion of the steel components on the towers and the pile caps supporting the tower foundations have many cracks, which is resulting in a deterioration of the foundation steel. This reauthorization is being requested so that the project team can evaluate whether a like-for-like replacement or other options, such as replacing the lines with submarine cables. are the best long-term solution for these critical lines. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-04 | 71 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence, Corrosion |  | NA | NA | 230 | NA | 598 | 1. Work that prevents fire ignition | 144 | RBPPF - TBD | Yes | 5777912 | T.0003592 | Pittsburg - San Mateo 230kV Twr Repl | 1 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2031-12-17 | NA | 2033-03-15 | NA | FALSE | NA | NA | 1380.7235 | 200027.7137 | 177.3971 | 184.3545 | 77.9334 | 348.7397 | 364.9184 | 19.6706 | 0 | 0 | 0 | 0 | 427.9194 | 1445.0893 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1018 | Borden-Gregg 230 kV 1 & 2 structure Repl |  |  | Merced ¦ Stanislaus | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Transmission Line - Pole/Tower | Replace | T.0004490 ¦ T.0009329 ¦ T.0008538 | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-09-13 | 93 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | 776 | 2. Overhead With Strong Safety Link | 832 | RBPPF - TBD | Yes | 5788378 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 70 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-08-29 | 2022-11-10 | 2025-12-18 | Land Rights | TRUE | 39900 | NA | 181.1598 | 19660.2152 | 0 | 103.12 | 24.5662 | 27.7167 | 23.6142 | 43.0214 | 19438.1767 | 0 | 0 | 0 | 0 | 179.0171 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1019 | Ravenswood Ames #1 Phase 1 |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Mountain View, Santa Clara ¦ Palo Alto, Santa Clara ¦ Santa Clara | The project scope of work includes following to eliminate NERC discrepancies over the Bay Waters: Replace eight lattice steel towers with taller towers, install one top cage, and install dampers at 17 locations. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-09 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | 2. Overhead With Strong Safety Link | 526 | RBPPF - TBD | Yes | 5791338 | T.0000397 | RAVENSWOOD-AMES#1 TR PROJECT | 3 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6599-E | 2022-05-19 | Approved | 2022 | On Hold | 4 | 2024-09-11 | NA | 2026-06-03 | NA | FALSE | NA | NA | 1241.4555 | 1683.8078 | 0 | 46.6535 | 215.4995 | 685.7843 | 293.5182 | 76.6076 | 0 | 0 | 0 | 0 | 500 | 1241.4555 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1020 | RAVENSWOOD-AMES#1 |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Mountain View, Santa Clara ¦ Palo Alto, Santa Clara ¦ Santa Clara | The project scope of work includes following to eliminate NERC discrepancies over the Bay Waters: Replace eight lattice steel towers with taller towers, install one top cage, and install dampers at 17 locations. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-09 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 228 | 2. Overhead With Strong Safety Link | 526 | RBPPF - TBD | Yes | 5792377 | T.0000397 | RAVENSWOOD-AMES#1 TR PROJECT | 3 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6599-E | 2022-05-19 | Approved | 2022 | On Hold | 4 | 2029-04-17 | NA | 2029-12-31 | NA | FALSE | NA | NA | 1935.0688 | 36288.7052 | 157.5893 | 229.4399 | 755.2796 | 262.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1935.0688 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1021 | Salt Pond Tower Repl Project |  |  | Fremont, Alameda ¦ Newark, Alameda | The project scope of work includes following: Replace Dumbarton – Newark 115 kV Line aging tower Nos. 3/24, 4/30, 4/34, 4/35, 5/36, 5/37, and 6/43 with degradation issues categorized as high risk with lattice steel towers. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-11 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | 2. Overhead With Strong Safety Link | 520 | RBPPF - TBD | Yes | 5782125 | T.0004260 | DUMBARTON-NEWARK 115KV Salt Pond TRP | 1 | 70 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | CPUC | TBD | PTC | TBD | TBD | TBD | On Hold | 4 | 2028-10-19 | NA | 2029-04-19 | NA | FALSE | NA | NA | 2264.0614 | 10431.3847 | 130.8692 | 578.9661 | 898.3819 | 311.3367 | 344.5074 | 0 | 0 | 0 | 0 | 0 | 300 | 2264.0614 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1022 | MARTIN-DALY CITY #1 115KV 3/20 TRP |  |  | Brisbane, San Mateo ¦ Daly City, San Mateo ¦ San Mateo | The project scope of work includes following: • Complete any necessary temporary repairs to the Tower 003/020. • Replace Tower 003/020. The Martin-Daly City Nos. 1 and 2 115 kV Lines supply power to Daly City Substation, which serves over 50,500 customers in Daly City and the southwestern portion of San Francisco. The No. 2 Line has a tap connection at Tower 002/014 that supplies power to Serramonte Substation, which serves over 9,200 customers. In September 2022, Transmission Engineering and Design South raised that three E-priority maintenance tags were created and evaluated by Tower, Engineering and Tower Coating on the Martin-Daly City Lines. The outcome of the review indicated that Tower 003/020 (122986585) needs immediate replacement and Tower 002/013 (123028780) and Tower 002/014 (122986380) can be replaced in a few years. The E-priority tag (122986585) for Tower 003/020 indicates several issues on the tower: minor cracks on the foundation, 15% material loss on stub on the tower’s D-Leg, no ground wire on the tower, a lot of surface rust, and the truss members have holes and need to be replaced. Refer to Attachment 2 for pictures for Tower 003/20. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2020-10-21 | 72 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5551123 | T.0008714 | MARTIN-DALY CITY #1 115KV 3/20 | 1 | 70 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 5 | 2026-10-02 | NA | 2026-10-29 | NA | TRUE | NA | NA | 1152.2806 | 2050.8349 | 0 | 0 | 0 | 105.4276 | 1046.853 | 0 | 0 | 0 | 0 | 0 | 900 | 1152.2806 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2026 | 0 | 0 | 0 | 105.4276 | 968.9248 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1023 | DUMBARTON-NEWARK 115KV TWR 6/48 TRP |  |  | Fremont, Alameda ¦ Newark, Alameda | The project scope of work includes following: • Complete any necessary temporary repairs to the Tower 06/048. • Replace Tower 06/048. In November 2019, an F-priority maintenance tag (118145965) was created and labelled tower 6/48 on the Dumbarton – Newark 115 kV to be replaced. The tag indicates that the Face struts and center plates have been replaced after the tower was inspected also cleaned and galvanized. Pack rust on shims throughout the tower. Spliced rusted through flat stock on first and second level of C face. Installed a strong back plate on C leg 8ft above pier and also above second splice. The engineering recommendation following July 2022 engineering review was the replacement of the tower. Tower #6/48 is under an elevated risk level of failure if the tower is not replaced within the next 2 years. Field crews will continue to FSR the structure every 90 days until the tower is replaced. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-11 | 99 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5550450 | T.0008563 | DUMBARTON-NEWARK 115KV TWR 6/48 TRP | 1 | 70 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-12-01 | 2023-10-21 | 2023-12-09 | NA | TRUE | 1350 | NA | 1647.4652 | 1692.4652 | 0 | 0 | 0 | 108.1605 | 1480.4292 | 103.8755 | 0 | 0 | 0 | 0 | 0 | 1588.5897 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 108.1605 | 1394.2401 | 58.6731 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1024 | Ravenswood - San Mateo 230kV 01/011 TRP |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The project scope of work includes following: • Complete necessary immediate foundation replacement on Tower 001/011. • Replace Tower 001/011. • Replace old insulators, hardware, and equipment on Tower 001/011. • Coordinate transmission outages with T-line Operations, Grid Control, and impacted local stakeholders. • Manage any supporting purchase orders such as vegetation management and engineering. In January 2020, Maintenance and Construction (M&C) crews doing a site walk observed the legs of Tower 001/007 showing deterioration, and the tower required immediate attention. An emergency fix was done, and the tower was then replaced in late 2020. In June 2022, during a planned inspection on this line, a field crew observed significant degradation of the wooden piles and concrete foundation supporting structure 001/011 during a low-tide event. The conditions were reported, and T-Line engineering reviewed the situation and determined that the foundation was in need of immediate and urgent reinforcement, and that the structure as a whole needs to be replaced in order to permanently improve conditions at this location and offset future maintenance and repair costs. This project addresses the Electric Operations risk of Failure of Transmission Overhead Assets. This project will replace a structure with poor asset health to mitigate any potential safety incidents or unplanned outages to serve the electric customers of San Mateo County safely and reliably. Completion of this project will reduce the risk of losing these critical lines that help deliver power to customers in the northern San Francisco Peninsula area. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-27 | 60 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801779 | T.0008449 | Ravenswood-SanMateo 230kV 01/011 TRP RPR | 2 | 70 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-10-16 | NA | 2026-02-25 | NA | TRUE | NA | NA | 550.0197 | 3141.4576 | 0 | 0 | 0 | 130.8998 | 390.1518 | 134.5926 | 0 | 0 | 0 | 0 | 8000 | 521.0516 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1025 | IGNACIO - SOBRANTE 230KV TRP PH2 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The project scope of work includes following: • Replace structures IG004/025, IG004/024, IG004/023, IG004/022, IG004/021, and IG003/020 and their foundations under phase 2. • Replace structures IG003/015 through IG002/010 and their foundations under phase 3. • Replace old insulators, hardware, and equipment on these structures. • Coordinate transmission outages with T-line Operations, Grid Control, and impacted local stakeholders. • Manage any supporting purchase orders such as engineering, Geotech, and construction. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-03 | 41 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5800801 | T.0008284 | IGNACIO - SOBRANTE 230KV TRP PH2 & PH3 | 2 | 70 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-10-03 | 2022-12-31 | 2022-11-21 | NA | TRUE | 11907 | NA | 10018.0869 | 10018.5869 | 0 | 0 | 0 | 9890.6442 | 125.2901 | 2.6527 | 0 | 0 | 0 | 0 | 0 | 10015.9342 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 9890.6442 | -777.0053 | 1.9574 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1026 | IGNACIO - SOBRANTE 230KV TRP PH3 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The project scope of work includes following: • Replace structures IG004/025, IG004/024, IG004/023, IG004/022, IG004/021, and IG003/020 and their foundations under phase 2. • Replace structures IG003/015 through IG002/010 and their foundations under phase 3. • Replace old insulators, hardware, and equipment on these structures. • Coordinate transmission outages with T-line Operations, Grid Control, and impacted local stakeholders. • Manage any supporting purchase orders such as engineering, Geotech, and construction. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-03 | 42 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5800802 | T.0008284 | IGNACIO - SOBRANTE 230KV TRP PH2 & PH3 | 2 | 70 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-05-30 | 2022-12-31 | 2029-12-18 | Scope Change | TRUE | 11907 | NA | 598.3509 | 12683.0071 | 0 | 0 | 0 | 116.5431 | 454.9508 | 296.8975 | 0 | 0 | 0 | 0 | 10226.0724 | 571.494 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1027 | EBMUD 115 kV Tap Pole Replacement |  |  | Contra Costa Centre CDP, Contra Costa ¦ Walnut Creek, Contra Costa | The project scope of work includes the following: Replace three (3) existing poles and associated equipment along the EBMUD 115 kV Tap T-Line and redesign accordingly. The EBMUD 115 kV Tap is a high pressure nitrogen filled system transitioning from overhead to underground. As a result, the three (3) poles are going to introduce complexity and cost than a typical pole replacement. The project proposes to replace 3 existing poles and associated equipment along the EBMUD 115 kV Tap T-Line located in Contra Costa County, CA. This projects need is because the current condition of the three (3) poles are deteriorated and at risk of failure. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-08-17 | 47 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5543819 | T.0006942 | EBMUD 115 kV Tap Pole Replacement | 1 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2031-05-29 | NA | 2031-09-15 | NA | TRUE | NA | NA | 465.6189 | 6284.8691 | 0 | 0 | 0 | 155.2084 | 310.4104 | 0 | 0 | 0 | 0 | 0 | 5305.8352 | 465.6189 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 | 0 | 0 | 0 | 139.6875 | 278.8459 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1028 | Wheeler Ridge-Tejon - Pole Replacement |  |  | Kern | The project will address California Public Utilities Commission (CPUC) General Order (GO)-95 and Pacific Gas and Electric Company (PG&E) standard requirements, in addition increase system performance in Kern County by performing the following work: • Replace forty-six (46) wood structures on the Wheeler Ridge – Tejon 70 kV Line; • Replacement of old insulators, hardware, and equipment on the structure; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-08-07 | 48 | Lifecycle Replacement Analysis | Other - Deferral | $2 Mil - $3 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798379 | T.0007564 | Wheeler Ridge-Tejon - Pole Replacement | 1 | 70 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6632-E | 2022-05-19 | Approved | 2022 | Operational | 2 | 2022-10-01 | 2023-12-01 | 2024-01-25 | NA | TRUE | 3447 | NA | 4773.9591 | 4818.7939 | 0 | 0 | 7.1413 | 2069.0544 | 2394.7967 | 347.8014 | 0 | 0 | 0 | 0 | 0 | 4470.9925 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 4602.006 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1029 | RAVENSWOOD-BAIR #1 115KV PH2 |  |  | Menlo Park, San Mateo ¦ Redwood City, San Mateo | The Ravenswood – San Mateo 115 kV Segment 2 NERC Project (the “Project”) has identified possibly 100 towers for replacement and the reconductoring of 4 spans of conductor on the towers that support the Ravenswood – San Mateo, the San Mateo – Belmont 115 kV and the Ravenswood – Bair No. 1 115 kV Lines. This project scope includes the replacement of 16 remaining towers identified as part of the North American Electric Reliability Corporation (NERC) remediation work not covered under the Segment 1 NERC project and 4 towers identified as part of the Tower Replacement Program. In addition, the project will need to evaluate another 80 towers to determine if those towers will need to replaced: 28 were identified through the coatings program, 45 through the asset strategy risk model, 2 from the NERC work, and 5 from the 2017 special assessment. To gain efficiencies in engineering, permitting, and construction, the NERC and Tower Replacement Program were merged into one scope of work. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-10 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | 2. Overhead With Strong Safety Link | 1253 | RBPPF - TBD | Yes | 5792443 | T.0002156 | RAVENSWOOD-SAN MATEO 115KV Ph2 NERC PROJ | 3 | 70 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2031-03-22 | NA | 2031-08-12 | NA | FALSE | 4900 | NA | 2425.8979 | 285356.8975 | 263.288 | 600.885 | 582.6353 | 171.3748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2425.8979 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1030 | SAN MATEO-BAYMDWS #1 & #2 PH2 |  |  | Foster City, San Mateo ¦ San Mateo, San Mateo | The Ravenswood – San Mateo 115 kV Segment 2 NERC Project (the “Project”) has identified possibly 100 towers for replacement and the reconductoring of 4 spans of conductor on the towers that support the Ravenswood – San Mateo, the San Mateo – Belmont 115 kV and the Ravenswood – Bair No. 1 115 kV Lines. This project scope includes the replacement of 16 remaining towers identified as part of the North American Electric Reliability Corporation (NERC) remediation work not covered under the Segment 1 NERC project and 4 towers identified as part of the Tower Replacement Program. In addition, the project will need to evaluate another 80 towers to determine if those towers will need to replaced: 28 were identified through the coatings program, 45 through the asset strategy risk model, 2 from the NERC work, and 5 from the 2017 special assessment. To gain efficiencies in engineering, permitting, and construction, the NERC and Tower Replacement Program were merged into one scope of work. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-22 | 87 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | 2. Overhead With Strong Safety Link | 1055 | RBPPF - TBD | Yes | 5792442 | T.0002156 | RAVENSWOOD-SAN MATEO 115KV Ph2 NERC PROJ | 3 | 70 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2029-08-31 | NA | 2029-12-21 | NA | FALSE | NA | NA | 436.4718 | 1901.8334 | 30.5205 | 108.0118 | 76.6149 | 31.9804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.4718 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1031 | RAVENSWOOD-SAN MATEO 115KV |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The Ravenswood-Bair No. 2 115 kV Line Segment 2 NERC Project (the “Project”) has identified approximately 30 towers for replacement. This project scope includes the replacement of 20 remaining towers identified as part of the North American Electric Reliability Corporation (NERC) remediation work not covered under the Segment 1 NERC project and 10 towers identified as part of the Tower Replacement Program. (All 10 towers were found as high priority from the asset strategy risk model, with 6 being confirmed as part of a 2017 special assessment and 4 that need further assessment.) | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-28 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 228 | 2. Overhead With Strong Safety Link | 504 | RBPPF - TBD | Yes | 5792440 | T.0002155 | RAVENSWOOD-BAIR #2 115KV Ph2 TR PROJEC | 1 | 70 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2029-01-19 | NA | 2029-11-30 | NA | FALSE | NA | NA | 1474.3097 | 11685.7275 | 168.1481 | 227.5365 | 243.8471 | 102.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1474.3097 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1032 | SAN MATEO-BELMONT 115KV PH2 |  |  | Belmont, San Mateo ¦ Foster City, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | The San Mateo - Bay Meadows 115kV Segment 2 NERC Project (the “Project”) initially identified approximately 13 towers for replacement and the reconductoring of 1 section (7 spans) on the San Mateo – Bay Meadows Nos. 1 and 2 115 kV Lines. That scope included the replacement of 8 towers identified as part of the North American Electric Reliability Corporation (NERC) remediation work and the replacement of 5 towers as part of the Tower Replacement (TR) Program. However, the project scope is being expanded to include an evaluation of the condition of the 17 remaining towers. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2022-11-04 | 87 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 228 | 2. Overhead With Strong Safety Link | 1304 | RBPPF - TBD | Yes | 5792441 | T.0002157 | SAN MATEO-BAYMDWS #1 & #2 TR Project | 1 | 70 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2029-03-30 | NA | 2029-07-27 | NA | FALSE | NA | NA | 1240.5921 | 41196.0333 | 152.8328 | 199.1371 | 248.2161 | 86.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.5921 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1033 | Ignacio-Alto-Sausalito 4/37 & 4/38 B Tag |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | The target structures of this project, 004/037 and 004/038, have been determined to require replacement via B-Tag assignment post inspection. This project will aim to replace both structures with new lattice steel design towers and engineered piling or pier foundations. This work, when complete, will mitigate all currently assigned B-tags on the two structures and enable PG&E to maintain compliance on this segment of the line. This project, when combined with other ongoing efforts to improve the functionality and dependency of the line, will allow PG&E to continue safe and reliable electric operation in the region. This project proposes to : • Replace foundations and lattice steel towers at locations 004/037 and 004/038 with new foundations and lattice steel towers ahead or back in line from original structure locations. • To mitigate B-Tags which have been assigned to each of these structures post inspection. • Completion of this work will mitigate all currently assigned B-Tags and improve system reliability in this segment of the line. • This work will be executed by an Engineer, Procure, Construction (EPC) contract. Awarded prime contractor will be responsible for the completion of the T-line and Civil engineering, material procurement, equipment procurement, construction and post-construction cleanup efforts. • PG&E will assist in customer outreach, permit application and attainment, land acquisition as needed, environmental clearances for work and confirmation of completion of work per scope. | Transmission Line - Pole/Tower | Replace | T.0008733 I T.0009146 | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-09 | 94 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5797979 | T.0007460 | Ignacio-Alto-Sausalito B Tag Projects | 1 | 70 | NA | 2021 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2021-06-01 | EIR | NA | CDFW | NA | NOC: AL 6970-E | 2023-06-26 | Approved | 2023 | Engineering more than 50% complete | 4 | 2024-09-02 | 2023-12-29 | 2024-11-17 | Prioritization | TRUE | 18460 | NA | 1885.5752 | 15902.4707 | 0 | 0 | 104.6644 | 381.5838 | 1178.2879 | 14154.4099 | 83.5246 | 0 | 0 | 0 | 0 | 1664.5362 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1034 | Almendra Jct 60k Mast Twr |  |  | East Nicolaus CDP, Sutter ¦ Nicolaus CDP, Sutter ¦ Sutter | This project proposes to replace 10 mast towers and/or their anchors in the Yuba Area in order to maintain reliable service. 3 transmission lines are impacted: Almendra Jct 60kV line, District 1500 60kV Tap, and the Colusa Jct #1 60kV line. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-03 | 99 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 60 | NA | 758 | 2. Overhead With Strong Safety Link | 298 | RBPPF - TBD | Yes | 5779004 | T.0003735 | Yuba Area 60kV Mast Twr Repl | 3 | 70 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2025-09-17 | NA | 2026-02-27 | NA | FALSE | NA | NA | 1395.2238 | 2560.3425 | 218.1296 | 257.3718 | 230.4588 | 261.2392 | 227.3516 | 86.5089 | 0 | 0 | 0 | 0 | 400 | 1395.2238 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1035 | District 1500 Tap 60kV Mast Twr |  |  | Sutter ¦ Yolo | This project proposes to replace 10 mast towers and/or their anchors in the Yuba Area in order to maintain reliable service. 3 transmission lines are impacted: Almendra Jct 60kV line, District 1500 60kV Tap, and the Colusa Jct #1 60kV line. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-01 | 99 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | 758 | 2. Overhead With Strong Safety Link | 1022 | RBPPF - TBD | Yes | 5779005 | T.0003735 | Yuba Area 60kV Mast Twr Repl | 3 | 70 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2025-05-06 | NA | 2025-07-03 | NA | TRUE | NA | NA | 595.547 | 1400.2285 | 75.2718 | 132.5717 | 138.2227 | 108.2574 | 90.6352 | 37.0626 | 767.6189 | 0 | 0 | 0 | 1000 | 595.547 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1036 | Middle River Tap 60kV Mast Twr |  |  | Contra Costa ¦ Discovery Bay CDP, Contra Costa ¦ San Joaquin | This project proposes to replace 11 mast towers and/or their anchors in the Sacramento Delta Area in order to maintain reliable service. 3 transmission lines are impacted: Rough and Ready 60kV Tap, McDonald 60kV Tap, and the Middle River 60kV Tap. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-06 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | 758 | 2. Overhead With Strong Safety Link | 1009 | RBPPF - TBD | Yes | 5779000 | T.0003734 | Sacramento Delta Area 60kV Mast Twr Repl | 3 | 70 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2025-10-03 | NA | 2025-11-13 | NA | TRUE | NA | NA | 1105.4266 | 9317.3606 | 189.1869 | 167.1385 | 235.9305 | 294.6765 | 168.1997 | 68.75 | 101.3497 | 0 | 0 | 0 | 2200 | 1105.4266 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1037 | Christie-Willow 60kV Mast Twr |  |  | Bay Point CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa | This project proposes to replace 2 mast towers and/or their anchors on the Christie – Willow Pass 60kV line in order to maintain reliable service. Engineering evaluations will be performed to determine the level of upgrades required for each structure. This project proposes to replace either anchors or full structure replacement for 2 aging lattice-steel poles and/or their anchors in order to maintain reliable service. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-05 | 99 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | 758 | 1. Work that prevents fire ignition | 94 | RBPPF - TBD | Yes | 5779001 | T.0003736 | Christie-Willow 60kV Mast Twr | 1 | 70 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2025-05-07 | NA | 2025-06-17 | NA | TRUE | NA | NA | 1115.0428 | 3206.2037 | 192.7726 | 181.7843 | 245.0282 | 212.9108 | 167.1476 | 69.4021 | 2021.7589 | 0 | 0 | 0 | 3000 | 1115.0428 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1038 | Lakeville No2 60kV Mast Twr |  |  | Marin ¦ Novato, Marin ¦ Petaluma, Sonoma ¦ Sonoma | This project proposes to replace 2 mast towers and/or their anchors on the Lakeville #2 60kV line in order to maintain reliable service. Engineering evaluations will be performed to determine the level of upgrades required for each structure. This project proposes to replace either anchors or full structure replacement for 2 aging lattice-steel poles and/or their anchors in order to maintain reliable service. In February 2017, structures on the Tesla-Salado-Manteca 115kV line collasped when wind gusts reached 45 mph. Upon investigation, the team concluded that the anchors on structure A31/248, a 167’ lattice steel pole, failed due to significant subsurface corrosion. The corrosion caused the anchor rods to become detached from the “dead-man” anchor and then pulled out out of the ground during the high winds. When this structure failed, the adjacent structure, A31/247 – a 171’ tall lattice steel pole, also failed. These towers were installed in 1925. This project will address 2 similar structures located on the Lakeville #2 60kV line within counties. Each structure will be evaluated for either an anchor replacement or a full structure replacement. A tower failure on the Lakeville #2 60kV line will impact 1,244 customers supported by the Peteluma A substation. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-12-21 | 99 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 758 | 1. Work that prevents fire ignition | 3 | RBPPF - TBD | Yes | 5779003 | T.0003738 | Lakeville No2 60kV Mast Twr | 1 | 70 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | On Hold | 4 | 2026-05-26 | NA | 2026-07-23 | NA | FALSE | NA | NA | 1153.7167 | 2044.3747 | 197.8313 | 238.2742 | 174.6896 | 212.0159 | 179.3925 | 71.6458 | 0 | 0 | 0 | 0 | 2500 | 1153.7167 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1039 | Vaca-Vacaville -Jameson 115kV TWR 24/171 |  |  | Benicia, Solano ¦ Fairfield, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | This project proposes to replace 2 severely rusted lattice steel towers with 2 new lattice steel towers (LST’s) to improve asset health and maintain reliable service. Tower 24/171 was removed and replaced with a two-pole shoofly in July 2022 to avoid structure failure. This tower replacement project will replace that tower and the preceding structure, 24/170. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-08 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5550039 | T.0008400 | Vaca-Vacaville -Jameson 115kV 24/170-171 | 1 | 70 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-07-17 | 2023-07-30 | 2023-07-20 | NA | TRUE | 1146 | NA | 1082.5467 | 1082.5467 | 0 | 0 | 0 | 274.238 | 808.3087 | 0 | 0 | 0 | 0 | 0 | 0 | 1082.5467 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 208.3223 | 645.1395 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1040 | Millbrae - San Mateo 115kV Twr Repl |  |  | Burlingame, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ San Mateo, San Mateo | This project proposes to replace 3 (1/14, 1/15, and 2/28) aging deteriorated steel structures and/or foundations on the Millbrae – San Mateo #1 115kV line. Engineering evaluations will be performed to determine the level of upgrades required for each structure. This project proposes to replace three aging deteriorated steel structures / foundations in order to maintain reliable service. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-12-01 | 77 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 598 | 2. Overhead With Strong Safety Link | 973 | RBPPF - TBD | Yes | 5777904 | T.0003583 | Millbrae - San Mateo 115kV Twr Repl | 1 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2026-09-09 | NA | 2026-11-17 | NA | FALSE | NA | NA | 614.0496 | 5701.0037 | 83.3201 | 125.3988 | 29.4894 | 202.2793 | 1.4268 | 75.1422 | 0 | 0 | 0 | 0 | 250 | 614.0496 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1041 | Woodleaf-Palermo 115kV-Steel Structure |  |  | Butte ¦ Forbestown CDP, Butte ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte | This project proposes to replace aging structures and insulators on the Woodleaf – Palermo 115 kV Line and associated 115 kV Tap lines to help mitigate high-risk components on these line. Scope in details: • Replace 124 of the 232 structures on the Woodleaf – Palermo 115 kV Line with steel structures; • Replace 69 insulators on the Woodleaf – Palermo 115 kV Line; • Perform field analysis on existing structures, Nos. 000/005, 006/053, and 013/128 on the Woodleaf – Palermo 115 kV Line to verify if replacements are needed; • Perform field analysis on 0.02 miles of Sly Creek Tap 115 kV from pole no. 000/006 to 000/008 to verify the age of the conductor and to determine if reconductor is needed; • Replace 3 structures, pole nos. 003/031A, 003/031B, and 003/031C and perform field analysis on 3 structures, pole nos. 002/019, 003/032, and 004/038 to determine if structure and insulator replacements are needed on the Sly Creek Tap 115 kV; • Replace all insulators on the Sly Creek Tap 115 kV; • Replace 1 structure, pole no. 004/039 and conduct field analysis on 3 structures, pole nos. 000/001A, 000/001B, and 000/001C to determine if structure and insulator replacements are needed on the Forbestown Tap 115 kV; • Perform field analysis on 9 structures, pole nos. 000/002, 001/008B, 001/008C, 001/010C, 001/011, 002/015, 002/016, 002/018A, and 002/018C, to verify if structure and insulator replacements are needed on the Kanaka Tap 115 kV; • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-04 | 62 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 4703 | 1. Work that prevents fire ignition | 151 | RBPPF - TBD | Yes | 5789806 | T.0005758 | Woodleaf-Palermo 115kV-Structure & Insul | 3 | 70 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-08-25 | NA | 2027-09-21 | NA | FALSE | NA | NA | 31.2596 | 5120.2148 | 0 | 0 | 20.3107 | 8.4394 | 2.1439 | 2.2642 | 0 | 0 | 0 | 0 | 227.8855 | 30.894 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1042 | Newark - Ames 115kV Twr Repl |  |  | Fremont, Alameda ¦ Mountain View, Santa Clara ¦ Newark, Alameda ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Sunnyvale, Santa Clara | This project proposes to replace at least one aging deteriorated steel structure and/or foundation on the Newark – Ames #1 and #2 115kV double circuit towers, at least one tower on the Newark – Ames #3 and Newark – Ames Distribution 115kV double circuit towers, and at least one tower on the Newark – Applied Materials and Newark – Lawrence 115kV double circuit towers in order to maintain reliable service. Engineering evaluations will be performed to determine the level of upgrades required for each structure. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-20 | 98 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | NA | NA | 115 | NA | 1142 | 2. Overhead With Strong Safety Link | 556 | RBPPF - TBD | Yes | 5777910 | T.0003590 | Newark - Ames 115kV Twr Repl | 1 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-01-18 | NA | 2027-03-26 | NA | FALSE | NA | NA | 943.4602 | 7757.4039 | 147.1287 | 192.3601 | 181.3895 | -0.0791 | 89.5802 | 0 | 0 | 0 | 0 | 0 | 250 | 943.4602 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1043 | Newark - N Receiving Stn 115kV Twr Repl |  |  | Fremont, Alameda ¦ San Jose, Santa Clara ¦ Santa Clara, Santa Clara | This project proposes to replace at least one aging deteriorated steel structure and/or foundation on the Newark – Northern Receiving Station #1 and #2 115kV double circuit towers in order to maintain reliable service. Engineering evaluations will be performed to determine the level of upgrades required for each structure. This project proposes to replace at least one aging deteriorated steel structures / foundations in order to maintain reliable service. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-22 | 92 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 115 | NA | 1142 | 2. Overhead With Strong Safety Link | 866 | RBPPF - TBD | Yes | 5777905 | T.0003585 | Newark - N Receiving Stn 115kV Twr Repl | 1 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2026-03-02 | NA | 2026-05-08 | NA | FALSE | NA | NA | 745.3058 | 1685.8532 | 89.4704 | 128.9283 | 107.2191 | 81.2422 | 153.4779 | 0 | 0 | 0 | 0 | 0 | 250 | 745.3058 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1044 | Newark - Ravenswood 230kV Twr Repl |  |  | Fremont, Alameda ¦ Menlo Park, San Mateo ¦ Newark, Alameda | This project proposes to replace at least one aging deteriorated steel structure and/or foundation on the Newark - Ravenswood and Tesla – Ravenswood 230kV double circuit towers in order to maintain reliable service. Engineering evaluations will be performed to determine the level of upgrades required for each structure. This project proposes to replace at least one aging deteriorated steel structures / foundations in order to maintain reliable service. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-12-21 | 62 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | NA | NA | 230 | NA | 1142 | 2. Overhead With Strong Safety Link | 502 | RBPPF - TBD | Yes | 5777911 | T.0003591 | Newark - Ravenswood 230kV Twr Repl | 1 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2026-04-20 | NA | 2026-06-26 | NA | FALSE | NA | NA | 725.1312 | 1128.1039 | 118.7824 | 128.2057 | 109.6622 | 91.7524 | 84.7507 | 0 | 0 | 0 | 0 | 0 | 250 | 725.1312 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1045 | San Mateo Martin No3 115kV Twr Repl |  |  | Foster City, San Mateo ¦ San Mateo, San Mateo | This project proposes to replace at least one aging deteriorated steel structure and/or foundation on the San Mateo – Martin #3 and San Mateo – Martin #4 115kV double circuit towers in order to maintain reliable service. Engineering evaluations will be performed to determine the level of upgrades required for each structure. This project proposes to replace at least one aging deteriorated steel structures / foundations in order to maintain reliable service. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-22 | 87 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 598 | 2. Overhead With Strong Safety Link | 831 | RBPPF - TBD | Yes | 5777909 | T.0003589 | San Mateo - Martin No3 115kV Twr Repl | 1 | 70 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2026-01-19 | NA | 2026-03-27 | NA | FALSE | NA | NA | 684.9485 | 1231.5146 | 77.1106 | 87.462 | 102.9017 | 81.6259 | 156.73 | 0 | 0 | 0 | 0 | 0 | 330.194 | 684.9485 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1046 | Tidewater-Sobrante 230 kV TR PH1 |  |  | Alhambra Valley CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa ¦ Orinda, Contra Costa ¦ Vine Hill CDP, Contra Costa | This project proposes to replace seven line structures (014/068, 014/069, 014/070, 014/071, 014/072, 014/073, and 015/074) on the Tidewater-Sobrante 230 kV Line in order to maintain reliable service and reduce the potential public safety risk due to hardware failures on the structures. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-14 | 53 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5799458 | T.0007860 | Tidewater-Sobrante 230 kV TR | 2 | 70 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6717-E | 2022-09-30 | Approved | 2022 | Operational | 2 | 2023-03-31 | 2023-05-24 | 2023-04-10 | NA | TRUE | 14000 | NA | 2877.7468 | 2877.7468 | 0 | 0 | 0 | 1149.8515 | 1741.0678 | -13.1724 | 0 | 0 | 0 | 0 | 7753.6777 | 2890.9192 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2866.6487 | -9.4288 | 0% | NA | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1047 | Tidewater-Sobrante 230 kV TR PH2 |  |  | Alhambra Valley CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa ¦ Orinda, Contra Costa ¦ Vine Hill CDP, Contra Costa | This project proposes to replace seven line structures (014/068, 014/069, 014/070, 014/071, 014/072, 014/073, and 015/074) on the Tidewater-Sobrante 230 kV Line in order to maintain reliable service and reduce the potential public safety risk due to hardware failures on the structures. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-14 | 53 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805660 | T.0007860 | Tidewater-Sobrante 230 kV TR | 2 | 70 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6717-E | 2022-09-30 | Approved | 2022 | Operational | 2 | 2024-03-01 | 2023-05-24 | 2024-03-10 | Scope Change | TRUE | 14000 | NA | 1654 | 1782 | 0 | 0 | 0 | 0 | 650.7834 | 1132 | 0 | 0 | 0 | 0 | 7753.6777 | 651 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 1623.0143 | 0% | NA | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1048 | Newark-Livermore 60 kV Tower Replacement |  |  | Alameda ¦ Fremont, Alameda ¦ Livermore, Alameda ¦ Sunol CDP, Alameda | This project proposes to replace towers 08/051 and 08/052 on the Newark-Livermore 60 kV Line to address aging transmission assets and maintain reliable service. Towers 08/051 and 08/052 were not originally issued replacement tags, but rather a maintenance crew observed the rust while performing a routine cleaning of the nearby transmission facilities. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-09 | 107 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Heat Wave |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | NA | NA | 5548162 | T.0007858 | Newark-Livermore 60 kV Tower Replacement | 1 | 70 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-10-09 | 2023-07-15 | 2023-10-13 | NA | TRUE | 2206 | NA | 1548.4316 | 1548.4316 | 0 | 0 | 0 | 361.0978 | 1167.727 | 19.6068 | 0 | 0 | 0 | 0 | 0 | 1528.8248 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 327.3557 | 1073.4691 | 16.1327 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1049 | Ignacio-Alto 60kV Twr Repl 13/114 |  |  | Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin | This project proposes to replace two aging, deteriorated, steel structures, towers 13/113 and 13/114 on the Ignacio – Alto 60kV line, their associated foundations in order to maintain reliable service, and reconductor the associated conductor with a summer emergency (SE) rating of at least 1124 Amps. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-02-28 | 57 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 214 | 1. Work that prevents fire ignition | 7 | RBPPF - TBD | Yes | 5781898 | T.0004219 | Ignacio-Alto 60kV Twr Repl 13/114 | 1 | 70 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6645-E | 2022-07-07 | Approved | 2022 | Operational | 2 | 2021-03-01 | 2023-10-01 | 2024-01-12 | NA | TRUE | 3902 | NA | 4689.0713 | 5721.9885 | 122.0977 | 299.6987 | 1393.4027 | 563.4045 | 1208.9658 | 1114.5614 | 929.7589 | 0 | 0 | 0 | 0 | 3677.6681 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 2670.9954 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1050 | Aged Tower Replacement Phase 1 |  |  | Auburn, Placer ¦ North Auburn CDP, Placer ¦ Placer | This project will proactively replace approximately 50 towers across entire PG&E Transmission grid identified based on a combination of age, deteriorated and obsolete designs that are difficult to maintain, as well as field inspection | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-11 | 71 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 598 | 2. Overhead With Strong Safety Link | 15 | NA | NA | 5777903 | T.0003582 | Aged Tower Replacement Phase 1 | 6 | 70 | NA | 2018 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-11-09 | 2020-06-05 | 2020-11-16 | NA | FALSE | 11965 | NA | 1638.8396 | 1638.8396 | 432.108 | 544.4826 | 96.8153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1638.8396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 1559.4699 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1051 | Aged TWR REP_ Rio Oso-Woodland #1 |  |  | East Nicolaus CDP, Sutter ¦ Madison CDP, Yolo ¦ Nicolaus CDP, Sutter ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ Woodland, Yolo ¦ Yolo | This project will proactively replace approximately 50 towers across entire PG&E Transmission grid identified based on a combination of age, deteriorated and obsolete designs that are difficult to maintain, as well as field inspection | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-12-08 | 71 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 | NA | 598 | 2. Overhead With Strong Safety Link | NA | NA | NA | 5781721 | T.0003582 | Aged Tower Replacement Phase 1 | 6 | 70 | NA | 2018 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-03-20 | 2019-06-05 | 2019-03-26 | NA | FALSE | 11965 | NA | 2522.8712 | 2522.8712 | 760.8892 | 262.5404 | 284.6935 | 1210.0062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2522.8712 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 862.8265 | 386.4543 | 1155.0683 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1052 | Ravenswood-San Mateo 230kV TWR 1/7 RPL |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | This project will proactively replace Tower 001/007 on the Ravenswood-San Mateo 230 kV Lines, which has deteriorated foundations and steel components | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-27 | 60 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 230 | NA | Not Available | 2. Overhead With Strong Safety Link | 880 | NA | NA | 5789620 | T.0005727 | Ravenswood-San Mateo 230kV TWR 1/7 RPL | 1 | 70 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-11-01 | 2020-12-31 | 2020-11-18 | NA | FALSE | 8900 | NA | 8863.4215 | 8863.4215 | 0 | 8879.198 | -15.7765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8863.4215 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 8879.1983 | -15.7764 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1053 | Martin_SFAirport_Tower Replacement |  |  | Brisbane, San Mateo ¦ San Mateo ¦ South San Francisco, San Mateo | This project will proactively replace Tower 002/021 on the Martin-SF Airport 115kV Line, which has deteriorated steel components. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-28 | 34 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5544971 | T.0007173 | Martin_SFAirport_Tower Replacement | 1 | 70 | NA | 2021 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6683-E | 2022-08-18 | Approved | 2022 | Operational | 2 | 2022-11-14 | 2021-10-31 | 2022-11-16 | Project Design | FALSE | 1652 | NA | 2070.0717 | 2070.0717 | 0 | 0 | 777.2327 | 1361.906 | -69.4018 | 0.3348 | 0 | 0 | 0 | 0 | 0 | 2069.7369 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 636.8445 | 1115.9236 | -56.866 | 0.27437 | 0% | NA | NA | NA | 44% | 56% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1054 | Tesla-Schulte SW Sta #2 115kV Twr Repl |  |  | Alameda ¦ San Joaquin | This project will replace 34 lattice steel towers on the Tesla-Schulte #2 115 kV Power Line with 3 TSPs and 31 lattice steel towers ahead or back of the existing structure locations and reconductor 1.41 miles of conductor with new 477 ACSS (same as existing). This project will also improve safety and reliability for the customers served in San Joaquin County by mitigating the risk of failure from aged, corroded, and hard-to-maintain lattice steel towers. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2021-11-09 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | 214 | 2. Overhead With Strong Safety Link | 995 | NA | NA | 5781561 | T.0004172 | Tesla-Schulte SW Sta #2 115kV Twr Repl | 2 | 70 | NA | 2018 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6508-E | 2022-02-18 | Approved | 2022 | Operational | 2 | 2022-09-15 | 2022-11-30 | 2023-01-10 | NA | TRUE | 15880 | NA | 6849.86 | 6858.2588 | 406.2591 | 423.1958 | 437.2004 | 4639.5566 | 882.4607 | 26.7147 | 0 | 0 | 0 | 0 | 0 | 6831.5441 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 6514.2248 | 23.04 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1055 | Lammers-Kasson 115kV Twr Repl |  |  | San Joaquin ¦ Tracy, San Joaquin | This project will replace 49 lattice steel towers on the Lammers-Kasson 115 kV Power Line with TSPs ahead or back of the existing structure locations and reconductor 3 spans of the line with new 477 ACSS (same as existing). This project will also improve safety and reliability for the customers served in San Joaquin County by mitigating the risk of failure from aged, corroded, and hard-to-maintain lattice steel towers. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2021-09-15 | 73 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 214 | 2. Overhead With Strong Safety Link | 748 | NA | NA | 5781560 | T.0004171 | Lammers-Kasson 115kV Twr Repl | 2 | 70 | NA | 2019 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6507-E | 2022-02-18 | Approved | 2022 | Operational | 2 | 2022-10-11 | 2022-12-31 | 2022-12-19 | NA | TRUE | 14906 | NA | 15996.7706 | 16177.1049 | 500.8082 | 473.7787 | 436.2332 | 12848.5951 | 1657.7312 | 230.0018 | 0 | 0 | 0 | 0 | 0 | 15947.1031 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 12599.8069 | 1384.6828 | 38.9878 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1056 | Sobrante-Moraga 115 kV Tower Replacement |  |  | Orinda, Contra Costa | This project will replace 7 lattice steel poles on 2 transmission lines: Poles #00/001A, 00/002A, 00/003A, 00/005A on the Sobrante-Moraga 115 kV Line; and Poles #00/001B, 00/002B, 00/003B on the Moraga-Lakewood 115 kV Line. All 7 structures will be replaced with TSP’s per engineering recommendations. These replacements will be made in order to maintain reliable electric service for the customers in Contra Costa County. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-03-29 | 73 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5797568 | T.0007396 | Sobrante-Moraga 115 kV Tower Replacement | 1 | 70 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6644-E | 2022-07-07 | Approved | 2022 | Operational | 2 | 2022-12-01 | 2022-12-31 | 2022-12-16 | NA | TRUE | 2813 | NA | 2027.6724 | 2027.6724 | 0 | 0 | 164.5531 | 1728.5483 | 134.5709 | 0 | 0 | 0 | 0 | 0 | 0 | 2027.6724 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1679.2472 | 119.0951 | 0 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1057 | Essex Jct-Arcata-Fairhaven 60 kV |  |  | Arcata, Humboldt ¦ Humboldt ¦ Manila CDP, Humboldt ¦ Samoa CDP, Humboldt | This project will replace existing double circuit lattice steel tower #004/022 on the Essex Jct-Arcata-Fairhaven 60 kV Line in order to maintain reliable electric service for the customers in Humboldt County. Furthermore, we need to investigate an over-tensioning condition and an issue with a clearance for the double circuit transmission line. Resolving these problems are likely to require a shoo-fly and potentially replacement of one or two adjacent towers on this line. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2023-11-27 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | NA | NA | 5545379 | T.0007238 | Essex Jct-Arcata-Fairhaven 60 kV | 1 | 70 | NA | 2021 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-05-20 | 2022-04-30 | 2022-05-23 | NA | TRUE | 1682 | NA | 1714.529 | 3064.604 | 0 | 0 | 312.7093 | 1067.6586 | 317.4533 | 338.0029 | 0 | 0 | 0 | 0 | 0 | 1697.8212 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 300.6822 | 1026.5977 | 305.2437 | 14.7809 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1058 | Cortina-Mendocino 115 kV - Twr 46/225 |  |  | Clearlake Oaks CDP, Lake ¦ Colusa ¦ Lake ¦ Lucerne CDP, Lake ¦ Mendocino ¦ Nice CDP, Lake | This project will replace the old double-circuit lattice steel tower #46/225 on the Cortina-Mendocino 115 kV and Mendocino-Redbud 115 kV Line The tower is situated on a slope that is prone to mudslides and posed an immediate safety threat during the recent heavy rains in December 2022 and January 2023. The tower footings were found to be in such critical condition that an emergency 4-pole shoofly was installed, and the tower was removed before a full failure occurred. The shoofly was only an immediate mitigation, so the project team is currently designing 2 permanent TSP’s offset to either side of the old tower location in order to reduce the likelihood of these being affected by future land/mudslides. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-12 | 46 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804087 | T.0008942 | Cortina-Mendocino 115 kV - Twr 46/225 | 1 | 70 | NA | 2023 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-07-09 | 2024-02-06 | 2024-07-12 | NA | TRUE | 1802.928 | NA | 1370.7722 | 1953.923 | 0 | 0 | 0 | 0 | 645.0941 | 1308.8289 | 0 | 0 | 0 | 0 | 60 | 645.0941 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1059 | PARKWAY-MORAGA 230kV 5/34-35-36 TRP |  |  | Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Orinda, Contra Costa ¦ Solano ¦ Vallejo, Solano | This project will replace three transmission line structures, 005/034, 006/035 and 006/036, that support the Parkway -Moraga 230kV and the Bahia – Moraga 230kV lines in order to maintain reliable electric service for customers in Solano County. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-06 | 79 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5802143 | T.0008555 | PARKWAY-MORAGA 230kV 5/34-35-36 TRP | 1 | 70 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-08-24 | NA | 2026-12-18 | NA | TRUE | NA | NA | 476.0317 | 35906.0722 | 0 | 0 | 0 | 93.5901 | 342.4753 | 658.0324 | 0 | 0 | 0 | 0 | 12592.3603 | 436.0654 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1060 | Vaca-Vacaville-Jameson 115k TWR 8/63 |  |  | Benicia, Solano ¦ Fairfield, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | This project will replace Tower 008/063 which supports the Vaca-Vacaville-Jameson-North Tower and Vaca-Vacaville-Cordelia 115 kV lines with a tubular steel pole (TSP) structure in the same location as the existing structure. Currently, Tower 008/063 has been removed and the two circuits are supported by a shoofly. The replacement of Tower 008/063 was necessary because the top cage of the tower was twisted, and the engineering recommendation was to replace the whole structure and not only the top cage due to structural stability concerns. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-08 | 74 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5795883 | T.0007123 | Vaca-Vacaville -Jameson 115kV TWR 8/63 | 1 | 70 | NA | 2021 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-05-06 | 2021-11-30 | 2022-05-11 | NA | FALSE | 3131 | NA | 5650.1638 | 5650.1638 | 0 | 0 | 1444.3807 | 4167.8781 | 37.905 | 0 | 0 | 0 | 0 | 0 | 0 | 5650.1638 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 4449.0396 | 29.9278 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1061 | Ignacio-Alto-Sausalito 115 kV 7/54 TRP |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | Tower 7/54 has an open E-priority tag, 119375345. In 2018/19 modifications were made to the supports of the tower. This tower has been identified as one to be in need to be repaired or replaced mainly due to the heavy rust around the anchor connections and top cage. Additional inspections were completed in September 2022 and again in January 2023. Engineering design need to be completed to determine what is needed to be done for the tower. Additionally, the Tiscornia Marsh restoration project, led by the city of San Rafael and Marin Audubon Society are planning to add about 5.5ft of fill material at the base of tower 08/046 on Ignacio-San Rafael 115 kV which could cause serious damage to the existing foundation pile caps. Additional Geotech studies need to be completed to determine the effects of this added fill material. Finally, this Marsh Restoration project might cause PG&E to replace or relocate the existing boardwalks to access these 2 towers. • Complete any necessary temporary repairs to the Tower 07/054. • Replace top cage if needed. • Coordinate with City of San Rafael and Audubon Society on tower access/boardwalks. • Review fill material to be added to the base of tower 08/046 on Ignacio-San Rafael 115 kV | Transmission Line - Pole/Tower | Replace | T.0007460 I T.0009146 | Asset Condition | Age/Condition - Replace Steel Poles | NA | 2024-04-09 | 94 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804586 | T.0008733 | Ignacio-Alto-Sausalito 60 kV 7/54 TRP | 2 | 70 | NA | 2023 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-10-09 | 2024-12-13 | 2024-11-08 | NA | TRUE | 2500 | NA | 216.6711 | 7952.9316 | 0 | 0 | 0 | 0 | 120.9573 | 7810.9743 | 21 | 0 | 0 | 0 | 0 | 120.9573 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1062 | CHRISTIE-WILLOW PASS Structure REplacement |  |  | Bay Point CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa | CHRISTIE-WILLOW PASS has a high Probability of failure. Per Maintenance this is a worst acting line with areas that are inaccessible and have high environmental requirements. Currently 270 wood poles on the line, with approximately 5% having existing 70Y tags or recently completed 70Y tags. Average age is 37 years old (third quartile). Approximately 42% of poles have a TCM Annual Probability of Failure of over 10%. Average annual probability of failure TCM is 16.93%. The oldest poles appear to be in the first two miles, but they are not the poles with the highest risk. A spot check on the inspection reports is spotty at best. Recommend new project in the 2 to 5 year plan for at the worst actors. The first two miles have very old poles, although they do not rank high on the TCM. A spot check on the inspection reports show that the conditions reported is the condition for the worst acting component on the line, not the wood structure. This likely impacted many of the younger poles with higher POFs. Propose a targeted replacement for worst actors. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Wood Poles | NA | 2024-04-05 | 37 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | Yes | Ex112926 | TBD | TBD | TBD | 70 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-03-01 | NA | 2030-12-31 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1063 | Colgate - Alleghany Wood Structure Repalcement |  |  | Alleghany CDP, Sierra ¦ Nevada ¦ Pike CDP, Sierra ¦ Sierra ¦ Yuba | Colgate - Alleghany current has 80 open and 13 recently closed 70Y tags. This is a Tier 2/3 area, so this will be a 2023 requirement. The 80 outstanding tags equates to $6.8 million in work. This was noted as a worst acting line for North Valley. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | 2024-04-02 | 70 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | Yes | Ex112927 | TBD | TBD | TBD | 70 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-01-01 | NA | 2031-12-31 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7411.32 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1064 | Contra Costa - Pittsburg Pole Relocation (024/034 to 025/019) |  |  | Antioch, Contra Costa ¦ Pittsburg, Contra Costa | Contra Costa-Pittsburg 60kV – ETL.6540, has approximately 34 wood poles between 024/024 to, and including 025/019, many of which are tagged as in swamp. Seven of these poles failed PTT in Sept 2022 and cannot be restored. We have a 5700’ Boardwalk construction project proposed for Contra Costa – Pittsburg between structures 024/034 and 025/019, but it makes more sense to relocate the line out of the marshland which has 33% soil corrosivity and lies underwater much of the time.. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Wood Poles | NA | 2023-10-02 | 80 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence, Corrosion |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | EX112653 | TBD | TBD | TBD | 70 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-01-15 | NA | 2029-01-15 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1065 | KING CITY-COBURN #1 Wood Structures |  |  | Greenfield, Monterey ¦ King City, Monterey ¦ Monterey ¦ Soledad, Monterey | KING CITY-COBURN #1, Over 15% of this line has less than 100% remaining strength per intrusive PTT inspections. Average age is 47 years old (second quartile). Approximately 94% of poles have a TCM Annual Probability of Failure of over 10% , which is significant considering there are over 350 wood poles on this line. Average annual probability of failure TCM is 22.94%, accounting for 14.8% of the entire line. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Wood Poles | NA | 2024-04-09 | 47 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | Yes | Ex112931 | TBD | TBD | TBD | 70 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2031-03-01 | NA | 2027-12-31 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1066 | LAYTONVILLE-WILLITS Repl Wood Structures |  |  | Laytonville CDP, Mendocino ¦ Mendocino | LAYTONVILLE-WILLITS has a high Probability of failure. Currently 127 wood poles on the line, with 36 existing and 6 recently completed 70Y Tags in the past year (~30%). Average age is 42.76 years old, with nearly 30% of the pole line over 70 years old. Approximately 43% of poles have a TCM Annual Probability of Failure of over 10%. Average annual probability of failure TCM is 15.57%. Average pole condition score is 1.76 and number of condition scores of 3 or higher is 30% (Top 15%). | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Wood Poles | NA | 2024-04-02 | 70 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | Yes | Ex112932 | TBD | TBD | TBD | 70 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-12-01 | NA | 2029-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1152.872 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1067 | TLine Estimating Contractor (Eng Poles) |  |  | NA | Bucket for Contractor Pole Replacements | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | 456 | NA | NA | 5511959 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 4589.0268 | 4589.0268 | 0 | -16.9087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4589.0268 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | -15.604 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1068 | TLine Construction by Contractor A |  |  | NA | Bucket for contractor replacement of wood poles | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 31 | Not Available | 4 | NA | NA | 5509659 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 87978.6856 | 87978.6856 | 2.325 | -28.5667 | 0 | 0.1647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87978.6856 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2022 ¦ 2023 ¦ 2024 | 2.0981 | -24.7988 | 0 | 0.13854 | 6.1021 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1069 | TLine Construction Contractor-Eng Poles |  |  | NA | Bucket for contractor replacement of wood poles | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 31 | Not Available | 167 | NA | NA | 5513319 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 17938.6842 | 17938.6842 | 0.806 | 0 | -5.9271 | 0.494 | -9.0414 | 0 | 0 | 0 | 0 | 0 | 0 | 17938.6842 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2022 ¦ 2023 ¦ 2024 | 0.7641 | 0 | -5.6369 | 0.43709 | -9.67 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1070 | WMP - MWC 70Y Forecast |  |  | NA | Bucket for MWC 70 WSIP Work | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3563 | Not Available | 106 | NA | NA | 5534223 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 4704.0326 | 4704.0326 | 18291.8703 | -17331.9725 | 672.2355 | 3071.6156 | 0.2835 | 0 | 0 | 0 | 0 | 0 | 0 | 4704.0326 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 266.5019 | 1400.9321 | 2470.165 | 0.22679 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1071 | Pole Replacement - North Bay/Coast |  |  | NA | Bucket for Pole Replacements in North Bay/Coast | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion, Weather |  | NA | NA | NA | NA | 31 | Not Available | 39 | RBPPF - TBD | Yes | 5509220 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 17971.9156 | 17971.9156 | 93.0248 | 388.6172 | 739.3633 | 2941.3651 | 8124.8243 | 4513.3181 | 0 | 0 | 0 | 0 | 0 | 13458.5975 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 78.6018 | 342.9125 | 553.5918 | 2656.8186 | 6278.075 | 5393.6505 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1072 | Pole Replacement - North Valley |  |  | NA | Bucket for pole replacements in the North Valley region. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | NA | NA | NA | 31 | Not Available | 4 | RBPPF - TBD | Yes | 5509219 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 421704.623 | 421704.623 | 6971.203 | 19550.6322 | 36019.3465 | 118537.0799 | 157220.0201 | 16689.5768 | 0 | 0 | 0 | 0 | 0 | 405015.0462 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 6373.9827 | 17488.1812 | 30523.1616 | 109274.6281 | 139209.7812 | 18158.5121 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1073 | Pole Replacement Service Territory |  |  | NA | Bucket for replacement of wood poles across the service territory | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 197 | Not Available | 1 | RBPPF - TBD | Yes | 5508619 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 171416.6276 | 171416.6276 | 19184.5945 | 8077.3699 | 14297.1306 | 49560.346 | 57000.7101 | 2005.5637 | 0 | 0 | 0 | 0 | 0 | 169411.0639 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 18883.5605 | 7117.8316 | 11657.4659 | 44026.5821 | 49952.7598 | 3637.6967 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1074 | 70Y 2020 Planning and Construction |  |  | NA | Bucket for replacement of wood poles in 2020 | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 31 | 2. Overhead With Strong Safety Link | 4 | RBPPF - TBD | Yes | 5529956 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 14186.4206 | 14186.4206 | 1988.4395 | 3442.5179 | 6218.9541 | 1741.556 | 746.8982 | 38.3231 | 0 | 0 | 0 | 0 | 0 | 14148.0975 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1742.9394 | 3150.0999 | 5511.3269 | 1624.8675 | 664.3631 | 59.2725 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1075 | Pole Replacement - Eureka BL |  |  | NA | Bucket for replacement of wood poles in Eureka area | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | Not Available | Not Available | 39 | RBPPF - TBD | Yes | 5519159 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 3891.8069 | 3891.8069 | 351.9312 | 1651.3162 | 606.5095 | 1043.4877 | 214.0625 | 5.5176 | 0 | 0 | 0 | 0 | 0 | 3886.2893 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 315.4429 | 1434.4404 | 527.0837 | 1042.9026 | 188.0231 | -273.2864 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1076 | Pole Replacement - South Coast Region |  |  | NA | Bucket for replacement of wood poles in the south coast region | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 31 | Not Available | 13 | RBPPF - TBD | Yes | 5502913 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 217467.3667 | 217467.3667 | 1606.7275 | 3429.9646 | 3671.8914 | 16617.7593 | 34986.5318 | 5287.0596 | 0 | 0 | 0 | 0 | 0 | 212180.3071 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1433.8146 | 2997.5282 | 2930.0239 | 14991.4484 | 30616.4522 | 8778.5774 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1077 | WMP - Pole Replacements |  |  | NA | Bucket for replacement of wood poles in Tier 2 & 3 HFTDs | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3563 | 1. Work that prevents fire ignition | 1 | RBPPF - TBD | Yes | 5533586 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 578530.1155 | 578530.1155 | 162324.4292 | 180084.1607 | 165370.8691 | 46688.9044 | 22019.7342 | 1836.1307 | 0 | 0 | 0 | 0 | 0 | 576693.9848 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 146575.4738 | 162555.3587 | 152387.681 | 42765.695 | 19572.1931 | 627.7303 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1078 | 70Y 2024 Planning and Construction |  |  | NA | Forecast placeholder for replacement of wood poles in 2024 | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Wood Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5531938 | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | TRUE | NA | NA | 0 | 760673.2432 | 0 | 0 | 0 | 0 | 0 | 156616 | 222142 | 157980.3059 | 142475.9425 | 121183.8987 | 114821.6701 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1079 | Jessup Tap 115kV |  |  | Shasta | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Pole/Tower | Replace | T.0000126 | Asset Condition | Age/Condition - Replace Wood Poles | NA | 2022-10-12 | 48 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5541501 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 6 | 70 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6191-E | 2021-05-12 | Approved | 2021 | Operational | 2 | 2021-08-09 | 2021-11-30 | 2021-10-27 | NA | FALSE | 18400 | NA | 1282.869 | 1282.869 | 0 | 26.5336 | 1204.2576 | 52.0778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1282.869 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1086.3758 | 45.9802 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1080 | Woodleaf-Palermo 115kV-Structure Replac |  |  | Butte ¦ Forbestown CDP, Butte ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte | This project proposes to replace aging structures and insulators on the Woodleaf – Palermo 115 kV Line and associated 115 kV Tap lines to help mitigate high-risk components on these line. Scope in details: • Replace 124 of the 232 structures on the Woodleaf – Palermo 115 kV Line with steel structures; • Replace 69 insulators on the Woodleaf – Palermo 115 kV Line; • Perform field analysis on existing structures, Nos. 000/005, 006/053, and 013/128 on the Woodleaf – Palermo 115 kV Line to verify if replacements are needed; • Perform field analysis on 0.02 miles of Sly Creek Tap 115 kV from pole no. 000/006 to 000/008 to verify the age of the conductor and to determine if reconductor is needed; • Replace 3 structures, pole nos. 003/031A, 003/031B, and 003/031C and perform field analysis on 3 structures, pole nos. 002/019, 003/032, and 004/038 to determine if structure and insulator replacements are needed on the Sly Creek Tap 115 kV; • Replace all insulators on the Sly Creek Tap 115 kV; • Replace 1 structure, pole no. 004/039 and conduct field analysis on 3 structures, pole nos. 000/001A, 000/001B, and 000/001C to determine if structure and insulator replacements are needed on the Forbestown Tap 115 kV; • Perform field analysis on 9 structures, pole nos. 000/002, 001/008B, 001/008C, 001/010C, 001/011, 002/015, 002/016, 002/018A, and 002/018C, to verify if structure and insulator replacements are needed on the Kanaka Tap 115 kV; • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Wood Poles | NA | 2024-04-04 | 62 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 4703 | 2. Overhead With Strong Safety Link | 151 | RBPPF - TBD | Yes | 5789804 | T.0005758 | Woodleaf-Palermo 115kV-Structure & Insul | 3 | 70 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-02-24 | NA | 2028-03-22 | NA | FALSE | NA | NA | 17.7744 | 5073.4886 | 0 | 0 | 1.3537 | 8.8893 | 7.3235 | 1.2875 | 0 | 0 | 0 | 0 | 900 | 17.5665 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1081 | Replace Deteriorated Boardwalks - 2018 |  |  | NA | Bucket for replacement of deteriorated boardwalks in 2018 & 2019 | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Salt Pond |  | NA | NA | NA | NA | 190 | Not Available | 7 | NA | NA | 5507682 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 49338.6856 | 49338.6856 | 13255.2906 | -221.2773 | -10.7452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49338.6856 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 13036.2386 | 2243.6989 | 441.9375 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1082 | Replace Deteriorated Boardwalks 2020 |  |  | NA | Bucket for replacement of deteriorated boardwalks in 2020 | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Salt Pond |  | NA | NA | NA | NA | Not Available | 9. Reliability (Low Safety Risk) | Not Available | Tier 4 | No | 5790558 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 20314.2233 | 20314.2233 | 0 | 12042.1299 | 7246.4127 | 1026.0985 | -0.4178 | 0 | 1162.854 | 719.756 | 4513.774 | 0 | 0 | 20314.2233 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 12809.0672 | 5464.7182 | -0.41779 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1083 | Boardwalks Planning |  |  | NA | Forecast placeholder for replacement of boardwalks for t-line access | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5549695 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | TRUE | NA | NA | 0 | 87771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1084 | Newark Replace Boardwalk 2022 -2023 |  |  | Fremont, Alameda ¦ Mountain View, Santa Clara ¦ Newark, Alameda ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Sunnyvale, Santa Clara | Replace approximately 2.4 miles of existing boardwalk for Newark-Ames #2, Newark-Ames #1, and Newark-Ames #3. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | 2023-11-20 | 51 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 2.4 | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5802621 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-12-21 | 2023-03-16 | 2023-12-22 | Weather | TRUE | 6629 | NA | 5163.8445 | 5163.8445 | 0 | 0 | 0 | 23.9956 | 5139.849 | 0 | 0 | 0 | 0 | 0 | 0 | 5163.8445 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 4617.8514 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1085 | Ignacio-Sobrante Replace Boardwalk 2022 |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace boardwalks on Ignacio-Sobrante 230 kV line | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | 2024-04-03 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 0.3 | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5800400 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-13 | NA | 2022-10-13 | NA | FALSE | NA | NA | 1482.729 | 1482.729 | 0 | 0 | 440.89 | 1041.5746 | 0.2643 | 0 | 0 | 0 | 0 | 0 | 0 | 1482.729 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1419.9319 | 0.25259 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1086 | Ravenswood-Ames #1 Replace Boardwalk 2022 |  |  | East Palo Alto, San Mateo ¦ Menlo Park, San Mateo ¦ Mountain View, Santa Clara ¦ Palo Alto, Santa Clara ¦ Santa Clara | Replace boardwalks on Ravenswood-Ames #1 115 kV line | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | 2024-04-09 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 4.58 | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5800399 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-06-23 | NA | 2022-01-14 | NA | FALSE | NA | NA | 15549.1617 | 15549.1617 | 0 | 0 | 13075.5308 | 2471.813 | 1.8179 | 0 | 0 | 0 | 0 | 0 | 0 | 15549.1617 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 15516.0819 | 1.8179 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1087 | Repl Deteriorated Boardwalks - Ignacio |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Black Point-Green Point CDP, Sonoma ¦ Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Orinda, Contra Costa ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | Replace deteriorated wooden boardwalk (access) with new plastic lumber based boardwalk. (Ignacio Sobrante between TWR 16/69 and 23/69.) | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | 2024-04-03 | 31 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 ¦ 115 ¦ 60 | NA | 190 | Not Available | 15 | NA | NA | 5786498 | NA | NA | NA | 71 | NA | NA | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-02-13 | 2019-12-31 | 2020-02-28 | NA | FALSE | 8500 | NA | 7960.9067 | 7960.9067 | 7065.1053 | 887.9792 | 7.8 | 0.0222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7960.9067 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 5785.0087 | 5.6301 | 0.01604 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1088 | Ravenswood San Mateo #2 - Repl Boardwalk |  |  | Bay Point CDP, Contra Costa ¦ Contra Costa ¦ Pittsburg, Contra Costa | Scope of work for construction services includes full boardwalk replacement, disposal, and installation of new 3X plastic. The existing boardwalk is located off Hwy 84 at the Ravenswood substation and would address a total of 33 towers. It will start from the West side of the substation at tower 000/001 and from the East side at tower 000/002. The existing wood boardwalk is mainly composed of a 2X planking system with some existing 3X planking sections with single handrailing. This boardwalk is all lumber. boardwalk of approximately 14,221 lineal feet (LF). Removal | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | 2021-12-08 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 3.07 | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5799001 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-09-01 | NA | 2022-12-28 | NA | FALSE | NA | NA | 6921.0178 | 6921.0178 | 0 | 0 | 0 | 7042.5152 | -121.4975 | 0 | 0 | 0 | 0 | 0 | 0 | 6921.0178 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 6918.3291 | -119.3378 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1089 | Pittsburg-Tidewater Replace Boardwalk 2022 |  |  | Bay Point CDP, Contra Costa ¦ Contra Costa ¦ Pittsburg, Contra Costa | The work will replace approximately 4,910 linear feet existing boardwalk to Pittsburg-Tidewater 230kV Towers 000/002, 000/003, and 000/004, and adjacent structures on Pittsburg-Eastshore 230kV, Pittsburg-Tesla #1 230kV, Pittsburg-San Ramon 230kV, Pittsburg-Martinez #1 115kV, Pittsburg-Clayton #1 115kV, Pittsburg-Clayton #3 115kV, and Pittsburg-Columbia Steel 115kV. Approximately 2,020 feet of existing boardwalk will be replaced in place, and 2,820 feet require replacement of cross braces, planks, and handrails on top of existing pilings that will remain. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Boardwalks | NA | 2021-12-08 | 21 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.93 | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5800398 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-02-07 | NA | 2022-10-18 | NA | FALSE | NA | NA | 2301.8044 | 2301.8044 | 0 | 0 | 79.7683 | 2221.8699 | 0.1662 | 0 | 0 | 0 | 0 | 0 | 0 | 2301.8044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1931.3802 | 0.13844 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1090 | TLine Access Road Work |  |  | NA | Bucket for TLine Access Road Work | Other | Replace | NA | Other [See Notes] | Construct Roads/Gates/Culverts | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5547687 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 5062.0286 | 5062.0286 | 1572.5668 | 622.8996 | 1010.4871 | 657.7747 | 816.806 | 8.1949 | 0 | 0 | 0 | 0 | 0 | 5053.8337 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1572.5668 | 622.8996 | 1008.4352 | 648.6625 | 827.9701 | 11.0478 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1091 | TLine Access Road Work |  |  | NA | Bucket for T-line access road work | Other | Replace | NA | Other [See Notes] | Construct Roads/Gates/Culverts | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 100 | 9. Reliability (Low Safety Risk) | Not Available | Tier 5 | No | 5502914 | NA | NA | NA | 71 | NA | NA | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 56076.645 | 105070.6118 | 4697.0279 | 6577.8574 | 8855.2211 | 7946.1006 | 7204.0687 | 14488.0134 | 11000.01 | 10000 | 10000 | 10000 | 10000 | 55576.9234 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 4682.7695 | 6333.5391 | 8856.0281 | 7658.1068 | 7691.6889 | 1192.8242 | 0% | NA | TBD | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1092 | TLine Access Road Work - New Exp |  |  | NA | Bucket for T-Line Access Road Work | Other | Replace | NA | Other [See Notes] | Construct Roads/Gates/Culverts | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5550888 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 4419.1442 | 4419.1442 | 0 | 0 | 0 | 2298.9384 | 2005.6001 | 114.6057 | 0 | 0 | 0 | 0 | 0 | 4304.5385 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2298.9384 | 2005.6001 | 157.8599 | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1093 | Cortina #3 |  |  | Colusa ¦ Colusa, Colusa ¦ Williams, Colusa | Vegeation Management of the CORTINA #3 circuit. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2024-04-10 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 24.8 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5554105 | TBD | TBD | TBD | 71 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300 | 1170 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1094 | Elk-Gualala |  |  | Anchor Bay CDP, Mendocino ¦ Manchester CDP, Mendocino ¦ Mendocino ¦ Point Arena, Mendocino | Vegeation Management of the ELK-GUALALA circuit. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2024-04-11 | NA | NA | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 29 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5554112 | TBD | TBD | TBD | 71 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 3600 | 3600 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1095 | Essex Jct-Arcata-Fairhaven |  |  | Arcata, Humboldt ¦ Humboldt ¦ Manila CDP, Humboldt ¦ Samoa CDP, Humboldt | Vegeation Management of the ESSEX JCT-ARCATA-FAIRHAVEN circuit. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2023-11-27 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 16.1 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5793182 | T.0006637 | Essex Jct-Arcata-Fairhaven | 1 | 71 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 2430 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1096 | Fort Bragg-Elk |  |  | Albion CDP, Mendocino ¦ Caspar CDP, Mendocino ¦ Fort Bragg, Mendocino ¦ Little River CDP, Mendocino ¦ Mendocino ¦ Mendocino CDP, Mendocino | Vegeation Management of the FORT BRAGG-ELK circuit. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2024-04-05 | NA | NA | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 24 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5554113 | TBD | TBD | TBD | 71 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 3000 | 3000 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1097 | Humboldt Bay-Humboldt #1 |  |  | Cutten CDP, Humboldt ¦ Eureka, Humboldt ¦ Humboldt ¦ Humboldt Hill CDP, Humboldt ¦ Pine Hills CDP, Humboldt | Vegeation Management of the HUMBOLDT BAY-HUMBOLDT #1 circuit. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2023-11-15 | NA | NA | TBD | TBD | Zone 1 - HHZ, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 6.3 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5554106 | TBD | TBD | TBD | 71 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 1200 | 990 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1098 | Humboldt Bay-Rio Dell Jct |  |  | Fortuna, Humboldt ¦ Humboldt ¦ Humboldt Hill CDP, Humboldt ¦ Hydesville CDP, Humboldt ¦ Pine Hills CDP, Humboldt | Vegeation Management of the HUMBOLDT BAY-RIO DELL JCT circuit. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2024-04-03 | NA | NA | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 18.4 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5554107 | TBD | TBD | TBD | 71 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 1200 | 3990 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1099 | Humboldt-Maple Creek |  |  | Humboldt | Vegeation Management of the HUMBOLDT-MAPLE CREEK circuit. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2024-04-08 | NA | NA | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 14.1 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5554108 | TBD | TBD | TBD | 71 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 900 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1100 | Santa Rosa-Corona |  |  | Cotati, Sonoma ¦ Penngrove CDP, Sonoma ¦ Petaluma, Sonoma ¦ Rohnert Park, Sonoma ¦ Santa Rosa, Sonoma ¦ Sonoma | Vegeation Management of the SANTA ROSA-CORONA circuit. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2024-04-09 | NA | NA | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 15.4 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5554109 | TBD | TBD | TBD | 71 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 1800 | 1320 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1101 | SONOMA-PUEBLO |  |  | Napa ¦ Napa, Napa ¦ Sonoma ¦ Sonoma, Sonoma | Vegeation Management of the SONOMA-PUEBLO circuit. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2023-12-20 | NA | NA | TBD | TBD | Zone 1 - HHZ, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 18.5 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5554110 | TBD | TBD | TBD | 71 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 2100 | 1914 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1102 | Valley Springs #2 |  |  | Calaveras ¦ San Joaquin ¦ Valley Springs CDP, Calaveras | Vegeation Management of the VALLEY SPRINGS #2 circuit. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2023-12-20 | NA | NA | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 37.3 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5554111 | TBD | TBD | TBD | 71 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 1980 | 2400 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1103 | Relicense FERC Elect Transmission Lines |  |  | NA | Bucket for relicensing transmission lines in national forests | Transmission Line - Right of Way | Replace | NA | Reliability | Safety - Line Right of Way Access | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5514479 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1602.5013 | 1602.5013 | 247.8428 | 4.4954 | 5.6098 | 42.3604 | 23.406 | 0.4007 | 0 | 0 | 0 | 0 | 0 | 1602.1006 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 247.8428 | 4.4954 | 5.6098 | 42.3604 | 23.406 | 0.40066 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1104 | Veg Mgt Reliability-2017/2018 Circuits |  |  | NA | Bucket for Vegetation Management for transmission circuits in 2017 & 2018 | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 430 | Not Available | Not Available | NA | NA | 5529599 | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2383.2898 | 2383.2898 | 50.6162 | 0 | 0 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2383.2898 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2022 ¦ 2024 | 50.6162 | 0 | 0 | 0.105 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1105 | Veg Mgt Reliability-2019 Circuits |  |  | NA | Bucket for Vegetation Management for transmission circuits in 2019 | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 430 | Not Available | Not Available | NA | NA | 5529943 | NA | NA | NA | 71 | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 16962.7424 | 16962.7424 | 5541.2244 | 1329.4582 | 0 | 2550.501 | 23.7076 | 0 | 0 | 0 | 0 | 0 | 0 | 16962.7424 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2022 ¦ 2023 ¦ 2024 | 5541.2244 | 1329.4582 | 0 | 2550.501 | 23.7076 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1106 | Veg Mgt Reliability-2020 Circuits |  |  | NA | Bucket for Vegetation Management for transmission circuits in 2020 | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 430 | 1. Work that prevents fire ignition | Not Available | Tier 4 | No | 5529944 | NA | NA | NA | 71 | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 38735.4784 | 38735.4784 | 13583.4071 | 4020.3768 | 3283.8565 | 2810.5761 | 92.7002 | 35.4582 | 0 | 0 | 0 | 0 | 918 | 38700.0202 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 13571.0052 | 4032.7787 | 3283.8565 | 2810.5761 | 92.7002 | 35.4582 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1107 | Veg Mgt Reliability-2021 Circuits |  |  | NA | Bucket for Vegetation Management for transmission circuits in 2021 | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 430 | 1. Work that prevents fire ignition | Not Available | Tier 4 | No | 5529945 | NA | NA | NA | 71 | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 38076.1745 | 38076.1745 | 6694.967 | 5899.7163 | 4880.8355 | 11982.0285 | 2785.1807 | 54.9167 | 4500 | 3417 | 0 | 0 | 2190 | 38021.2578 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 6694.967 | 5899.7163 | 4880.8355 | 11943.5431 | 2711.2004 | 60.7824 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1108 | Veg Mgt Reliability-2022 Circuits |  |  | NA | Bucket for Vegetation Management for transmission circuits in 2022 | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 430 | 1. Work that prevents fire ignition | Not Available | Tier 4 | No | 5529946 | NA | NA | NA | 71 | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 55251.931 | 55251.931 | 7231.6514 | 10172.5758 | 12983.8268 | 10259.5976 | 11605.6254 | 1729 | 3600 | 330 | 0 | 0 | 3198 | 53522.931 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 4117.0836 | 14179.33 | 13014.9863 | 9945.5276 | 3257.0201 | 369.2685 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1109 | Veg Mgt Reliability-2023 Circuits |  |  | NA | Bucket for Vegetation Management for transmission circuits in 2023 | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 430 | 1. Work that prevents fire ignition | Not Available | Tier 4 | No | 5529947 | NA | NA | NA | 71 | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 51723.9068 | 168640.7268 | 8097.1081 | 17823.3779 | 10528.4552 | 6718.6947 | 6385.0685 | 25973.6863 | 7704 | 4800 | 6510 | 3960 | 3192 | 51166.9205 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 8097.1081 | 17823.3779 | 10528.4552 | 6717.7808 | 6385.0004 | 1120.3192 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1110 | Fulton-Calistoga Land Rights Project |  |  | Deer Park CDP, Napa ¦ Fulton CDP, Sonoma ¦ Kenwood CDP, Sonoma ¦ Lake ¦ Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma | The Fulton-Calistoga 60 kV Line is located in Sonoma and Napa Counties. An emergency project was initiated in 2018 to reconductor 4.5 miles of the line from Fulton to Rincon Tap, which was damaged in the Tubbs Fire in 2017. The project scope was later expanded to completely rebuild the 16-mile section of the line from Fulton to St. Helena Junction, given the deteriorated equipment on the line and the line being in a Tier 3 high fire threat district (HFTD). During the detailed engineering phase of the emergency project, field inspections and a review of PG&E’s land rights documents found that some of the old documents did not meet the full legal requirements for sections of the existing line in the City of St. Helena. The scope of the Fulton-Calistoga Land Rights Project includes: • Determining what modifications are needed in the land rights documents with affected property owners to ensure full legal compliance; and • Getting the revised documents approved by PG&E and the affected property owners. Should some property owners refuse to agree to the revised land rights, the Company may need to initiate eminent domain (ED) proceedings in California State Court to complete this work. | Other | New | NA | Reliability | Safety - Line Right of Way Access | NA | 2024-04-09 | NA | NA | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5550726 | T.0006329 | Fulton-Calistoga Land Rights Project | 2 | 71 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | NA | NA | 2024-12-31 | NA | FALSE | NA | NA | 126.6488 | 2436.6488 | 0 | 0 | 0 | 0 | 126.6488 | 0 | 0 | 0 | 0 | 0 | 0 | 126.6488 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 0 | 0 | 126.6488 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1111 | Gualala-Monte RioColgate 60kV ROW Reliab |  |  | Mendocino | The purpose of this project is to improve the reliability of Gualala-Monte Rio 60kV line. This line is approximately 44 miles and has a total of 463 structures. This line presents a very high contribution to SAIFI from outages related to tree, weather and unknown conditions. The outages referred to in this document were recorded from 2007 to April of 2011. This project seeks to expand the Right of Way for the Gualala-Monte Rio 60kV line in order to prevent future outages due to trees; and possible improvements with the weather and unknown conditions. If this work is not completed, this line will continue to decrease in reliability with the possibility of more outages in the future. | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2024-02-15 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 44 | 0.41125 | 60 | NA | 412 | 1. Work that prevents fire ignition | Not Available | NA | NA | 5745743 | P.10541 | Gualala-Monte Rio: Land Acquis | 1 | 71 | NA | 2011 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-05-14 | 2020-01-27 | 2020-10-30 | Land Rights | FALSE | 1100 | NA | 1333.8607 | 1333.8607 | 65.679 | 61.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1333.8607 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 1333.8607 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1112 | HUMBOLDT-TRINITY |  |  | Humboldt ¦ Junction City CDP, Trinity ¦ Trinity ¦ Weaverville CDP, Trinity | Vegetation management of Humboldt-Trinity 115 kV line | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2024-04-11 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 68.58 | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5795263 | T.0007010 | HUMBOLDT- TRINITY | 1 | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-12-29 | NA | 2023-12-31 | NA | FALSE | NA | NA | 5021.9104 | 5021.9104 | 0 | 0 | 1753.545 | 501.6215 | 2693.3269 | 73.4171 | 0 | 0 | 0 | 0 | 0 | 4948.4933 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1113 | TRINITY-MAPLE CREEK |  |  | Humboldt ¦ Junction City CDP, Trinity ¦ Trinity ¦ Weaverville CDP, Trinity | Vegetation management of Trinity-Maple Creek 60 kV line | Transmission Line - Right of Way | Removal | NA | Reliability | Safety - Line Right of Way Access | NA | 2024-04-12 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 55.49 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5795264 | T.0007011 | TRINITY- MAPLE CREEK | 1 | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-12-29 | NA | 2024-12-31 | NA | FALSE | NA | NA | 2645.5968 | 2645.5968 | 0 | 0 | 164.1614 | 454.8962 | 1995.5991 | 30.9401 | 2325 | 300 | 0 | 0 | 0 | 2614.6567 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1114 | Low Pressure Trip Cabinet replacement |  |  | NA | Forecast placeholder for Low Pressure Trip Cabinet replacement | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | No | Tx001999 | NA | NA | NA | 72 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1115 | New overhead to underground line conversions |  |  | NA | Forecast placeholder for New overhead to underground line conversions | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | EX112178 | NA | NA | NA | 72 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1116 | Pipe Type Cable Replacement (1 mile) |  |  | NA | Forecast placeholder for Pipe Type Cable Replacement (1 mile) | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | No | Tx002008 | TBD | TBD | TBD | 72 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1117 | ETL UG Replace System_Planning |  |  | NA | Forecast placeholder for replacement of underground system | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5543226 | NA | NA | NA | 72 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1118 | Repl Trans Line UG-ETM (System |  |  | NA | Forecast placeholder for replacement of underground transmission line | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5502935 | NA | NA | NA | 72 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2013 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 162.8097 | 162.8097 | 0 | 0 | 0 | 0 | 162.8097 | 0.0982 | 0 | 0 | 0 | 0 | 2500 | 162.7115 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1119 | Transmission Underground Capital Projects |  |  | NA | Forecast placeholder for Transmission Underground Capital Projects | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | No | EX112180 | NA | NA | NA | 72 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1120 | ETL CEM Stock |  |  | NA | PG&E’s Transmission Line Asset Management team is proposing purchasing and properly storing emergency stock of the Electric Transmission Underground cables and associated hardware: cable splices cable terminations, etc. (further as hardware). Such cables and associated hardware are considered “long lead items” and not readily available in case of emergency. | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5802562 | T.0009802 | CEM for ETU Cables | 1 | 72 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 16.1338 | 16.1338 | 0 | 0 | 0 | 0 | 0 | 13.7578 | 6000 | 7000 | 6000 | 4000 | 2000 | 2.3759 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 1121 | Improve Cathodic Protection |  |  | NA | Bucket for cathodic protection improvements for underground transmission circuits | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 739 | 4. Underground / Network (Strong Safety Link) | Not Available | Tier 4 | No | 5505219 | NA | NA | NA | 72 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1160.8611 | 1160.8611 | 54.1834 | 330.2164 | 8.0867 | 97.3899 | 1.5254 | 0 | 0 | 0 | 0 | 0 | 1200 | 1160.8611 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 54.1834 | 330.2164 | 1.4007 | 104.0759 | 1.5254 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1122 | Pilot: Pipe-Type UG Cable Replacement |  |  | San Mateo ¦ South San Francisco, San Mateo | Replace the underground segment of the San Mateo - Martin #4 115kV pipe-type cable circuit in its existing conduit with non-pressurized Triplex XLPE cable. Because Pipe Type cable is no longer manufactured anywhere in the world and virtually all new underground transmission line circuits installed in the industry are of the cross-linked polyethylene (XLPE) type, PG&E Electric Standards initiated a pilot to install a replacement triplex XLPE cable that will fit into the existing steel pipe. | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | 2023-03-10 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.2 | NA | 115 | NA | 739 | 4. Underground / Network (Strong Safety Link) | Not Available | NA | NA | 5773938 | T.0002705 | Pilot: Pipe-Type UG Cable Replacement | 1 | 72 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-03 | 2019-02-20 | 2020-05-19 | Project Design | FALSE | 14169 | NA | 15343.054 | 15343.054 | 9364.4277 | 4744.4866 | 1.9367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15343.054 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 14124.0543 | 1.7767 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1123 | Jefferson-Las Pulgas Cable Replacement |  |  | San Mateo | The Jefferson-Las Pulgas Cable Replacement Project is located in San Mateo County. This 1100-foot long, cross-linked polyethylene (XLPE) 60 kV underground cable is located where the Jefferson-Las Pulgas Line crosses Alameda de las Pulgas. This project will replace the old cableconductor and the connections at the riser poles on Woodside Road and Hull Avenue, where the linetransitions from overhead to underground. | Transmission Line - Underground | Replace | TBD | Asset Condition | Age/Condition - Replace Underground System | NA | 2024-01-05 | 36 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 0.18 | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5793678 | T.0006738 | Jefferson-Las Pulgas Cable Replacement | 1 | 72 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-11-15 | NA | 2028-01-14 | NA | FALSE | NA | NA | 73.1154 | 7588.6487 | 0 | 0 | 33.9579 | 26.2219 | 11.8808 | 5.4636 | 0 | 0 | 0 | 0 | 2450 | 72.0606 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1124 | Los Esteros-Metcalf Cable Rack Work |  |  | Fremont, Alameda | The Los Esteros 230 kV Cable Rack Replacement Project will reduce the risk of a failure of the UG cable section on the Newark-Los Esteros and the Los Esteros-Metcalf 230 kV Lines by performing the following work: Replace all cable racks in the 10 manholes on both 230 kV lines, and Add sacrificial anodes onto the racks to prolong the cable rack life expectancy.Maintenance inspections of the underground cable sections have found that the cable racks in the manholes have severe corrosion. | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | 2024-01-01 | 20 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 2.8 | NA | 230 | NA | 240 | 4. Underground / Network (Strong Safety Link) | 1459 | NA | NA | 5790378 | T.0005870 | Los Esteros 230kV Cable Rack Replacement | 2 | 72 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-03-14 | 2022-05-11 | 2022-04-26 | NA | FALSE | 5710 | NA | 2521.362 | 2521.362 | 0 | 24.8869 | 1899.6614 | 596.8137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2521.362 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 2521.362 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1125 | NEWARK-LOS ESTEROS CABLE RACK WORK |  |  | Fremont, Alameda | The Los Esteros 230 kV Cable Rack Replacement Project will reduce the risk of a failure of the UG cable section on the Newark-Los Esteros and the Los Esteros-Metcalf 230 kV Lines by performing the following work: Replace all cable racks in the 10 manholes on both 230 kV lines, and Add sacrificial anodes onto the racks to prolong the cable rack life expectancy.Maintenance inspections of the underground cable sections have found that the cable racks in the manholes have severe corrosion. | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | 2024-01-01 | 21 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 2.8 | NA | 230 | NA | 240 | 4. Underground / Network (Strong Safety Link) | 1459 | NA | NA | 5790379 | T.0005870 | Los Esteros 230kV Cable Rack Replacement | 2 | 72 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-04-27 | 2022-05-11 | 2022-06-07 | NA | FALSE | 5710 | NA | 2420.6901 | 2420.6901 | 0 | 23.1885 | 1234.2831 | 1163.2185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2420.6901 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 2420.6901 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1126 | East Grand-San Mateo Cable Replacement |  |  | San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | TBD | Asset Condition | Age/Condition - Replace Underground System | NA | 2024-03-04 | 51 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.22 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5793679 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-05-17 | NA | 2028-06-08 | NA | FALSE | NA | NA | 1816.9472 | 11130.9829 | 0 | 196.2707 | 560.3938 | 409.0965 | 620.5019 | 141.778 | 0 | 0 | 0 | 0 | 7651 | 1786.2628 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1127 | Martin-Millbrae No. 1 Cable Replacement |  |  | San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | TBD | Asset Condition | Age/Condition - Replace Underground System | NA | 2024-03-04 | 51 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 0.22 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798142 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-05-29 | NA | 2027-03-03 | NA | FALSE | NA | NA | 19.8802 | 8677.7553 | 0 | 0 | 0 | 2.5191 | 17.0432 | 1.5279 | 0 | 0 | 0 | 0 | 1326 | 19.5623 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1128 | Martin-SF Airport Cable Replacement |  |  | San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | TBD | Asset Condition | Age/Condition - Replace Underground System | NA | 2024-03-04 | 51 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 0.23 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798143 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-02-03 | NA | 2027-05-18 | NA | FALSE | NA | NA | 20.8116 | 8800.3967 | 0 | 0 | 0 | 3.7745 | 16.4212 | 1.8825 | 0 | 0 | 0 | 0 | 1076 | 20.1958 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1129 | San Mateo-Martin No. 3 Cable Relocation |  |  | San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | TBD | Asset Condition | Age/Condition - Replace Underground System | NA | 2024-03-04 | 51 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 0.21 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798140 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-07-30 | NA | 2026-06-29 | NA | FALSE | NA | NA | 514.5295 | 5021.9776 | 0 | 0 | 0 | 99.0178 | 398.5833 | 48.4363 | 0 | 0 | 0 | 0 | 799 | 497.601 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1130 | San Mateo-Martin No. 6 Cable Relocation |  |  | San Mateo ¦ South San Francisco, San Mateo | The San Bruno Interchange 115 kV Upgrade Project is located in San Mateo County. This project will address capacity issues on the six 115 kV underground cables at the San Bruno Interchange (SBI). A pilot project was recently completed that replaced the old pipe-type cable conductor on one of the lines in the SBI corridor with a new triplex cable. During the engineering work for that project, it was found that some of the soil conditions around the cables in the corridor were different than what was modeled in the calculations to determine the ratings when the cables were first installed in the 1970’s. Thermal modeling studies by Black and Veatch and Power Delivery Consultants, Inc., are showing that the normal ratings on the six cables in the SBI corridor are noticeably lower than the 900-Amp ratings calculated back in the 1970’s. The rating for the cable on the East Grand-San Mateo Line, which is in the middle of the corridor, is significantly affected – and this is the most heavily loaded of the six 115 kV lines. This new project was initially planned to replace the cable on the East Grand-San Mateo Line with a higher capacity triplex cable. Since that option may not address the ratings issues for all cables in the SBI corridor, the project team will look at other options, which will include possibly relocating three of the 115 kV lines out of the corridor to increase the heat dissipation from the cables. | Transmission Line - Underground | Replace | TBD | Asset Condition | Age/Condition - Replace Underground System | NA | 2024-03-04 | 51 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 0.23 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798141 | T.0006739 | SAN BRUNO INTERCHANGE 115KV UPGRADE | 6 | 72 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-10-31 | NA | 2026-01-31 | NA | TRUE | NA | NA | 460.4105 | 9654.5892 | 0 | 0 | 0 | 99.6999 | 367.2191 | 21.5944 | 0 | 0 | 0 | 0 | 6738 | 466.919 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1131 | EO-SYSPLN 82 - ET WRO |  |  | NA | Forecast placeholder for load & generation interconnection projects | Transmission Line/Substation | New | NA | Work Requested by Others | Generation Interconnection | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | 6. Customer Commitments | Not Available | Tier 5 | No | 5533304 | NA | NA | NA | 82 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36439.3648 | 50957.2388 | 113179.1957 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 1132 | MW C82 Post-COD Work PG&E Funded |  |  | NA | Bucket for regulatory related WRO work | Transmission Line/Substation | New | NA | Work Requested by Others | Generation Interconnection | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | RBPPF - TBD | No | 5759001 | NA | NA | NA | 82 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1876.4005 | 1876.4005 | 53.8174 | 86.7302 | 83.1851 | 90.0846 | 99.296 | 16.8953 | 0 | 0 | 0 | 0 | 0 | 1859.5052 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,876 | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1133 | Newark-Ravenswood 230kV Line Raise |  |  | Fremont, Alameda ¦ Menlo Park, San Mateo ¦ Newark, Alameda | Raising of towers 000/004 and 000/005 on the Newark-Ravenswood 230kV line and replacing towers 006/045 and 006/046 on the Dumbarton-Newark 115kV line The Sobrato Organization is proposing a new, 469-unit residential development in the City of Newark. This development is called the Sanctuary West Residential Project and is located along the shore of the bay just west of Newark Substation. Stevenson Boulevard will be extended to create an access road to the development, and a new elevated roadway will need to be constructed over the UPRR tracks. The Newark-Ravenswood and Tesla-Ravenswood 230 kV Lines and the Dumbarton-Newark 115 kV Line are mounted on towers that cross over the UPRR tracks right where Stevenson Boulevard ends at the tracks. In order to provide adequate clearance between the new elevated roadway and the transmission lines, the developer has requested that PG&E raise both the 230kV and the 115 kV lines. The proposed work will modify Towers 000/004 and 000/005 on the 230 kV lines and replace Tower 006/045 and 006/046 on the115 kV line with a new TSP to achieve the appropriate clearances from the new roadway. | Transmission Line - Pole/Tower | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2023-12-21 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | NA | NA | 230 | NA | Not Available | 6. Customer commitments | Not Available | RBPPF - TBD | No | 5538439 | T.0005483 | Newark-Ravenswood 230kV Line Raise | 2 | 82 | NA | 2020 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-08-19 | 2024-07-01 | 2024-11-12 | NA | TRUE | 2160 | NA | -7.7755 | 1102.4858 | 0 | 28.379 | -66.3512 | -1122.4901 | 1131.9951 | 1128.2767 | 2.6764 | 0 | 0 | 0 | 0 | -28.4673 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 28.3691 | -66.3512 | -1122.4768 | 1137.692 | 23.4014 | 0% | 0% ¦ $0 | TBD | NA | 100% | 0%
| 1134 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC) has requested PG&E to serve the proposed data center. The project scope of work includes following: SUBSTATION • Relocate Bank #2 230 kV line to make room for the double circuit IC lines o Install two TSP’s and remove one TSP o Install three spans of conductor to reconnect the bank #2 • Install 230 kV complete BAAH Bay #5 o Three 230 kV breakers o Six 230 kV disconnects o Two 230 kV line disconnect switches o Wave-trap with 3 CCVT’s, with line tuner accessories o With an additional dead-end on the West side terminal for the IC • Install all line relays and controls for Bay #5 o Install additional conduits as needed o Install control wiring to all BAAH Bay #5 elements • Install 230 kV Dead-end East of bay #5 for the line disconnect switch and CCVT’s location for IC #2 line • Remove Line Trap and CCVT’s from Bay #4 • Install conduit extensions for fiber optic communications (protection) between PG&E and IC T-LINE • Two 230 kV Overhead (OH) Transmission lines made of 715.5 AAC conductor will be built to interconnect IC’s 230 kV substation to Eastshore 230 kV bus. The project will consist of 9 new Tubular Steel Poles (TSP) on drilled pier foundations, and about 0.5 double circuit miles of 230 kV transmission lines. TELEMETRY • Add telemetry from IC’s substation to PG&E system | Transmission Line - Conductor | New | T.0004581 | Work Requested by Others | Load Interconnection | NA | NA | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1 | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5794663 | T.0006960 | Private Load Interconnection Project | 5 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC: AL 6570-E | 2022-04-22 | Approved | 2022 | Construction (over 75%) | 3 | 2023-02-06 | 2023-06-30 | 2024-07-01 | Workforce | FALSE | 26700 | NA | -1836.0068 | 1326.7821 | 0 | 0 | 497.8649 | -3341.7926 | 1032.983 | 3137.7268 | 0 | 0 | 0 | 0 | 0 | -1810.9448 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | TBD | NA | 100% | 0% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - New Substation Alternative [Alternative Solutions and Costs - Costs] $15 Mil - $20 Mil ¦ $20 Mil - $30 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1135 | Private Load Interconnection Project |  |  |  | Construct new switching station and install additional conductor on the Morgan Hill-Llagas 115 kV tower line to a new switching station at the customer site | Transmission Line - Conductor | New | T.0004271 | Work Requested by Others | Load Interconnection | NA | 2024-04-10 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.16 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5547567 | T.0007676 | Private Load Interconnection Project | 6 | 82 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-01-23 | NA | 2027-01-29 | NA | FALSE | NA | NA | 176.2754 | 2545.0455 | 0 | 0 | 10.8115 | 129.0337 | 23.7731 | 824.5802 | 382.204 | 292.9933 | 881.6497 | 0 | 0 | 163.6183 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 0 | 0 | 0 | 139.8687 | 23.7731 | 15.36 | 0% | 0% ¦ $0 | TBD | NA | 44% | 56% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1136 | Private Load Interconnection Project |  |  |  | The Customer is planning on constructing a large data center facility, expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Trimble 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Loop the Newark-Trimble 115 kV Line into the new PG&E Switching Station; ● Reconductoring of 12.1 miles of the Newark-Trimble 115 kV Line from Newark to TSP 012/082; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The Customer has also requested that the two connections from the Newark-Trimble Line be routed separately from the PG&E switching station to the existing line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Work Requested by Others | Load Interconnection | NA | 2023-10-17 | 50 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Corrosion |  | 12.1 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5804165 | T.0009031 | Private Load Interconnection Project | 6 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2028-03-23 | NA | 2028-04-19 | NA | FALSE | NA | NA | 460.6322 | 9353.643 | 0 | 0 | 0 | 0 | 394.6072 | 925.4851 | 1366.1605 | 1422.3377 | 3543.3772 | 1693.9666 | 7.7086 | 394.6072 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 90% (The Trimble-Newark line would require reconductoring whether it was single or double circuit. Majority of costs will be recoverable based on load achievement by Interconnection Customer.) ¦ $8,418 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1137 | Private Load Interconnection Project |  |  |  | The Interconnection Customer (IC) has requested PG&E to serve the proposed data center. The project scope of work includes following: SUBSTATION • Relocate Bank #2 230 kV line to make room for the double circuit IC lines o Install two TSP’s and remove one TSP o Install three spans of conductor to reconnect the bank #2 • Install 230 kV complete BAAH Bay #5 o Three 230 kV breakers o Six 230 kV disconnects o Two 230 kV line disconnect switches o Wave-trap with 3 CCVT’s, with line tuner accessories o With an additional dead-end on the West side terminal for the IC • Install all line relays and controls for Bay #5 o Install additional conduits as needed o Install control wiring to all BAAH Bay #5 elements • Install 230 kV Dead-end East of bay #5 for the line disconnect switch and CCVT’s location for IC #2 line • Remove Line Trap and CCVT’s from Bay #4 • Install conduit extensions for fiber optic communications (protection) between PG&E and IC T-LINE • Two 230 kV Overhead (OH) Transmission lines made of 715.5 AAC conductor will be built to interconnect IC’s 230 kV substation to Eastshore 230 kV bus. The project will consist of 9 new Tubular Steel Poles (TSP) on drilled pier foundations, and about 0.5 double circuit miles of 230 kV transmission lines. TELEMETRY • Add telemetry from IC’s substation to PG&E system | Other | New | T.0004581 | Work Requested by Others | Load Interconnection | NA | NA | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5547320 | T.0006960 | Private Load Interconnection Project | 5 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC: AL 6570-E | 2022-04-22 | Approved | 2022 | Construction (50%-75%) | 3 | 2023-01-23 | 2023-06-30 | 2024-12-06 | Workforce | FALSE | 26700 | NA | 672.8501 | 1438.4476 | 0 | 0 | 19.5976 | 211.9143 | 408.4187 | 798.5171 | 0 | 0 | 0 | 0 | 0 | 639.9305 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 231.5343 | 408.4187 | 601.0814 | 0% | 0% ¦ $0 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - New Substation Alternative [Alternative Solutions and Costs - Costs] $15 Mil - $20 Mil ¦ $20 Mil - $30 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1138 | ROUGH & READY TAP 60KV: CAPACITY INCREAS |  |  | Stockton, San Joaquin | The Port of Stockton (Customer) has submitted an application to Pacific Gas and Electric (PG&E) for plans to increase electric load (Project) at their existing facilities in Stockton, California. The Customer is currently interconnected to PG&E’s existing transmission system near Rough & Ready Substation via PG&E’s Rough & Ready 60 kV Tap Line. This has triggered a network upgrade to reconductor sections of the Stockton A No. 1 60 kV Line and Rough & Ready 60 kV Tap with 715 AAC. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Work Requested by Others | Load Interconnection | NA | 2021-09-17 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 1 | NA | 60 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5780438 | T.0003979 | Rough & Ready Tap 60kV: Capacity Increas | 3 | 82 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC: AL 5482-E | 2019-02-25 | Approved | 2019 | Operational | 2 | 2019-05-31 | 2019-04-15 | 2019-10-18 | Workforce | FALSE | 9795 | NA | 8424.1012 | 8424.1012 | 7381.4787 | 808.1069 | -237.9835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8424.1012 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 8631.89 | -237.9835 | 0 | 0 | 0 | 0% | 96% ¦ $8,087 | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1139 | Private Load Interconnection Project |  |  |  | The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Milpitas No. 2 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Construction of two, new 1000-foot 115 kV line sections from the Newark-Milpitas No. 2 Line to the new PG&E-owned 115 kV switching station; ● Two 115 kV connectins to the Customer-owned substation; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The data center is expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. | Transmission Line - Conductor | New | T.0009536 | Work Requested by Others | Load Interconnection | NA | 2023-11-07 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion, Weather |  | 0.2 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5799904 | T.0008046 | Private Load Interconnection Project | 9 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-04-30 | NA | 2025-07-16 | NA | TRUE | NA | NA | 61.5252 | 2454.9858 | 0 | 0 | 0 | 192.1539 | 388.4194 | 300.6204 | 1396.9955 | 176.7967 | 0 | 0 | 0 | 580.5732 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1140 | Private Load Interconnection Project |  |  |  | The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Milpitas No. 2 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Construction of two, new 1000-foot 115 kV line sections from the Newark-Milpitas No. 2 Line to the new PG&E-owned 115 kV switching station; ● Two 115 kV connectins to the Customer-owned substation; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The data center is expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. | Transmission Line - Underground | New | T.0009536 | Work Requested by Others | Load Interconnection | NA | 2023-11-07 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion, Weather |  | 0.2 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5805060 | T.0008046 | Private Load Interconnection Project | 9 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-05-13 | NA | 2025-07-29 | NA | TRUE | NA | NA | -457.4345 | 3043.5057 | 0 | 0 | 0 | 0 | 97.5595 | 172.0468 | 2771.7672 | 2.1322 | 0 | 0 | 0 | 97.5595 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1141 | WRO Generator Network Upgrades |  |  |  | The project scope of work includes the following: Local Delivery Network Upgrade: Reconductor North Dublin – Cayetano 230kV Line: • Reconductor underground and overhead portion of the North Dublin – Cayetano 230kV line. Overhead and underground portions are 2.6 miles and 2.8 miles, respectivlety for a total of approximately 5.4 miles with 2000A capacity. This Local Delivery Upgrade project is tied to following Electric Generation Interconnection (EGI) project: • Solano 4 (Q1463) The project proposes to reconductor 5.4 miles of North Dublin – Cayetano 230kV Line with a higher capacity conductor. | Transmission Line - Conductor | Upgrade/Retrofit | T.0004421 | Generator Interconnection | Generation Interconnection | NA | 2024-04-09 | 18 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | 5.4 | NA | 230 | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799480 | T.0007846 | WRO Generator Network Upgrades | 1 | 82 | NA | 2022 | 2024 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-11-21 | 2025-05-25 | 2025-03-20 | NA | TRUE | 19600 | NA | 643.8243 | 19504.4139 | 0 | 0 | 0 | 168.0676 | 392.3385 | 11631.3175 | 7312.6904 | 0 | 0 | 0 | 0 | 560.4061 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $19,504 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1142 | HSR Interconnection ET Sites 8-13 (82) |  |  | Madera, Madera ¦ Fresno, Fresno ¦ Hanford, Kings ¦ Pixley, Kings ¦ Wasco, Kern ¦ Bakersfield, Kern ¦ Merced, Merced ¦ Waterford, Stanislaus¦ Kingsburg, Fresno ¦ Selma, Fresno¦ Buttonwillow CDP, Kern | California High Speed Rail (CHSR) Transmission Power Delivery Project – Sites 8 through 13. The Project will require the installation of a 25 kV AC Traction Electrification System (TES) to power the electric trains. In order to have adequate capacity for train operations, the proposed TES will interconnect into local utility networks at 115 kV or 230 kV, with approximately 30-mile intervals between the traction power substations. This substation spacing results in twelve (12) traction power substations for the 345-mile portion of the line running in PG&E’s service territory.There are six (6) interconnection sites located in the Madera to Bakersfield section. These sites have been designated as Sites 8 through 13. | Transmission Line - Conductor | New | T.0000005 ¦ T.0001650 ¦ T.0000924 ¦ T.0000204 ¦ T.0000980 ¦ T.0003202 ¦ T.0000220 ¦ T.0000143 ¦ T.0000156 | Work Requested by Others | Load Interconnection | NA | NA | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 61 | NA | 230 ¦ 115 | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5766318 | T.0000006 | CHSR Interconnections, Sites 8-13 | 2 | 82 | NA | 2015 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2033-05-24 | NA | 2035-05-04 | NA | FALSE | NA | NA | 389.5309 | 98212.8316 | 31.1961 | 24.0118 | 25.899 | 22.7949 | 41.9545 | 35.1295 | 30.2888 | 32.5088 | 34.8916 | 37.449 | 40.1939 | 378.1098 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% (Final allocation not yet finalized with CPUC & FERC) ¦ $0 | TBD | NA | 44% | 56% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1143 | HSR Heavy Maint. Facility |  |  | NA | Forecast placeholder for High Speed Rail Interconnections | Transmission Line - Conductor | New | NA | Work Requested by Others | Load Interconnection | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5772302 | NA | NA | NA | 82 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | TRUE | NA | NA | 0 | 6951.268 | 0 | 0 | 0 | 0 | 0 | 0 | 6951.268 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% (Final allocation not yet finalized with CPUC & FERC) ¦ $0 | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 1144 | WRO Generator Network Upgrades |  |  |  | Install a storage generation plant with a net output of 24.5 MW PG&Es 60 kV Tulucay Substation in Napa County, California. Tulucay Substation: • Extend maiNAux bus with DBSB, install aux switch, fence and grading • Install 2 DTT Receivers with new DTT panel Vaca-Dixon Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit Lakeville Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit | Transmission Line - Conductor | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-20 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 2 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5798546 | T.0007591 | WRO Generator Network Upgrades | 8 | 82 | NA | 2021 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-01-21 | 2025-10-10 | 2025-10-10 | NA | TRUE | 7800 | NA | 145.0085 | 1341.4962 | 0 | 0 | 0 | 19.9692 | 98.1176 | 79.9817 | 1113.6376 | 29.7901 | 0 | 0 | 0 | 118.0868 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,341 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1145 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 70.9 MW. This Generating Facility and the associated Interconnection Facilities plan connect to PG&E’s Lakeview Substation in Bakersfield, in Kern County. | Transmission Line - Conductor | New | NA | Generator Interconnection | Generation Interconnection | NA | 2021-10-28 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.5 | NA | 70 | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5791725 | T.0006097 | WRO Generator Network Upgrades | 9 | 82 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2020 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-09-17 | 2024-07-07 | 2025-10-17 | Prioritization | TRUE | 15200 | NA | 185.9846 | 1341.2702 | 0 | 0 | 5.1638 | 89.0225 | 78.9231 | 44.5077 | 1119.7698 | 3.8833 | 0 | 0 | 0 | 173.1094 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,341 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1146 | Padre Flat - Panoche#1 20074: Recon-Land |  |  | Fresno ¦ Merced | Reconductor 32.59 miles of the Padre Flat Switching Station - Panoche 230 kV Line No. 1 with 795 ACSS conductor. Upgrade associated equipment and structures to match the new conductor rating, as needed. | Other | New | T.0004490 ¦ T.0009329 | Generator Interconnection | Generation Interconnection | NA | 2021-11-19 | NA | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 32.6 | NA | 230 | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5536585 | T.0003792 | Padre Flat SS - Panoche #1 20267: Recon. | 4 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6857-E | 2022-11-21 | Approved | 2023 | Engineering more than 50% complete | 4 | NA | 2024-05-15 | 2024-04-15 | NA | TRUE | 61300 | NA | 1444.6414 | 1444.6414 | 0 | 0 | 0 | 271.3618 | 1130.3071 | 42.9725 | 0 | 0 | 0 | 0 | 0 | 1401.6689 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 246.6926 | 1027.5519 | 43.7054 | 0% | 100% ¦ $1,445 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1147 | PADRE FLAT- PANOCHE#1 20267: RECON - EGI |  |  | Fresno ¦ Merced | Reconductor 32.59 miles of the Padre Flat Switching Station - Panoche 230 kV Line No. 1 with 795 ACSS conductor. Upgrade associated equipment and structures to match the new conductor rating, as needed. | Transmission Line - Conductor | Upgrade/Retrofit | T.0004490 ¦ T.0009329 | Generator Interconnection | Generation Interconnection | NA | 2021-11-19 | 71 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 33.5 | NA | 230 | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5779058 | T.0003792 | Padre Flat SS - Panoche #1 20267: Recon. | 4 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6857-E | 2022-11-21 | Approved | 2023 | Construction (10%-25%) | 3 | 2023-11-02 | 2024-05-15 | 2025-05-19 | Material | TRUE | 61300 | NA | 21366.6563 | 62905.1741 | 353.0623 | 282.26 | 369.2148 | 1259.4602 | 14346.6458 | 30847.8078 | 15400.4737 | 17.9213 | 0 | 0 | 0 | 16638.9713 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $62,905 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1148 | LOS BANOS - PADRE FLAT SS 20266: RECON - |  |  | Fresno ¦ Merced | Reconductor 4.5 miles of the Los Banos - Padre Flat Switching Station 230 kV Line No. 1 with 1113 ACSS conductor. Upgrade associated equipment to 1,900 Amps to match the new conductor rating, as needed. Replace structures, as needed | Transmission Line - Conductor | Upgrade/Retrofit | NA | Generator Interconnection | Generation Interconnection | NA | 2021-11-19 | 70 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | 3.7 | NA | 230 | NA | 3 | 6. Customer commitments | Not Available | NA | NA | 5774966 | T.0003016 | Los Banos - Padre Flat SS 20266: Recon. | 3 | 82 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6527-E | 2022-03-11 | Approved | 2022 | Operational | 2 | 2022-10-31 | 2023-02-01 | 2022-12-24 | NA | TRUE | 10800 | NA | 5220.7914 | 5220.7914 | 213.2006 | 275.0248 | 513.4248 | 4070.6732 | 119.9182 | 0 | 0 | 0 | 0 | 0 | 0 | 5220.7914 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 4920.6048 | 115.5057 | 0 | 0% | 100% ¦ $5,221 | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1149 | LOS BANOS-QUINTO SS 20244: RECON. |  |  | Merced | Reconductor 6.11 miles of the Los Banos - Quinto Switching Station 230 kV Line with super bundled 795 ACSS conductor. Upgrade associated terminal equipment at Los Banos and Quinto Switching Station to match the new conductor rating as needed. Replace structures as needed | Transmission Line - Conductor | Upgrade/Retrofit | NA | Generator Interconnection | Generation Interconnection | NA | 2023-11-18 | 60 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | 12 | NA | 230 | NA | 3 | 6. Customer commitments | Not Available | NA | NA | 5779031 | T.0003789 | Los Banos - Quinto SS 20244: EGI Recon. | 2 | 82 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | NA | NA | NA | True | Final Certified | 2012-11-06 | EIR | NA | Merced County | NA | NOC: AL 4180-E | 2013-01-17 | Approved | 2013 | Operational | 2 | 2023-03-06 | 2022-05-06 | 2023-05-08 | Material | TRUE | 13300 | NA | 13865.2342 | 13865.2342 | 288.3112 | 276.402 | 545.8126 | 3907.6373 | 8797.5818 | 21.1611 | 0 | 0 | 0 | 0 | 0 | 13844.0731 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 13621.2672 | 22.493 | 0% | 100% ¦ $13,865 | NA | NA | 100% | 0% | [CPUC Filing Type] The reconductoring that occurred on 35 miles on Los Banos-Westley and the proposed reconductoring scope for 6 miles of Los Banos-Quinto were all included in the same 2013 NOC. The Los Banos-Quinto work was just a 6 mile portion of the project was deferred [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1150 | WRO Generator Network Upgrades |  |  |  | Reconductor Ripon – Manteca 115 kV Line 1.51 miles section of 2/0 Cu and 0.92 miles 4/0 ACSR (2.43 miles total) | Transmission Line - Conductor | Upgrade/Retrofit | T.0007445 ¦ T.0004515 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | 2023-12-20 | 6 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 0.9 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799798 | T.0007979 | WRO Generator Network Upgrades | 4 | 82 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2021 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-08-18 | 2025-01-07 | 2027-10-07 | Prioritization | FALSE | 13707 | NA | 301.1805 | 28419.8539 | 0 | 0 | 0 | 0 | 208.5399 | 786.8263 | 2495.1304 | 9295.9798 | 15619.6662 | 13.7112 | 0 | 208.5399 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $28,420 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1151 | WRO Generator Network Upgrades |  |  |  | Reconductor Stanislaus – Melones Sw. Station – Manteca # 1 115 kV line 25.23 miles section of various conductors from 018/115-043/277 | Transmission Line - Conductor | Upgrade/Retrofit | T.0007445 ¦ T.0004515 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | 2024-04-09 | 88 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | 25.23 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799799 | T.0007979 | WRO Generator Network Upgrades | 4 | 82 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2021 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2027-01-07 | 2025-01-07 | 2029-02-05 | Prioritization | FALSE | 13707 | NA | 203.4517 | 46077.6967 | 0 | 0 | 0 | 0 | 142.277 | 405.8282 | 3807.3681 | 3287.7661 | 18629.881 | 19278.3716 | 526.2045 | 142.277 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $46,078 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1152 | WRO Generator Network Upgrades |  |  |  | Reconductor the Bellota – Riverbank – Melones Sw. Station 115 kV Line (Tulloch Tap) section of 17 miles | Transmission Line - Conductor | Upgrade/Retrofit | T.0007445 ¦ T.0004515 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | 2024-04-06 | 67 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | 17 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799800 | T.0007979 | WRO Generator Network Upgrades | 4 | 82 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2021 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2028-02-16 | 2025-01-07 | 2028-08-07 | Prioritization | FALSE | 13707 | NA | 249.1053 | 39348.2685 | 0 | 0 | 0 | 0 | 94.8738 | 640.4787 | 3738.7585 | 1113.9051 | 24280.1434 | 9479.6999 | 0.4092 | 94.8738 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $39,348 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1153 | Grizzly PH Reconnect T-Line Work NU |  |  | Butte ¦ Plumas | The Caibou-Palermo 115 kV line, which connected the Powerhouse to the transmission grid, has been taken out of service for an extended timeframe in the aftermath of the November 2018 Camp Fire. This outage has disabled the Powerhouse’s ability to transmit power to SVP. The Powerhouse is currently generating a small amount to only provide station service. PG&E is obligated under the Agreement to transmit the power generated by the Powerhouse to SVP. The Agreement states that in the event of a transmission line outage, PG&E must work diligently to restore service on the same value-based schedule and priority as if it were a PG&E-owned facility. This project will provide an alternative interconnection for the Powerhouse. This project will connect the Powerhouse to the Bucks Creek-Rock Creek-Cresta 230 kV Line and install a 230/115kV step-up transformer at Bucks Creek Switchyard to facilitate the interconnection to the 230kV grid. | Transmission Line - Conductor | New | NA | Generator Interconnection | Load Interconnection | NA | 2023-06-28 | NA | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 3 - Extreme, Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 0.1 | NA | 230 ¦ 115 | NA | Not Available | 6. Customer commitments | Not Available | NA | NA | 5785300 | T.0004715 | Bucks Creek PH-Grizzly PH Reconnection | 5 | 82 | NA | 2019 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-07-11 | 2021-12-31 | 2023-12-20 | Weather | TRUE | 19981 | NA | 2559.2973 | 2655.9924 | 28.6138 | 130.5819 | 630.146 | 776.6927 | 986.0629 | 103.8951 | 0 | 0 | 0 | 0 | 0 | 2552.0973 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2164.393 | 7.1308 | 0% | 100% ¦ $2,656 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1154 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 100 megawatt (MW) (net output) solar-based generation facility to the Pacific Gas and Electric Company’s (PG&E’s) new 230 kV Bitterwater Switching Station which connects to the Midway – Wheeler Ridge 230 kV Line No.2 in Kern County, California. | Transmission Line - Conductor | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.02 | 10.403 | 230 | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5768562 | T.0001353 | WRO Generator Network Upgrades | 11 | 82 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2015 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6634-E | 2022-06-30 | Approved | 2022 | Construction (10%-25%) | 3 | 2024-02-27 | 2019-11-15 | 2024-04-22 | Customer Action | TRUE | 6600 | NA | 924.4884 | 2557.3467 | 22.3112 | 1.6586 | 4.7713 | 109.3635 | 495.477 | 1923.4753 | 0 | 0 | 0 | 0 | 0 | 633.8714 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,557 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1155 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Transmission Line - Conductor | Upgrade/Retrofit | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | 2024-04-08 | 58 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 500 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805808 | T.0009383 | WRO Generator Network Upgrades | 5 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2026-11-03 | NA | 2026-11-24 | NA | FALSE | NA | NA | 33.2796 | 2486.3515 | 0 | 0 | 0 | 0 | 2.0038 | 445.3985 | 1149.2229 | 889.7263 | 0 | 0 | 0 | 2.0038 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,486 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1156 | WRO Generator Network Upgrades |  |  |  | The Project is a combined photovoltaic solar and battery energy storage technology-based generation facility with a net output of 500.0 MW to the CAISO controlled grid. The Large Generating Facility and associated Interconnection Facilities connects to the new 230kV switching station (or the new “Q1593 Switching Station”) along PG&E’s Gates-Midway 230kV transmission line in Kettleman City, Kings County, California (the “Project”). | Transmission Line - Other Equipment | New | T.0008543 | Generator Interconnection | Generation Interconnection | NA | NA | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 10 | NA | 230 | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5803144 | T.0008735 | WRO Generator Network Upgrades | 9 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | NA | NA | NA | True | Final Certified | 2023-12-01 | EIR | NA | Kern County | NA | NOC: AL 7236-E | 2024-04-04 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2025-08-06 | NA | 2026-03-26 | NA | FALSE | 3500 | NA | 412.3717 | 3535.3288 | 0 | 0 | 0 | 0 | 322.4595 | 750.0732 | 2410.7432 | 52.053 | 0 | 0 | 0 | 322.4595 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,535 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1157 | WRO Generator Network Upgrades |  |  |  | The project is to accommodate the Energy Storage Project, which proposes to install 13 inverters rated at 1.9385 MW each with a maximum gross output of 25.2 MW. Auxiliary load of 0 MW and estimated losses of 0.2 MW. The net output is 25 MW to the CAISO Controlled Grid. This Generating Facility and the associated Interconnection Facilities plan to connect to Weber 60 kV Substation in San Joaquin County. Reconductor 0.9 mi of Stockton A0Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC | Transmission Line - Conductor | Upgrade/Retrofit | NA | Generator Interconnection | Generation Interconnection | NA | 2023-11-21 | 13 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 0.9 | NA | 60 | NA | Not Available | Not Available | Not Available | NA | NA | 5783875 | T.0004561 | WRO Generator Network Upgrades | 8 | 82 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 5770-E | 2020-02-25 | Approved | 2020 | Operational | 2 | 2022-01-18 | 2022-04-01 | 2022-02-28 | NA | FALSE | 12400 | NA | 1796.4792 | 1796.4792 | 0 | 111.6215 | 351.4127 | 1333.445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1796.4792 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 1688.8083 | 0 | 0 | 0% | 100% ¦ $1,796 | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1158 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) solar-based generation facility to Los Banos – Panoche 230 kV Line No. 1 by looping in through the Pacific Gas and Electric Company (PG&E)-owned new switching station in Merced County, California. Per recent MMA. | Transmission Line - Conductor | New | NA | Generator Interconnection | Generation Interconnection | NA | 2021-11-19 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.02 | NA | 230 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5772429 | T.0002321 | WRO Generator Network Upgrades | 9 | 82 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | 2014 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 5318-E | 2018-06-25 | Approved | 2018 | Operational | 2 | 2019-09-23 | 2019-04-23 | 2019-10-16 | NA | FALSE | 13620 | NA | 1504.8768 | 1504.8768 | 988.6522 | 3.4247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1504.8768 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1515.7997 | 3.4247 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,505 | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1159 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Transmission Line - Conductor | New | T.0009188 | Generator Interconnection | Generation Interconnection | NA | NA | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 2 | NA | 230 | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5775143 | T.0003035 | WRO Generator Network Upgrades | 7 | 82 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2017 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-12-06 | NA | 2028-03-15 | NA | FALSE | NA | NA | 134.2564 | 1204.1081 | 1.4072 | 2.267 | 68.1018 | 27.1872 | 7.1982 | 30.4471 | 21.9393 | 269.8271 | 749.2082 | 0 | 0 | 132.6863 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,204 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1160 | WRO Generator Network Upgrades |  |  |  | The project proposes to interconnect a 29.75 MW solar power-based generation facility to the PG&E’s CAISO controlled Chevron (Lost Hills) Tap 70 kV Line, via the customer owned Chevron Lost Hills 70 kV Substation in Kern County, California. The generation interconnection requires network upgrades and interconnection facilities work. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Generator Interconnection | Generation Interconnection | NA | 2023-11-16 | 46 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 4.15 | NA | 70 | NA | 3 | 6. Customer commitments | NA | NA | NA | 5780941 | T.0004052 | WRO Generator Network Upgrades | 4 | 82 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 5530-E | 2019-04-19 | Approved | 2019 | Operational | 2 | 2019-10-22 | 2019-12-16 | 2019-12-12 | NA | FALSE | 5895 | NA | 3749.984 | 3749.984 | 3120.5015 | 401.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3749.984 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 3123.6917 | 367.0471 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,750 | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1161 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 300 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) new Switching Station looped into the Quinto Switching Station - Westley 230 kV Line, in Stanislaus County, California. | Transmission Line - Conductor | New | NA | Generator Interconnection | Generation Interconnection | NA | 2023-09-13 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 0.02 | NA | 230 | NA | 3 | Not Available | Not Available | NA | NA | 5779143 | T.0003770 | WRO Generator Network Upgrades | 6 | 82 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2017 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6529-E | 2022-03-16 | Approved | 2022 | Operational | 2 | 2023-10-23 | 2022-12-31 | 2023-12-13 | Prioritization | TRUE | 27900 | NA | 3249.6764 | 3256.5185 | 0 | 58.3628 | 170.5564 | 510.2092 | 2478.2453 | 39.145 | 0 | 0 | 0 | 0 | 0 | 3217.3735 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 3126.2272 | 39.4314 | 0% | 100% ¦ $3,257 | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1162 | DOS AMIGOS PP-PANOCHE #3 20232: RECON. |  |  | Fresno ¦ Merced | The Project proposes to reconductor 23.63 miles of the Pacific Gas and Electric Company’s (PG&E’s) Dos Amigos - Panoche 230 kV Line No. 3 with a higher capacity conductor, in Merced and Fresno Counties, California. During the Cluster 9 Phase I Fresno Area Interconnection Study, the Dos Amigos - Panoche 230 kV Line No. 3 was found to be overloaded by roughly 84%. To eliminate this deliverability constraint, the CAISO requires reconductoring the overloaded line and the costs are allocated among multiple full capacity generation projects identified by the CAISO. | Transmission Line - Conductor | Upgrade/Retrofit | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | 2020-07-27 | 76 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 23.6 | NA | 230 | NA | 3 | 6. Customer commitments | 1162 | Tier 5 | Yes | 5782110 | T.0004255 | Dos Amigos PP-Panoche #3 230 kV Recondu. | 4 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-09-23 | 2025-05-31 | 2026-06-05 | Prioritization | FALSE | 49800 | NA | 2129.0984 | 30460.6208 | 369.8789 | 195.8126 | 160.507 | 866.9159 | 492.4483 | 1830.0418 | 12642.7252 | 13873.9629 | 0 | 0 | 0 | 2113.8909 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $30,461 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1163 | Borden - Gregg#1 20009: Recon-Land |  |  | Madera | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Transmission Line - Conductor | Upgrade/Retrofit | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | 2022-09-16 | 93 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.2 | NA | 230 | NA | 776 | Not Available | Not Available | Tier 5 | Yes | 5536587 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-08-07 | 2022-11-10 | 2025-10-30 | Land Rights | TRUE | 39900 | NA | 0.649 | 4250.649 | 0 | 0 | 0.3098 | 0 | 0.0392 | 2000.3 | 2250 | 0 | 0 | 0 | 0 | 0.349 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2025 | 0 | 0 | 0 | 0.30982 | 0.0392 | 0 | 0% | 100% ¦ $4,251 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1164 | BORDEN-GREGG #1 20009: RECON. |  |  | Madera | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Transmission Line - Conductor | Upgrade/Retrofit | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | 2022-09-16 | 93 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.2 | NA | 230 | NA | 776 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5779059 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-02-06 | 2022-11-10 | 2026-05-07 | Land Rights | FALSE | 39900 | NA | 1678.1237 | 29651.2385 | 150.6997 | 377.8031 | 278.6062 | 357.1707 | 359.6946 | 2591.019 | 11148.3435 | 14359.5735 | 0 | 0 | 0 | 1552.3025 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $29,651 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1165 | Q1284 WR Re-cond Fltn-Hoplnd 60 kV LN |  |  | Fulton CDP, Sonoma ¦ Healdsburg, Sonoma ¦ Larkfield-Wikiup CDP, Sonoma ¦ Mendocino ¦ Sonoma ¦ Windsor, Sonoma | The project scope of work includes the following: Local Delivery Network Upgrade: Reconductor Fulton-Hopland 60kV Line (Fitch Mountain Jct-Geysers Jct): • Reconductor Fulton-Hopland 60kV Line (Fitch Mountain Jct 009/005A – Geysers Jct 016/004) ~7 miles total length with 715 AAC. Reconductor Fulton-Hopland 60kV Line (Geysers Jct-Cloverdale Jct-Hopland): • Reconductor Fulton-Hopland 60kV Line (Geysers Jct 016/003A-Cloverdale Jct 026/002-Hopland) ~ 24.21 miles total length with 715 AAC and upgrade any limiting equipment. This Local Delivery Upgrade project is tied to following electric generation interconnection projects: • Janus Solar PV, LLC (Q1455), • Beauchamp Solar (Q1444), and • Walker Ridge Wind Energy Park (Q1284). The project proposes to reconductor 31.21 miles of Fulton-Hopland 60kV Line with a higher capacity conductor. | Transmission Line - Conductor | Upgrade/Retrofit | T.0008218 ¦ T.0006968 | Generator Interconnection | Generation Interconnection | NA | 2024-04-05 | 93 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | 24.21 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5798940 | T.0007629 | Re-cond Fulton-Hopland 60 kV LN (EGI) | 2 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2018 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-12-12 | NA | 2026-03-27 | NA | FALSE | 51170 | NA | 908.6338 | 51116.6967 | 0 | 0 | 0 | 0 | 831.1307 | 1603.3903 | 26360.9291 | 22317.3474 | 3.8993 | 0 | 0 | 831.1307 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $51,117 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1166 | Re-cond Fulton-Hopland 60 kV LN (EGI) |  |  | Fulton CDP, Sonoma ¦ Healdsburg, Sonoma ¦ Larkfield-Wikiup CDP, Sonoma ¦ Mendocino ¦ Sonoma ¦ Windsor, Sonoma | The project scope of work includes the following: Local Delivery Network Upgrade: Reconductor Fulton-Hopland 60kV Line (Fitch Mountain Jct-Geysers Jct): • Reconductor Fulton-Hopland 60kV Line (Fitch Mountain Jct 009/005A – Geysers Jct 016/004) ~7 miles total length with 715 AAC. Reconductor Fulton-Hopland 60kV Line (Geysers Jct-Cloverdale Jct-Hopland): • Reconductor Fulton-Hopland 60kV Line (Geysers Jct 016/003A-Cloverdale Jct 026/002-Hopland) ~ 24.21 miles total length with 715 AAC and upgrade any limiting equipment. This Local Delivery Upgrade project is tied to following electric generation interconnection projects: • Janus Solar PV, LLC (Q1455), • Beauchamp Solar (Q1444), and • Walker Ridge Wind Energy Park (Q1284). The project proposes to reconductor 31.21 miles of Fulton-Hopland 60kV Line with a higher capacity conductor. | Transmission Line - Conductor | Upgrade/Retrofit | T.0008218 ¦ T.0006968 | Generator Interconnection | Generation Interconnection | NA | 2024-04-05 | 93 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | 7 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5798804 | T.0007629 | Re-cond Fulton-Hopland 60 kV LN (EGI) | 2 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2018 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-11-03 | NA | 2026-03-27 | NA | FALSE | 12588 | NA | -12.2307 | 12331.3964 | 0 | 0 | 0 | 9.2205 | -67.9531 | 664.8266 | 6630.8565 | 5090.37 | 4.0758 | 0 | 0 | -58.7326 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $12,331 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1167 | Castanea Line Relocation |  |  | Fresno | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Transmission Line - Conductor | Relocate | NA | Generator Interconnection | Generation Interconnection | NA | 2023-12-08 | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.02 | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5795825 | T.0006452 | GATES BUS SECTION ""E"" | 9 | 82 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-03-13 | 2023-04-30 | 2023-05-24 | NA | TRUE | 58600 | NA | 2951.1665 | 2951.1665 | 0 | 0 | 109.4504 | 2064.435 | 779.2812 | -2 | 0 | 0 | 0 | 0 | 0 | 2953.1665 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 2883.4314 | -1.9509 | 0% | 100% ¦ $2,951 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1168 | GATES BUS SECTION "E" LINE RELOCATIONS |  |  | Fresno | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Transmission Line - Conductor | New | NA | Generator Interconnection | Generation Interconnection | NA | 2023-11-17 | NA | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | 3 | Not Available | Not Available | NA | NA | 5738327 | T.0006452 | GATES BUS SECTION ""E"" | 9 | 82 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-03-08 | 2021-04-30 | 2021-04-20 | NA | TRUE | 58600 | NA | 1440.1093 | 1440.1093 | 0.001 | 104.7345 | 1280.856 | 21.4777 | 33.0253 | 0.0002 | 0 | 0 | 0 | 0 | 0 | 1440.1091 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1279.8631 | 19.8379 | 30.5043 | 0 | 0% | 100% ¦ $1,440 | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1169 | Gates-Panoche 230 Line Relocation |  |  | Fresno | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Transmission Line - Conductor | Relocate | NA | Generator Interconnection | Generation Interconnection | NA | 2023-12-08 | 77 | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 0.02 | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5795899 | T.0006452 | GATES BUS SECTION ""E"" | 9 | 82 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-01-09 | 2023-04-30 | 2023-04-17 | NA | TRUE | 58600 | NA | 4636.9469 | 4636.9469 | 0 | 0 | 2920.1463 | 1347.7281 | 356.9053 | 12.1671 | 0 | 0 | 0 | 0 | 0 | 4624.7798 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 4430.8688 | 11.8513 | 0% | 100% ¦ $4,637 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1170 | HSR Interconnection ET Sites 4-7 (82) |  |  | Gilroy, Santa Clara ¦Morgan Hill, Santa Clara ¦ Dos Palos, Merced ¦ Los Banos, Merced ¦ Merced ,Merced ¦ Fresno | TPS Sites 4 to 7 will power the section of the rail line that connects the Bay Area with the Central Valley. When the CHSR Project is completed and in-service, the CHSR substation at Sites 4 to 7 will have a total power demand of over 230 megawatts (MW). The interconnections at Sites 4 to 7 will consist of the major work components shown below. There will be other system work needed to address protection and automation upgrades needed for the system reconfigurations resulting from the interconnections. Generally, “Network Upgrades” will be performed by PG&E, and work for new “Interconnection Facilities” will be performed by CHSRA or its contractors. | Transmission Line - Conductor | New | T.0000006 ¦ T.0002127 ¦ T.0004116 ¦ T.0002231 | Work Requested by Others | Load Interconnection | NA | NA | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 41 | NA | 230 ¦ 115 | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5766463 | T.0000005 | CHSR Interconnections, Sites 4-7 | 2 | 82 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-10-08 | NA | 2035-02-02 | NA | FALSE | NA | NA | 249.3777 | 62446.8505 | 48.2049 | 20.5267 | 18.2979 | 15.2051 | 22.1339 | 34.7385 | 39.9775 | 42.424 | 45.4906 | 48.5719 | 52.1675 | 246.3633 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% (Final allocation not yet finalized with CPUC & FERC) ¦ $0 | TBD | NA | 44% | 56% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1171 | Caltrain IC - T-Line Site 1 (82) |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Transmission Line - Conductor | Upgrade/Retrofit | NA | Work Requested by Others | Load Interconnection | NA | NA | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.25 | NA | 115 | NA | 3 | 6. Customer commitments | Not Available | NA | NA | 5766382 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | 5763023 | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2017 | FALSE | 2017 | NA | https://www.caiso.com/Documents/Board-Approved_2016-2017TransmissionPlan.pdf | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-05-08 | 2021-06-30 | 2022-03-13 | Construction Delays | TRUE | 46700 | NA | 1532.9891 | 1535.8497 | 627.458 | 659.8359 | -39.5173 | 50.0447 | 2.4087 | 2.8606 | 0 | 0 | 0 | 0 | 0 | 1532.9891 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1503.0812 | 2.3386 | 0 | 0% | 60% ¦ $922 | NA | NA | 0% | 100% | [Utility Unique ID 2] T.0000004 & T.0002226 are linked as part of the Caltrain Interconnection Project. Cost allocation has only been approved by the CPUC. FERC approval still needed. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1172 | Caltrain IC - T-Line Site 3 (82) |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Transmission Line - Conductor | New | NA | Work Requested by Others | Load Interconnection | NA | 2020-08-27 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.25 | NA | 115 | NA | 3 | 6. Customer commitments | Not Available | NA | NA | 5772269 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2017 | FALSE | 2017 | NA | https://www.caiso.com/Documents/Board-Approved_2016-2017TransmissionPlan.pdf | False | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 2 | 2019-05-13 | 2021-06-30 | 2022-08-29 | Construction Delays | FALSE | 64500 | NA | 1539.2556 | 1542.1477 | 325.0314 | 551.4713 | 196.6122 | 52.6397 | 8.726 | 5.0977 | 0 | 0 | 0 | 0 | 0 | 1537.05 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1455.0135 | 8.215 | 2.2252 | 0% | 60% ¦ $925 | NA | NA | 44% | 56% | [Utility Unique ID 2] T.0000004 & T.0002226 are linked as part of the Caltrain Interconnection Project. Cost allocation has only been approved by the CPUC. FERC approval still needed. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1173 | TESLA-SALADO#1 115kV Del Puerto Rsrvoir |  |  | Alameda ¦ San Joaquin ¦ Stanislaus | Del Puerto Water District (DPWD) and the San Joaquin River Exchange Contractors Water Authority (Exchange Contractors) are partnering to construct and operate the Del Puerto Canyon Reservoir. The reservoir will have the capacity to hold 85,000 acre-feet of water to be delivered for irrigation, groundwater recharge, or wildlife beneficial uses. Del Puerto Canyon Reservoir will be located in Del Puerto Canyon in the Coast Range foothills west of Patterson and south of the Sacramento-San Joaquin Delta, just west of I-5 in Stanislaus County, California. Currently, there are five (5) transmission lines and associated towers crossing the Del Puerto Canyon in the area that will be inundated by the reservoir. The Del Puerto Reservoir Relocation project proposes to relocate/modify two 500kV lines, one 230kV line and two 115kV lines that run through the region inundated by the reservoir. | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2024-04-09 | NA | NA | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Heat Wave |  | 2.1 | NA | 115 | NA | Not Available | 6. Customer commitments | Not Available | Tier 5 | No | 5787660 | T.0005159 | Del Puerto Reservoir | 5 | 82 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-11-19 | NA | 2029-12-27 | NA | FALSE | NA | NA | -1.4124 | 48980.621 | -37.0342 | 160.1374 | -44.8017 | -65.3122 | 23.0347 | 87.6408 | 279.1524 | 172.9423 | 1853.364 | 19682.189 | 26868.6201 | 36.024 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | TBD | NA | 0% | 100%
| 1174 | SMARTVILLE-MARYSVILLE 60KV RELO-LOMARICA |  |  | Marysville, Yuba ¦ Smartsville CDP, Yuba ¦ Yuba | Caltrans has a proposed project to upgrade SR 20 in Yuba County. The project will upgrade the roadway alignment by widening existing roadway shoulders. Caltrans has requested the Utility to relocate approximately 2.1 miles of Smartville - Marysville 60kv with 12 kV underbuild from Pole No. 011/214 to 012/251, which runs along SR 20 near Loma Rica Road. Work consists of installation of 39 transmission poles (3 TPD, 3 HPD, 33 T1), 2 distribution poles, 4 guy stubs, 1 clearance pole with all associated framing and guying, and removal of 40 wood poles and 2 LDSPs | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2023-12-08 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 2.1 | NA | 60 | NA | 3 | 6. Customer commitments | Not Available | NA | NA | 5774833 | T.0002940 | SMARTVILLE-MARYSVILLE 60KV RELO-LOMARICA | 1 | 82 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | False | Final Certified | 2016-08-17 | IS/MND | NA | CalTrans | NA | NOC: AL 5438-E | 2018-12-07 | Approved | 2019 | Operational | 2 | 2020-05-01 | 2019-06-30 | 2020-06-02 | Customer Action | FALSE | 1914 | NA | 3392.8308 | 3392.8308 | 867.6854 | 1936.2629 | 220.5562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3392.8308 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 2956.8744 | 205.3166 | 0 | 0 | 0 | 0% | 100% ¦ $3,393 | NA | NA | 0% | 100%
| 1175 | PALERMO-OROVILLE#2 60KV: RELO CALT HW162 |  |  | Butte ¦ Oroville East CDP, Butte ¦ Oroville, Butte ¦ Palermo CDP, Butte ¦ South Oroville CDP, Butte | Relocate and replace 18 wood poles, 4 guy stubs, and add 2 wood poles on the Palermo - Oroville #2 60 kV line. Caltrans is proposing to widen SR 162 from Foothill Boulevard in Oroville, California to the east for approximately 1.4 miles. The route widening plans are in conflict with PG&E’s Palermo-Oroville #2 60KV line in approximately 18 locations, and with an Electric Distribution (ED) line along the same route. This project will relocate the facilities onto a new Electric Transmission (ET) line with ED underbuilt to support Caltrans widening plans on Hwy 162. Caltrans has requested PG&E to relocate 18 conflicting wood poles on the Palermo-Oroville #2 60KV line to accommodate the road widening project. Some poles will be replaced in the same location while others will be replaced and relocated. The two new poles will be wood poles. | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2023-11-20 | 56 | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Subsidence |  | 1.4 | NA | 60 | NA | Not Available | 6. Customer commitments | Not Available | NA | NA | 5531454 | T.0004918 | Palermo-Oroville#2 60kV: Relo CalT HW162 | 1 | 82 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC: AL 5982-E | 2020-10-26 | Approved | 2020 | Operational | 2 | 2021-05-06 | 2022-05-01 | 2022-05-13 | NA | FALSE | 1692 | NA | 1373.1864 | 1373.1864 | 37.3423 | 204.7787 | 263.4262 | 1710.1765 | -842.5373 | 0 | 0 | 0 | 0 | 0 | 0 | 1373.1864 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 34.3776 | 174.1577 | 235.5736 | 1530.2592 | -753.9324 | 0 | 0% | 50% ¦ $687 | NA | NA | 44% | 56%
| 1176 | Konocti-Middletown 60 kV Relo Hwy 29 |  |  | Hidden Valley Lake CDP, Lake ¦ Lake ¦ Lower Lake CDP, Lake ¦ Middletown CDP, Lake | Relocate Konocti-Middletown 60 kV line at CA Highway 29 to support road work. | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2024-04-11 | 23 | NA | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5796491 | T.0007223 | Konocti-Middletown 60 kV Relo Hwy 29 | 1 | 82 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-02-10 | NA | 2025-03-10 | NA | TRUE | NA | NA | 8.7259 | 2037.2025 | 0 | 0 | 7.4811 | 0.5442 | 0.5985 | 141.0611 | 1887.5175 | 0 | 0 | 0 | 0 | 8.6239 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 10% ¦ $204 | TBD | NA | 0% | 100%
| 1177 | Pease-Marysville-Harter 60kV Levee 2B |  |  | Marysville, Yuba ¦ Sutter ¦ Yuba ¦ Yuba City, Sutter | Relocate the Smartville – Marysville and Pease – Marysville – Harter 60 kV lines to support the Marysville Ring Levee Phase 3 Project by the Marysville Levee District in Marysville, CA. | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2023-07-10 | 59 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 1.7 | NA | 60 | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | No | 5530048 | T.0003956 | Pease-Marysville-Harter 60kV Levee 3 | 2 | 82 | NA | 2017 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC: AL 6187-E | 2021-05-05 | Approved | 2021 | Construction (under 10%) | 3 | 2024-03-04 | 2021-06-30 | 2024-07-19 | Permitting | TRUE | 13800 | NA | 2228.6473 | 6874.5769 | 398.1923 | 505.7289 | 434.3083 | 600.0252 | 85.8423 | 4689.333 | 0 | 0 | 0 | 0 | 0 | 2185.244 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 199.0437 | 716.7524 | 406.3209 | 549.1137 | 79.8094 | 385.2143 | 0% | 75% ¦ $5,156 | TBD | NA | 0% | 100%
| 1178 | TESLA-STOCKTON 115KV TRACY REPLACEMENT |  |  | Alameda ¦ Lathrop, San Joaquin ¦ Manteca, San Joaquin ¦ Ripon, San Joaquin ¦ San Joaquin ¦ Tracy, San Joaquin | Replace 5 wood poles on Corral Hollow Road with wood poles and Tubular Steel Poles. Relocate the Tesla-Stockton Cogen Jct 115kV Line to support the City of Tracy’s road widening project in San Joaquin County, CA. | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2023-12-20 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.5 | NA | 115 | NA | 3 | 6. Customer commitments | Not Available | NA | NA | 5528514 | T.0003697 | TESLA-STOCKTON 115KV TRACY REPLACEMENT | 2 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC: AL 5687-E | 2019-11-15 | Approved | 2020 | Operational | 2 | 2020-09-23 | 2020-09-17 | 2020-10-12 | NA | FALSE | 2560 | NA | 1439.3398 | 1439.3398 | 334.4042 | 881.0961 | 29.0227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1439.3398 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 0.0084 | 1390.2112 | 28.6054 | 0 | 0 | 0 | 0% | 100% ¦ $1,439 | NA | NA | 0% | 100%
| 1179 | KASSON-CARBONA 60KV RELO MACARTHUR DR |  |  | San Joaquin ¦ Tracy, San Joaquin | The City of Tracy is performing a road widening project on MacArthur Drive between Schulte Road and Valpico Road in Tracy, CA. In order to accommodate the City of Tracy’s project, Pacific Gas and Electric Company (PG&E) will need to relocate 16 transmission poles on the Kasson – Carbona 60 kV Line and a total of 10 distribution poles, guy stubs, and service poles. This project precedes the Corral Hollow Relocation Project, which proposes to relocate 12 wood poles on the Kasson – Carbona 60 kV line due to the widening of Corral Hollow Road beteween West Schulte Road and West Linne Road in the City of Tracy, California. The Corral Hollow Relocation Project has a Q4 2019 forecasted construction date. | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2023-11-16 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 1 | NA | 60 | NA | 3 | Not Available | NA | NA | NA | 5526124 | T.0003061 | Kasson-Carbona - Macarthur Blvd Tracy | 2 | 82 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC: AL 4838-E | 2016-05-05 | Approved | 2016 | Operational | 2 | 2019-01-07 | 2019-01-31 | 2019-02-15 | NA | FALSE | 1659 | NA | 2379.1262 | 2379.1262 | 1729.0794 | 5.1187 | 0 | -58.1861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2379.1262 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2022 ¦ 2024 | 1424.132 | 272.8315 | 0 | -54.3793 | 0 | 0 | 0% | 76% ¦ $1,808 | NA | NA | 0% | 100%
| 1180 | East Grand-Caltrain TPS-1 115 kV Line |  |  | Burlingame, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ San Mateo, San Mateo ¦ South San Francisco, San Mateo | The double circuit 115 kV intertie between PG&E’s East Grand Substation (EGS) and Caltrain’s Traction Power Station 1 (TPS-1) station was completed in March 2022. A portion of that intertie was underground (UG), and a portion was routed overhead (OH). IQHQ, who is erecting a new building next to TPS-1 has requested (with Caltrain’s approval) that PG&E perform a preliminary study to convert the OH portion of the 115 kV lines from OH to UG. | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2020-10-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.1 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5804578 | T.0009135 | East Grand-Caltrain TPS-1 115 kV Line Re | 1 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-03-27 | NA | 2027-05-13 | NA | FALSE | NA | NA | -17.887 | 9363.0022 | 0 | 0 | 0 | 0 | -81.3231 | 329.9723 | 179.4253 | 6667.5995 | 2267.3282 | 0 | 0 | -81.3231 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | TBD | NA | 0% | 100%
| 1181 | Pease-Marysville-Harter 60kV Levee 3 |  |  | Marysville, Yuba ¦ Smartsville CDP, Yuba ¦ Yuba | The Marysville Levee District is initiating Phase B of their Marysville Ring Levee Project, which will upgrade an approximately 1-mile section of the levee between Highway 70 and Ramirez Street in Marysville, CA. This levee upgrade project is in conflict with facilities on three of PG&E’s transmission lines in the area: the Nicolaus – Marysville, Smartville – Marysville and Pease – Marysville – Harter 60 kV lines. Four transmission line structures will need to be relocated to accommodate the levee upgrade project. In addition, a 3-wood pole structure is expected to be replaced with tubular steel pole at the toe of the levee. | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2023-12-08 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | 0.12 | NA | 60 | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | No | 5528516 | T.0003703 | Pease-Marysville-Harter 60kV Levee 2B | 1 | 82 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC: AL 6187-E | 2021-05-05 | Approved | 2021 | Engineering more than 50% complete | 4 | 2024-04-08 | 2022-08-31 | 2024-06-10 | Prioritization | FALSE | 3500 | NA | 629.5555 | 2287.3738 | 207.8477 | -214.6934 | 127.3449 | 353.9298 | 426.5024 | 1261.9659 | 0 | 0 | 0 | 0 | 0 | 1025.4079 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 2.1774 | 101.0693 | 113.177 | 314.6311 | 331.003 | -208.5315 | 0% | 0% ¦ $0 | TBD | NA | 0% | 100%
| 1182 | SR 120 Manteca #1 60 kV Relo |  |  | Grayson CDP, Stanislaus ¦ Manteca, San Joaquin ¦ San Joaquin ¦ Stanislaus | The project proposes to relocate a section of the Manteca #1 60 kV Line to accommodate the Caltrans and the City of Manteca’s planned overcrossing widening project at the overcrossing of SR 120 at Union St, in Manteca, California. The project will need to relocate approximately 0.4 miles of the Manteca #1 60 kV Line, and its associated distribution under-build, from Pole Nos. 1/27 to 1/31. | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2023-12-20 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.4 | NA | 60 | NA | 3 | 6. Customer commitments | Not Available | NA | NA | 5777125 | T.0003411 | Manteca #1 60 kV Relo- SR 120 TSP PL_ENG | 1 | 82 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC: AL 5488-E | 2019-03-06 | Approved | 2019 | Operational | 2 | 2020-02-14 | 2019-06-21 | 2020-02-20 | Customer Action | FALSE | 3700 | NA | 1063.6643 | 1063.6643 | 102.3758 | 710.7354 | -91.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063.6643 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1157.5814 | -91.4956 | 0 | 0 | 0 | 0% | 50% ¦ $532 | NA | NA | 0% | 100%
| 1183 | TABLE MOUNTAIN-PEACHTON 60 KV RELOCATION |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Durham CDP, Butte | The project proposes to remove and relocate 11 transmission poles along State Road 99 at the Cottonwood Creek Bridge. The project scope of work includes the following: Remove and relocate 11 transmission poles staying within the Caltrans ROW. Engineering will determine if alterations of transmission poles adjacent to these three poles will be required due to altered forces from this project. . | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2024-04-08 | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 1 | NA | 60 | NA | 3 | 6. Customer commitments | Not Available | NA | NA | 5530519 | T.0004028 | Table Mountain-Peachton 60kV:Relocation | 1 | 82 | NA | NA | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-10-09 | 2019-12-31 | 2020-10-12 | Customer Action | FALSE | 945 | NA | 1138.1046 | 1138.1046 | 92.0404 | 965.7781 | -9.4746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1138.1046 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 74.5728 | 775.5481 | -7.6475 | 0 | 0 | 0 | 0% | 100% ¦ $1,138 | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1184 | LAKEVILLE_#2_60kV-RELO-NOVATO_CALTRNS101 |  |  | Marin ¦ Novato, Marin ¦ Petaluma, Sonoma ¦ Sonoma | The project scope of work addresses Poles A006/126 to A009/167 on the Lakeville #2 60kV line: • Relocate and replace forty (40) existing wood transmission poles with new wood transmission poles. • Relocate and upgrade two (2) wood transmission poles with new tubular steel poles (TSP). • Relocate 13,943 circuit feet of 1/0-7 CU and 397.5-19 AAC 60 kV conductor. o Note, no changes to existing conductor size. • Relocate distribution under-build. • Relocate and replace four (4) field switches. Caltrans has initiated the Highway 101 Improvement Project in Marin County, which proposes improvements to a segment of Highway 101, in Novato, CA. These improvements are in conflict with 42 overhead transmission poles on PG&E’s Lakeville #2 60 kV Line. This project proposes to relocate PG&E’s transmission infrastructure in conflict | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2023-12-21 | 99 | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 3 | NA | 60 | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | No | 5531919 | T.0004281 | Lakeville #2 60kV:RELO:Novato_CalT_101 | 1 | 82 | NA | 2018 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-04-08 | 2024-05-31 | 2025-04-25 | Prioritization | TRUE | 6235 | NA | 864.0905 | 2514.4205 | 127.9133 | 328.4807 | 165.4202 | 108.0173 | 70.4747 | 154.6143 | 1508.3897 | 0 | 0 | 0 | 0 | 851.4165 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 128.4812 | 328.4806 | 165.4202 | 62.7959 | 66.3935 | 18.9483 | 0% | 50% ¦ $1,257 | TBD | NA | 0% | 100%
| 1185 | Martin-Hunters Point Shoofly Project |  |  | San Francisco, San Francisco | The scope of work includes removing the two towers supporting the HP-3 line above ground to an underground system. The lattice structure provides power along the HP-3 line to the Hunters Point Switchyard. The plan is to tie into an existing vault located on Hawes St and run the 115 KV HPGF HP-3 line underground into the Hunters Point Switchyard. A new termination structure will dead end the underground system and tie into the existing tower at the switchyard. The majority of this work originally falls under the Hunters Point GIS Substation Project, while the scope of this project involves adding a shoofly/cutover at the corner of Hunters Point Blvd and Evans from the original route to the switchyard HP-3 termination point. A vault will be added at this corner for the future connection to the GIS substation along Evans Ave. | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2021-11-09 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 23.6 | NA | 230 | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5803358 | T.0008764 | Martin-Hunters Point Shoofly Project | 1 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | BCDC | TBD | NOC: AL 7127-E | 2024-01-10 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2025-04-01 | NA | 2026-04-30 | NA | TRUE | NA | NA | 670.5191 | 19396.4312 | 0 | 0 | 0 | 0 | 540.0005 | 7004.0093 | 11454.3346 | 398.0868 | 0 | 0 | 0 | 540.0004 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $19,396 | TBD | NA | 0% | 100%
| 1186 | WHEELER RIDGE-WEEDPATCH 70:Relo-184 |  |  | Bakersfield, Kern ¦ Kern ¦ Weedpatch CDP, Kern | This project proposes to relocate seven (7) transmission wood poles on Wheeler Ridge – Weedpatch 70 kV Line in support of Caltrans’ roundabout project on Sunset Boulevard in Bakersfield, CA | Transmission Line - Conductor | Relocate | NA | Work Requested by Others | Facility Relocation | NA | 2021-11-09 | 71 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 0.25 | NA | 70 | NA | Not Available | 6. Customer commitments | Not Available | NA | NA | 5536900 | T.0004942 | Wheeler Ridge-Weepatch 70 kV: Relo-184 | 1 | 82 | NA | 2019 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NOC: AL 5944-E | 2020-09-10 | Approved | 2020 | Operational | 2 | 2021-11-15 | 2020-11-01 | 2021-11-23 | Customer Action | FALSE | 920 | NA | 1001.7461 | 1001.7461 | 71.0708 | 235.2793 | 665.1398 | 29.5542 | 0 | 0.702 | 0 | 0 | 0 | 0 | 0 | 1001.0441 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 71.5527 | 180.6182 | 546.46 | 24.2809 | 0 | 0.32507 | 0% | 100% ¦ $1,002 | NA | NA | 0% | 100%
| 1187 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 50 megawatt (MW) (net output) solar-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) Borden Substation 70 kV bus, in Madera County, California. | Transmission Line - Conductor | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 2.5 | 7.1874 | 70 | NA | 3 | 6. Customer commitments | Not Available | NA | NA | 5770638 | T.0001627 | WRO Generator Network Upgrades | 5 | 82 | 5755747 | 2014 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2013 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-12-03 | 2020-01-03 | 2020-02-04 | NA | FALSE | 1100 | NA | 1693.5744 | 1693.5744 | 451.1327 | 1164.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1693.5744 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 1671.1388 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1188 | Private Load Interconnection Project |  |  |  | The project scope of work includes following: Install Gas Insulated Switchgear (GIS) Switching Station • Install two (2) GIS BAAH switching station looping into Grant-Eastshore #2 115kV Line • Provide dual 115kV service from a new GIS Switching station. • Install Station Service Voltage Transformer (SSVT) • Install a new MPAC building to accommodate the protective relays for the GIS and SSVT • Install access roads, grading, fencing and security Install T-Line • Two 115 kV Overhead (OH) Transmission lines will be built to interconnect 115 kV GIS switching station to Eastshore & Grant’s 115 kV bus. The new double circuit line would consist of new tubular steel poles(TSP) supporting approximately 0.40 double circuit miles of aluminum concentric stranded conductor. Eastshore: Remote End Upgrade • Install SMP breaker & Line package for CB 312 • Establish redundant communication path. Grant: Remote End Upgrade • Install SMP breaker & Line package for CB 122 • Establish redundant communication path. Direct Assignment • Install necessary relay upgrades. Metering • Add telemetry from Customer’s substation to PG&E system | Substation - Multiple | New | T.0004580 | Work Requested by Others | Load Interconnection | NA | 2024-03-11 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | TBD | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5807505 | T.0009652 | Private Load Interconnection Project | 6 | 82 | NA | 2024 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-08-27 | NA | 2027-07-22 | NA | FALSE | NA | NA | 36.5151 | 31639.2438 | 0 | 0 | 0 | 0 | 20.5192 | 769.6018 | 1726.0372 | 21598.1327 | 7524.5079 | 0.445 | 0 | 20.5192 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1189 | Private Load Interconnection Project |  |  |  | Construct new switching station and install additional conductor on the Morgan Hill-Llagas 115 kV tower line to a new switching station at the customer site | Substation - Other Equipment | New | T.0004271 | Work Requested by Others | Load Interconnection | NA | 2024-03-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.3037 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5800026 | T.0007676 | Private Load Interconnection Project | 6 | 82 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-06-26 | NA | 2025-11-05 | NA | TRUE | NA | NA | 57.447 | 2310.941 | 0 | 0 | 0 | 7.4653 | 46.4691 | 1094.7922 | 861.1121 | 301.1023 | 0 | 0 | 0 | 53.9344 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1190 | Private Load Interconnection Project |  |  |  | Construct new switching station and install additional conductor on the Morgan Hill-Llagas 115 kV tower line to a new switching station at the customer site | Substation - Other Equipment | New | T.0004271 | Work Requested by Others | Load Interconnection | NA | 2024-03-03 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.3037 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5800025 | T.0007676 | Private Load Interconnection Project | 6 | 82 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-06-26 | NA | 2025-11-05 | NA | TRUE | NA | NA | 184.0934 | 3235.982 | 0 | 0 | 0 | 32.95 | 137.1638 | 973.9568 | 1767.3367 | 324.5747 | 0 | 0 | 0 | 170.1138 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1191 | Private Load Interconnection Project |  |  |  | Construct new switching station and install additional conductor on the Morgan Hill-Llagas 115 kV tower line to a new switching station at the customer site | Substation - Other Equipment | New | T.0004271 | Work Requested by Others | Load Interconnection | NA | 2024-02-09 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.8017 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5800024 | T.0007676 | Private Load Interconnection Project | 6 | 82 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-06-26 | NA | 2025-11-07 | NA | TRUE | NA | NA | 123.4151 | 2437.3647 | 0 | 0 | 0 | 15.4679 | 92.1555 | 1200.2511 | 781.9144 | 347.5759 | 0 | 0 | 0 | 107.6233 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1192 | Private Load Interconnection Project |  |  |  | The Customer is planning on constructing a large data center facility, expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Trimble 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Loop the Newark-Trimble 115 kV Line into the new PG&E Switching Station; ● Reconductoring of 12.1 miles of the Newark-Trimble 115 kV Line from Newark to TSP 012/082; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The Customer has also requested that the two connections from the Newark-Trimble Line be routed separately from the PG&E switching station to the existing line. | Substation - Multiple | New | NA | Work Requested by Others | Load Interconnection | NA | 2024-02-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.8982 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5804166 | T.0009031 | Private Load Interconnection Project | 6 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2025-11-06 | NA | 2026-03-18 | NA | FALSE | NA | NA | 192.6773 | 2510.8656 | 0 | 0 | 0 | 0 | 153.0212 | 1161.3517 | 750.3793 | 446.1135 | 0 | 0 | 0 | 153.0212 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 20% (The primary costs of the Switching Station currently are non-refundable. The 20% costs are for the protection upgrades at the remote end sites.) ¦ $502 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1193 | Oakland Sub J Relay Upgrade |  |  | Oakland, Alameda | Oakland J-Alameda 115 kV line relay upgrade and fiber connection extension from Oakland J to Oakland C in PG&E's facilities per work agreement with Alameda Municipal Power (AMP) | Substation - Protection Relay | Upgrade/Retrofit | NA | Work Requested by Others | Load Interconnection | NA | 2024-02-28 | 17 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 2.5059 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5552179 | T.0009027 | Oakland J to Alameda 115kV Relay Upgrade | 1 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-10-30 | NA | 2026-01-15 | NA | FALSE | NA | NA | 75.2138 | 2476.7174 | 0 | 0 | 0 | 0 | 75.2138 | 0 | 2109.4479 | 292.0557 | 0 | 0 | 0 | 75.2138 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2026 | 0 | 0 | 0 | 0 | 67.6925 | 0 | 0% | 0% ¦ $0 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1194 | FMC: VTA INSTALL 115KV CB |  |  | San Jose, Santa Clara | The project scope of work includes following: Substation:  Install new 115kV circuit breaker in BAAH Bay 5, disconnect switches, line CCVTs, and H-frame dead end structures. Includes breaker relays and overhead conductor and drops between Bay 5 and new 115kV line termination structure  Install new line current differential relays and Digital Fault Recorder in FMC 115kV MPAC building  Install new line current differential relays in PG&E metering building located at VTA 115kV substation  Install fully redundant communication paths between FMC substation 115kV MPAC building, and PG&E metering building located at VTA 115kV substation. Physically separated independent communication paths required for set A and set B protection relaying  Install PG&E RTU at proposed VTA substation  Install PG&E meter and 115kV PT/CT combination metering transformers. Includes pulling secondary wires and installing one electronic meter Transmission Line:  Install approximately 300 circuit-feet of a new single-circuit 115 kV transmission line from PG&E’s FMC Substation Bay 5 to the proposed VTA substation. The new line will support the expected temporary load of 24.8 MVA | Substation - Circuit Breaker | New | NA | Work Requested by Others | Load Interconnection | NA | 2024-02-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.0642 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 4 | No | 5800518 | T.0008309 | FMC: VTA 115kV Interconnect | 4 | 82 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-05-07 | 2024-12-31 | 2024-12-09 | NA | TRUE | 11560 | NA | 357.1949 | 6293.0967 | 0 | 0 | 0 | -547.7853 | 637.794 | 6089.5125 | 113.5755 | 0 | 0 | 0 | 0 | 90.0087 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% (Final allocation not yet finalized with CPUC & FERC) ¦ $0 | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1195 | Private Load Interconnection Project |  |  |  | The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Milpitas No. 2 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Construction of two, new 1000-foot 115 kV line sections from the Newark-Milpitas No. 2 Line to the new PG&E-owned 115 kV switching station; ● Two 115 kV connectins to the Customer-owned substation; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The data center is expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. | Substation - Protection Relay | Upgrade/Retrofit | T.0009536 | Work Requested by Others | Load Interconnection | NA | 2024-02-08 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 3.3452 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | No | 5804015 | T.0008046 | Private Load Interconnection Project | 9 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-08-26 | NA | 2026-04-24 | NA | FALSE | NA | NA | 30.4988 | 4823.8555 | 0 | 0 | 0 | 0 | 25.6152 | 634.7321 | 3126.0203 | 1037.4878 | 0 | 0 | 0 | 25.6153 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1196 | Private Load Interconnection Project |  |  |  | The project will provide transmission service to the Customer data center substation from a new PG&E-owned 115 kV switching station that is connected into the Newark-Milpitas No. 2 115 kV Line. The proposed scope of work for the project includes: ● Construction of a new PG&E-owned 115 kV switching station on the Customer property, with initially two breaker-and-a-half (BAAH) bays; ● Construction of two, new 1000-foot 115 kV line sections from the Newark-Milpitas No. 2 Line to the new PG&E-owned 115 kV switching station; ● Two 115 kV connectins to the Customer-owned substation; and ● Upgrades to system protection and any Special Protection Scheme (SPS) in the area, as needed. The data center is expected to be on-line in 2024, with an initial load of 27 MW and an ultimate load of 90 MW by 2031. | Substation - Multiple | New | T.0009536 | Work Requested by Others | Load Interconnection | NA | 2024-02-08 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | TBD | NA | 115 kV | Not Available | Not Available | Not Available | Tier 4 | No | 5799905 | T.0008046 | Private Load Interconnection Project | 9 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-10-18 | NA | 2026-04-16 | NA | FALSE | NA | NA | 141.8389 | 7149.9377 | 0 | 0 | 0 | -343.6689 | 436.8111 | 1424.6585 | 4032.6206 | 1599.5163 | 0 | 0 | 0 | 93.1423 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | TBD | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1197 | WRO Generator Network Upgrades |  |  |  | Vander Schaaf Dairies Daisy 1, an Interconnection Customer (IC), has requested a Generating Facility (GF) interconnection for Vander Schaaf Dairies Daisy 1 (Project) to the Pacific Gas and Electric Company (PG&E)’s distribution system for a 720 kW Photovoltaic generating facility to be located at 13749 Murphy Rd, Escalon CA 95320. The Generating Facility will be connected to PG&E’s Avena 1701 distribution circuit. Interconnection will be in accordance with CPUC’s Generating Facility Interconnections, Electric Rule 21. Transmission Scope: 1. Overvoltage Protection - Part 1- Install CCVT’s on 115kV Line Side 2. Provide SCADA monitoring of the 3-115 kV CCVT potentials 3. Install New Control Building | Substation - Other Equipment | Upgrade/Retrofit | NA | Generator Interconnection | Generation Interconnection | NA | 2024-02-09 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.1347 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5807929 | T.0007443 | WRO Generator Network Upgrades | 2 | 82 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-11-06 | NA | 2027-03-18 | NA | FALSE | 3152 | NA | 73.7091 | 2291.9093 | 0 | 0 | 0 | 0 | 56.8097 | 83.6532 | 1480.6871 | 562.3997 | 108.3596 | 0 | 0 | 56.8096 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,292 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1198 | WRO Generator Network Upgrades |  |  |  | Lagorio Properties LP North, an Interconnection Customer (IC), has requested a Generating Facility (GF)interconnection for Lagorio Properties LP (Project) to the Pacific Gas and Electric Company (PG&E)’sdistribution system for a 576 kW Photovoltaic generating facility to be located at GPS: 37.921169, -121.038304, Stockton, CA 95320. The Generating Facility will be connected to PG&E’s Avena1702 distribution circuit. Interconnection will be in accordance with CPUC’s Generating Facility Interconnections, Electric Rule 21. Transmission Scope: 1. Avena Substation Install 115kV CCVTs - Overvoltage Protection scheme for Bank #1 | Substation - Other Equipment | Upgrade/Retrofit | NA | Generator Interconnection | Generation Interconnection | NA | 2024-02-09 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.1347 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5808018 | T.0008759 | WRO Generator Network Upgrades | 2 | 82 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-11-06 | NA | 2027-03-18 | NA | FALSE | 1708 | NA | 23.4606 | 1027.3998 | 0 | 0 | 0 | 0 | 15.3847 | 69.0041 | 375.9381 | 477.3865 | 89.6865 | 0 | 0 | 15.3847 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,027 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1199 | WRO Generator Network Upgrades |  |  |  | Acquisition of Padre Flat 230 kV Switching Station | Substation - Multiple | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-02-26 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 230 kV | 3 | Not Available | Not Available | NA | NA | 5772690 | T.0002321 | WRO Generator Network Upgrades | 9 | 82 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2014 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 5318-E | 2018-06-25 | Approved | 2018 | Operational | 2 | NA | 2020-01-31 | 2020-01-31 | NA | FALSE | 13620 | NA | 22597.5434 | 22597.5434 | 22403.6975 | 193.8459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22597.5434 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 22611.2503 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $22,598 | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1200 | HSR Interconnection Sub Sites 8-13 (82) |  |  | Madera, Madera ¦ Fresno, Fresno ¦ Hanford, Kings ¦ Pixley, Tulare ¦ Wasco, Kern ¦ Bakersfield, Kern | California High Speed Rail (CHSR) Transmission Power Delivery Project – Sites 8 through 13. The Project will require the installation of a 25 kV AC Traction Electrification System (TES) to power the electric trains. In order to have adequate capacity for train operations, the proposed TES will interconnect into local utility networks at 115 kV or 230 kV, with approximately 30-mile intervals between the traction power substations. This substation spacing results in twelve (12) traction power substations for the 345-mile portion of the line running in PG&E’s service territory.There are six (6) interconnection sites located in the Madera to Bakersfield section. These sites have been designated as Sites 8 through 13. | Substation - Multiple | New | T.0000005 ¦ T.0001650 ¦ T.0000924 ¦ T.0000204 ¦ T.0000980 ¦ T.0003202 ¦ T.0000220 ¦ T.0000143 ¦ T.0000156 | Work Requested by Others | Load Interconnection | NA | NA | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | TBD | NA | 230 ¦ 115 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5766319 | T.0000006 | CHSR Interconnections, Sites 8-13 | 2 | 82 | NA | 2015 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2033-06-28 | NA | 2035-06-05 | NA | FALSE | NA | NA | 4646.7145 | 362274.9452 | 500.1727 | 440.9154 | 390.468 | 438.9385 | 573.4193 | 855.1835 | 7756.027 | 10742.1015 | 10576.7416 | 58395.6013 | 22157.7562 | 4533.5521 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% (Final allocation not yet finalized with CPUC & FERC) ¦ $0 | TBD | NA | 44% | 56% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1201 | WRO Generator Network Upgrades |  |  |  | Construct the Energy Storage Project, which is comprised of 59 Inverters, each rated at 1.8 MW with a maximum gross output of 106.16 MW. Auxiliary load of 5.3 MW and estimated losses of 1.16 MW, results in a net output of 99.7 MW to the CAISO Controlled Grid. | Substation - Bus Arrangement | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 10.5414 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5796082 | T.0007181 | WRO Generator Network Upgrades | 7 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2020 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-06-01 | 2024-02-07 | 2024-01-23 | NA | TRUE | 6926 | NA | 2252.8352 | 2359.4928 | 0 | 0 | 42.5029 | 459.7308 | 1223.9427 | 633.3164 | 0 | 0 | 0 | 0 | 0 | 1726.1764 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 2229.2172 | 0% | 100% ¦ $2,359 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1202 | BART Extension Interconnection (82) |  |  | NA | Forecast placeholder for BART extension interconnections. | Substation - Multiple | New | NA | Work Requested by Others | Load Interconnection | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5775124 | NA | NA | NA | 82 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | TRUE | NA | NA | 0 | 31981 | 0 | 0 | 0 | 0 | 0 | 0 | 31981 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-D NOC, PTC or CPCN requirements
| 1203 | ET SI HSR SPO - MWC 82 |  |  | NA | Forecast placeholder for facility relocation in support of High Speed Rail | Substation - Multiple | Relocate | NA | Work Requested by Others | Facility Relocation | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5808350 | NA | NA | NA | 82 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 5098.2095 | 0 | 0 | 0 | 0 | 0 | 5098.2095 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% (Final allocation not yet finalized with CPUC & FERC) ¦ $0 | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1204 | Manteca Sub Install PTs & Cntrl Bldng |  |  | Manteca, San Joaquin | Install a new protection scheme for the incoming EGI connection. The new protection scheme will require the installation of three new CCVTs and expanding the control building. A new DC panel will be installed to provide the DC power supply the new relays. | Substation - Protection Relay | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 9.8539 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5792365 | T.0006364 | Manteca: Install PTs & Cntrl Bldg | 1 | 82 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-04-01 | 2022-07-01 | 2022-12-28 | NA | TRUE | 2831 | NA | 3394.2449 | 3475.12 | 0 | 4.2366 | 469.1321 | 2389.8109 | 497.2818 | 114.6586 | 0 | 0 | 0 | 0 | 0 | 3360.4614 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2860.5789 | 496.788 | 85.0654 | 0% | 100% ¦ $3,475 | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1205 | WRO Generator Network Upgrades |  |  |  | Install a storage generation plant with a net output of 24.5 MW PG&Es 60 kV Tulucay Substation in Napa County, California. Tulucay Substation: • Extend maiNAux bus with DBSB, install aux switch, fence and grading • Install 2 DTT Receivers with new DTT panel Vaca-Dixon Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit Lakeville Substation: • Install one (1) DTT Transmitter (s) with new T1 circuit | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 4.1869 | NA | 60 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5798548 | T.0007591 | WRO Generator Network Upgrades | 8 | 82 | NA | 2021 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | Other [See Notes] | 2024-04-08 | IS/MND | NA | County of Napa | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-04-07 | 2025-10-10 | 2025-10-10 | NA | TRUE | 7800 | NA | 906.3438 | 7700.5633 | 0 | 0 | 0 | 100.855 | 521.4118 | 1414.2936 | 5631.7711 | 32.2318 | 0 | 0 | 0 | 622.2668 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $7,701 | TBD | NA | 0% | 100% | [CEQA Status] CEQA being drafted [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1206 | WRO Generator Network Upgrades |  |  |  | Install one 230 kV BAAH bay with two CBS, gen-tie line deadend, line switches, CCVT’s, and protective relays at Tesla Sub. The project is to accommodate installment of the Wind project, a small generating facility comprised of 11 wind turbines, each rated at 2 MW. The Small Generating Facility and the associated Interconnection Facilities plan to connect to Tesla 230 kV Substation in Alameda, CA. | Substation - Circuit Breaker | New | T.0007288 ¦ T.0004673 | Generator Interconnection | Generation Interconnection | NA | 2024-03-15 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 69.382 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5782662 | T.0004354 | WRO Generator Network Upgrades | 5 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-06-24 | 2021-09-01 | 2025-04-07 | Customer Action | TRUE | 5467 | NA | 2215.5114 | 8127.7768 | 103.7408 | 373.6156 | 1154.22 | 127.6629 | 354.5138 | 4371.7314 | 1641.722 | 0 | 0 | 0 | 0 | 2114.3234 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $8,128 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1207 | WRO Generator Network Upgrades |  |  |  | Install series bus reactors between Gates Substation 230 kV bus sections E and F (18 ohms in parallel, 9 ohms equivalent/net) (Count: 6 Reactors) which will remove the overstress condition on the Gates Substation 230 kV Bus. This project will support California’s policy to increase renewable energy production and reduce greenhouse gas emission. Completion of the project will enable PG&E to purchase renewable energy from Generation Owners, under a California Public Utilities Commission (CPUC) approved power purchase agreement as part of PG&E’s effort to achieve its renewable portfolio standards (RPS) | Substation - Reactive Equipment | New | T.0008543 | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799287 | T.0008543 | WRO Generator Network Upgrades | 1 | 82 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-08-29 | 2025-10-01 | 2026-04-30 | Prioritization | FALSE | 10750 | NA | 1412.7441 | 11311.0329 | 0 | 0 | 0 | 149.8517 | 884.7763 | 7170.6578 | 2082.1482 | 1023.599 | 0 | 0 | 0 | 1034.628 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $11,311 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1208 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 200 MW. This Generating Facility and the associated Interconnection Facilities plan to connect to the 230 kV Bus at Wheeler Ridge Substation in Kern County. Wheeler Ridge Substation - Install (1) New 230 kV Bay, DTT Rx, & (2) 230 kV CB’s | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5787421 | T.0004974 | WRO Generator Network Upgrades | 6 | 82 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-10-03 | 2022-12-30 | 2024-02-08 | Prioritization | TRUE | 9100 | NA | 2995.1882 | 3011.4337 | 1.2351 | 16.3515 | 270.3739 | 1522.336 | 1113.1009 | 88.0362 | 0 | 0 | 0 | 0 | 0 | 2923.3975 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 2998.0905 | 0% | 100% ¦ $3,011 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1209 | WRO Generator Network Upgrades |  |  |  | Install Solar PV with a maximum gross output of 70.9 MW. This Generating Facility and the associated Interconnection Facilities plan connect to PG&E’s Lakeview Substation in Bakersfield, in Kern County. | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.3475 | NA | 70 kV | 3 | Not Available | Not Available | Tier 5 | Yes | 5791721 | T.0006097 | WRO Generator Network Upgrades | 9 | 82 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2020 | FALSE | NA | NA | NA | True | Final Certified | 2024-04-08 | EIR | NA | Kern County | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-01-06 | 2024-07-07 | 2026-05-05 | Prioritization | FALSE | 15200 | NA | 1576.8619 | 10192.9074 | 0 | 0 | 183.8598 | 863.0174 | 495.8573 | 334.503 | 7676.186 | 634.1098 | 5.3741 | 0 | 0 | 1542.7346 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $10,193 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1210 | WRO Generator Network Upgrades |  |  |  | Install the generation and energy storage project, which is comprised of photovoltaic solar panels, 37 Inverters, each rated at 1.8 MW, and a Battery Energy Storage System (“BESS”) comprised of 14 inverters each rated at 1.8 MW, with a maximum gross output of 66.6 MW. Auxiliary load of 1 MW and estimated losses of 0.7 MW, results in a net output of 64.9 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Arco 230 kV Substation in Kern County, California. Install one new 230 kV BAAH bay w/ three (3) CB, SW’s, new relays for Bank #2 at Arco Sub. | Substation - Circuit Breaker | New | T.0008073 | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.5471 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5796088 | T.0007165 | WRO Generator Network Upgrades | 7 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2023-07-24 | 2024-05-30 | 2024-07-30 | NA | TRUE | 15400 | NA | 6014.3959 | 8189.7935 | 0 | 0 | 30.2925 | 440.4212 | 4789.7095 | 2914.7371 | 14.6332 | 0 | 0 | 0 | 0 | 5260.4232 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $8,190 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1211 | WRO Generator Network Upgrades |  |  |  | Install the generation project, which is comprised of photovoltaic solar panels, 43 x 2.4225 MW inverters, with a maximum gross output of 102.5 MW and Auxiliary load of 1.08 MW results in a net output of 100 MW to the CAISO Controlled Grid. Install a new BAAH bay with two (2) new 230kV circuit breaker with breaker failure relays to The Los Banos 230kV BAAH substation, and (2) Bus Sectionalized CB's, Bus Extension, Site Grading, &New Ctrl Bldg | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5796583 | T.0007250 | WRO Generator Network Upgrades | 5 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-02-03 | 2025-03-31 | 2026-03-31 | Prioritization | TRUE | 17920 | NA | 5209.0904 | 18604.5652 | 0 | 0 | 8.419 | 689.3535 | 3250.2481 | 6291.3291 | 5266.5833 | 3098.6322 | 0 | 0 | 0 | 3948.0206 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $18,605 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1212 | WRO Generator Network Upgrades |  |  |  | Interconnect 300 MW battery storage generating facility to PG&E's Vaca Dixon 230 kV Sub. Vaca-Dixon Sub: Install one new 230 kV double bus bay w/ 1 CB, SWs | Substation - Circuit Breaker | New | T.0007288 | Generator Interconnection | Generation Interconnection | NA | 2024-03-12 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5796191 | T.0007195 | WRO Generator Network Upgrades | 5 | 82 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2020 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-12-17 | NA | 2027-05-10 | NA | TRUE | NA | NA | 1207.4277 | 3993.5251 | 0 | 0 | 2.7157 | 92.7603 | 664.9602 | 742.1695 | 1276.102 | 1023.51 | 190.2491 | 1.0582 | 0 | 760.4362 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,994 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1213 | WRO Generator Network Upgrades |  |  |  | Interconnect 99 MW battery energy storage project at the Ripon 115 kV substation by completing Ring Bus with 2 CBs at Ripon Sub. Reconductor Ripon-Manteca 115 kV Line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total). Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line 25.23 mi section of various conductors from 018/115-043/277. Reconductor Bellota-Riverbank-Melones Sw Sta 115 kV Line (Tulloch Tap) section of 17 miles. Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/0 | Substation - Circuit Breaker | New | T.0004515 ¦ T.0007979 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | 2024-02-07 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.0603 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5797828 | T.0007445 | WRO Generator Network Upgrades | 10 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 3 | 2024-02-12 | 2025-01-07 | 2024-12-19 | NA | TRUE | 13707 | NA | 751.4673 | 2009.491 | 0 | 0 | 13.8209 | 48.7145 | 584.154 | 1226.4842 | 136.3175 | 0 | 0 | 0 | 0 | 646.6893 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,009 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1214 | WRO Generator Network Upgrades |  |  |  | Interconnect 99 MW battery energy storage project at the Ripon 115 kV substation by completing Ring Bus with 2 CBs at Ripon Sub. Reconductor Ripon-Manteca 115 kV Line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total). Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line 25.23 mi section of various conductors from 018/115-043/277. Reconductor Bellota-Riverbank-Melones Sw Sta 115 kV Line (Tulloch Tap) section of 17 miles. Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/0 | Other - Operations Tech | New | T.0004515 ¦ T.0007979 ¦ T.0004301 | Generator Interconnection | Generation Interconnection | NA | 2024-02-07 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.3123 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5797831 | T.0007445 | WRO Generator Network Upgrades | 10 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-05-03 | 2025-01-07 | 2024-12-19 | NA | TRUE | 13707 | NA | 640.2298 | 1483.5324 | 0 | 0 | 2.1114 | 104.8051 | 137.2106 | 1190.8246 | 48.5807 | 0 | 0 | 0 | 0 | 244.1271 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,484 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1215 | WRO Generator Network Upgrades |  |  |  | Interconnect a 150 megawatt (MW) (net output) solar-based generation facility to Gates 230 kV BAAH Switchyard, in Fresno County, California. | Substation - Circuit Breaker | New | T.0003388 | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | NA | NA | 5757640 | T.0001403 | WRO Generator Network Upgrades | 5 | 82 | NA | 2016 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2015 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-01 | 2019-12-23 | 2023-02-17 | Customer action | TRUE | 3121 | NA | 2770.2344 | 2770.2344 | 135.2763 | 183.3289 | 208.2452 | 264.7772 | 60.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 2770.2344 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 2442.4284 | -2442.4284 | 2767.2534 | 0 | 0% | 100% ¦ $2,770 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1216 | WRO Generator Network Upgrades |  |  |  | Interconnect a 60 megawatt (MW) (net output) solar power-based generation and battery storage facility to Pacific Gas and Electric Company’s (PG&E’s) Arco 70 kV Substation. Arco Sub:  Install new partial Double Bus bay  Install one (1) 70kV CB, with breaker control relays  Install Four TSP's, Conductor, Relocate Arco-Tulare Lake 70kV line  Raise 230kV Arco-Gates and Arco-Midway double-circuit | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.5471 | NA | 70 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5545945 | T.0006119 | WRO Generator Network Upgrades | 7 | 82 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2020 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2023-11-15 | 2024-12-07 | 2024-12-02 | NA | TRUE | 7800 | NA | 2744.3629 | 3232.145 | 0 | 0 | 28.4007 | 447.8661 | 1632.7498 | 1095.7021 | 27.4263 | 0 | 0 | 0 | 0 | 2109.0166 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 476.2859 | 1609.0185 | 345.5907 | 0% | 100% ¦ $3,232 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1217 | WRO Generator Network Upgrades |  |  |  | Interconnect Solar Photovoltaic panels with 11 inverters, each rated at 2.08 MW and a 15 MW of Battery Energy Storage Systems to PG&Es Crow Creek 60 kV Sw Sta. Crow Creek Sub: Install new partial BAAH 60 kV bay, 2 CB | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-02-20 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.036 | NA | 60 kV | Not Available | Not Available | Not Available | NA | NA | 5795664 | T.0007108 | WRO Generator Network Upgrades | 6 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-01-02 | 2023-02-05 | 2023-03-14 | NA | TRUE | 4000 | NA | 1888.8946 | 1888.8946 | 0 | 0 | 32.7382 | 922.6989 | 933.2971 | 0.1603 | 0 | 0 | 0 | 0 | 0 | 1888.7343 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1799.1463 | 0.15254 | 0% | 100% ¦ $1,889 | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1218 | WRO Generator Network Upgrades |  |  |  | Interconnection to the Pacific Gas and Electric Company (PG&E)’s distribution system for a 2,344 kW Synchronous generating facility. Scope: 1. Install a new 19" Rack. Install DTT Transmitter to A G Wishon PH. 2. Wire the DTT Transmitter by CB 12 Line Relays, CB 22 Line Relays, CB 32 b Seals and Bank 1 Relays. 3. Install SCADA Controller Selector Switch between CB 12, 22 and 32 Trips to DTT. 4. Install Local Remote and SCADA DTT Cut in / Cut out Switch. 6. Provide DC Power to the DTT Rack. 7. Install MVAJ Relay for Bank 1 DTT Trip. Drawing 4159442 provides the DTT Scheme and its triggers. | Substation - Other Equipment | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-02-09 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.0827 | NA | 70 kV | Not Available | 6. Customer commitments | Not Available | Tier 5 | Yes | 5785891 | T.0004899 | WRO Generator Network Upgrades | 4 | 82 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2021-11-22 | 2022-08-30 | 2024-08-13 | Prioritization | TRUE | 490 | NA | 1770.3839 | 1837.0776 | 3.8787 | 114.6677 | 105.7196 | 49.193 | 1476.0176 | 87.6011 | 0 | 0 | 0 | 0 | 0 | 1749.4765 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,837 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1219 | Panoche: Upgrade Terminal Equipt. |  |  | Fresno | Reconductor 32.59 miles of the Padre Flat Switching Station - Panoche 230 kV Line No. 1 with 795 ACSS conductor. Upgrade associated equipment and structures to match the new conductor rating, as needed. | Substation - Line Termination | Upgrade/Retrofit | T.0004490 ¦ T.0009329 | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | 71 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | 3 | Not Available | Not Available | Tier 5 | Yes | 5794847 | T.0003792 | Padre Flat SS - Panoche #1 20267: Recon. | 4 | 82 | 5534921 | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2024-01-22 | 2024-05-15 | 2024-04-05 | NA | TRUE | 61300 | NA | 918.9576 | 1563.78 | 20.4089 | 54.752 | 72.1323 | 162.7113 | 172.9817 | 1080.7938 | 0 | 0 | 0 | 0 | 0 | 482.9862 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 20.4821 | 54.7501 | 72.1323 | 162.7132 | 144.2681 | 601.3461 | 0% | 100% ¦ $1,564 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1220 | Los Banos: Upgrade Terminal Equipt. |  |  | Merced | Reconductor 4.5 miles of the Los Banos - Padre Flat Switching Station 230 kV Line No. 1 with 1113 ACSS conductor. Upgrade associated equipment to 1,900 Amps to match the new conductor rating, as needed. Replace structures, as needed | Substation - Line Termination | Upgrade/Retrofit | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | 70 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 53.2803 | NA | 230 kV | 3 | Not Available | Not Available | NA | NA | 5794848 | T.0003016 | Los Banos - Padre Flat SS 20266: Recon. | 3 | 82 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6527-E | 2022-03-11 | Approved | 2022 | Operational | 2 | 2022-10-31 | 2023-02-01 | 2022-12-24 | NA | TRUE | 10800 | NA | 1370.3891 | 1370.3891 | 20.3192 | 25.1713 | 138.8551 | 1061.3064 | 124.7371 | 0 | 0 | 0 | 0 | 0 | 0 | 1370.3891 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 20.3786 | 25.1656 | 138.8551 | 1010.868 | 119.6862 | 0 | 0% | 100% ¦ $1,370 | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1221 | Replace Panoche 115 kV CB 112 with 50 kA |  |  | Fresno | Replace 115kV CB 112 at Panoche Substation 2000A 40 kA breaker with a 3000A 50 kA breaker equipped with 3000/5 CT to relieve breaker from being overstressed as a result of a 3rd party generation interconnection. | Substation - Circuit Breaker | Upgrade/Retrofit | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | 16 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 115 kV | 3 | 6. Customer commitments | Not Available | NA | NA | 5782068 | T.0004760 | Panoche CB 112 Overstress | 1 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2012 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-10-26 | 2021-04-30 | 2021-03-05 | NA | FALSE | 3100 | NA | 1917.0744 | 1917.0744 | 77.1358 | 817.3179 | 1022.2385 | 0 | 0.3822 | 0 | 0 | 0 | 0 | 0 | 0 | 1917.0744 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1759.4464 | 0 | 0.35012 | 0 | 0% | 100% ¦ $1,917 | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1222 | Gates: Replace CBs 352, 362, 372 |  |  | Fresno | Replace 230 kV Cap Bank Breakers: CB352, CB362, CB372 at Gates Substation as part of several generation interconnections required network upgrades. CAISO-approved Projects are directly impacting the overstressed level on breakers. Short circuit study in CAISO Generator Interconnection 2020 Annual Reassessment Study revealed that the Gates Cap Bank Breakers have become overstressed and that the overstress is caused by CAISO generation interconnection studies from cluster 10 through 12 for Electric Generation Interconnection projects. PG&E evaluated the short-circuit duty contributions to determine the projects triggering the circuit breaker overstressed and proposes to replace these breakers as part of Network Upgrade. | Substation - Circuit Breaker | Replace | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | 20 | Interconnection System Impact/Facilities Studies | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5796864 | T.0007289 | Gates: Replace CBs 352, 362, 372 | 1 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-10-24 | 2023-03-31 | 2023-05-25 | NA | TRUE | 4850 | NA | 4164.3893 | 4164.3893 | 0 | 0 | 63.9816 | 2346.9876 | 1742.0386 | 11.3815 | 0 | 0 | 0 | 0 | 0 | 4153.0078 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 3797.6746 | 6.6566 | 0% | 100% ¦ $4,164 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1223 | Tesla 500kV: Replace CB 542 |  |  | Alameda | Replace overstressed breakers 542, 612, & 642 at Tesla 500 kV sub to address a normal deficiency projected for 2021 and beyond. | Substation - Circuit Breaker | Replace | T.0007195 ¦ T.0004563 ¦ T.0004354 ¦ T.0007467 ¦ T.0007981 ¦ T.0008098 ¦ T.0008918 ¦ T.0004673 | Generator Interconnection | Generation Interconnection | NA | 2024-03-15 | 35 | Interconnection System Impact/Facilities Studies | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 69.382 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5796865 | T.0007288 | Tesla: Replace CB 542_CB 642_CB 612 | 3 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2020 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-11-04 | 2024-09-30 | 2025-02-28 | NA | TRUE | 14700 | NA | 3578.8718 | 12863.8062 | 0 | 0 | 57.5615 | 381.631 | 2583.0326 | 5936.5194 | 3905.0617 | 0 | 0 | 0 | 0 | 3022.2251 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $12,864 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1224 | Tesla 500kV: Replace CB 612 |  |  | Alameda | Replace overstressed breakers 542, 612, & 642 at Tesla 500 kV sub to address a normal deficiency projected for 2021 and beyond. | Substation - Circuit Breaker | Replace | T.0007195 ¦ T.0004563 ¦ T.0004354 ¦ T.0007467 ¦ T.0007981 ¦ T.0008098 ¦ T.0008918 ¦ T.0004673 | Generator Interconnection | Generation Interconnection | NA | 2024-03-15 | 35 | Interconnection System Impact/Facilities Studies | Other - Deferral | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 69.382 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5797750 | T.0007288 | Tesla: Replace CB 542_CB 642_CB 612 | 3 | 82 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2020 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-03-03 | 2024-09-30 | 2025-08-05 | Prioritization | TRUE | 14700 | NA | 346.9429 | 6531.8906 | 0 | 0 | 10.6595 | 109.7511 | 206.0561 | 2308.1657 | 3876.9805 | 20.2778 | 0 | 0 | 0 | 326.4666 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $6,532 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1225 | Metcalf: Replace Overstressed CBs |  |  | Santa Clara | Replace overstressed CB 492, CB 502, & CB 632 at Metcalf 115 kV substation. Replace overstressed CB 492, CB 502, & CB 632 at Metcalf 115 kV substation. | Substation - Circuit Breaker | Replace | T.0007467 ¦ T.0007032 ¦ T.0007981 | Generator Interconnection | Generation Interconnection | NA | 2024-03-13 | 21 | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5796866 | T.0007291 | Metcalf: Replace Overstressed CBs | 3 | 82 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2020 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-09-03 | NA | 2027-06-23 | NA | FALSE | NA | NA | 291.4349 | 9483.1997 | 0 | 0 | 67.0516 | 64.1256 | 138.6982 | 277.7568 | 4503.989 | 2062.6027 | 2368.9758 | 0 | 0 | 269.8753 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $9,483 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1226 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install an energy storage project, which is comprised of 123 batteries rated at 1.25 MW with a maximum gross output of 151.90 MW, limited to 150 MW net to CAISO grid at Point of Interconnection (POI). | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-01 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 14.7513 | NA | 115 kV | 3 | Not Available | Not Available | NA | NA | 5785810 | T.0004818 | WRO Generator Network Upgrades | 5 | 82 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2017 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6581-E | 2022-05-04 | Approved | 2022 | Operational | 2 | 2023-03-01 | 2022-04-02 | 2023-12-01 | Customer Action | TRUE | 2361 | NA | 3960.064 | 3960.064 | 35.7832 | 168.1232 | 319.7742 | 1919.9 | 1499.0786 | 17.4048 | 0 | 0 | 0 | 0 | 0 | 3942.6592 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 3492.8908 | 60.4726 | 0% | 100% ¦ $3,960 | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1227 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Other Equipment | New | T.0008048 | Generator Interconnection | Generation Interconnection | NA | 2024-02-02 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.373 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5789331 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA | 2020 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-11-05 | 2025-03-19 | 2025-12-19 | Prioritization | TRUE | 31200 | NA | 389.2137 | 1491.095 | 0 | 31.7954 | 56.3671 | 106.6652 | 181.0794 | 191.559 | 798.2977 | 125.3313 | 0 | 0 | 0 | 375.907 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,491 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1228 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Other Equipment | New | T.0008048 | Generator Interconnection | Generation Interconnection | NA | 2024-03-07 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 15.1779 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5792479 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA | 2020 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-01-28 | 2025-03-19 | 2025-03-05 | NA | TRUE | 14700 | NA | 269.712 | 1028.8013 | 0 | 13.8056 | 61.2689 | 118.1911 | 63.2178 | 204.8804 | 563.1804 | 4.257 | 0 | 0 | 0 | 256.4835 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,029 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1229 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Other Equipment | New | T.0008048 | Generator Interconnection | Generation Interconnection | NA | 2024-04-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 0.26068 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5795098 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA | 2020 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-01-22 | 2025-03-19 | 2025-03-20 | NA | TRUE | 31200 | NA | 279.764 | 1196.3864 | 0 | 0 | 30.4639 | 85.9446 | 152.8874 | 515.9798 | 404.1806 | 6.9301 | 0 | 0 | 0 | 269.2959 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,196 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1230 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Other Equipment | New | T.0008048 | Generator Interconnection | Generation Interconnection | NA | 2024-02-08 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 2.3791 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5792514 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA | 2020 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-12-10 | 2025-03-19 | 2025-04-01 | NA | TRUE | 31200 | NA | 537.1626 | 1577.8482 | 0 | 17.28 | 37.915 | 107.5189 | 323.1324 | 426.1881 | 665.8139 | 0 | 0 | 0 | 0 | 485.8463 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,578 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1231 | WRO Generator Network Upgrades |  |  |  | The “Interconnection Customer” (IC) plans to install the generation interconnection project, which is comprised of photovoltaic solar panels and battery energy storage, 41 Inverters, each rated at 2.5 MW (PV) and 41 inverters each rated at 2.5 MW (BESS) with a maximum gross output of 102.5 MW. Auxiliary load of 0.1 MW and estimated losses of 2.4 MW, results in a net output of 100 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Cayetano Substation in Alameda County, California (the “Project”). | Substation - Circuit Breaker | New | T.0008048 | Generator Interconnection | Generation Interconnection | NA | 2024-04-03 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 0.26068 | NA | 230 kV | 3 | Not Available | Not Available | Tier 5 | Yes | 5789329 | T.0005689 | WRO Generator Network Upgrades | 11 | 82 | NA | 2020 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-08-13 | 2025-03-19 | 2025-10-15 | Prioritization | TRUE | 31200 | NA | 2353.9649 | 15225.4772 | 0 | 28.3092 | 108.1569 | 385.5924 | 1218.0585 | 7353.2379 | 6049.5191 | 82.6032 | 0 | 0 | 0 | 1740.117 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $15,225 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1232 | BUCKS CREEK PH RECONNECTION SUB NU WORK |  |  | Plumas | The Caibou-Palermo 115 kV line, which connected the Powerhouse to the transmission grid, has been taken out of service for an extended timeframe in the aftermath of the November 2018 Camp Fire. This outage has disabled the Powerhouse’s ability to transmit power to SVP. The Powerhouse is currently generating a small amount to only provide station service. PG&E is obligated under the Agreement to transmit the power generated by the Powerhouse to SVP. The Agreement states that in the event of a transmission line outage, PG&E must work diligently to restore service on the same value-based schedule and priority as if it were a PG&E-owned facility. This project will provide an alternative interconnection for the Powerhouse. This project will connect the Powerhouse to the Bucks Creek-Rock Creek-Cresta 230 kV Line and install a 230/115kV step-up transformer at Bucks Creek Switchyard to facilitate the interconnection to the 230kV grid. | Substation - Transformer | New | NA | Generator Interconnection | Load Interconnection | NA | 2024-03-20 | NA | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 0.31219 | NA | 230 ¦ 115 kV | Not Available | 6. Customer commitments | Not Available | NA | NA | 5785299 | T.0004715 | Bucks Creek PH-Grizzly PH Reconnection | 5 | 82 | NA | 2019 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-04-25 | 2021-12-31 | 2023-12-20 | Weather | TRUE | 19981 | NA | 36545.5725 | 41331.3287 | 193.9146 | 3514.1524 | 3098.4621 | 18297.9835 | 11013.2824 | 5179.3027 | 34.2309 | 0 | 0 | 0 | 0 | 36117.7951 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 35784.2186 | 433.2498 | 0% | 100% ¦ $41,331 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1233 | CRESTA PH Remote Ends |  |  | Butte | The Caibou-Palermo 115 kV line, which connected the Powerhouse to the transmission grid, has been taken out of service for an extended timeframe in the aftermath of the November 2018 Camp Fire. This outage has disabled the Powerhouse’s ability to transmit power to SVP. The Powerhouse is currently generating a small amount to only provide station service. PG&E is obligated under the Agreement to transmit the power generated by the Powerhouse to SVP. The Agreement states that in the event of a transmission line outage, PG&E must work diligently to restore service on the same value-based schedule and priority as if it were a PG&E-owned facility. This project will provide an alternative interconnection for the Powerhouse. This project will connect the Powerhouse to the Bucks Creek-Rock Creek-Cresta 230 kV Line and install a 230/115kV step-up transformer at Bucks Creek Switchyard to facilitate the interconnection to the 230kV grid. | Substation - Other Equipment | Upgrade/Retrofit | NA | Generator Interconnection | Load Interconnection | NA | 2024-02-06 | NA | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.4913 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5790518 | T.0004715 | Bucks Creek PH-Grizzly PH Reconnection | 5 | 82 | NA | 2019 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-04-28 | 2021-12-31 | 2025-08-11 | Weather | TRUE | 19981 | NA | 875.1907 | 4459.0505 | 0 | 26.2358 | 179.8266 | 367.1815 | 270.4477 | 188.1875 | 3420.2927 | 6.8788 | 0 | 0 | 0 | 843.6915 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $4,459 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1234 | GRIZZLY PH Remote Ends |  |  | Plumas | The Caibou-Palermo 115 kV line, which connected the Powerhouse to the transmission grid, has been taken out of service for an extended timeframe in the aftermath of the November 2018 Camp Fire. This outage has disabled the Powerhouse’s ability to transmit power to SVP. The Powerhouse is currently generating a small amount to only provide station service. PG&E is obligated under the Agreement to transmit the power generated by the Powerhouse to SVP. The Agreement states that in the event of a transmission line outage, PG&E must work diligently to restore service on the same value-based schedule and priority as if it were a PG&E-owned facility. This project will provide an alternative interconnection for the Powerhouse. This project will connect the Powerhouse to the Bucks Creek-Rock Creek-Cresta 230 kV Line and install a 230/115kV step-up transformer at Bucks Creek Switchyard to facilitate the interconnection to the 230kV grid. | Substation - Other Equipment | Upgrade/Retrofit | NA | Generator Interconnection | Load Interconnection | NA | 2021-06-09 | NA | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 0.74169 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5790520 | T.0004715 | Bucks Creek PH-Grizzly PH Reconnection | 5 | 82 | NA | 2019 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-09-08 | 2021-12-31 | 2023-12-20 | Weather | TRUE | 19981 | NA | 3388.3765 | 3523.4668 | 0 | 28.8824 | 553.6471 | 1265.5587 | 1468.7185 | 206.6601 | 0 | 0 | 0 | 0 | 0 | 3316.8067 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 3316.8053 | 83.0395 | 0% | 100% ¦ $3,523 | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1235 | ROCK CREEK PH Remote Ends |  |  | Plumas | The Caibou-Palermo 115 kV line, which connected the Powerhouse to the transmission grid, has been taken out of service for an extended timeframe in the aftermath of the November 2018 Camp Fire. This outage has disabled the Powerhouse’s ability to transmit power to SVP. The Powerhouse is currently generating a small amount to only provide station service. PG&E is obligated under the Agreement to transmit the power generated by the Powerhouse to SVP. The Agreement states that in the event of a transmission line outage, PG&E must work diligently to restore service on the same value-based schedule and priority as if it were a PG&E-owned facility. This project will provide an alternative interconnection for the Powerhouse. This project will connect the Powerhouse to the Bucks Creek-Rock Creek-Cresta 230 kV Line and install a 230/115kV step-up transformer at Bucks Creek Switchyard to facilitate the interconnection to the 230kV grid. | Substation - Other Equipment | Upgrade/Retrofit | NA | Generator Interconnection | Load Interconnection | NA | 2024-02-12 | NA | Interconnection System Impact/Facilities Studies | Wires - Replacement Alternative | $15 Mil - $20 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 1.0255 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5790519 | T.0004715 | Bucks Creek PH-Grizzly PH Reconnection | 5 | 82 | NA | 2019 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-08-12 | 2021-12-31 | 2025-08-11 | Weather | TRUE | 19981 | NA | 1448.4553 | 6653.3107 | 0 | 30.7088 | 172.8791 | 671.8764 | 516.9503 | 1844.3725 | 3400.51 | 16.0135 | 0 | 0 | 0 | 1392.4146 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $6,653 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1236 | QC8RAS-08 Gates 500/230 kV Transformer B |  |  | Fresno | The Gates 500kv Bank 11/12 QRAS project will install a relay scheme at Gates substation and the Castanea customer site that will provide overload protection in the event of an outage on Gates 500kv Bank 11 or 12 | Other - Remedial Action Scheme/Special Protection Scheme | New | T.0008538 ¦ T.0008968 ¦ T.0008967 | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | NA | Interconnection System Impact/Facilities Studies | Other - Deferral | $2 Mil - $3 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 77.6619 | NA | 500 ¦ 230 kV | Not Available | 6. Customer commitments | Not Available | Tier 5 | Yes | 5774961 | T.0003009 | QC8RAS-08 Gates 500/230 kV Transformer B | 1 | 82 | NA | 2018 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2022-06-13 | 2023-05-01 | 2024-05-03 | Material | TRUE | 2800 | NA | 1695.7707 | 1960.9441 | 83.0699 | 68.6971 | 139.8447 | 744.1364 | 463.8683 | 461.3277 | 0 | 0 | 0 | 0 | 0 | 1499.6163 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,961 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1237 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 100 megawatt (MW) (net output) solar-based generation facility to the Pacific Gas and Electric Company’s (PG&E’s) new 230 kV Bitterwater Switching Station which connects to the Midway – Wheeler Ridge 230 kV Line No.2 in Kern County, California. | Substation - Multiple | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 10.403 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5768563 | T.0001353 | WRO Generator Network Upgrades | 11 | 82 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2015 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6634-E | 2022-06-30 | Approved | 2022 | Construction (over 75%) | 3 | 2023-02-14 | 2019-11-15 | 2024-04-30 | Customer Action | TRUE | 6600 | NA | 2514.9518 | 3539.1622 | 0.7485 | 1.2051 | 17.3905 | 174.9436 | 1895.0635 | 1435.7072 | 0 | 0 | 0 | 0 | 0 | 2103.455 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,539 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1238 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 100 megawatt (MW) (net output) solar-based generation facility to the Pacific Gas and Electric Company’s (PG&E’s) new 230 kV Bitterwater Switching Station which connects to the Midway – Wheeler Ridge 230 kV Line No.2 in Kern County, California. | Substation - Multiple | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-15 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5550944 | T.0001353 | WRO Generator Network Upgrades | 11 | 82 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2015 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6634-E | 2022-06-30 | Approved | 2022 | Construction (over 75%) | 3 | 2023-02-14 | 2019-11-15 | 2024-04-30 | Customer Action | TRUE | 6600 | NA | 0.5102 | 15452.5102 | 0 | 0 | 0 | 0.5102 | 0 | 15452 | 0 | 0 | 0 | 0 | 0 | 0.5102 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 0.51024 | 0 | 0 | 0% | 100% ¦ $15,453 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1239 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 200 megawatt (MW) (net output) energy-storage generation facility to the Pacific Gas and Electric Company’s (PG&E’s) Pittsburg 230kV Substation. | Substation - Switch | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.72358 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | NA | NA | 5779009 | T.0003747 | WRO Generator Network Upgrades | 4 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2017 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-12-01 | 2021-03-01 | 2021-06-14 | NA | FALSE | 8700 | NA | 3284.5004 | 3284.5004 | 19.9663 | 816.9566 | 2435.1748 | 1.7329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3284.5004 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 3056.6184 | 1.6139 | 0 | 0 | 0% | 100% ¦ $3,285 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1240 | WRO Generator Network Upgrades |  |  |  | The generation project proposes to interconnect a 75 megawatt (MW) (net output) energy storage generation facility to the Pacific Gas and Electric Company’s (PG&E’s) Metcalf 115 kV Substation, in Santa Clara County, California. | Substation - Circuit Breaker | New | T.0007291 | Generator Interconnection | Generation Interconnection | NA | 2024-03-13 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 37.8815 | NA | 115 kV | 3 | 6. Customer commitments | Not Available | NA | NA | 5784846 | T.0004676 | WRO Generator Network Upgrades | 3 | 82 | NA | 2019 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-10-21 | 2021-05-01 | 2023-10-13 | Customer Action | TRUE | 5000 | NA | 4570.3471 | 4574.8796 | 62.6732 | 523.0733 | 299.182 | 2544.0623 | 1142.7379 | 3.151 | 0 | 0 | 0 | 0 | 0 | 4571.7287 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 4571.7136 | -8.406 | 0% | 100% ¦ $4,575 | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1241 | WRO Generator Network Upgrades |  |  |  | The IC plans to install a Battery Energy Storage and Photovoltaic Solar System, 244 BESS Inverters, each rated at 2.09 MW and 235 PV inverters, each rated at 2.185 MW, with a maximum gross output of 511.9 MW. Auxiliary load of 5.1 MW and estimated losses of 11.9 MW, results in a net output of 500 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Delevan Substation in Colusa County, California (the “Project”). The project scope of work includes following: Interconnection Facility: Substation scope: Delevan Substation: • Install line relay package, voltage transformers, dead-end, and line switch • Install fiber terminations near the fence for LCD communications at Delevan Substation Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E RTU, EMS Telemetry, SCADA Transmission Line: • Install 2 spans of conductor, 1 TSP single circuit, and a Gen-Tie review by PG&E Reliability Network Upgrade: Substation scope: Delevan Substation (IRNU): • Install new CB to complete BAAH bay, with breaker control relays Cottonwood Substation (GRNU): • Replace 230 kV circuit breakers 232, 242 and associated switches/relays | Substation - Circuit Breaker | Replace | T.0009188¦ T.0001609 ¦ T.0008063 | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 26.1945 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799987 | T.0008063 | WRO Generator Network Upgrades | 6 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-08-15 | NA | 2027-03-30 | NA | FALSE | 5191 | NA | 204.7144 | 5146.0556 | 0 | 0 | 0 | 20.1054 | 139.1965 | 404.1095 | 2167.0703 | 2050.111 | 365.463 | 0 | 0 | 159.3018 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $5,146 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1242 | WRO Generator Network Upgrades |  |  |  | The IC plans to install a Battery Energy Storage and Photovoltaic Solar System, 244 BESS Inverters, each rated at 2.09 MW and 235 PV inverters, each rated at 2.185 MW, with a maximum gross output of 511.9 MW. Auxiliary load of 5.1 MW and estimated losses of 11.9 MW, results in a net output of 500 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities connects to the Participating TO (Pacific Gas and Electric Company (“PG&E”)) - owned Delevan Substation in Colusa County, California (the “Project”). The project scope of work includes following: Interconnection Facility: Substation scope: Delevan Substation: • Install line relay package, voltage transformers, dead-end, and line switch • Install fiber terminations near the fence for LCD communications at Delevan Substation Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E RTU, EMS Telemetry, SCADA Transmission Line: • Install 2 spans of conductor, 1 TSP single circuit, and a Gen-Tie review by PG&E Reliability Network Upgrade: Substation scope: Delevan Substation (IRNU): • Install new CB to complete BAAH bay, with breaker control relays Cottonwood Substation (GRNU): • Replace 230 kV circuit breakers 232, 242 and associated switches/relays | Substation - Circuit Breaker | New | T.0009188¦ T.0001609 ¦ T.0008063 | Generator Interconnection | Generation Interconnection | NA | 2024-03-07 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.7615 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799986 | T.0008063 | WRO Generator Network Upgrades | 6 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-12-05 | NA | 2025-06-03 | NA | TRUE | 1720 | NA | 290.9581 | 1720.1304 | 0 | 0 | 0 | 41.9215 | 235.6682 | 902.5233 | 540.0175 | 0 | 0 | 0 | 0 | 277.5896 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,720 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1243 | WRO Generator Network Upgrades |  |  |  | The IC plans to install the Energy Storage Project, which is comprised of three hundred and ninety six (396) Parker 890GT-B inverters rated at 1.976 MW each with auxiliary load and associated losses of 26.3 MW that result in a maximum net output of 750 MW to the CAISO Controlled Grid. The Large Generating Facility and associated Interconnection Facilities (the “Project”) connect to the Participating TO (Pacific Gas and Electric Company (“PG&E”) – owned 500 kV Moss Landing PP Substation in Monterey County California. | Substation - Circuit Breaker | New | T.0007288 ¦ T.0007291 | Generator Interconnection | Generation Interconnection | NA | 2024-03-12 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 41.3213 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5797901 | T.0007467 | WRO Generator Network Upgrades | 5 | 82 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-08-03 | NA | 2027-05-27 | NA | FALSE | NA | NA | 99.0045 | 9952.1898 | 0 | 0 | 0 | 13.6239 | 61.2168 | 690.5185 | 4351.2418 | 3630.8852 | 1204.7037 | 0 | 0 | 74.8407 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $9,952 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1244 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install generation interconnection project, which is comprised of photovoltaic solar panels, 13 PV Inverters, each rated at 3.3725 MW, with a maximum gross output of 41.05 MW. Auxiliary load of 0.411 MW and estimated losses of [0.639] MW, results in a net output of 40 MW to the CAISO Controlled Grid,, a 20 MW Battery Energy Storage System (“BESS”) using DC coupling is added to the PV system. | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-01 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.0905 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5794018 | T.0006847 | WRO Generator Network Upgrades | 8 | 82 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | 2020 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-05-13 | 2023-02-07 | 2023-10-13 | Prioritization | TRUE | 6500 | NA | 1742.3678 | 1874.5144 | 0 | 0 | 185.8287 | 918.2658 | 632.2351 | 69.1081 | 69.0766 | 0 | 0 | 0 | 0 | 1736.3297 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 1736.6445 | 7.5955 | 0% | 100% ¦ $1,875 | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1245 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Substation - Other Equipment | Upgrade/Retrofit | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805806 | T.0009383 | WRO Generator Network Upgrades | 5 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | CEC | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-03-01 | NA | 2029-02-27 | NA | FALSE | NA | NA | 0 | 10748.6241 | 0 | 0 | 0 | 0 | 0 | 80.2538 | 357.6407 | 331.3069 | 871.2733 | 6183.9449 | 2924.2045 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $10,749 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1246 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Substation - Other Equipment | Upgrade/Retrofit | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805805 | T.0009383 | WRO Generator Network Upgrades | 5 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | CEC | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-03-01 | NA | 2029-02-27 | NA | FALSE | NA | NA | 0 | 9867.6258 | 0 | 0 | 0 | 0 | 0 | 59.2399 | 164.7072 | 290.6488 | 646.2044 | 5805.9934 | 2900.8322 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $9,868 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1247 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Substation - Other Equipment | Upgrade/Retrofit | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | 2024-03-15 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805804 | T.0009383 | WRO Generator Network Upgrades | 5 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | CEC | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-03-01 | NA | 2029-02-27 | NA | FALSE | NA | NA | 0 | 9867.6258 | 0 | 0 | 0 | 0 | 0 | 59.2399 | 164.7072 | 290.6488 | 646.2044 | 5805.9934 | 2900.8322 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $9,868 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1248 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the generation plant with a maximum net output of 1150MW to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be new customer built switching station in Fresno County, California. The solar project proposes to construct a new 500kV switching station with 2 initial bays, install 5-500kV circuit breakers, 1 MPAC building, build a new 500kV transmission line loop-in for the Los Banos - Midway #2, build a new Darden - Los Banos 500kV Line, build a new Darden - Midway 500kV line. | Substation - Multiple | New | T.0010032 ¦ T.0008543 ¦ T.0001650 | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | TBD | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5554012 | T.0009383 | WRO Generator Network Upgrades | 5 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2023 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | CEC | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | NA | NA | 2026-01-30 | NA | FALSE | NA | NA | 0 | 16800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16800 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $16,800 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1249 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the Large Generation Facility project to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be Arco 230kV Substation. The Point of Change of Ownership (POCO), shall be one span outside of the POI. The total net output 150MW. This project proposes to install a new gen tie line from the Arcturus project(Q1586) site to Arco substation, replace 2 existing 230kV breakers, rearrange Arco bank 1 connection point to bay #2 on the 230kV bus at Arco, install 2 disconnect switches, and shares cost for new Arco 230kV control building. | Substation - Circuit Breaker | New | T.0008073 | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 4.5471 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805921 | T.0009393 | WRO Generator Network Upgrades | 3 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | 2023 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-03-25 | NA | 2027-09-14 | NA | FALSE | NA | NA | 0 | 2443.7736 | 0 | 0 | 0 | 0 | 0 | 432.729 | 253.7939 | 186.2916 | 1506.7711 | 64.188 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,444 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1250 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the Large Generation Facility project to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be Arco 230kV Substation. The Point of Change of Ownership (POCO), shall be one span outside of the POI. The total net output 150MW. This project proposes to install a new gen tie line from the Arcturus project(Q1586) site to Arco substation, replace 2 existing 230kV breakers, rearrange Arco bank 1 connection point to bay #2 on the 230kV bus at Arco, install 2 disconnect switches, and shares cost for new Arco 230kV control building. | Substation - Other Equipment | Upgrade/Retrofit | T.0008073 | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805922 | T.0009393 | WRO Generator Network Upgrades | 3 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | 2023 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-03-25 | NA | 2027-09-14 | NA | FALSE | NA | NA | 0 | 2058.0884 | 0 | 0 | 0 | 0 | 0 | 113.8837 | 386.7004 | 100.8431 | 1422.2385 | 34.4227 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,058 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1251 | WRO Generator Network Upgrades |  |  |  | The Interconnection Customer (IC) plans to install the Large Generation Facility project to the CAISO Controlled Grid. The Point of Interconnection (POI) of the project, shall be Arco 230kV Substation. The Point of Change of Ownership (POCO), shall be one span outside of the POI. The total net output 150MW. This project proposes to install a new gen tie line from the Arcturus project(Q1586) site to Arco substation, replace 2 existing 230kV breakers, rearrange Arco bank 1 connection point to bay #2 on the 230kV bus at Arco, install 2 disconnect switches, and shares cost for new Arco 230kV control building. | Substation - Other Equipment | Upgrade/Retrofit | T.0008073 | Generator Interconnection | Generation Interconnection | NA | 2024-03-15 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5805923 | T.0009393 | WRO Generator Network Upgrades | 3 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | 2023 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-03-24 | NA | 2027-09-13 | NA | FALSE | NA | NA | 0 | 2461.9403 | 0 | 0 | 0 | 0 | 0 | 664.6652 | 217.0166 | 126.8652 | 1426.6905 | 26.7028 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,462 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1252 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Storage generation plant with a net output of 250MW to Pacific Gas and Electric Company’s (PG&E’s) SF H (Martin) Substation 115kV bus in San Francisco CA. | Substation - Circuit Breaker | New | T.0007288 ¦ T.0007287 ¦ T.0001493 | Generator Interconnection | Generation Interconnection | NA | 2024-03-20 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 18.2105 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799981 | T.0008098 | WRO Generator Network Upgrades | 5 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-10-02 | NA | 2026-05-26 | NA | FALSE | NA | NA | 3.0201 | 1354.3447 | 0 | 0 | 0 | 0 | 2.9845 | 171.6638 | 828.8354 | 350.8611 | 0 | 0 | 0 | 2.9845 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,354 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1253 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Storage generation plant with a net output of 300.1 MW to Pacific Gas and Electric Company’s (PG&E’s) Gates Substation 500 kV bus in Huron, Fresno County, CA. The project scope of work includes following: Interconnection Facility: Gates Substation:  Install Gen. Tie BAAH Line Terminal Equipment  Install Fiber termination Generation Site:  PG&E pre-parallel inspection, Engineering Review  PG&E Install RTU, EMS Telemetry, SCADA Transmission Line:  Construct Gen-Tie conductors, 1 TSP single circuit, and PG&E review Reliability Network Upgrade: Gates Substation:  Install a new 500kV BAAH Bay with (2) 500kV breakers  Building and site expansion with security wall Midway Substation:  Replace 500kV breaker CB 722 (due to overstress) including relays  Replace CB 722 disconnects | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799148 | T.0007722 | WRO Generator Network Upgrades | 5 | 82 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-06-03 | 2025-08-01 | 2025-04-01 | NA | TRUE | 40600 | NA | 4814.1498 | 22781.5896 | 0 | 0 | 0 | 136.2726 | 2691.5593 | 18015.5612 | 1938.1966 | 0 | 0 | 0 | 0 | 2827.8318 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $22,782 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1254 | WRO Generator Network Upgrades |  |  |  | The Project is a Battery Storage generation plant with a net output of 300.1 MW to Pacific Gas and Electric Company’s (PG&E’s) Gates Substation 500 kV bus in Huron, Fresno County, CA. The project scope of work includes following: Interconnection Facility: Gates Substation:  Install Gen. Tie BAAH Line Terminal Equipment  Install Fiber termination Generation Site:  PG&E pre-parallel inspection, Engineering Review  PG&E Install RTU, EMS Telemetry, SCADA Transmission Line:  Construct Gen-Tie conductors, 1 TSP single circuit, and PG&E review Reliability Network Upgrade: Gates Substation:  Install a new 500kV BAAH Bay with (2) 500kV breakers  Building and site expansion with security wall Midway Substation:  Replace 500kV breaker CB 722 (due to overstress) including relays  Replace CB 722 disconnects | Substation - Circuit Breaker | Replace | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | 31 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799149 | T.0007722 | WRO Generator Network Upgrades | 5 | 82 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-01 | 2025-08-01 | 2025-04-04 | NA | TRUE | 40600 | NA | 1184.0848 | 3614.4824 | 0 | 0 | 0 | 71.2465 | 696.8936 | 2634.6991 | 211.6432 | 0 | 0 | 0 | 0 | 768.1401 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,614 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1255 | WRO Generator Network Upgrades |  |  |  | The Project is a combined photovoltaic solar and battery energy storage technology-based generation facility with a net output of 500.0 MW to the CAISO controlled grid. The Large Generating Facility and associated Interconnection Facilities connects to the new 230kV switching station (or the new “Q1593 Switching Station”) along PG&E’s Gates-Midway 230kV transmission line in Kettleman City, Kings County, California (the “Project”). | Substation - Multiple | New | T.0008543 | Generator Interconnection | Generation Interconnection | NA | 2024-03-15 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 94.5324 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5803145 | T.0008735 | WRO Generator Network Upgrades | 9 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | NA | NA | NA | True | Final Certified | 2024-12-05 | EIR | NA | Kern County | NA | NOC: AL 7236-E | 2024-04-05 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2025-04-25 | NA | 2026-01-29 | NA | FALSE | NA | NA | 197.7289 | 2253.5479 | 0 | 0 | 0 | 0 | 169.2074 | 339.2632 | 1273.5711 | 471.5063 | 0 | 0 | 0 | 169.2073 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,254 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1256 | WRO Generator Network Upgrades |  |  |  | The Project is a combined photovoltaic solar and battery energy storage technology-based generation facility with a net output of 500.0 MW to the CAISO controlled grid. The Large Generating Facility and associated Interconnection Facilities connects to the new 230kV switching station (or the new “Q1593 Switching Station”) along PG&E’s Gates-Midway 230kV transmission line in Kettleman City, Kings County, California (the “Project”). | Substation - Multiple | New | T.0008543 | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | TBD | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5803146 | T.0008735 | WRO Generator Network Upgrades | 9 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | NA | NA | NA | True | Final Certified | 2024-12-05 | EIR | NA | Kern County | NA | NOC: AL 7236-E | 2024-04-05 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2024-07-05 | NA | 2026-01-29 | NA | FALSE | NA | NA | 1.376 | 16801.5715 | 0 | 0 | 0 | 0 | 1.3599 | 0.0998 | 0.107 | 16800.0047 | 0 | 0 | 0 | 1.3599 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $16,802 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1257 | WRO Generator Network Upgrades |  |  |  | The Project is a PV and battery generation plant with a net output of 150 MW to Pacific Gas and Electric Company’s (PG&E’s) owned Cortina 115 kV Substation in Colusa County CA The high level project scope of work includes following: Interconnection Facility: Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E RTU, EMS Telemetry, SCADA Transmission Line: • Install 4 spans of conductor, 3 TSPs single circuit, and gen-tie review by PG&E Interconnection Facilities: • Cortina Substation: Install line relay package, voltage transformers, dead-end, and line switch; IT: Install fiber terminations near the fence for LCD communications Reliability Network Upgrade: Substation scope: • Cortina Substation: Install new BAAH bay, 3 CBs, with breaker control relays Deliverability Network Upgrade: • See separate Authorization for T.0007629 order 74043720 routed in Unifier. o Re-conductor Fulton – Hopland 60 kV Line (Fitch Mountain Tap 009/005A – Geysers Jct 016/004) ~7 mi total length with 715 AAC | Substation - Circuit Breaker | New | T.0001609 ¦ T.0007629 | Generator Interconnection | Generation Interconnection | NA | 2024-03-07 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.7436 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5800367 | T.0008218 | WRO Generator Network Upgrades | 4 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2022 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | CEC | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-11-25 | NA | 2026-01-02 | NA | FALSE | 3048 | NA | 416.2536 | 3047.4317 | 0 | 0 | 0 | 63.9599 | 271.3132 | 701.2259 | 1801.5978 | 209.335 | 0 | 0 | 0 | 335.2731 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $3,047 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1258 | WRO Generator Network Upgrades |  |  |  | The project is a solar generation plant with a net output of 800 MW to Pacific Gas and Electric Company’s (PG&E’s) Midway Substation in Kern County. The project scope of work includes following: Interconnection Facility (From LGIA Table A-1): Midway Substation: • The Point of Interconnection of the Project is Midway Substation, at Bay 5 between CBs 852 and 952 on the 500 kV bus in a breaker-and-a-half (“BAAH”) configuration. • Install fiber terminations near the fence for LCD communications. Generation Site: • PG&E Pre-Parallel Inspection, Engineering Review • PG&E Install RTU, EMS Telemetry, SCADA Transmission Line: • Gen-Tie: Install 2 conductors, 1 TSP single circuit, and PG&E review Reliability Network Upgrade (From LGIA Table G-1): Midway Substation: • Complete BAAH Bay, CB, Sw, • Install Dead-end structure, Bkr, Control Relays • Replace CB 712 with new breaker with 63kA interrupting capacity Gates Substation: • Install series bus reactors between Gates Substation 230kV bus sections E and F | Substation - Circuit Breaker | New | T.0008543 | Generator Interconnection | Generation Interconnection | NA | 2024-03-15 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799285 | T.0007731 | WRO Generator Network Upgrades | 6 | 82 | NA | 2022 | 2023 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-09-11 | 2025-12-01 | 2025-10-03 | NA | TRUE | 22700 | NA | 804.1054 | 13175.1798 | 0 | 0 | 0 | 85.6381 | 668.1337 | 4349.9893 | 5485.2008 | 2586.218 | 0 | 0 | 0 | 753.7718 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $13,175 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1259 | WRO Generator Network Upgrades |  |  |  | The Project is a Solar-PV, Wind, and Battery Storage generation plant with a net output of 400MW connects to Pacific Gas and Electric Company’s (PG&E’s) Tesla Substation in Tracy, San Joaquin County, CA. Tesla Substation 500 kV:  Expand 500 kV BAAH Bay expansion with (1) 500 kV CB. | Substation - Circuit Breaker | New | T.0001609 ¦ T.0007291 ¦ T.0007288 | Generator Interconnection | Generation Interconnection | NA | 2024-03-15 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | 69.382 | NA | 500 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803784 | T.0008918 | WRO Generator Network Upgrades | 4 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-07-26 | NA | 2028-04-03 | NA | FALSE | NA | NA | 87.4474 | 11359.8402 | 0 | 0 | 0 | 0 | 66.6191 | 1128.3732 | 777.601 | 3563.6384 | 3267.9024 | 2517.0493 | 38.6568 | 66.6191 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $11,360 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1260 | WRO Generator Network Upgrades |  |  |  | The Project is a Storage generation plant with a net output of 200.0 MW to Pacific Gas and Electric Company’s (PG&E’s) Los Esteros Substation San Jose CA. | Substation - Circuit Breaker | New | T.0007288 ¦ T.0007287 ¦ T.0007291 | Generator Interconnection | Generation Interconnection | NA | 2024-03-12 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5799786 | T.0007981 | WRO Generator Network Upgrades | 4 | 82 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-03-03 | NA | 2027-08-06 | NA | FALSE | NA | NA | 608.5834 | 10240.3823 | 0 | 0 | 0 | 11.2157 | 527.9499 | 654.1965 | 2340.0439 | 3906.3191 | 2758.1838 | 42.4732 | 0 | 539.1657 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $10,240 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1261 | WRO Generator Network Upgrades |  |  |  | The Project is a Wind generation plant with a net output of 1000MW connects to Pacific Gas and Electric Company’s (PG&E’s) Diablo Canyon Switching Station 500 kV in Avila Beach San Luis County, CA | Substation - Circuit Breaker | New | T.0003009 ¦ T.0008543 ¦ T.0007722 | Generator Interconnection | Generation Interconnection | NA | 2024-03-07 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 35.6227 | NA | 500 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5804097 | T.0008967 | WRO Generator Network Upgrades | 3 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | 2022 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-01-11 | NA | 2030-01-23 | NA | FALSE | NA | NA | 1298.9586 | 5599.0754 | 0 | 0 | 0 | 0 | 54.8057 | 424.2166 | 58.8969 | 510.742 | 485.1196 | 1715.3665 | 1363.2732 | 54.8057 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $5,599 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1262 | WRO Generator Network Upgrades |  |  |  | The project is to accommodate the Energy Storage Project, which proposes to install 13 inverters rated at 1.9385 MW each with a maximum gross output of 25.2 MW. Auxiliary load of 0 MW and estimated losses of 0.2 MW. The net output is 25 MW to the CAISO Controlled Grid. This Generating Facility and the associated Interconnection Facilities plan to connect to Weber 60 kV Substation in San Joaquin County. Reconductor 0.9 mi of Stockton A0Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 6.1366 | NA | 60 kV | 3 | Not Available | Not Available | NA | NA | 5783873 | T.0004561 | WRO Generator Network Upgrades | 8 | 82 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-02-01 | 2022-04-01 | 2023-05-31 | Customer Action | TRUE | 12400 | NA | 3549.7458 | 3641.7863 | 0 | 71.8666 | 867.2984 | 2209.916 | 395.2348 | 87.2707 | 10.1998 | 0 | 0 | 0 | 0 | 3544.3158 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 3429.1952 | 7.1787 | 0% | 100% ¦ $3,642 | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1263 | WRO Generator Network Upgrades |  |  |  | The project proposes to install 200 inverters rated at 2.09 MW each at 95% power factor with a maximum gross output of 418 MW. Auxiliary load of 4 MW and estimated losses of 4.54 MW. The net output is 400 MW to the CAISO Controlled Grid, interconnected to PG&E's Telsa 230 kV substation. | Substation - Circuit Breaker | New | T.0007288 ¦ T.0004673 | Generator Interconnection | Generation Interconnection | NA | 2024-03-15 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 69.382 | NA | 115 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5783904 | T.0004563 | WRO Generator Network Upgrades | 5 | 82 | NA | 2019 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-07-23 | 2025-03-01 | 2025-03-18 | NA | TRUE | 12020 | NA | 332.2843 | 5915.6438 | 35.7031 | 4.8685 | 38.8384 | 23.0333 | 202.4183 | 4387.157 | 1223.6252 | 0 | 0 | 0 | 0 | 304.8616 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $5,916 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1264 | WRO Generator Network Upgrades |  |  |  | The project proposes to install a battery generation plant with a total rated output of 400 megawatt (MW) (net output) to Pacific Gas and Electric Company’s (PG&E’s) Moss Landing Substation 500 kV in Moss Landing, Monterey, CA. The Project was modeled with a total installed capacity of 434.5 megawatt (MW) (gross output) and will have a net output of 400 megawatt (MW) (net output) to the California Independent System Operator (CAISO)Controlled Grid. The interconnection agreement for Q1472 was executed on March 17, 2020. | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 41.3213 | NA | 500 kV | 3 | 6. Customer commitments | Not Available | NA | NA | 5784784 | T.0004662 | WRO Generator Network Upgrades | 5 | 82 | NA | 2019 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-07-15 | 2021-08-03 | 2020-11-20 | NA | FALSE | 12700 | NA | 10903.4817 | 10903.4817 | 248.9523 | 10840.6891 | -201.0826 | 14.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10903.4817 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 11089.0783 | -201.0826 | 14.9229 | 0 | 0 | 0% | 100% ¦ $10,903 | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1265 | ARCO 230kV - MIDWAY LCD |  |  | Kern | The project proposes to install a new control building to accommodate several new Generation Interconnection and Storage Projects already in the queue for the 230kV bus at Arco. The station control building was installed in 1973. It houses both 230 and 70 kV, but the main issue is that the existing control building is deficient in space and location to be used for the new interconnections. | Substation - Other Equipment | Upgrade/Retrofit | T.0007165 | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.5471 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5803819 | T.0008073 | Arco 230kV Control Building NU | 2 | 82 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2020 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-01 | 2024-07-30 | 2026-03-31 | Project Design | FALSE | 22280 | NA | 60.8839 | 2073.4593 | 0 | 0 | 0 | 3.2452 | 38.7304 | 1118.5439 | 883.8685 | 29.0712 | 0 | 0 | 0 | 41.9756 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,073 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1266 | Arco 230kV Control Building NU |  |  | Kern | The project proposes to install a new control building to accommodate several new Generation Interconnection and Storage Projects already in the queue for the 230kV bus at Arco. The station control building was installed in 1973. It houses both 230 and 70 kV, but the main issue is that the existing control building is deficient in space and location to be used for the new interconnections. | Substation - Modular Protection and Automation Control Building | New | T.0007165 | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | 51 | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.5471 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5800064 | T.0008073 | Arco 230kV Control Building NU | 2 | 82 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2020 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 3 | 2023-08-21 | 2024-07-30 | 2024-07-31 | NA | TRUE | 22280 | NA | 10766.4919 | 21095.2962 | 0 | 0 | 0 | 660.4102 | 8829.0774 | 6213.565 | 3724.9648 | 1667.2787 | 0 | 0 | 0 | 9489.4877 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $21,095 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1267 | WRO Generator Network Upgrades |  |  |  | The project proposes to interconnect 80 MW (Net Output) Solar Photovoltaic/Battery Storage generation plant to CASIO grid at Point of Interconnection (POI) thru PG&E owned Cortina Substation 60 kV bus in Colusa County. Install a new 60 high voltage circuit breaker (HVCB). Place the new HVCB in the spare bay between existing HVCB 42 and 12. | Substation - Circuit Breaker | New | T.0007629 | Generator Interconnection | Generation Interconnection | NA | 2024-03-07 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 6.7436 | NA | 60 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5794559 | T.0006968 | WRO Generator Network Upgrades | 5 | 82 | NA | 2021 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2021 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2022-09-23 | 2023-09-07 | 2026-05-01 | Prioritization | TRUE | 3840 | NA | 816.181 | 1237.1049 | 0 | 0 | 73.9483 | 341.9868 | 225.0779 | 345.156 | 129.495 | 121.4409 | 0 | 0 | 0 | 641.0131 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,237 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1268 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 12 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) Woodland – Davis 115 kV Line, in Yolo County, California. Network Upgrades Scope of work • Install two (2) DTT receivers and perform associated relay setting changes at Woodland and Davis. • Install (1) new light duty steel pole to be used as the tap structure • Install (2) new SCADA Switches on the Woodland – Davis 115 kV Line, one on each side of the tap structure • Install (2) new TSPs on the Woodland – Davis 115 kV Line, one on each side of the tap structure | Substation - Other Equipment | Upgrade/Retrofit | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-04 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 1.7115 | NA | 115 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5770164 | T.0001728 | WRO Generator Network Upgrades | 4 | 82 | NA | 2014 | 2015 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2014 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2017-02-13 | 2016-10-15 | 2028-07-27 | Prioritization | TRUE | 3300 | NA | 863.4267 | 1176.8048 | 38.731 | 49.0966 | 47.6972 | 51.6534 | 90.5041 | 63.7436 | 67.1375 | 72.0585 | 77.3401 | 44.2904 | 0 | 852.2347 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | -0.41016 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,177 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1269 | WRO Generator Network Upgrades |  |  |  | The project proposes to interconnect a 150 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) existing Mustang 230 kV Breaker-and-a-half (BAAH) Switching Station, in Kings County, California. | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 7.0079 | NA | 230 kV | 3 | 6. Customer commitments | NA | NA | NA | 5771963 | T.0002125 | WRO Generator Network Upgrades | 5 | 82 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2016 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-04-25 | 2018-12-28 | 2019-03-27 | NA | FALSE | 1348 | NA | 1368.1564 | 1368.1564 | 136.853 | 77.0204 | 1.8077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1368.1564 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1283.8643 | 76.5921 | 1.7976 | 0 | 0 | 0 | 0% | 100% ¦ $1,368 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1270 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) solar-based generation facility to Los Banos – Panoche 230 kV Line No. 1 by looping in through the Pacific Gas and Electric Company (PG&E)-owned new switching station in Merced County, California. Per recent MMA. | Substation - Multiple | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 230 kV | 3 | 6. Customer commitments | NA | NA | NA | 5772423 | T.0002321 | WRO Generator Network Upgrades | 9 | 82 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2014 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 5318-E | 2018-06-25 | Approved | 2018 | Operational | 2 | 2019-01-02 | 2019-09-19 | 2019-11-02 | NA | FALSE | 13620 | NA | 2493.8095 | 2493.8095 | 1673.3173 | 42.4342 | 0.2996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2493.8095 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 2450.1903 | 42.4188 | 0.29953 | 0 | 0 | 0 | 0% | 100% ¦ $2,494 | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1271 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) solar-based generation facility to Los Banos – Panoche 230 kV Line No. 1 by looping in through the Pacific Gas and Electric Company (PG&E)-owned new switching station in Merced County, California. Per recent MMA. | Substation - Other Equipment | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 53.2803 | NA | 230 kV | 3 | 6. Customer commitments | NA | NA | NA | 5772426 | T.0002321 | WRO Generator Network Upgrades | 9 | 82 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2014 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 5318-E | 2018-06-25 | Approved | 2018 | Operational | 2 | 2019-01-02 | 2019-09-19 | 2019-11-02 | NA | FALSE | 13620 | NA | 1230.0629 | 1230.0629 | 820.8787 | 34.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.0629 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1178.7185 | 33.7767 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,230 | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1272 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Substation - Bus Arrangement | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 26.1945 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5775145 | T.0009188 | WRO Generator Network Upgrades | 1 | 82 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2017 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-09-10 | NA | 2025-02-19 | NA | TRUE | NA | NA | 263.4782 | 2844.4769 | 0.4713 | 0.7596 | 25.7448 | 106.8242 | 109.575 | 1473.308 | 526.1639 | 592.7437 | 0 | 0 | 0 | 252.2613 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,844 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1273 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Substation - Line Termination | New | T.0009188 | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 26.1945 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5775140 | T.0003035 | WRO Generator Network Upgrades | 7 | 82 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2017 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2031-03-17 | NA | 2031-08-21 | NA | FALSE | NA | NA | 133.5188 | 2164.8838 | 0.0456 | 0.0748 | 57.2779 | 72.2547 | 1.4401 | 9.688 | 49.1209 | 77.1048 | 36.0389 | 98.616 | 1090.9976 | 131.9573 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $2,165 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1274 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Substation - Line Termination | New | T.0009188 | Generator Interconnection | Generation Interconnection | NA | 2024-03-07 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.7679 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5775141 | T.0003035 | WRO Generator Network Upgrades | 7 | 82 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2017 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2028-04-28 | NA | 2028-09-25 | NA | FALSE | NA | NA | 39.1392 | 1788.6476 | 0.1163 | 0.1886 | 18.4283 | 15.1257 | 2.6338 | 2.8399 | 8.7715 | 60.2001 | 22.1122 | 172.0211 | 1321.9592 | 38.6815 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,789 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1275 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Other - Remedial Action Scheme/Special Protection Scheme | New | T.0009188 | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 26.1945 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5775144 | T.0003035 | WRO Generator Network Upgrades | 7 | 82 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2017 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2028-08-25 | NA | 2029-02-09 | NA | FALSE | NA | NA | 53.0936 | 9412.5075 | 0.1163 | 0.1886 | 15.9535 | 31.0664 | 2.9591 | 3.8524 | 33.5014 | 46.7422 | 81.2289 | 480.9197 | 8319.3386 | 52.4727 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $9,413 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1276 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 200 megawatt (MW) (net output) wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Pit #1 – Cottonwood 230 kV Line in Shasta County, California. | Substation - Multiple | New | T.0009188 | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | TBD | NA | 230 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5545804 | T.0003035 | WRO Generator Network Upgrades | 7 | 82 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2017 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-03-29 | NA | 2027-09-03 | NA | FALSE | NA | NA | 0 | 15402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6234.143 | 9167.857 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $15,402 | TBD | NA | 44% | 56% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1277 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 250 megawatt (MW) (net output) solar power-based generation facility to the PG&E-owned Gates 230 kV Substation in Fresno County, California. | Substation - Bus Arrangement | New | T.0003388 | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | NA | NA | 5779030 | T.0003750 | WRO Generator Network Upgrades | 5 | 82 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2017 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-04-06 | 2020-11-17 | 2021-03-15 | NA | FALSE | 7350 | NA | 4992.8242 | 4992.8242 | 256.7928 | 2728.9439 | 2010.3877 | -4.2589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4992.8242 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 4955.2889 | -4.2221 | 0 | 0 | 0% | 100% ¦ $4,993 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1278 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 300 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) new Switching Station looped into the Quinto Switching Station - Westley 230 kV Line, in Stanislaus County, California. | Substation - Multiple | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-02-01 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.67641 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5779140 | T.0003770 | WRO Generator Network Upgrades | 6 | 82 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2017 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6529-E | 2022-03-16 | Approved | 2022 | Operational | 2 | 2022-12-13 | 2022-12-31 | 2024-03-06 | Prioritization | TRUE | 27900 | NA | 21414.3067 | 21986.9252 | 15.8436 | 61.6737 | 2705.6196 | 3803.3395 | 14338.5676 | 1015.2245 | 26.7905 | 0 | 0 | 0 | 0 | 20944.9102 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 22058.9725 | 0% | 100% ¦ $21,987 | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1279 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 300 megawatt (MW) (net output) solar power-based generation facility to Pacific Gas and Electric Company’s (PG&E’s) new Switching Station looped into the Quinto Switching Station - Westley 230 kV Line, in Stanislaus County, California. | Substation - Circuit Breaker | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5779104 | T.0003770 | WRO Generator Network Upgrades | 6 | 82 | NA | 2018 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | 2017 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NOC: AL 6529-E | 2022-03-16 | Approved | 2022 | Operational | 2 | 2022-06-29 | 2022-12-31 | 2023-11-02 | Prioritization | TRUE | 27900 | NA | 2077.3443 | 2087.594 | 0 | 8.5908 | 528.724 | 229.0131 | 1241.1168 | 79.9203 | 0.229 | 0 | 0 | 0 | 0 | 2007.4447 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 1999.6579 | 100.1816 | 0% | 100% ¦ $2,088 | NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1280 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 400 megawatt (MW) (net output) solar power-based generation facility to the PG&E-owned 230 kV Tranquillity Switching Station in Fresno County, California. | Substation - Bus Arrangement | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 6.7555 | NA | 230 kV | 3 | 6. Customer commitments | Not Available | NA | NA | 5778461 | T.0003742 | WRO Generator Network Upgrades | 5 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-04-19 | 2022-10-31 | 2023-04-28 | NA | TRUE | 5500 | NA | 7069.3162 | 7090.4261 | 130.7637 | 118.2897 | 212.4329 | 5707.6534 | 881.5375 | 28.627 | 0 | 0 | 0 | 0 | 0 | 7061.7991 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 7061.3135 | 6.5228 | 0% | 100% ¦ $7,090 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1281 | WRO Generator Network Upgrades |  |  |  | The Project proposes to interconnect a 76.35 wind generation facility to Pacific Gas and Electric Company’s (PG&E’s) Los Banos Substation in Merced, California | Substation - Circuit Breaker | New | T.0007906 | Generator Interconnection | Generation Interconnection | NA | 2024-03-06 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 53.2803 | NA | 70 kV | 3 | Not Available | Not Available | Tier 5 | Yes | 5783302 | T.0004423 | WRO Generator Network Upgrades | 6 | 82 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2018 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2023-07-03 | 2023-08-30 | 2025-03-03 | Customer Action | TRUE | 17500 | NA | 8953.1199 | 13595.3381 | 7.1871 | 73.9806 | 294.2066 | 684.2893 | 6746.6052 | 4577.7308 | 1014.8485 | 196.49 | 0 | 0 | 0 | 7806.2688 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $13,595 | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1282 | PANOCHE: UPGD EQUIP TO 1517AûEGI DOS AMI |  |  | Fresno | The Project proposes to reconductor 23.63 miles of the Pacific Gas and Electric Company’s (PG&E’s) Dos Amigos - Panoche 230 kV Line No. 3 with a higher capacity conductor, in Merced and Fresno Counties, California. During the Cluster 9 Phase I Fresno Area Interconnection Study, the Dos Amigos - Panoche 230 kV Line No. 3 was found to be overloaded by roughly 84%. To eliminate this deliverability constraint, the CAISO requires reconductoring the overloaded line and the costs are allocated among multiple full capacity generation projects identified by the CAISO. | Substation - Line Termination | Upgrade/Retrofit | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | 76 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 19.3832 | NA | 230 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5805074 | T.0004255 | Dos Amigos PP-Panoche #3 230 kV Recondu. | 4 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-01-06 | 2025-05-31 | 2026-06-09 | Land Rights | FALSE | 49800 | NA | 366.5539 | 1982.8695 | 27.4168 | 33.7487 | 81.1738 | 103.9315 | 114.6554 | 69.8732 | 174.5694 | 1377.5007 | 0 | 0 | 0 | 360.9262 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 27.5529 | 33.7456 | 81.1738 | 103.9379 | -246.4102 | 0 | 0% | 100% ¦ $1,983 | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1283 | BORDEN - GREGG#1: OPGW EGI |  |  | Madera | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Transmission Line - Other Equipment | New | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | 2022-09-16 | 93 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 6.25 | NA | 230 | NA | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5787080 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-11-10 | 2022-11-10 | 2026-05-07 | Land Rights | FALSE | 39900 | NA | 26.3894 | 1795.5982 | 0 | 6.2749 | 10.982 | 7.0505 | 1.7733 | 55.1616 | 1467.0355 | 247.3203 | 0 | 0 | 0 | 26.0808 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 100% ¦ $1,796 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1284 | Borden: Upgrade Terminal Equipt. |  |  | Madera | The Project proposes to reconductor 6.25 miles of the Pacific Gas and Electric Company’s (PG&E’s) Borden – Gregg 230 kV Line No. 1 (the existing Borden - Gregg 230 kV Line) with a higher capacity conductor, in Madera County, California. | Substation - Line Termination | Upgrade/Retrofit | T.0004490 ¦ T.0009329 ¦ T.0008538 | Generator Interconnection | Generation Interconnection | NA | 2024-03-05 | 93 | Interconnection System Impact/Facilities Studies | Wires - New T-Line Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 7.1874 | NA | 230 kV | Not Available | 6. Customer commitments | Not Available | Tier 5 | Yes | 5534923 | T.0007056 | Borden-Gregg 230kV Lines 1 & 2 Reconduct | 9 | 82 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | 2019 | FALSE | NA | NA | NA | True | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-01-09 | 2022-11-10 | 2026-05-05 | Land Rights | TRUE | 39900 | NA | 92.7662 | 1668.0201 | 22.651 | 35.8793 | 15.3787 | 7.1589 | 4.0165 | 69.1578 | 161.3219 | 1352.456 | 0 | 0 | 0 | 85.0843 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 22.8293 | 35.8778 | 15.3787 | 7.1594 | 4.0165 | 10.6249 | 0% | 100% ¦ $1,668 | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1285 | Gates Sub Bus Section E(RNU) |  |  | Fresno | The proposed project will install three bays of new 230kV BAAH Bus Section E, with two half-bay and one full-bay BAAH, including an empty bay for the future capacity needs. Specific components of the project include: • Build a new three bay 230kV BAAH Bus Section E • Connect the new Bus Section E to the existing DBSB and the existing BAAH Bus Section F • Install two sectionalizing breakers between Bus Section D and new Bus Section E • Transfer existing 500kV Bank 11 low side connection to new Bus Section E • Install a new 230kV MPAC building with new Sustainable Modular Protection (SMP) relays • Expand about 1,500 feet of existing security wall and install security cameras • Upgrade terminal equipment at Panoche, Vacaville Grid Control Center, and San Francisco Grid Control Center | Substation - Bus Arrangement | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-03-08 | 63 | Interconnection System Impact/Facilities Studies | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 77.6619 | NA | 230 kV | Not Available | Not Available | Not Available | NA | NA | 5787158 | T.0006452 | GATES BUS SECTION ""E"" | 9 | 82 | NA | 2019 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | 2019 | FALSE | NA | NA | NA | True | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-09-23 | 2023-04-30 | 2023-04-17 | NA | TRUE | 58600 | NA | 37553.0988 | 37553.0988 | 12.5029 | 353.055 | 14702.0445 | 15120.0677 | 7203.1832 | 162.2456 | 0 | 0 | 0 | 0 | 0 | 37390.8532 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 36455.5986 | 197.011 | 0% | 100% ¦ $37,553 | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $125 Mil - $150 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1286 | NU upgrade Los Gatos Sub Install PTs |  |  | Los Gatos, Santa Clara | This project proposes to connect 160kW Photovoltaic generating facility to PG&E’s Los Gatos 1101 distribution circuit. MWC 82 • Replace existing C-phase PT with three new PTs and associated support structures | Substation - Protection Relay | New | NA | Generator Interconnection | Generation Interconnection | NA | 2024-02-05 | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 0.7484 | NA | 60 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5548348 | T.0008054 | NU upgrade Los Gatos Sub Install PTs | 1 | 82 | NA | 2023 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-01-17 | NA | 2025-04-17 | NA | TRUE | NA | NA | 113.1763 | 2220.3209 | 0 | 0 | 0 | 27.9633 | 75.175 | 241.8713 | 1875.3113 | 0 | 0 | 0 | 0 | 103.1383 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 27.9633 | 75.175 | 23.9691 | 0% | 100% ¦ $2,220 | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1287 | HSR Interconnection Sub Sites 4-7 (82) |  |  | Gilroy, Santa Clara ¦Merced | TPS Sites 4 to 7 will power the section of the rail line that connects the Bay Area with the Central Valley. When the CHSR Project is completed and in-service, the CHSR substation at Sites 4 to 7 will have a total power demand of over 230 megawatts (MW). The interconnections at Sites 4 to 7 will consist of the major work components shown below. There will be other system work needed to address protection and automation upgrades needed for the system reconfigurations resulting from the interconnections. Generally, “Network Upgrades” will be performed by PG&E, and work for new “Interconnection Facilities” will be performed by CHSRA or its contractors. | Substation - Multiple | New | T.0000006 ¦ T.0002127 ¦ T.0004116 ¦ T.0002231 | Work Requested by Others | Load Interconnection | NA | NA | NA | Interconnection System Impact/Facilities Studies | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | TBD | NA | 230 ¦ 115 kV | 3 | 6. Customer commitments | Not Available | Tier 5 | Yes | 5766464 | T.0000005 | CHSR Interconnections, Sites 4-7 | 2 | 82 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2018 | FALSE | 2018 | NA | https://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | False | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-10-18 | NA | 2030-10-02 | NA | FALSE | NA | NA | 4904.4501 | 218941.5807 | 522.5386 | 456.0012 | 410.4698 | 459.078 | 564.9902 | 738.2531 | 1296.7555 | 4789.5439 | 45321.0587 | 16183.0226 | 13543.1983 | 4797.5369 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% (Final allocation not yet finalized with CPUC & FERC) ¦ $0 | TBD | NA | 44% | 56% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1288 | Caltrain IC - Remote End at Martin (82) |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Other Equipment | Upgrade/Retrofit | NA | Work Requested by Others | Load Interconnection | NA | 2024-04-02 | NA | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 3.3775 | NA | 115 kV | 3 | 6. Customer commitments | Not Available | NA | NA | 5776103 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2017 | FALSE | 2017 | NA | https://www.caiso.com/Documents/Board-Approved_2016-2017TransmissionPlan.pdf | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-02-01 | 2021-06-30 | 2021-03-23 | NA | FALSE | 46700 | NA | 1060.8973 | 1060.8973 | 108.0261 | 74.6992 | 672.2738 | -25.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060.8973 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1078.9708 | -25.7234 | 0 | 0 | 0% | 60% ¦ $637 | NA | NA | 100% | 0% | [Utility Unique ID 2] T.0000004 & T.0002226 are linked as part of the Caltrain Interconnection Project. Cost allocation has only been approved by the CPUC. FERC approval still needed. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1289 | Caltrain IC - Substation Site 1 (82) |  |  | South San Francisco, San Mateo | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Work Requested by Others | Load Interconnection | NA | 2024-04-02 | 68 | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.3775 | NA | 115 kV | 3 | 6. Customer commitments | Not Available | NA | NA | 5766383 | T.0000004 | Caltrain Interconnections Site 1 | 14 | 82 | 5743532 | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | 2017 | FALSE | 2017 | NA | https://www.caiso.com/Documents/Board-Approved_2016-2017TransmissionPlan.pdf | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-05-08 | 2021-06-30 | 2021-03-24 | NA | TRUE | 46700 | NA | 28727.5293 | 29204.8174 | 14932.672 | 11656.1313 | -9107.0438 | 2580.1411 | 1399.4282 | 598.2826 | 0 | 0 | 0 | 0 | 0 | 28606.5348 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 24458.1622 | 2560.5445 | 1390.0049 | 173.837 | 0% | 60% ¦ $17,523 | NA | NA | 0% | 100% | [Utility Unique ID 2] T.0000004 & T.0002226 are linked as part of the Caltrain Interconnection Project. Cost allocation has only been approved by the CPUC. FERC approval still needed. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1290 | Caltrain IC - Substation Site 3 (82) |  |  | San Jose, Santa Clara | Upgrade East Grand Substation in South San Francisco, CA and FMC Substation in San Jose, CA to provide 115kV interconnections to the Caltrain Traction Power Stations (TPS) for the electrification of the trains’ electrical systems | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Work Requested by Others | Load Interconnection | NA | 2024-02-06 | 25 | Interconnection System Impact/Facilities Studies | Wires - System Configuration Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 4.0642 | NA | 115 kV | 3 | 6. Customer commitments | Not Available | NA | NA | 5772270 | T.0002226 | Caltrain Interconnections Site 3 | 17 | 82 | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | 2017 | FALSE | 2017 | NA | https://www.caiso.com/Documents/Board-Approved_2016-2017TransmissionPlan.pdf | False | Final Certified | 2017-10-10 | EIR | NA | CalTrain | NA | NOC: AL 5442-E | 2018-12-12 | Approved | 2019 | Operational | 2 | 2019-05-13 | 2021-06-30 | 2022-03-24 | Construction Delays | TRUE | 64500 | NA | 28712.3913 | 29432.0338 | 15471.6503 | 10508.9554 | -12980.2996 | 5723.1113 | 656.6039 | 994.7539 | 0 | 0 | 0 | 0 | 0 | 28437.2799 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 27585.1078 | 652.3603 | 83.9066 | 0% | 60% ¦ $17,659 | NA | NA | 44% | 56% | [Utility Unique ID 2] T.0000004 & T.0002226 are linked as part of the Caltrain Interconnection Project. Cost allocation has only been approved by the CPUC. FERC approval still needed. [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1291 | Fully Reimbursed ElecTransmission WRO |  |  | NA | Bucket for fully reimbursable WRO work | Substation - Multiple | New | NA | Work Requested by Others | Facility Relocation | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | NA | NA | 5716639 | NA | NA | NA | 82 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 9706.4249 | 9706.4249 | -110.971 | -65.9949 | -23.229 | -32.6412 | -1.4265 | 0 | 0 | 0 | 0 | 0 | 0 | 9706.4249 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | -88.6844 | -62.6853 | -39.3451 | -31.0872 | -1.4265 | 0 | 0% | 0% ¦ $0 | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1292 | Private Load Interconnection Project |  |  |  | The following scope of work is required to interconnect the Customer's data center into PG&E’s Los Esteros Substation: • Construct two, 2000-foot 115 kV underground cables from Los Esteros Substation to Customer’s McCarthy Substation. The cables will have normal and emergency ratings of 500 Amps (= 100 MVA). • Connect riser structures for the two 115 kV cables at Los Esteros Substation and connect the lines into 115 kV Bays 7 and 8. Install Circuit Breakers 772 and 872 and Disconnect Switches 773 and 783 to complete the break-and-a-half bay configuration. • Install 115 kV metering equipment at Micosoft’s McCarthy Substation. • Install protective relay packages at Los Esteros and McCarthy Substations for line protection. • Install fiber line for communication between Los Esteros and McCarthy Substations. | Substation - Other Equipment | Upgrade/Retrofit | NA | Generator Interconnection | Load Interconnection | NA | 2024-03-12 | NA | Interconnection System Impact/Facilities Studies | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 13.1703 | NA | 115 kV | Not Available | Not Available | Not Available | Tier 5 | Yes | 5549904 | T.0005903 | Private Load Interconnection Project | 1 | 82 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | False | Other [See Notes] | 2024-04-08 | EIR | NA | San Jose City | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-08-13 | 2023-08-30 | 2025-01-15 | Prioritization | TRUE | 18600 | NA | 310.7412 | 1104.4202 | 0 | 0 | 0 | 86.0748 | 131.5259 | 810.183 | 76.6364 | 0 | 0 | 0 | 0 | 217.6007 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 66.9471 | 102.2979 | 75.2159 | 0% | 0% ¦ $0 | TBD | NA | 0% | 100% | [CEQA Status] EIR addendum being drafted [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1293 | Regulatory Amount MWC 82 |  |  | NA | Bucket for regulatory related WRO work | Substation - Multiple | New | NA | Generator Interconnection | Facility Relocation | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3 | Not Available | Not Available | RBPPF - TBD | No | 5505967 | NA | NA | NA | 82 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | False | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 2882.3261 | 2882.3261 | 5.7374 | 9.2462 | 8.8683 | 9.6039 | 10.5618 | 1.8009 | 0 | 0 | 0 | 0 | 0 | 2880.5252 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% ¦ $0 | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1294 | MWC 92: A Tag HFTD/HFRA |  |  | NA | Forecast Placeholder for Completion of urgent/emergency tags (A priority) to mitigate conditions that may pose immediate risk (30 days or less). | Transmission Line - Multiple | Replace | NA | Emergency Event | T-Line Emergency | NA | NA | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | Ex112942 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 525.3575 | 525.3575 | 525.3575 | 525.3575 | 525.3575 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 1295 | MWC 92: A Tag Non-HFTD/HFRA |  |  | NA | Forecast Placeholderfor Completion of urgent/emergency tags (A priority) to mitigate conditions that may pose immediate risk (30 days or less). | Transmission Line - Multiple | Replace | NA | Emergency Event | T-Line Emergency | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | Ex112943 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1471.0011 | 1471.0011 | 1471.0011 | 1889.4558 | 1889.4558 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 1296 | Emergency - Non-Fire Rebuild |  |  | NA | Forecast Placeholder for Mitigation after an emergency (e.g. storm damage) occurs. Allows for system safety and reliability after events. | Transmission Line - Multiple | Replace | NA | Emergency Event | T-Line Emergency | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | Ex112941 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9574 | 9574 | 9574 | 9574 | 9574 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 1297 | EO-SYSPLN 92 - ET Line Emg Repl |  |  | NA | Forecast placeholder for emergency replacement of t-line equipment | Transmission Line - Multiple | Replace | NA | Emergency Event | T-Line Emergency | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5533315 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 34848.1818 | 0 | 0 | 0 | 0 | 0 | 34848.1818 | 0 | 30070.8604 | 30070.8604 | 29652.4057 | 30000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 1298 | Trans Emergency Response - 921 |  |  | NA | Bucket for Priority 1 Wood Structure Emergency Replacement | Transmission Line - Pole/Tower | Replace | NA | Emergency Event | Priority 1 Wood Structure Replacement | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5555285 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 5074.8763 | 5074.8763 | 0 | 45.8922 | 266.3711 | 1990.443 | 2587.1684 | 185.0011 | 0 | 0 | 0 | 0 | 0 | 4889.8752 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 39.4296 | 129.3675 | 1594.3387 | 2426.0591 | 159.5739 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1299 | Capital Wood Misc |  |  | NA | Bucket for COE Material Stock of wood poles | Transmission Line - Pole/Tower | Replace | NA | Emergency Event | Emergency Response - Storm Related | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | NA | 1088 | Not Available | Not Available | NA | NA | 5768059 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1759.0091 | 1759.0091 | 9.7469 | 3.1391 | -65.5046 | 0.2463 | 0.0912 | 0 | 0 | 0 | 0 | 0 | 0 | 1759.0091 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 9.7469 | 3.1391 | -65.5046 | 0.24626 | 0.09119 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1300 | 2019 Emergency Response |  |  | NA | Bucket for transmission line emergency response for 2019. | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Storm Related | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 1088 | Not Available | 70 | NA | NA | 5529948 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1576.7473 | 1576.7473 | 819.3144 | 85.1455 | 6.0569 | 0.6593 | 0.4436 | 0 | 0 | 0 | 0 | 0 | 0 | 1576.7473 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 715.0327 | 81.6085 | 5.3472 | 0.60542 | 0.40479 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1301 | 2021 Emergency Response |  |  | NA | Bucket for transmission line emergency response for 2021 | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Storm Related | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 1088 | Not Available | Not Available | NA | NA | 5529950 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1244.0045 | 1244.0045 | 0 | 0 | 1170.8499 | 70.1108 | 2.9455 | 0.0982 | 0 | 0 | 0 | 0 | 0 | 1243.9063 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 879.795 | 154.5664 | 13.5689 | 0.0795 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1302 | Trans Emergency Response |  |  | NA | Bucket for transmission line emergency response. | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Storm Related | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 1088 | 2. Overhead With Strong Safety Link | 3 | Tier 5 | No | 5505341 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 146179.7688 | 146179.7688 | 3366.8361 | 4656.772 | 10880.9315 | 3794.0043 | 18870.4783 | 5190.4892 | 0 | 0 | 0 | 0 | 0 | 140989.2796 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 3278.1624 | 2580.1837 | 9459.5944 | 4550.6973 | 14752.7584 | 6436.324 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1303 | TESLA SALADO MANTECA RPLC TOWER |  |  | Alameda ¦ Manteca, San Joaquin ¦ San Joaquin ¦ Stanislaus | Lattice Steel Poles (LSP’s) A30/247 and A31/248 failed due to failed guy anchor at A31/248. LSP’s to be replaced permanently in existing alignment with two 150’ tall river crossing special towers. In addition, line to be restored temporarily in new temporary alignment with six pole shoofly, if temporary easements are available. This project will replace failed lattice steel poles A30/247 and A31/248 permanently in existing alignment with two river crossing special towers. In addition, line to be restored temporarily in new temporary alignment with six pole shoofly, if temporary easements are available. | Transmission Line - Pole/Tower | Replace | NA | Emergency Event | Emergency Response - Storm Related | NA | 2024-04-09 | 98 | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 | NA | 1088 | 1. Work that prevents fire ignition | 198 | Tier 5 | No | 5526594 | T.0003140 | TESLA SALADO MANTECA RPLC TOWER | 1 | 92 | NA | NA | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-08-11 | NA | 2025-11-18 | NA | TRUE | NA | NA | 1866.6496 | 6390.2544 | 51.8339 | 58.5666 | 155.3257 | 197.2449 | 382.0931 | 1700.0599 | 2882.4271 | 0 | 0 | 0 | 0 | 1779.7343 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 51.8339 | 58.5666 | -29.6857 | 166.8446 | 323.2031 | 118.2194 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1304 | CZU Fire Related Response |  |  | NA | Bucket for CZU Fire related response | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Fire Related | NA | NA | NA | NA | Other - Status Quo | NA | NA | TRUE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5541802 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1093.6969 | 1093.6969 | 0 | 454.4918 | 638.7255 | 0.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093.6969 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 454.4918 | 638.7255 | 0.47954 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1305 | Emergency Fire Response - NORTH |  |  | NA | Bucket for fire related t-line emergency replacement | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Fire Related | NA | NA | NA | NA | Other - Status Quo | NA | NA | TRUE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5542431 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 15795.3486 | 15795.3486 | 0 | 0 | 11117.2401 | 4473.4636 | 204.6448 | 0 | 0 | 0 | 0 | 0 | 0 | 15795.3486 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 10168.9868 | 4065.8341 | 183.1801 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1306 | Emergency Response Fire-Related |  |  | NA | Bucket for transmission line emergency response related to fire. | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Fire Related | NA | NA | NA | NA | Other - Status Quo | NA | NA | TRUE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 318 | 2. Overhead With Strong Safety Link | 12 | Tier 5 | No | 5508839 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 182715.1037 | 182715.1037 | 2175.3054 | 21041.99 | 48896.4655 | 32098.7823 | 7874.9503 | 305.1227 | 0 | 0 | 0 | 0 | 0 | 182409.981 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1877.8451 | 16569.2671 | 45422.6793 | 17950.3512 | 11223.2816 | -2102.3186 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1307 | Caribou #2 60016: Removal Work |  |  | Keddie CDP, Plumas ¦ Paxton CDP, Plumas ¦ Plumas ¦ Quincy CDP, Plumas ¦ Twain CDP, Plumas | Rebuild a portion of Caribou #2 and Caribou-Plumas Jct lines between Caribou PH and Grays flat which were damaged due to recent Dixie fire. In this project, portion of Caribou #2 line is routed on a newer right of way and it now travels along the Caribou-Plumas Jct line in a DCTL configuration between Caribou PH and Grays Flat . Due to this reroute Caribou#2 line mileage is effectively reduced by approx. 11 miles. Additionally, both the lines in DCTL configuration are being reconductored. | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Fire Related | NA | 2024-04-12 | 45 | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | TRUE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | 6.25 | NA | 60 | NA | Not Available | Not Available | Not Available | NA | NA | 5798457 | T.0007507 | Caribou-Plumas Jct Rebuild | 3 | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-09-21 | NA | 2021-11-30 | NA | FALSE | 1978 | NA | 1978.0591 | 1978.0591 | 0 | 0 | 2498.5531 | -520.4939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1978.0591 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1449.3607 | -1437.7821 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1308 | Caribou-Plumas Jct Rebuild |  |  | East Quincy CDP, Plumas ¦ Plumas ¦ Quincy CDP, Plumas ¦ Twain CDP, Plumas | Rebuild a portion of Caribou #2 and Caribou-Plumas Jct lines between Caribou PH and Grays flat which were damaged due to recent Dixie fire. In this project, portion of Caribou #2 line is routed on a newer right of way and it now travels along the Caribou-Plumas Jct line in a DCTL configuration between Caribou PH and Grays Flat . Due to this reroute Caribou#2 line mileage is effectively reduced by approx. 11 miles. Additionally, both the lines in DCTL configuration are being reconductored. | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Fire Related | NA | 2024-04-12 | 45 | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | TRUE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | 6.25 | NA | 60 | NA | Not Available | Not Available | Not Available | NA | NA | 5798127 | T.0007507 | Caribou-Plumas Jct Rebuild | 3 | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-09-21 | NA | 2021-12-10 | NA | TRUE | 9081 | NA | 83703.8002 | 103120.5551 | 0 | 0 | 56079.1543 | 12454.8549 | 14925.732 | 7055.9517 | 12604.8622 | 0 | 0 | 0 | 0 | 83459.7412 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 52052.4609 | 11553.9492 | 13846.0982 | -233.4792 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1309 | Fulton-Calistoga 60 kV Line Reconductor |  |  | Deer Park CDP, Napa ¦ Fulton CDP, Sonoma ¦ Kenwood CDP, Sonoma ¦ Lake ¦ Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma | Rebuild the 16.6-mile section of the Fulton-Calistoga 60kV Line from Fulton to St. Helena Junction. A section of the line was damaged during the Tubbs Fire in Napa County in Fall 2017, and an emergency project was initiated to reconductor 4.5 miles of the line from Fulton to Rincon Tap, which is on the Fulton to St. Helena Junction section of the line. As the project team started working on the project, it was discovered that the old copper conductors on the line were extremely brittle and have a potentially high risk of failure. Given the Tier 3 HFTD’s in which the line is located, this poses a significant customer safety risk. The proposed project work is taking place in two phases: • Phase 1 work rebuilt the 4.5-mile section from Fulton to Rincon Tap with new lattice steel poles (LSP’s) and new 397.5 thousands of circular mils (kcmil) aluminum conductor steel-reinforced (ACSR). Work was completed in August 2019. • Phase 2 work will rebuild the 12-mile section from Rincon Tap to St. Helena Junction with new LSP’s and the new ACSR. | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Fire Related | NA | 2024-04-09 | 20 | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | TRUE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 4.5 | NA | 60 | NA | 448 | 3. Emergency Preparedness | NA | NA | NA | 5781618 | T.0004167 | Fulton-Calistoga 60 kV Line Reconductor | 2 | 92 | NA | NA | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5500-E | 2019-03-20 | Approved | 2019 | Operational | 2 | 2018-12-24 | 2019-06-28 | 2019-08-28 | NA | FALSE | 31000 | NA | 14817.0926 | 14817.0926 | 10309.4878 | 681.8215 | 85.028 | -4.9821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14817.0926 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 14055.2252 | 334.0221 | 82.9642 | -4.8612 | 0 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1310 | FULTON-CALISTOGA 60 KV LREC 12 Miles |  |  | Deer Park CDP, Napa ¦ Fulton CDP, Sonoma ¦ Kenwood CDP, Sonoma ¦ Lake ¦ Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma | Rebuild the 16.6-mile section of the Fulton-Calistoga 60kV Line from Fulton to St. Helena Junction. A section of the line was damaged during the Tubbs Fire in Napa County in Fall 2017, and an emergency project was initiated to reconductor 4.5 miles of the line from Fulton to Rincon Tap, which is on the Fulton to St. Helena Junction section of the line. As the project team started working on the project, it was discovered that the old copper conductors on the line were extremely brittle and have a potentially high risk of failure. Given the Tier 3 HFTD’s in which the line is located, this poses a significant customer safety risk. The proposed project work is taking place in two phases: • Phase 1 work rebuilt the 4.5-mile section from Fulton to Rincon Tap with new lattice steel poles (LSP’s) and new 397.5 thousands of circular mils (kcmil) aluminum conductor steel-reinforced (ACSR). Work was completed in August 2019. • Phase 2 work will rebuild the 12-mile section from Rincon Tap to St. Helena Junction with new LSP’s and the new ACSR. | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Fire Related | NA | 2024-04-09 | 20 | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | TRUE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 12 | NA | 60 | NA | 1088 | 1. Work that prevents fire ignition | 70 | NA | NA | 5784504 | T.0004167 | Fulton-Calistoga 60 kV Line Reconductor | 2 | 92 | NA | NA | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5500-E | 2019-03-20 | Approved | 2019 | Operational | 2 | 2019-08-22 | 2019-08-29 | 2020-06-08 | Prioritization | FALSE | 31000 | NA | 52617.2666 | 52617.2666 | 28598.8451 | 24336.5562 | -299.4392 | 46.3473 | -65.0427 | 0 | 0 | 0 | 0 | 0 | 0 | 52617.2666 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 50638.0869 | -285.9638 | 44.2616 | -62.1157 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1311 | Atascadero-Cayucos 70kV Emerg Replacemt |  |  | Atascadero, San Luis Obispo ¦ San Luis Obispo | Replace conductor and structures to prevent another open jumper incident that can impact service to over 13,900 electric customers in the San Luis Obispo County, the following proposed scopes will increase system performance and reliability and reduce fire ignition risk: • Replace 5 wood structures with steel poles (total of 9 poles due to two 3 pole structures). • Replace 1.33 miles of existing conductor with a larger conductor; • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Multiple | Replace | TBD | Emergency Event | Emergency Response - Fire Related | NA | 2024-03-27 | 69 | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | TRUE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1.33 | NA | 70 | NA | Not Available | Not Available | Not Available | NA | NA | 5801178 | T.0008335 | Atascadero-Cayucos 70kV Emerg Replacemt | 2 | 92 | NA | NA | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-10-03 | 2022-10-17 | 2022-10-17 | NA | FALSE | 2076 | NA | 1887.5193 | 1887.5193 | 0 | 0 | 0 | 1879.5385 | 7.9808 | 0 | 0 | 0 | 0 | 0 | 0 | 1887.5193 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1747.5567 | 86.3992 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1312 | Drum-Rio Oso South 115kV Emerg reinforce |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | The Drum-Rio Oso #1 & #2 115kV Emergency Mitigation project will impact 78 structures 012/113A-025/189. The general scope of work is to re-tension the existing conductor, remove existing v-strings located on the middle phase, and add arm extensions to the middle phase to increase phase to tower steel clearance. | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Fire Related | NA | 2024-04-01 | 108 | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | TRUE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | 14 | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5792541 | T.0006378 | Drum-Rio Oso South 115kV Emerg reinforce | 1 | 92 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-11-09 | 2021-04-20 | 2021-04-20 | NA | FALSE | 10009 | NA | 10084.9603 | 10084.9603 | 0 | 3082.8342 | 7024.1644 | -22.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10084.9603 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 8952.7344 | -19.4819 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1313 | Weimar #1 Emergency Rebuild |  |  | Foresthill CDP, Placer ¦ Placer | The scope of work includes reconductoring portions of the Weimar #1, Middle Fork #1, Oxbow Tap, French Meadows-Middle Fork, and Middle-Fork Gold Hill transmission lines due to the Mosquito fire. Approximately 23.5 miles of overhead transmission cable will be replaced in addition to approximately 398 wood poles. | Transmission Line - Multiple | Replace | NA | Emergency Event | Emergency Response - Fire Related | NA | 2024-04-08 | 78 | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated | TRUE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | 23.5 | NA | 60 | NA | Not Available | Not Available | Not Available | NA | NA | 5802819 | T.0008688 | Weimar #1 Emergency Rebuild | 1 | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-09-15 | NA | 2022-12-21 | NA | TRUE | 4172 | NA | 17380.0327 | 17380.0327 | 0 | 0 | 0 | 18354.443 | -966.2609 | -8.1494 | 0 | 0 | 0 | 0 | 0 | 17388.1821 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 15646.6547 | -877.0489 | -2.9145 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1314 | Trans Emergency Response - 92S |  |  | NA | Bucket for Priority 1 Steel Structure Emergency Replacement | Transmission Line - Pole/Tower | Replace | NA | Emergency Event | Priority 1 Steel Structure Replacement | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5555287 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2531.7535 | 2531.7535 | 0 | 0 | 0 | 34.5743 | 2466.6042 | 30.5752 | 0 | 0 | 0 | 0 | 0 | 2501.1783 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 34.5743 | 1434.5022 | -311.3249 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1315 | Priorty 1 Seel Emergency |  |  | NA | Bucket for transmission line emergency response for steel towers. | Transmission Line - Pole/Tower | Replace | NA | Emergency Event | Priority 1 Steel Structure Replacement | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 1099 | 2. Overhead With Strong Safety Link | 4 | NA | NA | 5525777 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 30944.404 | 30944.404 | 11065.5748 | 3035.8676 | 973.2991 | 780.1873 | 297.4513 | -90.5477 | 0 | 0 | 0 | 0 | 0 | 31034.9517 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 11200.2765 | 2835.1065 | 739.1161 | -1078.2389 | 108.9898 | -389.302 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1316 | TABLE MTN-TESLA 500KV TWR 109/429 |  |  | Alameda ¦ Butte ¦ Contra Costa ¦ Discovery Bay CDP, Contra Costa ¦ Knightsen CDP, Contra Costa ¦ Oakley, Contra Costa ¦ Robbins CDP, Sutter ¦ Sacramento ¦ Solano ¦ Sutter ¦ Sutter CDP, Sutter ¦ Yolo | Table Mtn-Tesla 500kV Install new foundation to support staircase to tower 109/429. | Transmission Line - Pole/Tower | Replace | NA | Emergency Event | Priority 1 Steel Structure Replacement | NA | 2024-04-11 | 57 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 500 | NA | 1099 | 2. Overhead With Strong Safety Link | 382 | NA | NA | 5782136 | T.0003139 | TABLE MTN_TESLA AND VACA-TESLA TWRS | 4 | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-06-18 | NA | 2021-09-29 | NA | FALSE | 2382 | NA | 2382.0036 | 2382.0036 | 37.3369 | 143.5161 | 2217.5471 | -19.8396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2382.0036 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 2401.8432 | -19.8396 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1317 | VACA-TESLA 500KV TWR 031/132 |  |  | Alameda ¦ Byron CDP, Contra Costa ¦ Contra Costa ¦ Discovery Bay CDP, Contra Costa ¦ Knightsen CDP, Contra Costa ¦ Oakley, Contra Costa ¦ Sacramento ¦ Solano ¦ Vacaville, Solano | Table Mtn-Tesla 500kV Install new foundation to support staircase to tower 109/429. | Transmission Line - Pole/Tower | Replace | NA | Emergency Event | Priority 1 Steel Structure Replacement | NA | 2024-04-11 | 56 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 500 | NA | 1099 | 2. Overhead With Strong Safety Link | 694 | NA | NA | 5782137 | T.0003139 | TABLE MTN_TESLA AND VACA-TESLA TWRS | 4 | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-06-18 | NA | 2021-09-28 | NA | FALSE | 1375 | NA | 1374.6196 | 1374.6196 | 2.7004 | 55.0612 | 1306.5754 | 1.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1374.6196 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 1372.9596 | 1.66 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1318 | Trans Emergency Response - 92T |  |  | NA | Bucket for emergency replacement due to 3rd parrty damage | Transmission Line - Multiple | Replace | NA | Emergency Event | 3rd Party Damage | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5555284 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 8579.1616 | 8579.1616 | 0 | 878.9213 | 3201.8529 | 2377.1863 | 2642.9592 | -521.7583 | 0 | 0 | 0 | 0 | 0 | 9100.9199 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 247.4965 | 2830.4184 | 2086.2868 | 2164.4101 | -398.9088 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1319 | 3rd Party Damage |  |  | NA | Bucket for transmission line emergency response for 3rd party damages | Transmission Line - Multiple | Replace | NA | Emergency Event | 3rd Party Damage | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 1099 | 3. Emergency Preparedness | 3 | Tier 5 | No | 5516801 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 15999.3212 | 15999.3212 | 2564.9233 | 1521.1728 | -109.2913 | 1169.927 | 2380.214 | -30.5009 | 3687 | 3687 | 3687 | 3687 | 3687 | 16029.8221 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 2162.8209 | 1224.762 | -120.0202 | 959.464 | 2167.1163 | -557.949 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1320 | UG Elec Trans Emerg Resp |  |  | NA | Bucket for underground transmission line emergency response | Transmission Line - Underground | Replace | NA | Emergency Event | Underground Emergency | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 340 | 3. Emergency Preparedness | Not Available | Tier 5 | No | 5505899 | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 7323.6204 | 7323.6204 | 6.9892 | 11.2621 | 10.8023 | 11.6984 | 12.8652 | 2.1937 | 0 | 4671.781 | 4671.781 | 4671.781 | 4671.781 | 7321.4267 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1321 | GREATER BAY AREA ER STORAGE FACILITY SF |  |  | Brisbane, San Mateo ¦ Daly City, San Mateo ¦ San Francisco, San Francisco | Design, permitting and material procurement for emergency transmission power restoration to the city of San Francisco in the event of a major earthquake. According to the latest U.S Geologic Survey, within the next thirty years there is a 63% change that a large earthquake (6.7M) will occur. PG&E’s Underground electric transmission system traverses many areas of high liquefaction potential in Oakland, such that buried transmission line is subject to change of damage due to liquefaction. | Transmission Line - Underground | Replace | NA | Emergency Event | Underground Emergency | NA | 2024-02-19 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 1099 | 3. Emergency Preparedness | 1086 | NA | NA | 5774870 | T.0002935 | GREATER BAY ER STORAGE SF | 2 | 92 | NA | 2011 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-08-07 | 2018-02-23 | 2021-05-21 | Construction Delays | TRUE | 12623 | NA | 18634.9235 | 18645.8781 | 2355.0892 | 1798.1717 | 3381.7919 | 1181.6458 | 336.9871 | -111.253 | 0 | 0 | 0 | 0 | 0 | 18757.1311 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 17321.3965 | 1181.6458 | 336.9871 | -116.0845 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1322 | Greater Bay Area Emergency Storage Facility OAK |  |  | Oakland, Alameda | Implement an emergency restoration plan to restore underground electric transmission service to the City of Oakland in the event of a major earthquake. It identifies cables at risk, proposes restoration plans for earthquake-damaged cables, and actions recommended by the Underground Cable Reliability Team for future development. | Transmission Line - Underground | Replace | NA | Emergency Event | Underground Emergency | NA | 2024-03-11 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | NA | 512 | 3. Emergency Preparedness | 1204 | NA | NA | 5774147 | T.0002735 | GREATER BAY ER STORAGE OAK | 2 | 92 | NA | 2013 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-05-10 | 2018-02-23 | 2020-03-30 | Construction Delays | FALSE | 11921 | NA | 12532.7344 | 12543.689 | 1167.3338 | 43.9578 | 2184.4779 | 734.5285 | -289.0715 | 165.5219 | 0 | 0 | 0 | 0 | 0 | 12378.1671 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 9777.4653 | 2184.4779 | 734.5285 | -289.0715 | 157.1915 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1323 | Gates-Tulare Lake 70kV Emergency Work |  |  | Avenal, Kings ¦ Fresno ¦ Kettleman City CDP, Kings ¦ Kings | Re-conductor approximately 8.5 miles on the Gates-Tulare Lake 70kV. Pole 8/0C to Pole 13/1 and Pole 15/4 to Tulare Lake Substation. 2/0 copper to be re-conductored to 4/0 AAC. Line number: 0702 , TLine RCC 10939 , Fresno RCC 10176 | Transmission Line - Pole/Tower | Replace | NA | Emergency Event | Priority 1 Wood Structure Replacement | NA | 2023-11-17 | 119 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 10 | NA | 70 | NA | 1088 | Not Available | NA | NA | NA | 5780339 | T.0003953 | Gates-Tulare Lake 70kV Emergency Work | 1 | 92 | NA | NA | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-05-14 | 2019-03-25 | 2019-03-21 | NA | FALSE | 2500 | NA | 4982.8726 | 4982.8726 | 2257.1698 | -60.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4982.8726 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 4442.9795 | -52.7463 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1324 | HP-3 Grounding Project |  |  | San Francisco, San Francisco | While grading the land on the Hunters Point Recovery Project, a copper cable was uncovered. Testing the cable determined that the cable, likely used for grounding was floating. This project involves installing grounding equipment at the HP-3 and PX-2 Transition Stations to reduce the touch and step potential of the equipment to acceptable and safe levels. | Transmission Line - Underground | Replace | NA | Emergency Event | Underground Emergency | NA | 2021-11-09 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 115 | NA | 146 | Not Available | 992 | NA | NA | 5772862 | T.0002394 | HP-3 and PX-2 Grounding | 2 | 92 | NA | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-19 | 2017-06-30 | 2020-01-02 | Construction Delays | FALSE | 1668 | NA | 1627.2694 | 1627.2694 | 56.1821 | 7.593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1627.2694 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 1475.3306 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1325 | MWC 93 tag work Non-HFTD_Planning |  |  | NA | Forecast placeholder for Non-HFTD T-line Tag Work | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | 2. Overhead with Strong Safety Link | Not Available | Tier 5 | No | 5543229 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96457.104 | 99061.4458 | 83180.6607 | 68665.129 | 11806.1924 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1326 | T-Line Miscellaneous 93# |  |  | NA | Bucket for transmission line preventative maintenance | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | 764 | NA | NA | 5518470 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2087.0197 | 2087.0197 | 1044.0113 | 11944.6259 | -12784.2543 | 97.5768 | 24.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 2087.0197 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 25.3306 | 100.0644 | 59.5921 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1327 | WSIP - MWC 93 Forecast |  |  | NA | Bucket for transmission line preventative maintenance | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 4478 | Not Available | Not Available | RBPPF - TBD | Yes | 5534224 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 9638.9237 | 9638.9237 | 5849.6092 | -3538.0911 | 42967.1455 | -40442.3013 | 1159.1826 | 3643.3788 | 0 | 0 | 0 | 0 | 0 | 5995.5449 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1328 | MWC 93 tag work HFTD_Planning |  |  | NA | Forecast placeholder for HFTD T-line Tag Work | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5543228 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 79000 | 0 | 0 | 0 | 0 | 0 | 79000 | 0 | 70920.8258 | 70781.9819 | 53966.7797 | 65617.1718 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1329 | EO-SYSPLN 93 - ET Prev Work |  |  | NA | Forecast placeholder for transmission line preventative maintenance | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5533321 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 26390.9091 | 0 | 0 | 0 | 0 | 0 | 26390.9091 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1330 | Anti-Climb Guard Installation |  |  | NA | Bucket for anti-climb guard installation in HFTD Tier 1 | Transmission Line - Pole/Tower | New | NA | Asset Condition | Age/Condition - Anti Climb Guards | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 180 | 2. Overhead With Strong Safety Link | 4 | RBPPF - TBD | Yes | 5522082 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 6838.7862 | 6838.7862 | 795.0331 | 484.5372 | 238.8159 | 847.0174 | 546.5911 | 87.5856 | 0 | 0 | 0 | 0 | 0 | 6751.2006 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 785.9568 | 252.5769 | 336.668 | 874.5657 | 412.6469 | 242.1289 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1331 | WSIP - Anti-Climb Guards |  |  | NA | Bucket for anti-climb guard installation in HFTD Tier 2 & 3 | Transmission Line - Pole/Tower | New | NA | Asset Condition | Age/Condition - Anti Climb Guards | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 569 | 2. Overhead With Strong Safety Link | 2 | RBPPF - TBD | Yes | 5533587 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 7656.6065 | 7656.6065 | 3730.7149 | 1852.1257 | 343.6661 | 940.3705 | 624.7604 | 164.9693 | 0 | 0 | 0 | 0 | 0 | 7491.6372 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 3698.781 | 1527.3767 | 438.4509 | 993.7109 | 264.8288 | 418.7296 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1332 | Shunt Splice Program |  |  | NA | Forecast placeholder for Installation of shunted splices to prevent single point of failure on certain splice types. Accounts for approximately 20-30 lines worth of shunt mitigation per year, targeting HFTD areas first | Transmission Line - Other Equipment | New | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | TRUE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | Ex112977 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 5000 | 5000 | 5000 | 5000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | 0.1 ¦ Electric Operations Risk Management | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1333 | Conductor Segment Replacement |  |  | NA | Forecast placeholder for Replacement of conductor segments (typically ruling spans) | Transmission Line - Conductor | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | Ex112953 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 10000 | 10000 | 10000 | 10000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1334 | Rebuild Transmission Line |  |  | NA | Forecast placeholder for transmission line rebuild | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | Yes | 5507699 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 12.7164 | 12.7164 | 0 | 0 | 0 | 0 | 12.7164 | 0 | 0 | 0 | 0 | 0 | 6000 | 12.7164 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1335 | TO Maint 93C |  |  | NA | Bucket for conductor replacement | Transmission Line - Conductor | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5555067 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1150.5172 | 1150.5172 | 4.9444 | 2.062 | 5.0171 | 135.4579 | 793.9605 | 36.445 | 0 | 0 | 0 | 0 | 0 | 1114.0722 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2023 ¦ 2024 | 4.8919 | 0 | 2.3096 | 103.0806 | 694.4902 | 31.0182 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1336 | EO-SYSPLN 93C - ET Prev Work |  |  | NA | Forecast placeholder for conductor replacement | Transmission Line - Conductor | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5533324 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 9800 | 0 | 0 | 0 | 0 | 0 | 9800 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1337 | MIDWAY-WHEELER RIDGE #1 & #2 INS SHIELD |  |  | Buttonwillow CDP, Kern ¦ Kern | Install overhead shield wire over the entirety of both Midway-Wheeler Ridgle #1 & #2 230kV lines with required 221 tower peaks & associated tower reinforcements. | Transmission Line - Other Equipment | New | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2021-11-17 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | 55 | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5553042 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2022-10-21 | NA | 2024-12-31 | NA | FALSE | NA | NA | 5960.2596 | 5960.2596 | 1.3975 | 74.9826 | 549.483 | 4887.2769 | 447.1196 | 0 | 0.001 | 0 | 0 | 0 | 0 | 5960.2596 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1.3985 | 74.9826 | 549.483 | 4887.2769 | 447.1196 | 0.11445 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1338 | COTTNWD-RED BLUFF - RECONDUCTOR |  |  | Cottonwood CDP, Shasta ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama | Rebuild the 16.5 miles-long Cottonwood-Red Bluff 60 kV Line and release the project to operations, The proposed project would rebuild the 16.5 mile Cottonwood-Red Bluff 60 kV line with new transmission poles and new conductor. The project scope of work includes the following:•Replace 304 transmission poles with 240 light duty steel poles (LDSPs), 7 tubular steel poles (TSPs), and 57 higher-class wood poles as identified by design.•Reconductor the Cottonwood-Red Bluff 60 kV line (16.5 miles) with 715 kcmil aluminum conductor.•Reroute a 3-pole section of the line to a new location and alignment. | Transmission Line - Conductor | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-09 | 81 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 16.5 | NA | 60 | NA | 197 | 1. Work that prevents fire ignition | 207 | NA | NA | 5767628 | T.0000456 | Cottonwood-Red Bluff Reconductor | 5 | 93 | 5732727 | 2008 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5311-E | 2018-06-15 | Approved | 2018 | Operational | 2 | 2019-09-03 | 2019-12-27 | 2021-03-22 | Permitting | FALSE | 47000 | NA | 25081.6054 | 25081.6054 | 5673.5124 | 12859.7238 | 2928.2344 | 151.5912 | -0.0994 | -23.4484 | 0 | 0 | 0 | 0 | 0 | 25105.0538 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 22897.9255 | 137.3909 | -0.09011 | -21.2519 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1339 | OLEUM - G #1 CONDUCTOR REPL (7/50-11/72) |  |  | Contra Costa ¦ El Cerrito, Contra Costa ¦ El Sobrante CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Pinole, Contra Costa ¦ Richmond, Contra Costa ¦ Rodeo CDP, Contra Costa | Reconductor 9.7 miles of 366 ACSR and 1.3 miles of 250 CU of Oleum-G #1 & #2 115 kV lines. This conductor failed while raising towers for a NERC related project. Subsequent testing performed by PG&E’s ATS department determined that the conductor has deteriorated to the end of the asset life. | Transmission Line - Conductor | Replace | T.0004296 | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-11 | 94 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $400 Mil - $500 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 11 | NA | 115 | NA | 604 | 1. Work that prevents fire ignition | 145 | RBPPF - TBD | No | 5785358 | T.0003634 | Oleum - G 115kV Reconductoring | 7 | 93 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | On Hold | 4 | 2026-08-12 | 2026-01-31 | 2028-04-04 | Prioritization | FALSE | 123300 | NA | 2381.7092 | 2381.7092 | 191.842 | 649.7825 | 919.3155 | 566.8084 | 53.9608 | 0 | 0 | 0 | 0 | 0 | 0 | 2381.7092 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1340 | OLEUM - G #2 CONDUCTOR REPL (7/50-11/72) |  |  | Contra Costa ¦ El Cerrito, Contra Costa ¦ El Sobrante CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Pinole, Contra Costa ¦ Richmond, Contra Costa ¦ Rodeo CDP, Contra Costa | Reconductor 9.7 miles of 366 ACSR and 1.3 miles of 250 CU of Oleum-G #1 & #2 115 kV lines. This conductor failed while raising towers for a NERC related project. Subsequent testing performed by PG&E’s ATS department determined that the conductor has deteriorated to the end of the asset life. | Transmission Line - Conductor | Replace | T.0004296 | Asset Condition | Age/Condition - Replace Conductor | NA | 2022-08-16 | 81 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $400 Mil - $500 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 11 | NA | 115 | NA | 448 | 1. Work that prevents fire ignition | 449 | RBPPF - TBD | Yes | 5778135 | T.0003634 | Oleum - G 115kV Reconductoring | 7 | 93 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | On Hold | 4 | 2028-10-09 | 2026-01-31 | 2030-02-05 | Project Design | FALSE | 123300 | NA | 2355.5245 | 85914.5272 | 692.2317 | 132.4212 | 849.6031 | 519.613 | 57.3132 | 0 | 0 | 0 | 0 | 0 | 2000 | 2355.5245 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1341 | PH 2-CARIBOU#2 GRAYS FLAT-SPANISH CRK |  |  | Keddie CDP, Plumas ¦ Paxton CDP, Plumas ¦ Plumas ¦ Quincy CDP, Plumas ¦ Twain CDP, Plumas | Reconductor approximately 7.5 miles of transmission line from #2 Cu to 397 ACSR from Grays Flat Substation to Spanish Creek Substation. Scope includes replacing switches 23 and 27. | Transmission Line - Conductor | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-12 | 76 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 7.5 | NA | 60 | NA | 448 | 1. Work that prevents fire ignition | Not Available | NA | NA | 5781478 | T.0000040 | CARIBOU#2 GRAYS FLAT TO SPANISH CREEK | 3 | 93 | NA | 2010 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5051-E | 2017-04-19 | Approved | 2017 | Operational | 2 | 2020-05-11 | 2019-08-01 | 2020-09-21 | Clearances | FALSE | 33600 | NA | 8838.6629 | 8838.6629 | 358.9051 | 8505.9079 | -144.9222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8838.6629 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 8983.5869 | -618.1221 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1342 | CAMANCHE TAP 115KV RECONDUCTOR |  |  | San Joaquin | Reconductor the 6.6 mile section of the Camanche Tap 115 kV Line. The Camanche Tap 115kV Tap Line is served from the Gold Hill-Lockeford-Bellota 115 kV Line and is located in San Joaquin adjacent to Camanche Reservoir and near the town of Lockeford. This line is a radial line serving the Camanche Power House, owned by East Bay Municipal Utility District (EBMUD). This line is 6.6 miles long and is composed of 4/0 AAC supported by 100 wood poles, using T-1 framing. The average span distance is 375 feet. This line was originally constructed in 1983, or 35 years ago. From October 2007 to January 2012, there were a total of 7 outages. Almost all of these outages were caused by conductor failures occurring beneath the armor rod at the conductor clamps. When this line was constructed, the project did not call for vibration dampers at each structure location. From 2012 through 2017 there were 8 sustained outages. Four of these were conductor failures with wire-down. The other 4 were flashed or broken insulators. The conductor on this tap has had a field risk assessment and it is determined that there are wind-induced vibration fractures under the armor rod at the connection points due to the absence of vibration dampeners. There is no maintenance mitigation to this long term deterioration. This line section is a tap off of the Gold Hill-Bellota-Lockeford 115 kV line and as a result does not have a specific line ranking. However since 2007, 8 of the 12 outages due to equipment failure have been wire-down conductor failure on the Camanche Tap. | Transmission Line - Conductor | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2023-08-15 | 37 | Lifecycle Replacement Analysis | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 6.6 | NA | 115 | NA | 214 | Not Available | NA | NA | NA | 5752196 | T.0000045 | Camanche Tap 115kV Reconductor | 1 | 93 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5101-E | 2017-06-07 | Approved | 2017 | Operational | 2 | 2018-10-01 | 2019-02-28 | 2019-01-14 | NA | FALSE | 7088 | NA | 4924.6609 | 4924.6609 | 57.3253 | -0.6834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4924.6609 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 4328.1056 | -0.5978 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1343 | HUMB BAY-HUMB #1 RE-CONDUCTOR LINE |  |  | Bayview CDP, Humboldt ¦ Cutten CDP, Humboldt ¦ Eureka, Humboldt ¦ Humboldt ¦ Humboldt Hill CDP, Humboldt ¦ Myrtletown CDP, Humboldt ¦ Pine Hills CDP, Humboldt | Replace 4.1 miles of existing 336 AAC conductor and 3.7 miles of 2/0 CU wire on the Humboldt Bay-Humboldt #1 60kV transmission line (HB-H #1), and 0.6 miles of 336AAC conductor on the Humboldt Bay-Eureka 60kV transmission line (HB-E), with 715 AL conductor and supporting structures, | Transmission Line - Conductor | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2023-11-21 | 61 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 7.4 | NA | 60 | NA | 252 | 2. Overhead With Strong Safety Link | 892 | NA | NA | 5732884 | T.0000106 | Humboldt Bay-Humboldt #1 60kV Reconductr | 2 | 93 | NA | 2010 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2020-11-23 | IS/MND | NA | CPUC | NA | PTC: A.19-02-004 | 2019-02-15 | Approved | 2020 | Operational | 2 | 2022-07-25 | 2022-11-03 | 2022-11-14 | NA | TRUE | 18935 | NA | 26915.7871 | 27317.3105 | 884.3044 | 1389.9949 | 1862.3618 | 12419.5095 | 6583.2237 | 217.7818 | 106.2609 | 0 | 0 | 0 | 0 | 26838.3691 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 18432.5004 | 5901.6303 | 123.6508 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1344 | Smartville - Nicolas #1 Conductor Repl |  |  | Beale AFB CDP, Yuba ¦ East Nicolaus CDP, Sutter ¦ Placer ¦ Rio Oso CDP, Sutter ¦ Smartsville CDP, Yuba ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ Wheatland, Yuba ¦ Yuba | Restore Wheatland from the Smartville-Nicolaus #2 60kV line (Close Wheatland SW 65, Open SW 45) OR consider restoring from the Smartville source after isolating trouble, if between Wheatland and East Nicolaus | Transmission Line - Conductor | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-04 | 118 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 13 | NA | 60 | NA | 44 | 1. Work that prevents fire ignition | 133 | RBPPF - TBD | Yes | 5778137 | T.0003636 | Smartville - Nicolas #1 Conductor Repl | 1 | 93 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-08-18 | NA | 2028-04-04 | NA | FALSE | NA | NA | 479.9339 | 20318.7105 | 0.6211 | 65.7978 | 102.7004 | 272.3577 | 30.6191 | 34.7628 | 0 | 0 | 0 | 0 | 409 | 474.3211 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1345 | Stan-Melones Tap Lines: Repl CU cond |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Manteca, San Joaquin ¦ Murphys CDP, Calaveras ¦ San Joaquin ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | The project scope of work includes following: • Rebuild 7.55 miles of 2/0 CU and 4/0 AAC conductors on the Stanislaus-Melones Sw Sta-Manteca No. 1 115 kV Line from Melones Substation to structure 018/115. • Rebuild 7.53 miles of 2/0 CU and 4/0 AAC conductors on the Stanislaus-Melones Sw Sta-Riverbank Jct 115 kV Line from Melones Substation to structure 007/043. The Stanislaus-Melones SS-Manteca No. 1 and Stanislaus-Melones SS-Riverbank Jct SS 115 kV lines are comprised of 2/0 7-strand hemp core copper (2/0 CU) and 4/0 AAC conductors mounted on lattice steel towers. The 2/0 CU conductor is no longer being used in the system and must be repaired using parts that are difficult to procure, which contribute to extended outages caused by conductor failures. Since 2007, a review of historical outage data shows that these T-Lines experienced 27 outages caused by conductor failure. The 2/0 CU has the second highest failure rate per mile of any conductor in the PG&E Transmission System. The poor conductor reliability is exacerbated by the fact that these T-Lines are in a Tier 2 HFTD and that wire down, or asset failure is a potential ignition source. Overall, these lines experienced a total of 186 outages in the past fifteen years. The primary causes of the outages included equipment failure (conductor, connector, insulator, structure, circuit breaker, and relay), animal contacts (bird contact and animal waste), vegetation encroachment, and external contacts (vandalism and safety clearances). In addition, weather events (fire, snow, lightning, rain, and wind) have a secondary role in these outages. These conditions could result in future electrical T-Line outages and fire ignition. Engineering analysis indicated that the Stanislaus-Melones SS-Manteca No. 1 line has approximately 56 twist splices and the Stanislaus-Melones SS-Riverbank Jct SS line has approximately 103 twist splices. A total of 159 twist splices were found in these two lines and the lines are in Tier 2 HFTD. A splice failure in a HFTD can result in a wildfire ignition and twist splices are known to have higher rates of failure when compared to other splices. One existing energy storage generation plant, totaling 99 MW, in the San Joaquin County is currently awaiting this project to allow full deliverability of their generation. Additionally, the Stanislaus-Melones SS-Manteca No. 1 and Stanislaus-Melones SS-Riverbank Jct SS 115 kV lines have been identified as a constraint for full deliverability for the planned generator, which have a signed interconnection agreement. The planned energy storage generation plant is planned to be online by 2027. If the Stanislaus-Melones SS-Manteca No. 1 and Stanislaus-Melones SS-Riverbank Jct SS 115 kV lines are not reconductored, the full deliverability of existing and planned generation will be impacted which will jeopardize achieving California’s Renewable Portfolio Standard goals and may lead to financial penalties. | Transmission Line - Conductor | Replace | T.0004301 ¦ T.0008743 ¦ T.0007979 | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-09 | 88 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 15.1 | NA | 115 | NA | Not Available | 2. Overhead With Strong Safety Link | 103 | RBPPF - TBD | Yes | 5783641 | T.0004515 | Stan-Melones Tap Lines: Repl CU cond | 1 | 93 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2028-03-23 | NA | 2028-04-19 | NA | FALSE | NA | NA | 1258.6975 | 31342.4348 | 0 | 18.4744 | 15.4449 | 97.6304 | 956.6546 | 2098.8824 | 1225.0407 | 1823.8356 | 14416.5164 | 2659.8932 | 0 | 1088.2044 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1346 | Martinez Junction to Christie Substation |  |  | Contra Costa ¦ Crockett CDP, Contra Costa ¦ Rodeo CDP, Contra Costa ¦ Solano ¦ Vallejo, Solano | The project will improve system performance and reduce public safety risk and fire ignition risk in Contra Costa County by reinforcing approximately 11.5 circuit miles of the 115 kV transmission lines by performing thefollowing work on the line sections from Oleum to Martinez Junction and Martinez Junction down to Christie. The line section from Martinez Junction up to North Tower Substation will be addressed in the North TowerLooping Project. | Transmission Line - Conductor | Replace | T.0003634 | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-03-26 | 103 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $300 Mil - $350 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 4.7 | NA | 115 | NA | 20007 | Not Available | Not Available | NA | NA | 5797244 | T.0004296 | Oleum-North Tower-Christie 115 kV Line | 8 | 93 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6202-E | 2021-05-26 | Approved | 2021 | Operational | 2 | 2022-05-10 | 2021-04-27 | 2023-01-31 | Prioritization | TRUE | 39900 | NA | 2027.4849 | 2027.4849 | 0 | 0 | 673.2984 | 883.6042 | 449.8732 | 20.7092 | 0 | 0 | 0 | 0 | 0 | 2006.7757 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1347 | Martinez Junction to Oleum Substation |  |  | Contra Costa ¦ Crockett CDP, Contra Costa ¦ Rodeo CDP, Contra Costa ¦ Solano ¦ Vallejo, Solano | The project will improve system performance and reduce public safety risk and fire ignition risk in Contra Costa County by reinforcing approximately 11.5 circuit miles of the 115 kV transmission lines by performing thefollowing work on the line sections from Oleum to Martinez Junction and Martinez Junction down to Christie. The line section from Martinez Junction up to North Tower Substation will be addressed in the North TowerLooping Project. | Transmission Line - Conductor | Replace | T.0003634 | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-03-26 | 103 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $300 Mil - $350 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 6.5 | NA | 115 | NA | 20007 | 1. Work that prevents fire ignition | 244 | RBPPF - TBD | Yes | 5782298 | T.0004296 | Oleum-North Tower-Christie 115 kV Line | 8 | 93 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6202-E | 2021-05-26 | Approved | 2021 | Engineering more than 50% complete | 4 | 2027-10-14 | 2021-04-27 | 2028-12-13 | Prioritization | FALSE | 39900 | NA | 8225.7477 | 103469.9357 | 520.6695 | 1463.0481 | 2557.1348 | 2681.013 | 862.2691 | 619.3358 | 0 | 0 | 0 | 0 | 20000 | 8107.0638 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1348 | Recon Stanislaus-Melones Riverbank 115kV |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | The project will increase system performance and reduce fire ignition risk in Calaveras, San Joaquin, Stanislaus, and Tuolumne counties by the following: • Replacement of approximately 30.6 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Manteca No. 1 115 kV Line on the following sections: o Stanislaus Powerhouse (PH) to Tower No. 020/132 (21.2 miles) o Tower No. 021/136 to Tower No. 030/195 (9.4 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Manteca No. 2 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Riverbank Jct SS 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 410 existing structures with new steel structures • Upgrade terminal equipment at Stanislaus PH | Transmission Line - Conductor | Replace | T.0004515 ¦ T.0007979 ¦T.0008743 | Asset Condition | Age/Condition - Replace Conductor | NA | 2023-04-19 | 98 | Lifecycle Replacement Analysis | Other - Deferral | $250 Mil – $300 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 21.4 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801741 | T.0004301 | Stanislaus Manteca T-Line Rebuild-PH2 | 6 | 93 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6382-E | 2021-10-28 | Approved | 2021 | Engineering more than 50% complete | 4 | 2028-02-27 | 2030-05-01 | 2028-09-17 | NA | FALSE | 242000 | NA | 1569.304 | 52055.2284 | 0 | 0 | 0 | 0 | 428.1356 | 3233.0992 | 19555.2991 | 7951.5487 | 4031.1749 | 11466.3674 | 17423.4558 | 428.1356 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1349 | STANISLAUS-MELONES-MANTECA 115 KV RPL P2 |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Manteca, San Joaquin ¦ Murphys CDP, Calaveras ¦ San Joaquin ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | The project will increase system performance and reduce fire ignition risk in Calaveras, San Joaquin, Stanislaus, and Tuolumne counties by the following: • Replacement of approximately 30.6 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Manteca No. 1 115 kV Line on the following sections: o Stanislaus Powerhouse (PH) to Tower No. 020/132 (21.2 miles) o Tower No. 021/136 to Tower No. 030/195 (9.4 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Manteca No. 2 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Riverbank Jct SS 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 410 existing structures with new steel structures • Upgrade terminal equipment at Stanislaus PH | Transmission Line - Conductor | Replace | T.0004515 ¦ T.0007979 ¦T.0008743 | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-09 | 88 | Lifecycle Replacement Analysis | Other - Deferral | $250 Mil – $300 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 30.6 | NA | 115 | NA | 448 | 1. Work that prevents fire ignition | 103 | RBPPF - TBD | Yes | 5782307 | T.0004301 | Stanislaus Manteca T-Line Rebuild-PH2 | 6 | 93 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6382-E | 2021-10-28 | Approved | 2021 | Engineering more than 50% complete | 4 | 2027-06-02 | 2030-05-01 | 2027-10-23 | NA | FALSE | 242000 | NA | 24654.7112 | 77734.4211 | 236.31 | 1509.4311 | 1469.4391 | 1133.6855 | 16696.8315 | 33316.376 | 21880.2497 | 48041.5127 | 2387.5 | 7655.6117 | 8216.7374 | 21045.6973 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1350 | Stan-Mel-Manteca #1 Phase 2C |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Manteca, San Joaquin ¦ Murphys CDP, Calaveras ¦ San Joaquin ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | The project will increase system performance and reduce fire ignition risk in Calaveras, San Joaquin, Stanislaus, and Tuolumne counties by the following: • Replacement of approximately 30.6 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Manteca No. 1 115 kV Line on the following sections: o Stanislaus Powerhouse (PH) to Tower No. 020/132 (21.2 miles) o Tower No. 021/136 to Tower No. 030/195 (9.4 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Manteca No. 2 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Riverbank Jct SS 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 410 existing structures with new steel structures • Upgrade terminal equipment at Stanislaus PH | Transmission Line - Conductor | Replace | T.0004515 ¦ T.0007979 ¦T.0008743 | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-09 | 88 | Lifecycle Replacement Analysis | Other - Deferral | $250 Mil – $300 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 34.3 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803427 | T.0004301 | Stanislaus Manteca T-Line Rebuild-PH2 | 6 | 93 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6382-E | 2021-10-28 | Approved | 2021 | Engineering more than 50% complete | 4 | 2028-09-18 | 2030-05-01 | 2029-06-01 | NA | FALSE | 79900 | NA | 15.5024 | 65081.1104 | 0 | 0 | 0 | 0 | 15.3197 | 1.1262 | 0 | 0 | 0 | 0 | 0 | 15.3197 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1351 | Stan-Mel-Riverbank Phase 2D |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | The project will increase system performance and reduce fire ignition risk in Calaveras, San Joaquin, Stanislaus, and Tuolumne counties by the following: • Replacement of approximately 30.6 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Manteca No. 1 115 kV Line on the following sections: o Stanislaus Powerhouse (PH) to Tower No. 020/132 (21.2 miles) o Tower No. 021/136 to Tower No. 030/195 (9.4 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Manteca No. 2 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 34.3 miles of 2/0 7-strand CU conductor on the Stanislaus-Melones SS-Riverbank Jct SS 115 kV Line on the following sections: o Stanislaus PH to Tower No. 021/125 (21.4 miles) o Tower No. 022/129 to Tower No. 035/212 (13.0 miles) • Replacement of approximately 410 existing structures with new steel structures • Upgrade terminal equipment at Stanislaus PH | Transmission Line - Conductor | Replace | T.0004515 ¦ T.0007979 ¦T.0008743 | Asset Condition | Age/Condition - Replace Conductor | NA | 2023-04-19 | 98 | Lifecycle Replacement Analysis | Other - Deferral | $250 Mil – $300 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 13 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5803428 | T.0004301 | Stanislaus Manteca T-Line Rebuild-PH2 | 6 | 93 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6382-E | 2021-10-28 | Approved | 2021 | Engineering more than 50% complete | 4 | 2029-05-12 | 2030-05-01 | 2030-11-27 | Prioritization | FALSE | 79900 | NA | 5.612 | 33064.8126 | 0 | 0 | 0 | 0 | 4.7106 | 1.243 | 0 | 0 | 0 | 0 | 0 | 4.7106 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1352 | Parkway-Moraga 230kV Shield Wire Rep |  |  | Contra Costa ¦ Crockett CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Orinda, Contra Costa ¦ Solano ¦ Vallejo, Solano | The project will install new shield wire in the sections below to replace the old shield wire that has become ineffective due to corrosion and degradation: • Vaca-Parkway 230kV and Vaca-Bahia 230kV: • From 014/077 to 18/097 (4 miles) • From 021/111 to 25/135 (4 miles) • From 001/009 to 001/010 (0.12 miles) • Parkway-Moraga 230kV and Bahia-Moraga 230kV • From 001/012 to 005/033 (3.5 miles) • From 008/051 to 017/098 (8.5 Miles) • From 023/127 to 023/128 (0.16 Miles) There is a recently completed project that removed approximately 20.3 miles of shield wire in the circuits around the Carquinez straits due to wire corrosion, degradation, and wires pulling in different directions thereby causing imbalance in the towers. Adding to the safety concerns, some of the shield wires are in highway crossings posing significant risk of failure. The removed shield wires expose PG&E’s overhead and underground assets to the effects of lightning strikes. The proposed project to replace the removed damaged shield wires will mitigate risks (public safety, wildfire and compliance) associated with lightning strikes in the area. The replacement project will offer protection against lightning to both PG &E and 3rd party underground assets. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-06 | 25 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 12.16 | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5800029 | T.0008051 | Vaca-Parkway-Morage 230kV Shield Wire Re | 2 | 93 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-09-21 | 2022-11-06 | 2022-11-08 | NA | TRUE | 7300 | NA | 3559.5136 | 3559.5136 | 0 | 0 | 0 | 3529.8171 | 29.6965 | 0 | 0 | 0 | 0 | 0 | 0 | 3559.5136 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 3044.4645 | 25.5618 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1353 | Vaca-Parkway 230kV Shield Wire Rep |  |  | Fairfield, Solano ¦ Green Valley CDP, Solano ¦ Hartley CDP, Solano ¦ Napa ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | The project will install new shield wire in the sections below to replace the old shield wire that has become ineffective due to corrosion and degradation: • Vaca-Parkway 230kV and Vaca-Bahia 230kV: • From 014/077 to 18/097 (4 miles) • From 021/111 to 25/135 (4 miles) • From 001/009 to 001/010 (0.12 miles) • Parkway-Moraga 230kV and Bahia-Moraga 230kV • From 001/012 to 005/033 (3.5 miles) • From 008/051 to 017/098 (8.5 Miles) • From 023/127 to 023/128 (0.16 Miles) There is a recently completed project that removed approximately 20.3 miles of shield wire in the circuits around the Carquinez straits due to wire corrosion, degradation, and wires pulling in different directions thereby causing imbalance in the towers. Adding to the safety concerns, some of the shield wires are in highway crossings posing significant risk of failure. The removed shield wires expose PG&E’s overhead and underground assets to the effects of lightning strikes. The proposed project to replace the removed damaged shield wires will mitigate risks (public safety, wildfire and compliance) associated with lightning strikes in the area. The replacement project will offer protection against lightning to both PG &E and 3rd party underground assets. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-06 | 25 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 8.12 | NA | 230 | NA | Not Available | Not Available | Not Available | NA | NA | 5800028 | T.0008051 | Vaca-Parkway-Morage 230kV Shield Wire Re | 2 | 93 | NA | 2022 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-08-08 | 2022-11-06 | 2022-12-02 | NA | TRUE | 7300 | NA | 4365.26 | 4365.26 | 0 | 0 | 0 | 4325.3709 | 39.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 4365.26 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 3680.3369 | 33.8224 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1354 | Hamilton Branch Chester Conductor Repl |  |  | Chester CDP, Plumas ¦ East Shore CDP, Plumas ¦ Plumas | The purpose of the project is to improve the reliability performance of the Hamilton Branch-Chester 60kV transmission line. The scope of the project is to rebuild 12 miles of the Hamilton Branch-Chester 60kV line with a combination of direct embedded engineered steel poles (EDEP) and tubular steel poles (TSP) with galvanize finish for the majority of the route. Five locations where a distribution service is attached will require a fiber glass pole. The project will install new 397ACSR conductor for the transmission circuit and replace all existing distribution underbuild with 1/0ACSR tree wire. In addition, a new OPGW will be installed between structures 000/002 and 012/250. A new ADSS cable will be installed between structures 000/002 and 000/001 as well as between 012/250 and 012/251. The ADSS will then be routed to the control building at Hamilton Branch and Chester substations via a riser at structure 000/001 and 012/251 respectively. Also included in the scope is the external generation of Chester Substation during the 6-8 month construction schedule. This generation is necessary due to the 60kv circuit being the only feed to Chester Substation and providing Distribution service. The generator’s location will be at Collins Pine Lumber Company property and the Collins Pine 60kV Tap will act as a Distribution shoofly back to the Chester Substation main Distribution Feeder. The project will include upgrading or replacing 30 poles on this tap to upgrade the 60kv circuit to 397 in-lieu of the existing 2-6/1 ACSR. Scope: replace or upgrade poles 000/001 to 000/029. | Transmission Line - Conductor | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-02 | 67 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 12 | NA | 60 | NA | 120 | 1. Work that prevents fire ignition | 132 | RBPPF - TBD | Yes | 5778198 | T.0003637 | Hamilton Branch - Chester Conductor Repl | 3 | 93 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-06-07 | NA | 2028-01-14 | NA | FALSE | NA | NA | 2190.2195 | 36035.5076 | 124.6431 | 417.5448 | 838.546 | 567.4274 | 51.5712 | 147.1345 | 0 | 0 | 0 | 0 | 0 | 2190.2195 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1355 | Weimar#1 Conductor Repl Project |  |  | Foresthill CDP, Placer ¦ Placer | The Weimar No. 1 60 kV Line is located in Plaecr County. The line is approximately 13.8 miles long and is supported by 210 structures, of which, 208 are in Tier 2 and Tier 3 high fire tier districts (HFTD’s). The project will increase system performance and reduce fire ignition risk in Placer County by performing the following work: • Reconductor the approximately 9 miles of the Weimar No. 1 60 kV Line • Replace at least 157 structures (152 wood & 5 steel poles) 2 • Inspect 4 structures and replace if necessary (000/001, 000/011, 009/143, 009/144) • Replace all insulators on at least 42 pole structures, if all not replaced due to reconductoring • Replace KPF Switch No. 15 on Pole No. 009/143 • Assess remainder of line to ensure safety and compliance • Identify any distribution underbuild and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. • Include all open maintenance tags within the project scope where applicable | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-08 | 78 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | TRUE | Heat Wave, Weather |  | 9 | NA | 115 | NA | Not Available | 1. Work that prevents fire ignition | 6 | RBPPF - TBD | Yes | 5789865 | T.0005798 | Weimar#1 | 3 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Construction (under 10%) | 3 | 2024-03-01 | NA | 2025-12-19 | NA | TRUE | NA | NA | 885.3706 | 18618.6448 | 0 | 236.9796 | 243.1539 | 128.2942 | 236.8681 | 692.581 | 16802.0724 | 52 | 0 | 0 | 0 | 845.2957 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | 0.8 ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1356 | Centerville - Table Mnt Conductor Repl |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Durham CDP, Butte | This project proposes to reconductor 1.2 miles of 477 AA. This 477 AA section is the only identified section of this type of conductor within the company. Spare parts utilized in emergency restorations are not available and the current solution is to reconductor a span or two and install double dead-ends. Its origin is not recorded, and the structures are wood poles that have been replaced over the years so the age cannot be determined. It is appropriate to replace the wood poles in the reconductor section with composite poles to add resilience to the circuit. 100 percent of the 1.2 miles proposed in this project is located within a Tier 3 wildfire risk area. | Transmission Line - Conductor | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-08 | 61 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 1.2 | NA | 60 | NA | 1125 | 1. Work that prevents fire ignition | NA | NA | NA | 5778136 | T.0003635 | Centerville - Table Mnt Conductor Repl | 1 | 93 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5480-E | 2019-02-14 | Approved | 2019 | Operational | 2 | 2019-06-19 | 2020-01-09 | 2019-07-31 | NA | FALSE | 3200 | NA | 1978.2136 | 1978.2136 | 1788.6383 | 4.6881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1978.2136 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1692.3402 | 4.3993 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1357 | STANISLAUS-MELONES ST STA-MANTECA RPL P1 |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Manteca, San Joaquin ¦ San Joaquin ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | This project proposes to reconductor three 1.5 miles sections on the Riverbank – Manteca, Stanislaus – Melonies – Manteca #1, and the Stanislaus – Manteca #2. All three circuits are in the same corridor and consist of 2/0 7 strand Hemp Core CU. The preferred reconductoring option will be 715 AA. The 2/0 Hemp Core Copper has the second highest failure rate per mile of any conductor in the PG&E Transmission System. These sections of circuit have 5.5 miles of legacy and end-of-life conductor in Tier 1 risk Fire Zone. It has surpassed its life expectancy of 90 years by 21 years. Aside from fire risk, when the conductor fails, repairs consist of a nonstandard procedure of unwinding the seven strand CU, cutting out the hemp core and utilizing a standard 2/0 sleeve | Transmission Line - Conductor | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-12 | 88 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 4.5 | NA | 115 | NA | 1554 | 1. Work that prevents fire ignition | 174 | RBPPF - TBD | Yes | 5778199 | T.0003638 | Stanislaus-Manteca Corridor #1 Cond Rpl | 1 | 93 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2030-02-01 | NA | 2030-02-28 | NA | FALSE | NA | NA | 885.7754 | 42311.215 | 502.5296 | 232.1899 | 59.1835 | 81.4464 | 1.3219 | 0 | 0 | 0 | 0 | 0 | 0 | 885.7754 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1358 | Potrero-Mission #2 115 kV (A-X-2) |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Transmission Line - Conductor | Replace | T.0002705 ¦ T.0000557 ¦ T.0000934 | Asset Condition | Seismic Upgrade - Replace Conductor | NA | 2024-03-14 | 74 | Lifecycle Replacement Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 2.7 | NA | 115 | NA | 434 | 4. Underground / Network (Strong Safety Link) | 1143 | RBPPF - TBD | Yes | 5765141 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 93 | NA | 2015 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 4 | 2029-11-15 | 2025-06-20 | 2030-10-08 | Prioritization | FALSE | 191100 | NA | 3871.7861 | 73811.7577 | 373.9101 | 351.2576 | 379.2021 | 837.4605 | 319.0996 | 271.8463 | 0 | 0 | 0 | 0 | 3869 | 3834.9684 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1359 | WSIP - Wood Pole Reframe |  |  | NA | Bucket for wood pole reframing in HFTD Tier 2 & 3 | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 3557 | 2. Overhead With Strong Safety Link | 1 | RBPPF - TBD | Yes | 5533589 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 53062.7771 | 53062.7771 | 23761.9995 | 15065.4091 | 9701.1599 | 3192.4976 | 1230.7868 | 102.038 | 0 | 0 | 0 | 0 | 0 | 52960.7391 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 21257.9092 | 12056.2924 | 8506.5774 | 3812.4256 | 930.1 | 91.9324 | 0% | NA | NA | NA | 44% | 56% | [Year of Business Case Approval] Job Estimate serves as Utility Approval. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements.
| 1360 | T Line Wood Pole Reframe - Fresno |  |  | NA | Bucket for wood pole reframing in the Fresno area. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 211 | 2. Overhead With Strong Safety Link | 304 | NA | NA | 5517321 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1520.9781 | 1520.9781 | 199.1833 | 42.3384 | 8.8374 | -0.7939 | 3.3792 | 0.1964 | 0 | 0 | 0 | 0 | 0 | 1520.7817 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 188.5013 | 41.1247 | 4.5169 | 7.1077 | -5.8439 | 0.75241 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1361 | T Line Wood Pole Reframe - Moss Landing |  |  | NA | Bucket for wood pole reframing in the Moss Landing area. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 211 | 2. Overhead With Strong Safety Link | 13 | NA | NA | 5517326 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1977.4471 | 1977.4471 | 437.0361 | 116.5503 | 7.4198 | -49.3011 | -2.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 1977.4471 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 406.2038 | 100.0752 | 6.817 | -42.3474 | -2.6008 | -4.7487 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1362 | Pole Reframing - Wood (North) |  |  | NA | Bucket for wood pole reframing in the North region | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 211 | Not Available | 3 | RBPPF - TBD | Yes | 5513326 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 45107.7192 | 45107.7192 | 3745.3931 | 3695.1246 | 6605.9641 | 9997.9389 | 11192.9636 | 1167.6399 | 0 | 0 | 0 | 0 | 0 | 43940.0793 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 3399.8722 | 3009.5823 | 4613.4642 | 8428.2072 | 9080.9245 | 1981.1459 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1363 | T Line Wood Pole Reframe - Sac |  |  | NA | Bucket for wood pole reframing in the Sacramento area. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 211 | 2. Overhead With Strong Safety Link | 6 | NA | NA | 5517328 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 4400.0129 | 4400.0129 | 188.1382 | 1.0973 | 5.1703 | -48.5563 | 1.4008 | 0.2947 | 0 | 0 | 0 | 0 | 0 | 4399.7182 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 166.3031 | 1.351 | 4.5962 | -42.7842 | 1.2525 | 0.26347 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1364 | Pole Reframing - Wood (Central) |  |  | NA | Bucket for wood pole reframing in the South region | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | 13 | RBPPF - TBD | Yes | 5513327 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 3674.2057 | 3674.2057 | 20.7621 | -12.6883 | 35.1064 | 471.5376 | 1021.6096 | 157.5693 | 0 | 0 | 0 | 0 | 0 | 3516.6364 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 19.41 | -3.8188 | 17.0436 | 419.0353 | 937.9762 | 130.714 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1365 | T Line Wood Pole Reframe - Table Mountai |  |  | NA | Bucket for wood pole reframing in the Table Mountain area. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 211 | 2. Overhead With Strong Safety Link | 14 | NA | NA | 5517314 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 5777.0929 | 5777.0929 | 1656.1211 | 82.0343 | 54.2973 | 9.5692 | 6.6109 | 0 | 0 | 0 | 0 | 0 | 0 | 5777.0929 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1376.5503 | 46.716 | 68.4405 | 4.8886 | 56.9592 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1366 | Wood Pole Reframe - Victor |  |  | NA | Bucket for wood pole reframing in the Victor area. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 211 | 2. Overhead With Strong Safety Link | 41 | NA | NA | 5517329 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1501.6577 | 1501.6577 | 106.5334 | -58.2687 | 19.5475 | 7.1062 | 22.6025 | 0.0105 | 0 | 0 | 0 | 0 | 0 | 1501.6472 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 97.4337 | -31.8783 | 17.1275 | 0.13381 | 28.6097 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1367 | 93G: GO-95 Mitigation |  |  | NA | Forecast placeholder for potential mitigation needed for GO-95 mitigation on HFTD Lines. This work will be developed after line assessments/LiDAR analysis. Represents mitigation on wood pole lines. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | EX112094 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28500 | 40800 | 40800 | 40800 | 40800 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1368 | GO95 Wood - Low Cond Proj (North) |  |  | NA | Bucket for GO95 Low conductor work on wood poles in Northern region | Transmission Line - Multiple | Replace | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | 70 | RBPPF - TBD | No | 5510405 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2013 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 15440.3097 | 15440.3097 | 0 | 0 | 5.4442 | 1259.5741 | 9762.4321 | 3589.2402 | 0 | 0 | 0 | 0 | 0 | 11851.0695 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 2.65 | 1101.1241 | 9565.2789 | 5226.8451 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1369 | GO95 Low Wire - Wood |  |  | NA | Bucket for GO95 Low Wire work on wood poles | Transmission Line - Multiple | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | 38 | RBPPF - TBD | No | 5505379 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 21848.581 | 21848.581 | 250.2043 | 455.0307 | 1048.5186 | 868.6095 | 13950.0999 | 3884.9963 | 0 | 0 | 0 | 0 | 0 | 17963.5847 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 215.3979 | 422.0885 | 855.7157 | 660.4594 | 9847.4798 | 5800.3275 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1370 | GO95 Mitigation - Wood - Lakeville |  |  | NA | Bucket for GO95 Mitigation work on wood poles in Lakeville area | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | NA | 197 | 5. Compliance/Commitments With Strong Safety Link | 7 | NA | NA | 5517249 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1202.9791 | 1202.9791 | 5.4817 | 8.8342 | 7.6557 | 5.7276 | 0.5309 | 0 | 0 | 0 | 0 | 0 | 0 | 1202.9791 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 40.965 | 32.2323 | 60.665 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1371 | Gerber Jct Switch 23 Capability Upgrade |  |  | Corning, Tehama ¦ Cottonwood CDP, Shasta ¦ Gerber CDP, Tehama ¦ Las Flores CDP, Tehama ¦ Proberta CDP, Tehama ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama | Replace switch 23 with an upgrade that has loop breaking and line dropping capability on Cottonwood #1 60kV. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Asset Condition | Age/condition - Switch Replacement - Wood | NA | 2023-11-18 | 88 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 5 | No | EX112704 | TBD | TBD | TBD | 93 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2030-01-01 | NA | 2030-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1372 | Switch Repl - Wood - Fresno BL |  |  | NA | Bucket for switch replacement on wood poles in the Fresno area | Transmission Line - Switch | Replace | NA | Asset Condition | Age/condition - Switch Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5519269 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 5944.1116 | 5944.1116 | 0 | 0 | 13.4185 | 5928.5348 | 2.1374 | 0.021 | 0 | 0 | 0 | 0 | 0 | 5944.0906 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 5518.7722 | 1.9851 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1373 | WSIP - Switch Replacement (Wood) |  |  | NA | Bucket for switch replacements on wood poles as part of WSIP program | Transmission Line - Switch | Replace | NA | Asset Condition | Age/condition - Switch Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3574 | 1. Work that prevents fire ignition | Not Available | RBPPF - TBD | Yes | 5533591 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1162.3944 | 1162.3944 | 177.0205 | 177.9933 | 148.865 | 137.5196 | 462.8257 | 58.1703 | 0 | 0 | 0 | 0 | 0 | 1104.2241 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 165.872 | 168.9395 | 142.3691 | 117.5527 | 399.1243 | 82.6328 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1374 | Insulator Replacements-HFTD-Wood |  |  | NA | Forecast placeholder for Insulator Replacements-HFTD-Wood | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | EX112185 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1375 | Insulator Replacements-Non-HFTD-Wood |  |  | NA | Forecast placeholder for Insulator Replacements-Non-HFTD-Wood | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | EX111866 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1376 | WSIP - Insulator Replacement - Wood |  |  | NA | Bucket for insulator replacement on wood poles in HFTD Tier 2 & 3 | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3566 | 1. Work that prevents fire ignition | 1 | RBPPF - TBD | Yes | 5533592 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 32439.3434 | 32439.3434 | 7827.5276 | 9855.1664 | 8033.9186 | 3755.1037 | 2662.7913 | 277.1196 | 0 | 0 | 0 | 0 | 0 | 32162.2238 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 7014.4912 | 6952.6467 | 6381.1174 | 5611.8507 | 2539.3483 | 316.6819 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1377 | Insulator Replacement - Wood - Eureka |  |  | NA | Bucket for insulator replacement on wood poles in the Eureka area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 84 | NA | NA | 5517291 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1320.0442 | 1320.0442 | 311.9492 | 12.4986 | 13.1477 | -9.0899 | 0.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 1320.0442 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 284.0088 | 11.3201 | 11.2953 | -9.3142 | 0.66212 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1378 | Insulator Replacement - Wood - Fresno |  |  | NA | Bucket for insulator replacement on wood poles in the Fresno area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 52 | NA | NA | 5517292 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 2804.3314 | 2804.3314 | 587.8556 | 39.6233 | 60.8802 | 2.6114 | 0.6406 | 0.0982 | 0 | 0 | 0 | 0 | 0 | 2804.2332 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 526.2277 | 34.648 | 53.5008 | 2.4002 | -9.1288 | -1.8733 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1379 | Insulator Replacement - Wood - Lakeville |  |  | NA | Bucket for insulator replacement on wood poles in the Lakeville area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 8 | NA | NA | 5517293 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1376.6434 | 1376.6434 | 80.2403 | 28.2712 | 6.7425 | -17.0999 | -2.8812 | 0 | 0 | 0 | 0 | 0 | 0 | 1376.6434 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 70.9364 | 24.1318 | 36.8058 | -16.0423 | -2.6305 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1380 | Insulator Replacement - Wood - Midway |  |  | NA | Bucket for insulator replacement on wood poles in the Midway area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 40 | NA | NA | 5517296 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1156.5022 | 1156.5022 | 130.2504 | -10.7248 | 0.915 | 3.0263 | 1.6267 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.5022 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 136.3698 | -7.9208 | -1.1401 | 2.8141 | -1.8284 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1381 | Insulator Replacements - Wood (North) |  |  | NA | Bucket for insulator replacement on wood poles in the North region | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 220 | Not Available | 1 | RBPPF - TBD | Yes | 5505339 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 161355.4651 | 161355.4651 | 4231.9469 | 4383.7989 | 10110.1319 | 22393.145 | 28881.8884 | 1873.0454 | 0 | 0 | 0 | 0 | 0 | 159482.4197 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 3362.2224 | 3500.4358 | 7637.5499 | 18539.3046 | 25648.4598 | 3396.6928 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1382 | Insulator Replacement - Wood-Pismo Beach |  |  | NA | Bucket for insulator replacement on wood poles in the Pismo Beach area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 229 | NA | NA | 5517298 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 3455.5203 | 3455.5203 | 107.1388 | 0.4073 | 0 | 5.3717 | 24.8999 | 0 | 0 | 0 | 0 | 0 | 0 | 3455.5203 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2023 ¦ 2024 | 90.9992 | 0.36929 | 0 | 4.8346 | 11.187 | 1.5663 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1383 | Insulator Replacement - Wood-Sacramento |  |  | NA | Bucket for insulator replacement on wood poles in the Sacramento area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 6 | NA | NA | 5517299 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 2699.972 | 2699.972 | 402.5573 | 51.8592 | 75.4269 | 15.5914 | 0.5477 | 0 | 0 | 0 | 0 | 0 | 0 | 2699.972 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 358.2172 | 46.5517 | 70.3912 | 12.7555 | 0.48457 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1384 | Insulator ReplacementWood-Table Mountain |  |  | NA | Bucket for insulator replacement on wood poles in the Table Mountain area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 4 | NA | NA | 5517301 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 2593.8665 | 2593.8665 | 775.2313 | 22.6977 | 0.7904 | -11.3181 | 1.4883 | 0 | 0 | 0 | 0 | 0 | 0 | 2593.8665 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 682.9211 | 21.1371 | 3.6391 | -9.4163 | -2.9719 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1385 | Insulator Replacements - Wood (Central) |  |  | NA | Bucket for Insulator Replacements on Wood poles in the Central region | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 220 | Not Available | Not Available | NA | NA | 5513325 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2070.8923 | 2070.8923 | 0 | 0 | 0 | -6.7076 | 4.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 2070.8923 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | -5.4969 | -9.364 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1386 | Woodleaf-Palermo 115kV - Insulator |  |  | Butte ¦ Forbestown CDP, Butte ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte | This project proposes to replace aging structures and insulators on the Woodleaf – Palermo 115 kV Line and associated 115 kV Tap lines to help mitigate high-risk components on these line. Scope in details: • Replace 124 of the 232 structures on the Woodleaf – Palermo 115 kV Line with steel structures; • Replace 69 insulators on the Woodleaf – Palermo 115 kV Line; • Perform field analysis on existing structures, Nos. 000/005, 006/053, and 013/128 on the Woodleaf – Palermo 115 kV Line to verify if replacements are needed; • Perform field analysis on 0.02 miles of Sly Creek Tap 115 kV from pole no. 000/006 to 000/008 to verify the age of the conductor and to determine if reconductor is needed; • Replace 3 structures, pole nos. 003/031A, 003/031B, and 003/031C and perform field analysis on 3 structures, pole nos. 002/019, 003/032, and 004/038 to determine if structure and insulator replacements are needed on the Sly Creek Tap 115 kV; • Replace all insulators on the Sly Creek Tap 115 kV; • Replace 1 structure, pole no. 004/039 and conduct field analysis on 3 structures, pole nos. 000/001A, 000/001B, and 000/001C to determine if structure and insulator replacements are needed on the Forbestown Tap 115 kV; • Perform field analysis on 9 structures, pole nos. 000/002, 001/008B, 001/008C, 001/010C, 001/011, 002/015, 002/016, 002/018A, and 002/018C, to verify if structure and insulator replacements are needed on the Kanaka Tap 115 kV; • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Other Equipment | Replace | TBD | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | 2024-04-04 | 62 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 4703 | 2. Overhead With Strong Safety Link | 151 | RBPPF - TBD | Yes | 5789805 | T.0005758 | Woodleaf-Palermo 115kV-Structure & Insul | 3 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-05-04 | NA | 2029-05-31 | NA | FALSE | NA | NA | 2.8325 | 5521.9423 | 0 | 0 | 1.0249 | 1.5802 | 0.1943 | 0.2052 | 0 | 0 | 0 | 0 | 184.9065 | 2.7994 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1387 | Systemwide Idle Line Removal |  |  | NA | Foreast placeholder for Idle Line Removal Program | Transmission Line - Multiple | Removal | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5510559 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 41.6221 | 41.6221 | 0 | 0 | 0 | 0 | 41.6221 | 0 | 0 | 0 | 0 | 0 | 7500 | 41.6221 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2021 | 0.15315 | 0 | -57.7212 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1388 | Caribou-Palermo Idle Facility Removal |  |  | Palermo CDP, Butte ¦ Plumas | Bucket for removal of idle transmission lines in Caribou-Palermo area | Transmission Line - Multiple | Removal | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | 2024-03-20 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 55 | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5541326 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 8494.4337 | 8494.4337 | 0 | 4507.6861 | 4002.2839 | -16.1137 | 0.5775 | 0 | 0 | 0 | 0 | 0 | 0 | 8494.4337 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 4507.6861 | -638.139 | 252.9809 | 0.57749 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1389 | Remove Idle Facilities |  |  | NA | Bucket for removal of idle transmission lines. | Transmission Line - Multiple | Removal | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 124 | 9. Reliability (Low Safety Risk) | 1179 | RBPPF - TBD | No | 5725566 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2023.6652 | 9523.6652 | 0 | 8.1889 | 87.8839 | 296.3678 | 71.9159 | 7523.803 | 0 | 0 | 0 | 0 | 0 | 1999.8622 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 85.9517 | 226.3481 | 39.6668 | 19.5907 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1390 | WSIP - Remove Idle Facilities |  |  | NA | Bucket for removal of t-line idle facilities in HFTD | Transmission Line - Multiple | Removal | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | 1. Work that prevents fire ignition | 4 | NA | NA | 5536740 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1797.0311 | 1797.0311 | 124.1525 | 176.0611 | 788.1281 | 702.0956 | 6.5939 | 0 | 0 | 0 | 0 | 0 | 0 | 1797.0311 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 124.1525 | 102.9843 | 479.6883 | 319.6659 | -12.597 | -21.943 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1391 | BRIGHTON-CLAYTON #2 IDLE CIRCUIT REMOVAL |  |  | Antioch, Contra Costa ¦ Clayton, Contra Costa ¦ Pittsburg, Contra Costa | The project scope includes removing the double lattice steel tower line from Tower A00/001 to Tower 050/376. The tower line will be left in place from Tower 050/377 to Tower 051/386. Tower A00/001 was analyzed and determined to require replacement, which has extended our completion date. | Transmission Line - Multiple | Removal | TBD | Asset Condition | Compliance - Remove Idle Facilities | NA | 2022-07-12 | 89 | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 10.6 | NA | 115 | NA | 4 | 8. Compliance/Commitments With Low Safety Risk | 521 | NA | NA | 5760868 | T.0000413 | BRIGHTON-CLAYTON #2 NERC PROJECT | 1 | 93 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-07-18 | 2017-12-29 | 2021-11-16 | Project Design | FALSE | 4125 | NA | 5913.6593 | 5913.6593 | 31.6711 | 105.2633 | 1927.698 | -92.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5913.6593 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 6.3887 | 21.2336 | 388.8524 | -18.5834 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1392 | Insulator Replacements-HFTD-Steel |  |  | NA | Forecast placeholder for Insulator Replacements-HFTD-Steel | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | No | EX111869 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1393 | Insulator Replacements-Non-HFTD-Steel |  |  | NA | Forecast placeholder for Insulator Replacements-Non-HFTD-Steel | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | No | EX111871 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1394 | CH-S-S # 1 115 kV Insulator Replacement |  |  | Monterey ¦ Prunedale CDP, Monterey ¦ Salinas, Monterey ¦ Soledad, Monterey | Replace Polymer insulators on 45 Structures with glass in an inverted V configuration to meet the 51” clearance requirement. These lines have experienced multiple insulator related outages due to contamination. Replacing the polymer insulators with glass will facilitate the mitigation of future outages related to contamination. | Transmission Line - Other Equipment | Replace | TBD | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2023-05-19 | 100 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5801819 | T.0009090 | CH-S-S # 1 & # 2 115 kV Insulator Repl | 2 | 93 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-11-01 | NA | 2030-03-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1395 | CH-S-S # 2 115 kV Insulator Replacement |  |  | Monterey ¦ Prunedale CDP, Monterey ¦ Salinas, Monterey ¦ Soledad, Monterey | Replace Polymer insulators on 45 Structures with glass in an inverted V configuration to meet the 51” clearance requirement. These lines have experienced multiple insulator related outages due to contamination. Replacing the polymer insulators with glass will facilitate the mitigation of future outages related to contamination. | Transmission Line - Other Equipment | Replace | TBD | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2021-08-24 | 100 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5801820 | T.0009090 | CH-S-S # 1 & # 2 115 kV Insulator Repl | 2 | 93 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-11-01 | NA | 2030-03-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1396 | Round Mtn-Table Mtn #1 500kV Insulators |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Chico, Butte ¦ Cohasset CDP, Butte ¦ Round Mountain CDP, Shasta ¦ Shasta ¦ Tehama ¦ Whitmore CDP, Shasta | A previous project replaced the insulators on 121 of the 368 total structures. Following an outage on the Tesla-Los Banos 500kV line and subsequent inspections, The Round Mountain-Table Mountain #1 500kV line was found to have insulators of the same type in a deteriorated condition with damage at some locations. This project proposes to replace the insulators, hardware and install corona rings on the remaining 247 structures to prevent failures resulting in outages or possible fire ignition. | Transmission Line - Other Equipment | Replace | TBD | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-12 | 59 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Extreme Heat |  | NA | NA | 500 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5786185 | T.0004860 | Round Mtn-Table Mtn #1 500kV Insulators | 1 | 93 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-01-01 | NA | 2031-05-15 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1397 | Round Mtn-Table Mtn #2 500kV Insulators |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Butte Valley CDP, Butte ¦ Chico, Butte ¦ Cohasset CDP, Butte ¦ Manton CDP, Shasta ¦ Manton CDP, Tehama ¦ Paynes Creek CDP, Tehama ¦ Round Mountain CDP, Shasta ¦ Shasta ¦ Tehama ¦ Whitmore CDP, Shasta | A previous project replaced the insulators on 79 of the 366 total structures. Following an outage on the Tesla-Los Banos 500kV line and subsequent inspections, The Round Mountain-Table Mountain #2 500kV line was found to have insulators of the same type in a deteriorated condition with damage at some locations. This project proposes to replace the insulators, hardware and install corona rings on the remaining 287 structures to prevent failures resulting in outages or possible fire ignition. | Transmission Line - Other Equipment | Replace | TBD | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-12 | 59 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Extreme Heat |  | NA | NA | 500 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5786186 | T.0004862 | Round Mtn-Table Mtn #2 500kV Insulators | 1 | 93 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-01-01 | NA | 2031-05-15 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1398 | Insulator Rep Steel - Moss Landing |  |  | NA | Bucket for insulator replacement on steel poles in the Moss Landing area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 13 | RBPPF - TBD | No | 5517285 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 4362.6787 | 4362.6787 | 321.4005 | 1709.7876 | 163.6703 | 4.1096 | 10.2143 | 1.0639 | 0 | 0 | 0 | 0 | 0 | 4361.6148 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 279.8306 | 1476.6674 | 138.1884 | 26.4347 | 3.8598 | 1.2668 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1399 | Insulator Rep Steel - Concord |  |  | NA | Bucket for insulator replacement on steel towers in the Concord area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Heat Wave |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 144 | RBPPF - TBD | No | 5517258 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 2671.9627 | 2671.9627 | 468.0932 | 227.5766 | 411.0943 | 157.188 | 30.3119 | 1.3012 | 0 | 0 | 0 | 0 | 0 | 2670.6615 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 467.5297 | 180.0298 | 334.6172 | 157.4702 | -13.1324 | 2.0234 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1400 | Insulator Rep Steel - Lakeville |  |  | NA | Bucket for insulator replacement on steel towers in the Lakeville area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 2 | RBPPF - TBD | No | 5517281 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 3589.3141 | 3589.3141 | 162.9616 | 606.1142 | 1125.7015 | 441.7104 | 311.6833 | 25.5646 | 0 | 0 | 0 | 0 | 0 | 3563.7495 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 144.1581 | 507.3303 | 989.8502 | 494.8826 | 235.0502 | 16.5036 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1401 | Insulator Rep Steel - Metcalf |  |  | NA | Bucket for insulator replacement on steel towers in the Metcalf area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 91 | RBPPF - TBD | No | 5517283 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 6589.89 | 6589.89 | 277.0998 | 1127.6397 | 723.2787 | 2653.37 | 1239.2033 | 55.6806 | 0 | 0 | 0 | 0 | 0 | 6534.2094 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 271.7637 | 1006.3393 | 668.8773 | 2435.2425 | 934.5566 | -274.9106 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1402 | Insulator Rep Steel - Midway |  |  | NA | Bucket for insulator replacement on steel towers in the Midway area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 21 | NA | NA | 5517284 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 6916.8643 | 6916.8643 | 1413.2731 | 1053.8248 | 439.5356 | 95.4361 | 11.605 | 0.3355 | 0 | 0 | 0 | 0 | 0 | 6916.5288 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1002.2065 | 856.4418 | 404.862 | 61.9091 | 4.8052 | 0.58754 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1403 | Insulator Rep Steel - Pismo Beach |  |  | NA | Bucket for insulator replacement on steel towers in the Pismo Beach area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 21 | RBPPF - TBD | No | 5517286 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 15082.4138 | 15082.4138 | 3228.8583 | 3768.2976 | 1386.2011 | 182.3998 | 47.7507 | 4.1958 | 0 | 0 | 0 | 0 | 0 | 15078.218 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 2702.5224 | 3748.0224 | 1369.681 | 428.218 | -256.4932 | 3.8405 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1404 | Insulator Rep Steel - Sacramento |  |  | NA | Bucket for insulator replacement on steel towers in the Sacramento area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 37 | RBPPF - TBD | No | 5517287 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 6713.379 | 6713.379 | 1053.5498 | 962.5164 | 140.1312 | 423.1585 | 11.0918 | 49.5064 | 0 | 0 | 0 | 0 | 0 | 6663.8726 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1012.8443 | 965.3193 | 139.2267 | 271.5358 | -11.0925 | 61.0377 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1405 | Insul Repl - Steel - Table Mountain BL |  |  | NA | Bucket for insulator replacement on steel towers in the Table Mountain area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5519144 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2699.266 | 2699.266 | 0 | 0 | 128.3294 | 2472.0564 | 88.158 | 10.7222 | 0 | 0 | 0 | 0 | 0 | 2688.5438 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 116.1819 | 2484.2039 | -504.7767 | 11.4032 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1406 | Insulator Rep Steel - Table Mountain |  |  | NA | Bucket for insulator replacement on steel towers in the Table Mountain area. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 4 | RBPPF - TBD | No | 5517288 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 9252.9002 | 9252.9002 | 1644.9256 | 1133.3386 | 2233.1709 | 565.5939 | 166.511 | 133.0427 | 0 | 0 | 0 | 0 | 0 | 9119.8575 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 1510.5959 | 1108.9304 | 2177.4012 | 436.6733 | 29.9616 | 177.8116 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1407 | 500/230kV Insulators&Struct-N Steel |  |  | NA | Bucket for replacement or installation of 500/230 kV insulators on steel structures in North region | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | NA | 500 ¦ 230 | NA | 202 | Not Available | 67 | NA | NA | 5510403 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 10334.0502 | 10334.0502 | 18.911 | 0 | 0.1306 | 35.2502 | 0 | 0.021 | 0 | 0 | 0 | 0 | 0 | 10334.0292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2022 ¦ 2024 | 13.1857 | 0 | 0 | 35.3808 | 0 | 0.15217 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1408 | 500/230kV Insulators & Struct - S Steel |  |  | NA | Bucket for replacement or installation of 500/230 kV insulators on steel structures in South region | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | 500 ¦ 230 | NA | 202 | Not Available | 27 | RBPPF - TBD | No | 5506219 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 20558.6192 | 20558.6192 | 0 | 0 | 693.0058 | 4295.0448 | 159.5033 | 2.5877 | 0 | 0 | 0 | 0 | 0 | 20556.0315 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 600.4612 | 4034.8058 | -262.7018 | 51.2748 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1409 | 60/70/115kV N Insulators & Struc - Steel |  |  | NA | Bucket for replacement or installation of 60/70/115 kV insulators on steel structures in North region | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | 115 ¦ 70 ¦ 60 | NA | 202 | Not Available | 12 | RBPPF - TBD | No | 5510406 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 13053.5928 | 13053.5928 | 0 | 4.9185 | 542.7533 | 6227.3403 | 910.6017 | 132.8611 | 0 | 0 | 0 | 0 | 0 | 12920.7317 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 431.5574 | 5723.0344 | 404.9598 | 65.3964 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1410 | WSIP - Insulator Replacement - Steel |  |  | NA | Bucket for replacement or installation of insulators on steel structures in HFTD Tier 2 & 3 | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3562 | 1. Work that prevents fire ignition | 2 | RBPPF - TBD | No | 5533593 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 260745.5853 | 260745.5853 | 26742.3764 | 20879.8816 | 40269.7687 | 72572.5265 | 92301.3694 | 7886.9609 | 0 | 0 | 0 | 0 | 0 | 252858.6244 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 26480.1847 | 17403.0907 | 36900.0179 | 64852.4542 | 70590.7354 | 7126.0064 | 0% | NA | NA | NA | 100% | 0% | [Year of Business Case Approval] Job Estimate serves as Utility Approval. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements.
| 1411 | 2020-2022 Insulator program |  |  | NA | Bucket for replacement or installation of insulators on transmission lines. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 75 | RBPPF - TBD | No | 5507680 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 10685.1265 | 27351.7932 | 0 | 0 | 0 | 0 | 0 | 16666.6667 | 0 | 0 | 0 | 0 | 0 | 10685.1265 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1412 | Pit#3-Pit#1 230 kV Insulators |  |  | Burney CDP, Shasta ¦ Johnson Park CDP, Shasta ¦ Shasta | Increase reliability by replacing insulators and hardware on 183 structures on Pit #3-Pit #1 230kV circuit | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-03-20 | 97 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | NA | 230 | NA | 202 | 1. Work that prevents fire ignition | 150 | NA | NA | 5772999 | T.0002405 | Pit#3-Pit#1 230 kV Insulators | 2 | 93 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-09-21 | 2019-09-05 | 2020-10-12 | Material | FALSE | 6300 | NA | 2681.4471 | 2681.4471 | 435.6103 | 1950.9112 | 274.9382 | 9.0566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2681.4471 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 2672.3903 | 9.0566 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1413 | Pit #3-Carberry Sta Insulators |  |  | Shasta | Increase reliability by replacing insulators and hardware on 89 structures on Pit #3-Carberry SW Station 230kV circuit. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2022-07-06 | 97 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | NA | 230 | NA | 202 | 1. Work that prevents fire ignition | 313 | NA | NA | 5773000 | T.0002406 | Pit #3-Carberry Sta Insulators | 1 | 93 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-01-12 | 2020-10-09 | 2020-10-20 | NA | FALSE | 3900 | NA | 2649.7402 | 2649.7402 | 228.9313 | 1923.7992 | 442.3136 | 41.1972 | 1.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 2649.7402 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 2606.6495 | 41.1972 | 1.8932 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1414 | Tesla-Metcalf 500 kV Insulator Replace |  |  | Alameda ¦ San Jose, Santa Clara ¦ Santa Clara | Insulators on 28 towers of the line have already been replaced after the insulators flashed and failed. The Tesla – Metcalf 500 kV Line Insulator Replacement Project (Project) will replace the insulators on the remaining 120 transmission line structures. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-03-26 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 253 | NA | NA | 5774626 | T.0002836 | Tesla-Metcalf 500 kV Insulator Replace | 1 | 93 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-06-20 | 2020-02-28 | 2022-07-19 | Bundling Dependencies | FALSE | 6647 | NA | 14398.6853 | 14398.6853 | 231.9514 | 4936.9055 | 3546.0945 | 5663.5324 | 12.8614 | 0 | 0 | 0 | 0 | 0 | 0 | 14398.6853 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 13576.4456 | 12.0836 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1415 | Pit#1-Cottonwood 230kV Insulators |  |  | Burney CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Johnson Park CDP, Shasta ¦ Millville CDP, Shasta ¦ Oak Run CDP, Shasta ¦ Round Mountain CDP, Shasta ¦ Shasta | Over the decades the insulators and steel members have been exposed to avian nesting, guano and streamers. There have been relatively few failures, however with this prolonged exposure and age consideration. The project is to increase reliability by replacing insulators and hardware on 530 structures on Pit #1-Cottonwood 230kV circuit. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-04 | 96 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat, Weather |  | NA | NA | 230 | NA | 446 | 1. Work that prevents fire ignition | 19 | NA | NA | 5782138 | T.0002407 | Pit#1-Cottonwood 230kV Insulators | 2 | 93 | NA | 2018 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-08-13 | 2019-11-21 | 2020-09-14 | Prioritization | FALSE | 8671 | NA | 8584.6851 | 8584.6851 | 1350.5083 | 6286.2354 | 823.3386 | 95.9985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8584.6851 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 5881.6132 | 65.3722 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1416 | Gates-Midway 500 kV Line Ins Replacement |  |  | Avenal, Kings ¦ Buttonwillow CDP, Kern ¦ Fresno ¦ Kern ¦ Kings | The majority of the structures have the original ceramic insulators. Over the decades the insulators and steel members have been exposed to avian nesting, guano, streamers, and other type of contamination. Although there have been relatively few failures, the consequences have been and can be significant due to the inherit risk associated with 500 kV lines. The objective is to replace existing insulators and associated hardware on 22 towers on the Gates – Midway 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2020-08-10 | 56 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | NA | 500 | NA | 202 | 2. Overhead With Strong Safety Link | 801 | NA | NA | 5772889 | T.0002381 | Gates-Midway 500kV Line Insulator Replac | 1 | 93 | NA | 2018 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-19 | 2019-10-20 | 2021-05-13 | Prioritization | FALSE | 1600 | NA | 4611.9052 | 4611.9052 | 738.8482 | 1632.5232 | 2061.0183 | 3.7807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4611.9052 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 3728.9896 | 95.047 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $2 Mil - $3 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1417 | Los Banos-Gates #1 500 kV Line Ins Repl |  |  | Fresno ¦ Merced | The majority of the structures have the original ceramic insulators. Over the decades, the insulators and steel members have been exposed to avian nesting, guano, streamers, and other types of contamination. Although there have been relatively few failures, the consequences have been and can be significant due to the inherit risk associated with 500 kV lines. The objective is to replace existing insulators and associated hardware on 200 structures on the Los Banos - Gates No. 1 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-08 | 61 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | NA | 500 | NA | 202 | 2. Overhead With Strong Safety Link | 450 | NA | NA | 5772896 | T.0002388 | Los Banos-Gates #1 500kV Line Insulator | 1 | 93 | NA | 2018 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-07-06 | 2019-12-31 | 2020-12-15 | Prioritization | FALSE | 4911 | NA | 6710.918 | 6710.918 | 2076.9332 | 3979.4539 | 430.9735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6710.918 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 5379.005 | 367.6322 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1418 | Los Banos-Midway #2 Line Ins Repl |  |  | Avenal, Kings ¦ Buttonwillow CDP, Kern ¦ Fresno ¦ Kern ¦ Kings ¦ Merced | The majority of the structures have the original ceramic insulators. Over the decades, the insulators and steel members have been exposed to avian nesting, guano, streamers, and other types of contamination. Although there have been relatively few failures, the consequences have been and can be significant due to the inherit risk associated with 500 kV lines. The objective is to replace existing insulators and associated hardware on 151 structures on the Los Banos - Midway No. 2 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-08 | 54 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | NA | 500 | NA | 202 | 2. Overhead With Strong Safety Link | 398 | NA | NA | 5772897 | T.0002389 | Los Banos-Midway #2 500kV Line Insulator | 1 | 93 | NA | 2019 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-08-20 | 2019-12-31 | 2021-05-27 | Prioritization | FALSE | 10590 | NA | 8875.6179 | 8875.6179 | 1622.5287 | 5175.7461 | 1865.6855 | 4.8613 | 0.3156 | 0 | 0 | 0 | 0 | 0 | 0 | 8875.6179 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 7840.7449 | 4.2715 | -120.5751 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1419 | Malin-Round Mountain #2-500 kV Ins Repl |  |  | Montgomery Creek CDP, Shasta ¦ Round Mountain CDP, Shasta ¦ Shasta ¦ Siskiyou | The purpose of this project is to replace the 500kV insulators on the Malin-Round Mountain #2 transmission line. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-12 | 56 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 35 | NA | NA | 5772895 | T.0002387 | Malin-Round Mountain #2-500 kV Ins Repl | 1 | 93 | NA | 2011 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-08-24 | 2020-12-31 | 2021-06-21 | NA | FALSE | 8000 | NA | 14040.9279 | 14040.9279 | 55.8062 | 8874.2781 | 4856.571 | -0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14040.9279 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 14041.0922 | -0.3 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1420 | Diablo-Gates #1 500 kV Insl Replace |  |  | Atascadero, San Luis Obispo ¦ El Paso de Robles, San Luis Obispo ¦ Fresno ¦ Kings ¦ Los Osos CDP, San Luis Obispo ¦ Monterey ¦ San Luis Obispo | This project proposes to replace insulators and associated hardware on 311 structures within the Diablo – Gates No. 1 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-11 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 33 | NA | NA | 5774629 | T.0002839 | Diablo-Gates #1 500 kV Insl Replace | 1 | 93 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-10-01 | 2021-11-30 | 2021-11-22 | NA | FALSE | 10200 | NA | 13674.6909 | 13674.6909 | 0 | 264.9886 | 13625.5507 | -215.8484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13674.6909 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 12720.3236 | -197.5497 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1421 | Diablo-Midway #2 500 kV Insl Replace |  |  | Avila Beach CDP, San Luis Obispo ¦ Buttonwillow CDP, Kern ¦ Kern ¦ San Luis Obispo | This project proposes to replace insulators and associated hardware on 350 structures on the Diablo – Midway No. 2 500 kV Line. The main type of insulator for replacement are first generation Sediver as these have experience failures from years of contamination which ATS and the vendor have analyzed and confirm replacement. In addition, the associated corona rings, or lack there of, are being replaced/installed accordingly primarily due to corrosion. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-12 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 21 | NA | NA | 5774631 | T.0002841 | Diablo-Midway #2 500 kV Insl Replace | 1 | 93 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-02-17 | 2022-04-08 | 2022-03-21 | NA | FALSE | 8650 | NA | 11037.4705 | 11037.4705 | 0 | 240.4445 | 1357.6026 | 9439.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11037.4705 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 10141.2262 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1422 | Diablo-Midway #3 500 kV Insl Replace |  |  | Avila Beach CDP, San Luis Obispo ¦ Buttonwillow CDP, Kern ¦ Kern ¦ San Luis Obispo | This project proposes to replace insulators and associated hardware on 362 structures on the Diablo – Midway No. 3 500 kV Line. The main type of insulator for replacement are first generation Sediver as these have experience failures from years of contamination which ATS and the vendor have analyzed and confirm replacement. In addition, the associated corona rings, or lack there of, are being replaced/installed accordingly primarily due to corrosion. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-12 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 27 | NA | NA | 5774630 | T.0002840 | Diablo-Midway #3 500 kV Insl Replace | 1 | 93 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-01-11 | 2022-02-18 | 2022-04-06 | NA | FALSE | 6520 | NA | 9051.1528 | 9051.1528 | 0 | 228.7847 | 3883.952 | 4937.5629 | 0.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 9051.1528 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 8876.9136 | 0.83648 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1423 | Replace Insulators - Vaca-Tesla 500kV |  |  | Alameda ¦ Byron CDP, Contra Costa ¦ Contra Costa ¦ Discovery Bay CDP, Contra Costa ¦ Knightsen CDP, Contra Costa ¦ Oakley, Contra Costa ¦ Sacramento ¦ Solano ¦ Vacaville, Solano | This project proposes to replace insulators and associated hardware on 39 structures on the Vaca – Tesla 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-11 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | NA | 500 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5782299 | T.0004299 | Replace Insulators - Vaca-Tesla 500kV | 1 | 93 | NA | 2018 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2024-12-11 | 2022-12-31 | 2025-03-06 | Prioritization | TRUE | 7400 | NA | 2896.053 | 6991.4791 | 0 | 0 | 61.5021 | 2830.1299 | 4.421 | 3881.3075 | 214.1186 | 0 | 0 | 0 | 4000 | 2896.053 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1424 | Moss Landing-Metcalf 500 kV Insl Rep |  |  | Elkhorn CDP, Monterey ¦ Monterey ¦ Prunedale CDP, Monterey ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Santa Cruz | This project proposes to replace insulators on 125 structures on the Moss Landing – Metcalf 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-03-29 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 73 | NA | NA | 5774628 | T.0002838 | Moss Landing-Metcalf 500 kV Insl Rep | 1 | 93 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-12-27 | 2021-11-05 | 2022-02-14 | NA | FALSE | 6430 | NA | 7228.1033 | 7228.1033 | 4.8234 | 203.5149 | 3350.7045 | 3669.0605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7228.1033 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 6659.1636 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1425 | Moss Landing-Los Banos 500 kV Insl Rep |  |  | Merced ¦ Monterey ¦ Prunedale CDP, Monterey ¦ Ridgemark CDP, San Benito ¦ San Benito ¦ Tres Pinos CDP, San Benito | This project proposes to replace insulators on 185 structures on the Moss Landing – Los Banos 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | 2024-04-11 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 248 | NA | NA | 5774627 | T.0002837 | Moss Landing-Los Banos 500 kV Insl Rep | 1 | 93 | NA | 2018 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-08-08 | 2021-12-24 | 2022-08-26 | Clearances | FALSE | 6530 | NA | 7675.0542 | 7675.0542 | 3.8324 | 204.2028 | 4820.9758 | 2641.6551 | 4.3882 | 0 | 0 | 0 | 0 | 0 | 0 | 7675.0542 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 7076.0488 | -213.0732 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1426 | System NERC Mitigation Project (North) |  |  | NA | Bucket for System NERC Mitigation Project in Northern Service Territory | Transmission Line - Multiple | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 228 | Not Available | 5 | NA | NA | 5510301 | NA | NA | NA | 93 | 5520745 | 2014 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 72011.8842 | 72011.8842 | 40.8563 | 530.7272 | -232.4718 | -340.3501 | 329.5932 | -145.4333 | 0 | 0 | 0 | 0 | 0 | 72157.3175 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 116.0419 | 397.9866 | -167.5529 | -341.3523 | 329.4723 | -143.512 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1427 | Rio Oso-West Sacramento 115kV NERC |  |  | Arden-Arcade CDP, Sacramento ¦ Elverta CDP, Sacramento ¦ Rio Linda CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ West Sacramento, Yolo | Install 23 top cage extensions and replace 49 towers on the Rio Oso-West Sacramento 115kV circuit. This mitigation work will eliminate clearance issues and allow operation of the line at full capacity. The project is a result of assessment work completed as part of the NERC Alert – Electric Transmission Project. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2022-09-27 | 86 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 43.6 | NA | 115 | NA | 228 | Not Available | NA | NA | NA | 5774458 | T.0002765 | Rio Oso-West Sacramento 115kV NERC | 1 | 93 | NA | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-10 | 2017-06-17 | 2019-10-11 | Prioritization | FALSE | 11135 | NA | 10738.0738 | 10738.0738 | 905.9339 | 34.9623 | 9410.0384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10738.0738 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 815.8692 | 31.4865 | 8148.4642 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1428 | TRINITY-COTTONWOOD 115kV Ph 2 |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Multiple | Replace | T.0000126 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | 71 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 7.1 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 61 | NA | NA | 5784199 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 6 | 93 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5685-E | 2019-11-13 | Approved | 2019 | Operational | 2 | 2020-07-01 | 2020-12-31 | 2020-09-23 | NA | FALSE | 18400 | NA | 7663.9766 | 7663.9766 | 815.6518 | 6853.2044 | 51.4385 | -56.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7663.9766 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 6407.1073 | 42.8736 | -46.9406 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1429 | Trinity-Cottonwood 115kV Ph. 3 |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Multiple | Replace | T.0000126 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | 74 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 6 | NA | 115 | NA | 228 | Not Available | Not Available | NA | NA | 5790355 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 6 | 93 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6191-E | 2021-05-12 | Approved | 2021 | Operational | 2 | 2021-08-09 | 2021-11-30 | 2022-01-07 | NA | FALSE | 18400 | NA | 6873.5314 | 6873.5314 | 0 | 247.8077 | 6784.2537 | -158.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6873.5314 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 6070.3633 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1430 | Trinity-Cottonwood 115kV Ph. 4 |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Multiple | Replace | T.0000126 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | 75 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 18.5 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 61 | Tier 5 | No | 5792158 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 6 | 93 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6602-E | 2022-05-19 | Approved | 2022 | Construction (50%-75%) | 3 | 2022-09-06 | 2022-11-30 | 2024-12-09 | Prioritization | TRUE | 18400 | NA | 11272.5565 | 14106.7017 | 0 | 91.8992 | 1241.8912 | 10098.8328 | -367.221 | 3039.2995 | 2 | 0 | 0 | 0 | 0 | 11065.4022 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1431 | Trinity-Cottonwood Land Acquisition |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Other | New | T.0000126 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | NA | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5545327 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 6 | 93 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | NA | 2022-11-30 | 2024-12-01 | Prioritization | TRUE | 18400 | NA | 912.3178 | 1012.3178 | 0 | 0 | 10.5 | 212.3126 | 607.9813 | 181.5239 | 0 | 0 | 0 | 0 | 0 | 830.7939 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 222.8126 | 607.9813 | 86.1376 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1432 | TRINITY-COTTONWOOD NERC PROJECT |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Pole/Tower | Replace | T.0000126 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | 71 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 228 | Not Available | NA | NA | NA | 5760929 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 6 | 93 | 5767318 | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5685-E | 2019-11-13 | Approved | 2019 | Operational | 2 | 2019-06-25 | 2020-12-31 | 2019-07-17 | NA | FALSE | 18400 | NA | 6616.3147 | 6616.3147 | 5729.9997 | 27.6445 | -10.8535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6616.3147 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 5660.7503 | 25.4504 | -9.2684 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1433 | Mesa-Santa Maria 115kV NERC |  |  | Nipomo CDP, San Luis Obispo ¦ San Luis Obispo ¦ Santa Maria, Santa Barbara | Raise 9 Structures by installing 4 Waist Cage and 5 Top Cage Extensions, install 1 interset TSP and new shieldwire over 30 spans, and re-tension 2 parallel circuits for 29 spans each to address 6 GO 95 clearance issues, conductor over-tension issues and close gas line proximity to towers identified on the Mesa – Santa Maria 115kV Transmission Line to allow operation at full capacity. The project is a result of assessment work completed as part of the NERC Alert – Electric Transmission Project. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2023-11-20 | 68 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 4.3 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 22 | NA | NA | 5774250 | T.0002756 | Mesa-Santa Maria 115kV NERC | 1 | 93 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5874-E | 2020-07-09 | Approved | 2020 | Operational | 2 | 2020-10-26 | 2020-05-31 | 2021-02-15 | Prioritization | FALSE | 5700 | NA | 8433.0597 | 8433.0597 | 558.1485 | 5719.0974 | 1611.9231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8433.0597 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | 0 | 8267.0407 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1434 | Temblor-San Luis Obispo 115kV NERC Prj |  |  | Kern ¦ San Luis Obispo | Replace single conductor on 38 miles, retension 8 spans, raise 8 towers via top cage extensions, install 3 interset Tubular Steel Poles, convert 6 suspension towers to dead-ends, replace 2 switches, and modify 64 tower foundations on the Temblor-San Luis Obispo 115kV line to comply with CPUC General Order 95 (GO-95) requirements. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-09 | 82 | Lifecycle Replacement Analysis | Other - Deferral | $20 Mil - $30 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 38 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 23 | RBPPF - TBD | Yes | 5750606 | T.0000423 | TEMBLOR-SAN LUIS OBISPO 115KV NERC | 1 | 93 | NA | 2013 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | On Hold | 4 | 2026-12-03 | 2020-11-07 | 2027-08-26 | Prioritization | FALSE | 26061 | NA | 5346.7265 | 43536.9508 | 221.922 | 881.7843 | 1158.6415 | 573.0664 | 89.1467 | -31.3768 | 0 | 1381.1001 | 5773.8744 | 32137.2173 | 63.3761 | 5346.7265 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1435 | IGNACIO-MARE ISL 115KV (HWY SUB/COR SUB) |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The Ignacio-Mare Island #1 and #2 115kV NERC project team will be performing work from the Highway Substation to Cordelia Substation to replace and install structures, install cage extensions, and reconductor approximately 16.0 miles due to over-tension issues. It will also perform work from Jameson Substation to the North Tower and Mare Island Substations to replace and install structures and reconductor approximately 5.2 miles due to over-tension issues. The project team will improve system performance and reduce extended outage risk on the Ignacio-Mare Island 115kV transmission line by completing the scopes shown below. | Transmission Line - Multiple | Replace | T.0002886 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-14 | 73 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $350 Mil – $400 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 16 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 295 | RBPPF - TBD | Yes | 5774831 | T.0000415 | IGNACIO-MARE ISLD Jameson/Hwy - Cordelia | 6 | 93 | NA | 2017 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6601-E | 2022-05-18 | Approved | 2022 | Engineering more than 50% complete | 4 | 2025-07-22 | 2023-09-30 | 2025-10-31 | Material | TRUE | 28300 | NA | 6329.9181 | 15149.1173 | 60.7802 | 450.0761 | 1267.9409 | 2787.7935 | 206.1373 | 813.7276 | 8240.0877 | 0 | 0 | 0 | 0 | 6074.1921 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1436 | IGNACIO-MARE ISLAND 1-2 115KV NERC |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The Ignacio-Mare Island #1 and #2 115kV NERC project team will be performing work from the Highway Substation to Cordelia Substation to replace and install structures, install cage extensions, and reconductor approximately 16.0 miles due to over-tension issues. It will also perform work from Jameson Substation to the North Tower and Mare Island Substations to replace and install structures and reconductor approximately 5.2 miles due to over-tension issues. The project team will improve system performance and reduce extended outage risk on the Ignacio-Mare Island 115kV transmission line by completing the scopes shown below. | Transmission Line - Multiple | Replace | T.0002886 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-14 | 73 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $350 Mil – $400 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 5.2 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 295 | RBPPF - TBD | Yes | 5754759 | T.0000415 | IGNACIO-MARE ISLD Jameson/Hwy - Cordelia | 6 | 93 | NA | 2017 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6601-E | 2022-05-18 | Approved | 2022 | Engineering more than 50% complete | 4 | 2024-06-10 | 2023-09-30 | 2024-11-04 | Prioritization | TRUE | 28300 | NA | 5011.7813 | 14074.5274 | 88.4898 | 331.6946 | 1062.6375 | 2363.0564 | 52.9869 | 9195.7076 | 54.5052 | 0 | 0 | 0 | 0 | 4824.3146 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1437 | Ignacio-Mare Island Hwy Sub-Jameson Shoo |  |  | American Canyon, Napa ¦ Benicia, Solano ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The Ignacio-Mare Island #1 and #2 115kV NERC project team will be performing work from the Highway Substation to Cordelia Substation to replace and install structures, install cage extensions, and reconductor approximately 16.0 miles due to over-tension issues. It will also perform work from Jameson Substation to the North Tower and Mare Island Substations to replace and install structures and reconductor approximately 5.2 miles due to over-tension issues. The project team will improve system performance and reduce extended outage risk on the Ignacio-Mare Island 115kV transmission line by completing the scopes shown below. | Transmission Line - Multiple | Replace | T.0002886 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2020-07-20 | 73 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $350 Mil – $400 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.1 | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5801318 | T.0000415 | IGNACIO-MARE ISLD Jameson/Hwy - Cordelia | 6 | 93 | NA | 2017 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6601-E | 2022-05-18 | Approved | 2022 | Operational | 2 | 2022-10-01 | 2023-09-30 | 2022-10-20 | NA | TRUE | 28300 | NA | 1830.8413 | 1830.8413 | 0 | 0 | 0 | 1698.6354 | 120.5067 | 11.6992 | 0 | 0 | 0 | 0 | 0 | 1819.1421 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1533.5832 | 108.6655 | 12.6472 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1438 | Ignacio-Mare Isld #1 - Support of Ignacio |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The Ignacio-Mare Island #1 and #2 115kV NERC project team will be performing work from the Highway Substation to Cordelia Substation to replace and install structures, install cage extensions, and reconductor approximately 16.0 miles due to over-tension issues. It will also perform work from Jameson Substation to the North Tower and Mare Island Substations to replace and install structures and reconductor approximately 5.2 miles due to over-tension issues. The project team will improve system performance and reduce extended outage risk on the Ignacio-Mare Island 115kV transmission line by completing the scopes shown below. | Transmission Line - Multiple | Replace | T.0002886 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-14 | 73 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $350 Mil – $400 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | NA | NA | 5551781 | T.0000415 | IGNACIO-MARE ISLD Jameson/Hwy - Cordelia | 6 | 93 | NA | 2017 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-10-04 | 2023-09-30 | 2023-11-14 | NA | TRUE | 28300 | NA | 1392.118 | 1401.568 | 0 | 0 | 0 | 0 | 1220.557 | 181.011 | 0 | 0 | 0 | 0 | 0 | 1220.557 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 1098.957 | 146.5436 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1439 | IGNACIO-SAN RAFAEL 3 115KV NERC WOOD P2 |  |  | Marin ¦ Novato, Marin ¦ San Rafael, Marin | The IGNACIO-SAN RAFAEL # 3 115kV project will replace 40 wood poles with new wood poles, 3 lower distribution, 8 cross-arm replacements, 3 reframes, and 2 switch replacements to allow operation of the line at full capacity. The project is a result of assessment work completed as part of the NERC Alert – Electric Transmission Project | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-19 | 63 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 2 | NA | 115 | NA | 228 | Not Available | Not Available | NA | NA | 5774249 | T.0002764 | IGNACIO-SAN RAFAEL 3 115KV NERC WOOD P2 | 1 | 93 | NA | 2014 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-07-05 | 2017-07-17 | 2021-03-19 | Prioritization | FALSE | 5725 | NA | 5100.2998 | 5100.2998 | 1.4408 | 547.6029 | 105.4248 | 0.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5100.2998 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 1.3593 | 288.4061 | 94.5236 | 0.85101 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1440 | KINGSBURG CORCORAN 1 AND 2 115KV NERC |  |  | Corcoran, Kings ¦ Fresno ¦ Kings | The Kingsburg-Corcoran #1 & #2 115kV circuits were analyzed as part of the 2011 Priority 1 NERC Assessment. The analysis consisted of LiDAR surveying and PLS CADD modeling to identify non-compliant spans. The completed analysis identified 153 of the 199 spans (77%) with clearance issues on the Kingsburg-Corcoran #1 and 139 of the 200 spans (70%) with clearance issues on the Kingsburg-Corcoran #2 electric transmission lines. The Kingsburg-Corcoran #1 and #2 115kV NERC project will address the above discrepancies and return the line back to compliance. Of the total 200 spans and 201 structures being replaced, the Kingsburg-Corcoran #1 and #2 115kV NERC project is responsible for replacement and reconductoring of 137 structures and spans. The High Speed Rail (HSR) relocation program will replace and reconductor the balance of the scope. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-09 | 95 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 36.7 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 432 | Tier 5 | No | 5767509 | T.0000434 | KINGSBURG CORCORAN 1 AND 2 115KV NERC | 1 | 93 | 5751061 | 2013 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | On Hold | 4 | 2026-11-01 | 2022-03-31 | 2027-03-31 | Prioritization | FALSE | 25658 | NA | 11043.7724 | 59494.9399 | 195.0367 | 34.4892 | 748.9744 | 5050.4626 | 1507.7703 | 2645.0655 | 1671.7996 | 39200.8247 | 8836.8684 | 0 | 0 | 8406.6751 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1441 | Silverado-Fulton 115kV Sw. No. 147 149 |  |  | Napa ¦ Saint Helena, Napa ¦ Yolo | The objective of this project is to design and replace the structures and switches at Silverado Jct. The new design will replace two (2) switches, two (2) wood structures with TSPs, and one wood tap pole to LDSP. This mitigation work will eliminate clearance issues and allow operation of the line at full capacity with work | Transmission Line - Switch | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-02-27 | 103 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 | NA | 228 | Not Available | NA | NA | NA | 5530982 | T.0004130 | Silverado Fulton 115kV Sw. No. 147/149E | 1 | 93 | NA | 2012 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-20 | 2019-10-31 | 2019-11-23 | NA | FALSE | 3061 | NA | 1361.9496 | 1361.9496 | 1187.6959 | 23.8178 | 0 | 103.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1361.9496 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2022 ¦ 2024 | 1234.5747 | -27.3257 | 0 | 99.3483 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1442 | VACA-VACAVILLE-JMSN-N TWR 115KV NERC Ph2 |  |  | Benicia, Solano ¦ Fairfield, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | The project addresses the GO-95 clearance issues associated with the Vaca-Vacaville-Jameson North Tower 115kV line. The project’s key scope elements include: • Install 24 Top Cage Extensions • Replace 1 wood pole with a tubular steel pole • Replace conductor on both circuits for 18.4 miles • Install Federal Aviation Administration (FAA) Obstruction Lighting at one tower • Convert 3 tangent towers to dead-ends • Retension 7 spans • Install body modifications and cross arm extensions to 87 towers • Install 58 screw anchor foundations and one grade beam foundation | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-08 | 54 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 19.3 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 11 | NA | NA | 5775602 | T.0001546 | VAC-VACAVILLE-JAMESON-N TWR 115KVNERC | 2 | 93 | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5120-E | 2017-08-02 | Approved | 2017 | Operational | 2 | 2018-05-19 | 2018-12-13 | 2021-05-30 | Clearances | FALSE | 44000 | NA | 11373.5704 | 11373.5704 | 0.2936 | 1545.2304 | 1579.9719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11373.5704 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 0.21415 | 1126.9001 | 1152.2361 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1443 | VAC-VACAVILLE-JAMESON-N TWR 115KVNERC |  |  | Benicia, Solano ¦ Fairfield, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | The project addresses the GO-95 clearance issues associated with the Vaca-Vacaville-Jameson North Tower 115kV line. The project’s key scope elements include: • Install 24 Top Cage Extensions • Replace 1 wood pole with a tubular steel pole • Replace conductor on both circuits for 18.4 miles • Install Federal Aviation Administration (FAA) Obstruction Lighting at one tower • Convert 3 tangent towers to dead-ends • Retension 7 spans • Install body modifications and cross arm extensions to 87 towers • Install 58 screw anchor foundations and one grade beam foundation | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-08 | 74 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 17.5 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 11 | NA | NA | 5769960 | T.0001546 | VAC-VACAVILLE-JAMESON-N TWR 115KVNERC | 2 | 93 | 5754763 | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5120-E | 2017-08-02 | Approved | 2017 | Operational | 2 | 2018-01-03 | 2017-12-16 | 2020-06-21 | Clearances | FALSE | 44000 | NA | 17111.8752 | 17111.8752 | -23.9181 | 1258.7862 | -62.5707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17111.8752 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | -17.8005 | 936.8175 | -46.5665 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ NA [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1444 | Middle Fork #1 60kv |  |  | Placer | The project scope of work will mitigate 1 GO 95 clearance issues on the Middle Fork-Gold Hill 230kV circuit between structure number 008/118 and 008/114. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-10 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 0.4 | NA | 60 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 16 | NA | NA | 5782183 | T.0004288 | Middle Fork #1 60kv NERC | 1 | 93 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-09-13 | 2020-10-17 | 2021-10-17 | Project Design | FALSE | 4780 | NA | 3749.0776 | 3749.0776 | 68.487 | 339.8639 | 3167.4645 | -1.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3749.0776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 25.3267 | 52.7821 | 2971.5154 | -1.7242 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1445 | Cragview-Cascade 115kV Ph. 3 |  |  | Lakehead CDP, Shasta ¦ Mountain Gate CDP, Shasta ¦ Redding, Shasta ¦ Shasta | The project team will address CPUC GO-95 and PG&E standard requirements, in addition to increasing system performance and reducing fire ignition risk in Shasta County by performing the following work: • Replace 21.6 miles of existing conductor with 397 Aluminum Conductor Steel Reinforced (ACSR) conductor (Phase 1 = ~8.6 miles & Phase 2 = ~13 miles). • Replace 99 existing structures with new steel structures (Phase 1 = 37 structures & Phase 2 = 63). • Re-tension Optical Ground Wire (OPGW) In 2018 and 2019, PG&E’s Wildfire Safety Inspection Program (WSIP) identified 46 spans with transmission-line-to-fiber and six transmission-line-to-ground clearance discrepancies on the Crag View-Cascade 115kV Line. Engineering efforts commenced in June 2020 to develop the project scope to mitigate the identified discrepancies which resulted in 37 structure replacements. Between 30% and 60% engineering, the team identified overtension that exceeded CPUC GO-95 tension limits throughout the first 8.6 miles of the Crag View-Cascade 115kV Line. As a result of the identified overtension, it was deemed by the project team that the first 8.6 miles of conductor and 37 structures be replaced to address the identified overtension issues. If the overtension issues on the existing conductor is not corrected, more stress on the existing insulators and structures may occur, which potentially put the components at risk of failing. | Transmission Line - Multiple | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | 81 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $300 Mil - $350 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | TRUE | Heat Wave, Weather |  | 21.6 | NA | 115 | NA | Not Available | 5. Compliance/Commitments With Strong Safety Link | 53 | NA | NA | 5790354 | T.0005874 | CRAG VIEW-CASCADE 115KV NERC PROJECT | 2 | 93 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6547-E | 2022-03-31 | Approved | 2022 | Operational | 2 | 2022-06-21 | 2022-10-31 | 2023-02-23 | NA | TRUE | 50200 | NA | 17343.9684 | 17545.9684 | 0 | 298.3826 | 765.2524 | 13173.995 | 2974.2485 | 334.0899 | 0 | 0 | 0 | 0 | 0 | 17211.8785 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 14777.2746 | 108.3246 | 0% | NA | 2.3 ¦ Electric Operations Risk Management | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1446 | Cragview-Cascade 115kV Ph4 |  |  | Lakehead CDP, Shasta ¦ Mountain Gate CDP, Shasta ¦ Redding, Shasta ¦ Shasta | The project team will address CPUC GO-95 and PG&E standard requirements, in addition to increasing system performance and reducing fire ignition risk in Shasta County by performing the following work: • Replace 21.6 miles of existing conductor with 397 Aluminum Conductor Steel Reinforced (ACSR) conductor (Phase 1 = ~8.6 miles & Phase 2 = ~13 miles). • Replace 99 existing structures with new steel structures (Phase 1 = 37 structures & Phase 2 = 63). • Re-tension Optical Ground Wire (OPGW) In 2018 and 2019, PG&E’s Wildfire Safety Inspection Program (WSIP) identified 46 spans with transmission-line-to-fiber and six transmission-line-to-ground clearance discrepancies on the Crag View-Cascade 115kV Line. Engineering efforts commenced in June 2020 to develop the project scope to mitigate the identified discrepancies which resulted in 37 structure replacements. Between 30% and 60% engineering, the team identified overtension that exceeded CPUC GO-95 tension limits throughout the first 8.6 miles of the Crag View-Cascade 115kV Line. As a result of the identified overtension, it was deemed by the project team that the first 8.6 miles of conductor and 37 structures be replaced to address the identified overtension issues. If the overtension issues on the existing conductor is not corrected, more stress on the existing insulators and structures may occur, which potentially put the components at risk of failing. | Transmission Line - Multiple | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | 81 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $300 Mil - $350 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 21.6 | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5795434 | T.0005874 | CRAG VIEW-CASCADE 115KV NERC PROJECT | 2 | 93 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6547-E | 2022-03-31 | Approved | 2022 | Engineering more than 50% complete | 4 | 2025-07-21 | 2023-10-31 | 2026-01-31 | Prioritization | TRUE | 50200 | NA | 1127.6157 | 27147.5906 | 0 | 0 | 289.9528 | 747.8073 | 9.8205 | 1013.3202 | 5329.8936 | 20469.2972 | 0 | 0 | 0 | 1047.5807 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1447 | Vasco-Herdlyn Clearance Mitigation |  |  | Alameda ¦ Contra Costa ¦ Livermore, Alameda | The project will address California Public Utilities Commission (CPUC) General Order 95 (GO-95) and Pacific Gas and Electric Company (PG&E) standard requirements, in addition increase system performance in Alameda and Contra Costa counties by performing the following work: • Replace sixty-one (61) wood structures on the Vasco-Herdlyn 60 kV Line; • Reframe one (1) wood structure • Install 19 bypass loops to mitigate magenetic heating effects • Reframe distribution underbuild at 25 locations with inadequate ground clearance • Install conductor temperature monitoring device • Replacement of old insulators, hardware, and equipment on the structure; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Multiple | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Heat Wave |  | 10.97 | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5798811 | T.0007628 | Vasco-Herdlyn NERC Mitigation | 2 | 93 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6756-E | 2022-11-09 | Approved | 2023 | Construction (50%-75%) | 3 | 2023-09-11 | 2023-07-31 | 2024-07-31 | Project Design | TRUE | 13832 | NA | 5321.0577 | 7916.7002 | 0 | 0 | 75.9357 | 941.4075 | 4113.9778 | 2785.3793 | 0 | 0 | 0 | 0 | 0 | 5131.3209 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1448 | Hetch Hetchy Wtr & Pwr Discrepancies |  |  | Fremont, Alameda | The project will address clearance issues that the Newark-Nummi 115 kV Line and the Newark-Livermore 60 kV Line have with the Moccasin Creek-Newark Nos. 3 and 4 115 kV Lines, which are operated by the Hetch Hetchy Water and Power Transmission System. The project scope of work includes following: • Install 10-foot top cage extensions on Towers 000/004 and 000/005 to increase the clearance separation between the lines; and • Replace the old copper conductor, insulators and other hardware on both PG&E lines between Towers 000/003 to 000/005. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2021-11-15 | 102 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 115 ¦ 60 | NA | Not Available | Not Available | Not Available | NA | NA | 5544747 | T.0007119 | Hetch Hetchy Wtr & Pwr Discrepancies | 1 | 93 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-08-28 | 2022-08-12 | 2023-09-28 | Prioritization | TRUE | 962 | NA | 1305.0968 | 1305.0968 | 0 | 0 | 124.928 | 538.2758 | 637.074 | 4.819 | 0 | 0 | 0 | 0 | 0 | 1300.2778 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 110.8736 | 529.4618 | 598.0727 | 4.5897 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1449 | SycamoreCreek-NotreDame-TableMtn Ph 2 |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Chico, Butte | The project will replace 19 old wood poles with 11 new LDSPs and 8 new wood poles; reframe 7 wood poles. This project will mitigate 14 NERC discrepancies. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2022-09-06 | 20 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 20.3 | NA | 115 | NA | 228 | Not Available | NA | NA | NA | 5527180 | T.0003333 | SycamoreCreek-NotreDame-TableMtn Ph 2 | 1 | 93 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-03-18 | 2019-01-30 | 2019-04-08 | NA | FALSE | 2424 | NA | 2006.1199 | 2006.1199 | 1152.689 | -3.6357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2006.1199 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 1066.7497 | -3.3647 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1450 | TABLE MOUNTAIN-BUTTE #1 NERC PROJECT |  |  | Butte ¦ Chico, Butte ¦ Durham CDP, Butte | The project will replace 61 wood poles with 59 LDSPs and 2 new wood poles, complete 6 reframes and install 1 LSP extension to address ground clearance issues on the Table Mtn-Butte #1 115kV Transmission Lines to allow operation at full capacity. In addition, the remaining idle section of the guest circuit Chico A – Dayton 60kV will be removed from the Table Mtn – Butte #1 structures (14 spans). | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2023-11-20 | 25 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 5 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 419 | NA | NA | 5760926 | T.0000125 | Table Mountain-Butte #1 | 2 | 93 | 5520749 | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-05-14 | 2017-05-31 | 2020-11-19 | Workforce | FALSE | 2556 | NA | 3176.4837 | 3176.4837 | 254.5793 | 683.4071 | -99.1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3176.4837 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 235.2133 | 631.4202 | -91.6018 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1451 | SILVERADO-FULTON JCT NERC PROJECT |  |  | Napa ¦ Saint Helena, Napa ¦ Yolo | The Silverado – Fulton Junction 115kV NERC project will be completed by reconductoring 24 spans (4.9 miles double circuit) and replacing impacted insulators (24 structures); installing 1 Interset (LSP); replacing 1 Lattice Steel Tower; converting 3 towers to dead-ends; installing 1 top cage extension; and restoring 14 foundations. Once completed, the Silverado – Fulton Junction 115kV circuit will comply with GO 95 ground clearance and conductor tension requirements. The North American Electric Reliability Corporation (NERC) will be notified that all discrepancies have been addressed which is a requirement of the NERC Alert – Electric Transmission Project. Operating restrictions will be eliminated which supports the NERC and Western Electricity Coordinating Council (WECC) reliability requirements. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-02-27 | 103 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 9.8 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5769966 | T.0001552 | SILVERADO-FULTON JCT NERC PROJECT | 1 | 93 | 5510301 | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5280-E | 2018-04-26 | Approved | 2018 | Operational | 2 | 2019-08-05 | 2018-05-31 | 2019-12-17 | Permitting | FALSE | 9240 | NA | 10662.3275 | 10662.3275 | 9031.9167 | 243.1674 | -33.7655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10662.3275 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 10168.5345 | 237.644 | -32.8233 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1452 | Smyrna-Semitrop-Midway 115kV NERC Alert |  |  | Buttonwillow CDP, Kern ¦ Kern | The Smyrna-Semitropic-Midway 115kV NERC project will rebuild the line to meet NERC compliance. The major project scope items are as follows:•Replace 155 lattice steel pole (LSP) structures with a new-design LSP structure.•Replace 6 lattice steel towers with Tubular Steel Poles (TSPs); 5 of the 6 TSPs will be installed with SCADA operated switches – 3 at the Semitropic junction and 2 at the Ganso Substation. The 6th TSP is a replacement for an existing lattice steel tower.•Replace existing 266 kcmil AAC single circuit all-aluminum conductors on the 22.3-mile transmission line with 1,113 AAC conductor on the west side of the circuit. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2021-11-23 | 17 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 22.3 | NA | 115 | NA | 228 | Not Available | NA | NA | NA | 5744339 | T.0000448 | SMYRNA-SEMITROP-MIDWAY 115KV NERC | 1 | 93 | NA | 2013 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5299-E | 2018-05-21 | Approved | 2018 | Operational | 2 | 2018-10-22 | 2018-02-14 | 2019-03-31 | Project Design | FALSE | 22888 | NA | 27776.664 | 27776.664 | 16821.8322 | 129.3967 | 64.4631 | 4.1865 | -6.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 27776.664 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 22678.4822 | 107.6538 | 52.7282 | 3.4245 | -4.9646 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1453 | TES Tap 230kV (Steel) NERC |  |  | Danville, Contra Costa ¦ San Ramon, Contra Costa | The TES Tap 230kV NERC Project will replace 3 TSPs with 3 new TSPs and 1 span re-tension to address existing ground clearance issues. Once completed, the TES Tap 230kV circuit will be in compliance with G.O. 95 ground clearance requirements under emergency operating conditions. The North American Electric Reliability Corporation (NERC) will be notified that all discrepancies have been addressed which is a requirement of the NERC Alert – Electric Transmission Project. Operating restrictions will be eliminated which supports the NERC and Western Electricity in Coordinating Council (WECC) reliability requirements. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2021-11-04 | 100 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | 3.3 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 932 | NA | NA | 5525496 | T.0002775 | TES Tap 230kV (Steel) NERC | 1 | 93 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-12 | 2018-03-19 | 2020-12-04 | Prioritization | FALSE | 1664 | NA | 1234.2943 | 1234.2943 | 172.0631 | 213.1926 | 130.7098 | 4.3388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2943 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 149.4684 | 185.197 | 113.5456 | 3.769 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1454 | Humboldt - Trinity 115kV NERC |  |  | Humboldt ¦ Junction City CDP, Trinity ¦ Trinity ¦ Weaverville CDP, Trinity | The total project proposes to addresses the GO-95 clearance issues associated with the Humboldt-Trinity 115kV line. There are a total of 175 structures and locations that are included in this scope as a few areas in the circuit require construction at two structures to mitigate a single discrepancy. | Transmission Line - Multiple | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | 71 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 12 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 48 | NA | NA | 5776099 | T.0000126 | HUMBOLDT-TRINITY NERC PROJECT | 2 | 93 | NA | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-01 | 2018-12-31 | 2020-11-20 | Workforce | FALSE | 44600 | NA | 12378.6482 | 12378.6482 | 4627.2732 | 1843.4774 | 74.7291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12378.6482 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 4317.6443 | 1720.1231 | 69.7287 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1455 | HUMBOLDT-TRINITY NERC PROJECT |  |  | Humboldt ¦ Junction City CDP, Trinity ¦ Trinity ¦ Weaverville CDP, Trinity | The total project proposes to addresses the GO-95 clearance issues associated with the Humboldt-Trinity 115kV line. There are a total of 175 structures and locations that are included in this scope as a few areas in the circuit require construction at two structures to mitigate a single discrepancy. | Transmission Line - Multiple | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | 71 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 13 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 48 | NA | NA | 5760883 | T.0000126 | HUMBOLDT-TRINITY NERC PROJECT | 2 | 93 | 5767321 | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-01 | 2017-09-30 | 2020-11-20 | Workforce | FALSE | 44600 | NA | 18563.0177 | 18563.0177 | 3217.9712 | 589.7582 | 14.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18563.0177 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 3022.7016 | 553.9711 | 14.038 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $30 Mil - $40 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1456 | EAGLE ROCK-FULTON-SILVERADO NERC PROJECT |  |  | Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma | The work on Eagle Rock-Fulton-Silverado 115kV NERC project will be completed by replacing all conductor on this circuit for total of 8.3 continuous miles, installing (3) Top Cage Extensions, modifying (32) towers, converting (1) towers to a Dead-End and re-tensioning (1) span and reinforcing (15) foundations. Once completed, the Eagle Rock-Fulton-Silverado 115kV circuit will be in compliance with G.O. 95 ground clearance requirements under emergency operating conditions. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-04 | 93 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 8.3 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5769963 | T.0001549 | EAGLE ROCK-FULTON-SILVERADO NERC PROJECT | 1 | 93 | 5510301 | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5115-E | 2017-07-24 | Approved | 2017 | Operational | 2 | 2019-05-01 | 2017-11-22 | 2019-06-29 | Weather | FALSE | 688 | NA | 10951.1562 | 10951.1562 | 3605.1316 | 85.3681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10951.1562 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 9267.0076 | 74.0663 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1457 | COLGATE-RIO OSO 230KV NERC PROJECT |  |  | Loma Rica CDP, Yuba ¦ Sutter ¦ Yuba | This project involves installing 1 - Dead End Conversion; 2 - TCE; 15 - Damper Replacements; 4 - Replace Insulators on the Colgate-Rio Oso 230kV circuit to eliminate blow-out issues related to right-of-way and operate the line at full capacity. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2023-11-16 | 66 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 6 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 42 | NA | NA | 5767083 | T.0000117 | COLGATE-RIO OSO 230KV NERC PROJECT | 1 | 93 | 5510301 | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-01 | 2017-05-30 | 2020-01-18 | Weather | FALSE | 850 | NA | 1204.4877 | 1204.4877 | 465.6294 | 12.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1204.4877 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 400.4384 | 10.4907 | 9e-05 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1458 | FULTON-LAKEVILLE 230KV (P3) NERC |  |  | Fulton CDP, Sonoma ¦ Larkfield-Wikiup CDP, Sonoma ¦ Santa Rosa, Sonoma ¦ Sonoma | This project involves installing 1 Top Cage Extensions on the Fulton-Lakeville 230kV circuit. This will eliminate clearance issues and operate the line at full capacity. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-11 | 119 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 0.1 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 109 | NA | NA | 5769967 | T.0001553 | FULTON-LAKEVILLE 230KV (P3) NERC | 1 | 93 | 5510301 | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-11-19 | 2017-11-22 | 2020-04-01 | Permitting | FALSE | 553 | NA | 1776.1662 | 1776.1662 | 650.8579 | 905.3344 | 0.9014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1776.1662 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 630.5657 | 877.1084 | 47.7011 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1459 | PALERMO-COLGATE+ 230KV NERC PROJECT |  |  | Butte ¦ Loma Rica CDP, Yuba ¦ Palermo CDP, Butte ¦ Yuba | This project involves installing one Top Cage Extension, one Tubular Steel Pole, and 21 Dampers on the PALERMO-COLGATE 230KV circuit. This will eliminate clearance issues and operate the line at full capacity. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-26 | 66 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 0.4 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 97 | NA | NA | 5767084 | T.0000118 | PALERMO-COLGATE+ 230KV NERC PROJECT | 1 | 93 | 5510301 | 2015 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-01 | 2017-01-19 | 2020-03-03 | Workforce | FALSE | 886 | NA | 1610.3436 | 1610.3436 | 383.0843 | 179.0235 | -0.0177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1610.3436 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 344.7765 | 161.1214 | -0.0159 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1460 | Smyrna-Semitropic-Midway 115kV Maintenan |  |  | Buttonwillow CDP, Kern ¦ Kern | This project proposes to address the 25 leaning poles by replacing each with a new-design lattice steel pole. These towers were installed in 1928 and are direct embedded towers (no foundations). The towers when replaced will be raised to also address conductor ground clearance issues on both sides of the tower in support of the ongoing NERC Mitigation Program. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2021-11-23 | 17 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 3.5 | NA | 115 | NA | 228 | Not Available | NA | NA | NA | 5774045 | T.0002721 | Smyrna-Semitropic-Midway 115kV Maintenan | 1 | 93 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5299-E | 2018-05-21 | Approved | 2018 | Operational | 2 | 2018-10-22 | 2019-02-07 | 2019-03-31 | NA | FALSE | 3411 | NA | 3593.1602 | 3593.1602 | 1357.4761 | 0.4503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3593.1602 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 3069.5181 | 0.4808 | 2e-05 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1461 | Olive Sw Sta-Smyrna 115kV Maintenance Re |  |  | Kern ¦ Tulare | This project proposes to address the 9 leaning poles by replacing each with a new-design lattice steel pole. Transmission Line Maintenance identified 9 leaning lattice steel poles on the Olive Sw Sta-Smyrna 115kV circuit. The towers when replaced will be raised to also address conductor ground clearance issues on both sides of the tower in support of the ongoing NERC Mitigation Program. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2021-11-03 | 61 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 1.5 | NA | 115 | NA | 228 | Not Available | NA | NA | NA | 5774044 | T.0002720 | Olive Sw Sta-Smyrna 115kV Maintenance Re | 1 | 93 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-01-01 | 2018-01-28 | 2019-03-12 | Permitting | FALSE | 1342 | NA | 1368.7005 | 1368.7005 | 18.7332 | 0.3416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1368.7005 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1220.2054 | 0.34163 | 9e-05 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1462 | MORRO BAY-GATES 230KV NERC PH2 |  |  | Atascadero, San Luis Obispo ¦ El Paso de Robles, San Luis Obispo ¦ Monterey ¦ Morro Bay, San Luis Obispo ¦ San Luis Obispo | This project proposes to address the CPUC G.O. 95 clearance issues by installing 2 top cage extensions, leg extensions on 1 tower, 1 interset tubular steel pole and 2 section (4 continuous spans) re-tensions on the Morro Bay – Gates 230kV Pedestrian Access circuit. This mitigation work will eliminate clearance and over-tension issues and allow operation of the line at full capacity with work. | Transmission Line - Multiple | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-05 | 69 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 46 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 124 | NA | NA | 5523094 | T.0002059 | Morro Bay-Gates 230kV Pedestrian Acc | 1 | 93 | 5513299 | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-06 | 2019-05-03 | 2020-05-20 | Project Design | FALSE | 2010 | NA | 1628.8238 | 1628.8238 | 82.9142 | 1086.438 | 2.4784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1628.8238 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 80.7785 | 1058.4542 | 2.4146 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1463 | Brighton-Grand Islan PH 5 - River Towers |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-14 | 25 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 4 | No | 5797638 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | NA | 2013 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2024-08-16 | 2024-07-30 | 2024-11-30 | NA | TRUE | 150900 | NA | 731.6998 | 4543.2522 | 0 | 0 | 12.4586 | 193.6601 | 169.4152 | 4163.6033 | 4.115 | 0 | 0 | 0 | 0 | 375.5339 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1464 | Brighton-Grand Island: PH1 I-5 W Twr |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-14 | 24 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 228 | Not Available | Not Available | NA | NA | 5794778 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | 5750422 | 2013 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-08-24 | 2021-10-31 | 2021-12-07 | NA | FALSE | 150900 | NA | 2581.5579 | 2581.5579 | 0 | 4.267 | 2526.9939 | 50.2969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2581.5579 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 2261.3243 | 44.1972 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1465 | Brighton-Grand Island: PH2 I-5 W Piling |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-14 | 25 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 228 | Not Available | Not Available | Tier 3 | No | 5794779 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | 5750422 | 2013 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6463-E | 2022-01-18 | Approved | 2022 | On Hold | 3 | 2022-05-10 | 2022-12-31 | 2025-09-30 | Prioritization | TRUE | 150900 | NA | 27324.9299 | 34807.7089 | 0 | 0 | 947.7301 | 17799.6456 | 8625.6253 | -54.6665 | 7489.3744 | 0 | 0 | 0 | 0 | 27373.0009 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1466 | Brighton-Grand Island: PH3 I-5 E Develop |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-14 | 97 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 228 | Not Available | Not Available | Tier 3 | No | 5794780 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | 5750422 | 2013 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | On Hold | 4 | 2026-09-01 | 2024-12-31 | 2027-11-30 | Prioritization | FALSE | 150900 | NA | 789.4643 | 56082.5438 | 0 | 0 | 242.5574 | 589.6488 | -42.7419 | -0.85 | 0 | 1093.066 | 1933.5004 | 24102.2074 | 31161.9657 | 789.4643 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1467 | Brighton-Grand Island: PH4 I-5 W Last Sec |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Transmission Line - Multiple | Replace | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-14 | 25 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 26 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 388 | Tier 4 | No | 5750422 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | NA | 2013 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | On Hold | 4 | 2026-08-16 | 2025-11-30 | 2026-11-30 | Prioritization | FALSE | 150900 | NA | 2773.4561 | 21427.8764 | 126.0512 | 32.8292 | 272.2067 | 472.3685 | 739.6845 | -0.1964 | 0 | 1758.6768 | 17582.6155 | 0 | 0 | 2773.4561 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1468 | METCALF-SALINAS #2 NERC PROJECT |  |  | Gilroy, Santa Clara ¦ San Benito ¦ Santa Clara | This project scope includes the following: 14 tower replacements, 41 span re-tensions (6 sections) circuit to address the 23 ground clearance issues on the Metcalf – Salinas #2 115kV line | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-09 | 91 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 4 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 1459 | NA | NA | 5771275 | T.0002054 | Metcalf-Salinas No. 2 (Idle) (P3) | 1 | 93 | 5760897 | 2015 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-08-01 | 2018-01-31 | 2020-11-07 | Permitting | FALSE | 3162 | NA | 5719.073 | 5719.073 | 365.9597 | 1746.6958 | 13.9008 | 4.4471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5719.073 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 4858.2655 | 11.5553 | 15.4222 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1469 | Llagas-Hollister 115kV |  |  | Gilroy, Santa Clara ¦ San Benito ¦ Santa Clara | This project scope includes the following: 4 tower replacements, 1 span re-tension (9 sections) circuit to address the ground clearance issues on the Llagas - Hollister 115kV line to address 3 identified ground clearance. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-09 | 20 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 408 | NA | NA | 5769221 | T.0001417 | Llagas-Hollister 115kV | 1 | 93 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-10-17 | 2018-12-31 | 2020-11-07 | Permitting | FALSE | 1578 | NA | 2263.841 | 2263.841 | 90.0865 | 1180.6737 | -18.6099 | 3.5109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2263.841 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 75.3201 | 987.1457 | -15.5594 | 2.9354 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1470 | Llagas-Hollister 115kV (Wood) |  |  | Gilroy, Santa Clara ¦ San Benito ¦ Santa Clara | This project scope includes the following: Replace 19 wood poles with Light Duty Steel Poles, replace 1 wood pole with 1 wood pole, re-frame 13 wood pole locations on the Llagas-Hollister circuit and remove 2 wood poles to address the ground clearance issues on the Llagas-Hollister Transmission Line to allow operation. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-04-09 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 21.6 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 408 | NA | NA | 5778239 | T.0003249 | LLAGAS-HOLLISTER 115kV (Wood) | 1 | 93 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-09-21 | 2019-08-31 | 2020-10-17 | Project Design | FALSE | 3200 | NA | 1451.3294 | 1451.3294 | 93.0481 | 1155.4132 | 6.3178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1451.3294 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 1239.877 | 31.9843 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1471 | Cresta-Rio Oso 230kV Ph. 2 |  |  | Butte ¦ Oroville East CDP, Butte ¦ Oroville, Butte ¦ Palermo CDP, Butte ¦ South Oroville CDP, Butte ¦ Sutter ¦ Yuba | This project scope involves 3 - Delta Cage Top Extensions, replacing 1 – Lattice Steel Tower (LST) with a 3-pole Tubular Steel Pole (TSP) structure with micro-pile foundations, and 4 – re-tension spans and associated hardware replacements. This mitigation work will eliminate clearance issues and allow operation of the line at full capacity with work | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2023-06-21 | 19 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 2 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5528379 | T.0003683 | Cresta-Rio Oso 230kV Ph. 2 NERC | 1 | 93 | NA | 2017 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-16 | 2019-09-30 | 2019-12-10 | NA | FALSE | 2534 | NA | 2469.2445 | 2469.2445 | 2229.526 | 115.5029 | 2.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2469.2445 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1948.9929 | 287.28 | 1.968 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1472 | Vaca-Tulucay-Lakeville 230kV |  |  | Green Valley CDP, Napa ¦ Green Valley CDP, Solano ¦ Hartley CDP, Solano ¦ Napa ¦ Solano ¦ Vacaville, Solano | This project will address 27 spans with CPUC G.O. 95 clearance issues by replacing 21 Top Cage Extension with 2 Dead-end Structures and 1 Re-Sag. This mitigation work will eliminate clearance issues and allow operation of the line at full capacity. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2024-03-20 | 64 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 8 | NA | 230 | NA | 228 | Not Available | NA | NA | NA | 5773073 | T.0002425 | Vaca-Tulucay-Lakeville 230kV | 1 | 93 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-06 | 2018-05-07 | 2019-10-15 | Bundling Dependencies | FALSE | 5264 | NA | 7098.0864 | 7098.0864 | 5373.9614 | 19.3706 | 328.0234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7098.0864 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 6412.0237 | 19.293 | 311.1021 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1473 | BIRDS LANDING SS CONTRA COSTA PP 230KV |  |  | Antioch, Contra Costa ¦ Contra Costa ¦ Sacramento ¦ Solano | This project will address the clearance issues associated with the Birds Landing SS-Contra Costa PP SS 230kV transmission line by increasing the height of the transmission crossing, to 161 ft. above MHW, over the Sacramento River. The project team will replace and increase the height of four towers / foundations, replace ~1.5 miles of double-circuit conductor, and perform tower modifications on two adjacent towers. | Transmission Line - Multiple | Replace | T.0008048 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2020-08-10 | 19 | Lifecycle Replacement Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 1.5 | NA | 230 | NA | 228 | Not Available | Not Available | Tier 5 | No | 5791742 | T.0002081 | Birds Landing SS-Contra Costa PP 230kV | 1 | 93 | NA | 2017 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6131-E | 2021-03-26 | Approved | 2021 | Construction (50%-75%) | 3 | 2021-09-17 | 2022-12-31 | 2025-06-10 | Material | TRUE | 5700 | NA | 32490.776 | 67157.4898 | 381.3532 | 1235.9056 | 8741.535 | 13150.2336 | 7378.5052 | 25420.0704 | 10068.4551 | 0 | 0 | 0 | 0 | 31668.9643 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 352.8951 | -1076.0134 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1474 | MONTA VISTA-JEFFERSON #2 230KV NERC |  |  | Cupertino, Santa Clara ¦ Palo Alto, Santa Clara ¦ San Mateo ¦ Santa Clara ¦ Woodside, San Mateo | This project will install 1 top cage extension and replace hardware on 1 tower hardware to address GO95 clearance issues and operate the line at full capacity | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2023-09-29 | 61 | Lifecycle Replacement Analysis | Other - Deferral | $0 Mil – $1 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 0.05 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 181 | NA | NA | 5520750 | T.0000402 | MONTA VISTA-JEFFERSON #2 230KV NERC | 1 | 93 | 5510301 | NA | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-02-26 | 2017-04-01 | 2021-03-04 | Prioritization | FALSE | 534 | NA | 1096.1916 | 1096.1916 | 55.4739 | 226.2842 | 458.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1096.1916 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 51.3888 | 209.621 | 420.8152 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1475 | Pittsburg 60kV Tap Project |  |  | Pittsburg, Contra Costa | This project will proactively replace 16 structures and replace all conductor on the Pittsburg 60kV Tap Line to address a deteriorating structure (000/001), mitigate induction risk due to an adjacent gas distribution line, remove idle distribution conductor, replace over-tensioned transmission conductor and mitigate 7 GO95 clearance infractions. To support PG&E top-level initiatives to manage asset risk for the benefit of public and employee safety, service reliability, operational flexibility, and cost reduction, the proposed Pittsburg 60kV Tap Line Project will proactively replace all structures and conductor on this line. | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2020-08-29 | 51 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1.19 | NA | 60 | NA | Not Available | Not Available | Not Available | NA | NA | 5797938 | T.0007454 | Pittsburg 60kV Tap Project | 1 | 93 | 5544346 | 2021 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6446-E | 2021-12-28 | Approved | 2022 | Operational | 2 | 2022-03-29 | 2022-03-31 | 2022-05-18 | NA | FALSE | 4500 | NA | 2690.5496 | 2690.5496 | 0 | 0 | 0 | 2669.2593 | 21.2903 | 0 | 0 | 0 | 0 | 0 | 0 | 2690.5496 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 2024.4256 | 16.1299 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1476 | Corcoran-Smyrna 115kV NERC Alert |  |  | Corcoran, Kings ¦ Kings ¦ Tulare | Update the Corcoran-Smyrna 115kV NERC transmission line to comply with California Public Utilities Commission (CPUC) General Order 95 (GO-95) requirements by replacing 224 existing lattice steel pole structures, installing two Supervisory Control and Data Acquisition (SCADA)-operated switches, and replacing existing single circuit all-aluminum conductors on the 29.4-mile transmission line | Transmission Line - Multiple | Replace | TBD | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | 2023-09-22 | 91 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 29.4 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 529 | NA | NA | 5744341 | T.0000418 | CORCORAN SMYRNA 115KV NERC | 1 | 93 | NA | 2013 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5681-E | 2019-11-05 | Approved | 2019 | Operational | 2 | 2021-08-25 | 2020-03-31 | 2022-02-15 | Clearances | FALSE | 41592 | NA | 40240.4732 | 40240.4732 | 6284.959 | 3862.8687 | 25525.7285 | 3568.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40240.4732 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 31806.1913 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1477 | CALISTOGA-ST. HELENA 60 KV REINFORCEMENT |  |  | Deer Park CDP, Napa ¦ Fulton CDP, Sonoma ¦ Kenwood CDP, Sonoma ¦ Lake ¦ Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma | An emergency project was recently completed that replaced all of the structures, conductors and associated hardware on the 16.6-mile section of the line from Fulton to St. Helena Junction. This new project will further increase system performance and reduce fire ignition risk in Sonoma and Napa Counties by reconductoring the Fulton-Calistoga 60 kV line from St. Helena Junction up to Middletown Substation and from St. Helena Junction down to Dunbar Substation. | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-09 | 94 | Lifecycle Replacement Analysis | Wires - Reconductor/Line Rebuild Alternative | $150 Mil - $175 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | TRUE | Weather |  | 13 | NA | 60 | NA | 20074 | 1. Work that prevents fire ignition | 70 | NA | NA | 5790867 | T.0005946 | Fulton-Calistoga 60 kV Line | 2 | 93 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6429-E | 2021-12-08 | Approved | 2022 | Operational | 2 | 2022-02-01 | 2023-03-30 | 2023-04-17 | NA | TRUE | 71400 | NA | 16369.5803 | 16369.5803 | 0 | 10.2758 | 723.0128 | 12815.4744 | 2807.2662 | 13.5511 | 0 | 0 | 0 | 0 | 0 | 16356.0292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 15510.8186 | 21.3834 | 0% | NA | 2.3 ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1478 | FULTON-CALISTOGA 60 KV REINFORCEMENT |  |  | Deer Park CDP, Napa ¦ Fulton CDP, Sonoma ¦ Kenwood CDP, Sonoma ¦ Lake ¦ Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma | An emergency project was recently completed that replaced all of the structures, conductors and associated hardware on the 16.6-mile section of the line from Fulton to St. Helena Junction. This new project will further increase system performance and reduce fire ignition risk in Sonoma and Napa Counties by reconductoring the Fulton-Calistoga 60 kV line from St. Helena Junction up to Middletown Substation and from St. Helena Junction down to Dunbar Substation. | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-09 | 94 | Lifecycle Replacement Analysis | Wires - Reconductor/Line Rebuild Alternative | $150 Mil - $175 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | 11.3 | NA | 60 | NA | Not Available | 1. Work that prevents fire ignition | 70 | RBPPF - TBD | Yes | 5790901 | T.0005946 | Fulton-Calistoga 60 kV Line | 2 | 93 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6429-E | 2021-12-08 | Approved | 2022 | Engineering less than 50% complete | 5 | 2027-12-30 | 2025-04-30 | 2028-08-08 | Prioritization | FALSE | 71400 | NA | 623.4895 | 24538.9105 | 0 | 0 | 1.1961 | 333.8871 | 281.1146 | 45.2398 | 0 | 0 | 0 | 0 | 0 | 616.1978 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1479 | FAA Non-SCADA Beacon Replacements 2020 |  |  | NA | Bucket for FAA Non-SCADA Beacon Replacements 2020 | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | 2. Overhead With Strong Safety Link | 880 | NA | NA | 5538267 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1150.4173 | 1150.4173 | 0 | 249.9601 | 822.6756 | 77.7817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150.4173 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 249.9601 | 822.6756 | -96.6964 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1480 | FAA Capital Maintenance Program |  |  | NA | Bucket for maintenance of Tower Lighting in accordance with FAA | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 566 | 2. Overhead With Strong Safety Link | 144 | Tier 4 | No | 5529049 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 4885.5118 | 5656.2318 | 452.5176 | 274.3957 | 984.1456 | 951.5847 | 1203.4638 | 1133.8796 | 0 | 1200 | 1200 | 1200 | 1200 | 4522.3522 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 452.5175 | 274.3957 | 984.1456 | 1079.9897 | 1434.0732 | 498.5527 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1481 | Marker Balls |  |  | NA | Bucket for replacement or installation of marker balls on conductors. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 380 | 2. Overhead With Strong Safety Link | Not Available | Tier 4 | No | 5529739 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 1903.3075 | 2361.6408 | 56.5261 | 274.0537 | 538.5384 | 851.4558 | 84.4128 | 236.2922 | 250 | 540 | 540 | 540 | 540 | 1875.3486 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 56.5261 | 172.3757 | 555.5012 | 778.1401 | -30.5463 | -29.4036 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1482 | COTTNWD-RED BLUFF INSTALL TSP'S |  |  | Cottonwood CDP, Shasta ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama | Rebuild the 16.5 miles-long Cottonwood-Red Bluff 60 kV Line and release the project to operations, The proposed project would rebuild the 16.5 mile Cottonwood-Red Bluff 60 kV line with new transmission poles and new conductor. The project scope of work includes the following:•Replace 304 transmission poles with 240 light duty steel poles (LDSPs), 7 tubular steel poles (TSPs), and 57 higher-class wood poles as identified by design.•Reconductor the Cottonwood-Red Bluff 60 kV line (16.5 miles) with 715 kcmil aluminum conductor.•Reroute a 3-pole section of the line to a new location and alignment. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-09 | 81 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 197 | 1. Work that prevents fire ignition | 207 | NA | NA | 5767629 | T.0000456 | Cottonwood-Red Bluff Reconductor | 5 | 93 | 5732727 | 2008 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-11-01 | 2019-10-07 | 2020-05-18 | Permitting | FALSE | 47000 | NA | 3933.4744 | 3933.4744 | 3021.588 | 94.6131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3933.4744 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 3933.9724 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1483 | Coleman Jct -Vina -Gerber 60 kV Str |  |  | Gerber CDP, Tehama ¦ Los Molinos CDP, Tehama ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama ¦ Tehama, Tehama | The Coleman Junction -Vina - Gerber 60 kV Line section is part of the Coleman - Red Bluff 60 kV Line located in Tehama County. The Coleman - Red Bluff 60 kV Line is approximately 48.1 miles long and is supported by 834 structures; 312 of these structures are in High Fire Threat Districts (HFTDs). There is an ongoing project to replace structures and conductor on the Coleman - Red Bluff 60 kV Line, between Coleman Power House and Red Bluff Substation. This new project will complete work on the remaining portions of the line between Coleman Junction, Vina and Gerber substations. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2023-12-20 | 91 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 10.6 | NA | 60 | NA | 20074 | 1. Work that prevents fire ignition | 65 | RBPPF - TBD | Yes | 5790859 | T.0005935 | Coleman Jct -Vina -Gerber 60 kV Str | 1 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-10-13 | NA | 2029-04-27 | NA | FALSE | NA | NA | 3.4866 | 44766.4649 | 0 | 0 | 0 | 2.9055 | 0.5403 | 0.2526 | 0 | 0 | 0 | 0 | 0 | 3.4458 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1484 | Ignacio-Alto 60kV Reinf Proj repl struc |  |  | Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin | The assessment by Transmission Line Asset Strategy (TLAS) on Ignacio-Alto 60 kV Line was done on this line only. The associated Ignacio-San Rafael No. 1 115 kV Line that is supported by the DCTL was excluded from this assessment. The project will increase system performance and reduce fire ignition risk in Marin County by performing the following work: ● Replace nine (9) steel structures ● Replace 114 non-steel structures ● Replace 105 insulators ● Replace 5.7 miles of 397.5 all-aluminum conductor (AAC) and review the conductor on the other 12.1 miles of conductor for possible replacement ● Replace insulators and hardware on 16 steel towers ● Perform structure modification in four (4) lattice steel poles, 14 steel towers and two (2) tubular steel poles to accommodate new conductor replacement. ● Identify any distribution under-build and coordinate with distribution planning ● Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring | Transmission Line - Multiple | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-02-28 | 62 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | 5.7 | NA | 60 | NA | Not Available | 1. Work that prevents fire ignition | 7 | RBPPF - TBD | Yes | 5790910 | T.0005966 | Ignacio-Alto 60kV Reinf | 1 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-03-27 | NA | 2031-05-21 | NA | FALSE | NA | NA | 6.9672 | 7523.6622 | 0 | 0 | 0 | 6.4078 | 0.4778 | 0.5034 | 0 | 0 | 0 | 0 | 0 | 6.8857 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1485 | Centerville-Table Mtn-Oroville-SCADA Sw |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Butte Valley CDP, Butte ¦ Oroville, Butte ¦ Paradise, Butte ¦ Thermalito CDP, Butte | The Centerville – Table Mountain – Oroville 60 kV Line is located in Butte County. The Centerville – Table Mountain – Oroville 60 kV Line is approximately 25.6 miles long and is supported by 481 structures. The Centerville – Table Mountain – Oroville 60 kV Line is configured as a single conductor line and is supported by 481 structures, of which 169 structures are in high fire threat districts (HFTDs). The project will increase system performance and reduce fire ignition risk in Butte County by performing the following work: • Replace 122 existing structures with Light Duty Steel (LDS) Poles on the Centerville – Table Mountain – Oroville 60 kV Line; • Perform field analysis on the entire 25.6 mile long Centerville – Table Mountain – Oroville 60 kV Line to verify if conductor replacement is needed; • Replace Switch Nos. 27 and 67 with a Supervisory Control and Data Acquisition (SCADA)-operable switch on the Centerville – Table Mountain – Oroville 60 kV Line; • Replace existing ceramic insulators on 96 structures with modern equivalent insulators on the Centerville – Table Mountain – Oroville 60 kV Line; • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Switch | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-04 | 94 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 3612 | 2. Overhead With Strong Safety Link | 76 | RBPPF - TBD | Yes | 5790821 | T.0005931 | Centerville-Table Mtn-Oroville | 1 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2030-08-09 | NA | 2030-09-06 | NA | FALSE | NA | NA | 501.9754 | 3123.6159 | 0 | 49.8929 | 147.1545 | 71.8016 | 227.2559 | 36.4228 | 0 | 0 | 0 | 0 | 0 | 496.1048 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1486 | PH 2_CENTERVILLE-TABLEMTN-OROVILLE-60KV |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Butte Valley CDP, Butte ¦ Oroville, Butte ¦ Paradise, Butte ¦ Thermalito CDP, Butte | The Centerville – Table Mountain – Oroville 60 kV Line is located in Butte County. The Centerville – Table Mountain – Oroville 60 kV Line is approximately 25.6 miles long and is supported by 481 structures. The Centerville – Table Mountain – Oroville 60 kV Line is configured as a single conductor line and is supported by 481 structures, of which 169 structures are in high fire threat districts (HFTDs). The project will increase system performance and reduce fire ignition risk in Butte County by performing the following work: • Replace 122 existing structures with Light Duty Steel (LDS) Poles on the Centerville – Table Mountain – Oroville 60 kV Line; • Perform field analysis on the entire 25.6 mile long Centerville – Table Mountain – Oroville 60 kV Line to verify if conductor replacement is needed; • Replace Switch Nos. 27 and 67 with a Supervisory Control and Data Acquisition (SCADA)-operable switch on the Centerville – Table Mountain – Oroville 60 kV Line; • Replace existing ceramic insulators on 96 structures with modern equivalent insulators on the Centerville – Table Mountain – Oroville 60 kV Line; • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Multiple | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-04 | 94 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 25.6 | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5804594 | T.0005931 | Centerville-Table Mtn-Oroville | 1 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-09-13 | NA | 2029-10-10 | NA | FALSE | NA | NA | 0 | 5765.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1487 | Colgate-Grass Valley 60kV Structure Repl |  |  | Grass Valley, Nevada ¦ Nevada ¦ Yuba | The Colgate-Grass Valley 60 kV Line is located in Nevada County. The Colgate-Grass Valley 60 kV Line is approximately 13.2 miles long and is supported by 326 structures, of which, 287 are in Tier 2 and Tier 3 high fire threat districts (HFTDs). The project will increase system performance and reduce fire ignition risk in Nevada County by performing the following work: • Replace 139 wood poles on the Colgate-Grass Valley 60 kV Line2 • Replace insulators on 8 structures not identified for repalcement • Replace Colgate-Grass Valley 60 kV Line Switch No. 47 • Review Colgate-Grass Valley 60 kV Line Switch No. 75 • Review Structure Nos. 000/003, A003/091, 010/232 and 012/303 for age and condition • Review all conductor for age and condition to determine if replacement is required • Identify any distribution underbuild and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring • Include all open maintenance tags within the project scope where applicable | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-03-21 | 99 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 13.2 | NA | 60 | NA | 11293 | 1. Work that prevents fire ignition | 81 | RBPPF - TBD | Yes | 5790356 | T.0005865 | Colgate-Grass Valley 60kV | 1 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-11-27 | NA | 2030-12-24 | NA | FALSE | NA | NA | 66.4331 | 7094.4709 | 0 | 38.857 | 3.9256 | 13.1283 | 9.7452 | 0.7769 | 0 | 0 | 0 | 0 | 0 | 65.6562 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1488 | Colgate-Smartville #2 Reinf Sw Repl |  |  | Nevada ¦ Smartsville CDP, Yuba ¦ Yuba | The Colgate-Smartville #2 60 kV Reinforcement Project is located in Yuba and Nevada Counties. The Colgate-Smartville #2 60 kV line is 11.13 miles long and is supported by 155 structures. The line is a single circuit that is supported on single wood poles. All the structures are in Tier 2 high fire tier districts (HFTDs). The assessment by Transmission Line Asset Strategy (TLAS) included the two 60 kV taps connected to the Colgate-Smartville #2 60 kV line. They are the Narrows #2 Tap at structure 010/127 and the Smartville Tap at structure 000/001. The project will increase system performance and reduce fire ignition risk in Yuba and Nevada Counties by performing the following work: ● Replace 98 non-steel structures on Colgate-Smartville #2 60 kV line that includes reviewing 11.13 miles of conductor and increase inspection because of aging asset. ● Replace 68 insulators on the Colgate-Smartville #2 line ● Replace 2 non-steel structures on Smartville Tap ● Replace 47 non-steel structures for Narrows #2 Tap ● Replace one (1) steel structure for Narrows #2 Tap ● Replace one (1) switch with SCADA on Colgate-Smartville #2 line; SW#29 ● Replace two (2) switches with SCADA on Smartville Tap; SW#97 & SW#99 ● Replace two (2) switches with SCADA on Narrows #2 Tap; SW#47 & SW#59 | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-03-28 | 94 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 11.13 | NA | 60 | NA | Not Available | 1. Work that prevents fire ignition | 164 | RBPPF - TBD | Yes | 5790663 | T.0005916 | Colgate-Smartville #2 | 4 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-03-20 | NA | 2028-04-14 | NA | FALSE | NA | NA | 483.3987 | 8861.181 | 0 | 35.122 | 296.7894 | 105.5722 | 40.2618 | 34.9331 | 0 | 0 | 0 | 0 | 0 | 477.7454 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1489 | Eagle Rock-Cortina Struc Repl & Reinsul |  |  | Clearlake, Lake ¦ Colusa ¦ Lake ¦ Lower Lake CDP, Lake ¦ Sonoma | The Eagle Rock-Cortina 115 kV line is approximately 43.4 miles long with 322 structures that is located in the Northern region. Two hundred Ninety-Two (292) of these structures are in high fire tier districts (HFTD’s). In order to increase system performance and reduce fire ignition risk, asset components on the line are being performed with the following scope of work: • Replacement of 112 wood pole with steel structures; • Replacement of aging insulators on 119 structures; • Replacement of aging switch on structure 000/001; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring • Include all open maintenance tags within the project scope where applicable | Transmission Line - Multiple | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-11 | 73 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 | NA | 20067 | Not Available | 82 | RBPPF - TBD | Yes | 5789714 | T.0005743 | Eagle Rock-Cortina Struc Repl & Reinsul | 2 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-02-25 | NA | 2027-02-25 | NA | FALSE | NA | NA | 7.6259 | 10314.705 | 0 | 0 | 0 | 0.9093 | 6.6274 | 0.5533 | 0 | 0 | 0 | 0 | 0 | 7.5367 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1490 | Eagle Rock-Cortina Struc Repl & Reinsul |  |  | Clearlake, Lake ¦ Colusa ¦ Lake ¦ Lower Lake CDP, Lake ¦ Sonoma | The Eagle Rock-Cortina 115 kV line is approximately 43.4 miles long with 322 structures that is located in the Northern region. Two hundred Ninety-Two (292) of these structures are in high fire tier districts (HFTD’s). In order to increase system performance and reduce fire ignition risk, asset components on the line are being performed with the following scope of work: • Replacement of 112 wood pole with steel structures; • Replacement of aging insulators on 119 structures; • Replacement of aging switch on structure 000/001; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring • Include all open maintenance tags within the project scope where applicable | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-11 | 46 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 43.4 | NA | 115 | NA | 20067 | 2. Overhead With Strong Safety Link | 82 | RBPPF - TBD | Yes | 5789712 | T.0005743 | Eagle Rock-Cortina Struc Repl & Reinsul | 2 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-02-11 | NA | 2027-06-04 | NA | FALSE | NA | NA | 137.8538 | 18115.071 | 0 | 58.576 | 10.7529 | 51.3533 | 15.5594 | 10.0025 | 0 | 0 | 0 | 0 | 0 | 136.2416 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1491 | MORAGA-OAKLAND X 115KV #1&2: RECOND |  |  | Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa ¦ Piedmont, Alameda | The project proposes to replace the structures, conductors, and hardware in the same overhead alignment between Moraga Substation and California State Highway 13 and also to relocate the line sections between Highway 13, and Oakland X underground (UG) within city streets. By replacing the aging facilities PG&E can improve wildfire safety and public safety and increase path capacity into the Oakland area. The project scope of work includes: • Removal of 78 existing lattice steel transmission towers • Removal of approximately 20 circuit miles of conductor • Installation of approximately 60 new lattice steel transmission towers • Installation of approximately 11 miles of Aluminum Conductor Composite Reinforced (ACCR) conductor • Installation of three 115kV underground duct banks with 115kV transmission cables totaling approximately six miles • Installation of new 115kV circuit breakers and air switches at Moraga Substation • Upgrade the 115kV bus at Oakland X Substation to complement the higher capacity ACCR conductor | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-12 | 93 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | 6 | NA | 115 | NA | 228 | Not Available | Not Available | RBPPF - TBD | Yes | 5793947 | T.0000349 | Moraga-Oakland #1-#4 Rebuild | 12 | 93 | 5789523 | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-12-10 | 2025-07-31 | 2028-12-13 | Prioritization | FALSE | 212000 | NA | 9653.7538 | 133722.8827 | 0 | 2145.8684 | 4157.1539 | 1462.6327 | 1536.8403 | 2164.0857 | 2088.1625 | 20057.67 | 70479.0421 | 18791.6792 | 9100 | 9302.4954 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1492 | MORAGA-OAKLAND X 115KV #3&4 RECOND |  |  | Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa ¦ Piedmont, Alameda | The project proposes to replace the structures, conductors, and hardware in the same overhead alignment between Moraga Substation and California State Highway 13 and also to relocate the line sections between Highway 13, and Oakland X underground (UG) within city streets. By replacing the aging facilities PG&E can improve wildfire safety and public safety and increase path capacity into the Oakland area. The project scope of work includes: • Removal of 78 existing lattice steel transmission towers • Removal of approximately 20 circuit miles of conductor • Installation of approximately 60 new lattice steel transmission towers • Installation of approximately 11 miles of Aluminum Conductor Composite Reinforced (ACCR) conductor • Installation of three 115kV underground duct banks with 115kV transmission cables totaling approximately six miles • Installation of new 115kV circuit breakers and air switches at Moraga Substation • Upgrade the 115kV bus at Oakland X Substation to complement the higher capacity ACCR conductor | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-02 | 58 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | 6 | NA | 115 | NA | 228 | Not Available | Not Available | Tier 3 | No | 5793948 | T.0000349 | Moraga-Oakland #1-#4 Rebuild | 12 | 93 | 5789524 | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | Expected PEA Completion | TBD | EIR | NA | CPUC | NA | PTC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-12-10 | 2025-07-31 | 2028-12-13 | Prioritization | FALSE | 212000 | NA | 6308.5785 | 114034.4314 | 0 | 860.01 | 3044.8561 | 806.7845 | 1331.0454 | 1725.3111 | 1405.6846 | 4773.7361 | 21876.2275 | 67167.3456 | 9100 | 6042.696 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1493 | Tulucay-Napa #1-Repl Steel Poles |  |  | Green Valley CDP, Napa ¦ Green Valley CDP, Solano ¦ Napa ¦ Napa, Napa ¦ Solano | The project will increase system performance and reduce fire ignition risk in Napa County by performing the following work: • Replace 4 steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 8 steel structures on the Cordelia #2 Tap 60 kV; • Replace 126 existing wood poles with steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 19 existing wood poles with steel structures on the Cordelia #1 Tap 60 kV; • Replace 77 existing wood poles with steel structures on the Cordelia #2 Tap 60 kV; • Replace 2.33 miles of conductor from pole no. T001/006 to 006/107 on the Cordelia #1 Tap 60 kV; • Replace existing ceramic insulators on 26 structures with modern equivalent insulators; • Replace 5 existing switches with Supervisory Control and Data Acquisition (SCADA)-operable switches; • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2023-09-28 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 25.66 | NA | 60 | NA | 11313 | 1. Work that prevents fire ignition | 161 | RBPPF - TBD | Yes | 5791021 | T.0005976 | Tulucay-Napa #1 | 4 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-05-03 | NA | 2028-10-26 | NA | FALSE | NA | NA | 840.1627 | 28354.017 | 0 | 18.4024 | 348.4271 | 423.6989 | 39.8086 | 60.9614 | 0 | 0 | 0 | 0 | 0 | 830.337 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1494 | Drum-Rio Oso 115kV- Dutch Flat #2 Tap |  |  | Nevada | The project will increase system performance and reduce fire ignition risk in Nevada and Placer Counties by performing the following work: • Replace approximately 34.0 miles of conductor on the Drum – Rio Oso #1 and #2 115 kV Lines from structure no. 011/111 to Rio Oso Substation with 477 aluminum conductor steel supported (ACSS); • Upgrade substation terminal equipment to match new conductor rating, if needed; • Replace existing 408 structures with self-weathering tubular steel poles (TSPs) on the Drum – Rio Oso #1 and #2 115 kV Line; • Replace existing 40 structures with self-weathering steel poles on the Brunswick #1 and #2 Tap 115 kV; • Replace existing 4 structures with self-weathering steel poles on the Dutch Flat #2 Tap 115 kV; • Replace existing ceramic insulators on all structures with modern equivalent insulators on the Drum – Rio Oso #1 and #2 115 kV Lines, Brunswick #1 and #2 Tap 115 kV and Dutch Flat #2 Tap 115 kV; • Conduct field verification on the Dutch Flat #2 Tap 115 kV to determine if conductor replacement is needed; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring | Transmission Line - Multiple | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-03-19 | 34 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5796875 | T.0006067 | Drum-Rio Oso 115kV Line Reinforcement | 3 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-06-13 | NA | 2030-07-15 | NA | FALSE | NA | NA | 28.3089 | 31882.2331 | 0 | 0 | 1.4176 | 23.0112 | 3.549 | 2.0541 | 0 | 0 | 0 | 0 | 0 | 27.9778 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1495 | Drum-Rio Oso 115kV Line Reinforcement |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | The project will increase system performance and reduce fire ignition risk in Nevada and Placer Counties by performing the following work: • Replace approximately 34.0 miles of conductor on the Drum – Rio Oso #1 and #2 115 kV Lines from structure no. 011/111 to Rio Oso Substation with 477 aluminum conductor steel supported (ACSS); • Upgrade substation terminal equipment to match new conductor rating, if needed; • Replace existing 408 structures with self-weathering tubular steel poles (TSPs) on the Drum – Rio Oso #1 and #2 115 kV Line; • Replace existing 40 structures with self-weathering steel poles on the Brunswick #1 and #2 Tap 115 kV; • Replace existing 4 structures with self-weathering steel poles on the Dutch Flat #2 Tap 115 kV; • Replace existing ceramic insulators on all structures with modern equivalent insulators on the Drum – Rio Oso #1 and #2 115 kV Lines, Brunswick #1 and #2 Tap 115 kV and Dutch Flat #2 Tap 115 kV; • Conduct field verification on the Dutch Flat #2 Tap 115 kV to determine if conductor replacement is needed; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring | Transmission Line - Multiple | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-01 | 111 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 68 | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5791639 | T.0006067 | Drum-Rio Oso 115kV Line Reinforcement | 3 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2030-10-08 | NA | 2030-12-06 | NA | FALSE | NA | NA | 371.9003 | 243672.1498 | 0 | 1.5607 | 242.4266 | 185.9406 | -62.3769 | 26.9848 | 0 | 0 | 0 | 0 | 0 | 367.5509 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1496 | Drum-Rio Oso 115kV-Brunswick 1 & 2 Tap |  |  | Grass Valley, Nevada ¦ Nevada | The project will increase system performance and reduce fire ignition risk in Nevada and Placer Counties by performing the following work: • Replace approximately 34.0 miles of conductor on the Drum – Rio Oso #1 and #2 115 kV Lines from structure no. 011/111 to Rio Oso Substation with 477 aluminum conductor steel supported (ACSS); • Upgrade substation terminal equipment to match new conductor rating, if needed; • Replace existing 408 structures with self-weathering tubular steel poles (TSPs) on the Drum – Rio Oso #1 and #2 115 kV Line; • Replace existing 40 structures with self-weathering steel poles on the Brunswick #1 and #2 Tap 115 kV; • Replace existing 4 structures with self-weathering steel poles on the Dutch Flat #2 Tap 115 kV; • Replace existing ceramic insulators on all structures with modern equivalent insulators on the Drum – Rio Oso #1 and #2 115 kV Lines, Brunswick #1 and #2 Tap 115 kV and Dutch Flat #2 Tap 115 kV; • Conduct field verification on the Dutch Flat #2 Tap 115 kV to determine if conductor replacement is needed; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring | Transmission Line - Multiple | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-04-03 | 49 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5796876 | T.0006067 | Drum-Rio Oso 115kV Line Reinforcement | 3 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-06-13 | NA | 2030-07-15 | NA | FALSE | NA | NA | 10.8242 | 31862.3247 | 0 | 0 | 1.5751 | 5.7665 | 3.3561 | 0.7854 | 0 | 0 | 0 | 0 | 0 | 10.6976 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1497 | Spaulding Summit 60kV Replacement - Ph 1 |  |  | Kingvale CDP, Nevada ¦ Nevada ¦ Placer ¦ Soda Springs CDP, Nevada | The Spaulding – Summit 60 kV Line is located in Placer and Nevada counties. The Line is 19.65 miles long and is supported by 594 non-steel structures and 31 steel structures, a total of 626 structures. 460 of these structures are located in high fire threat districts (HFTD). The project will increase system performance and reduce fire ignition risk in Placer and Nevada counties by performing the following work: • Replace 574 Structures on the Spaulding - Summit 60 kV Line2 • Review 7.86 miles of AAC, ACSR and CU conductor on the Spaulding - Summit 60 kV Line, due to age, to determine if replacement is required • Replace 0.97 miles of ACSR conductor on the Spaulding - Summit 60 kV Line, due to high probability of failure • Replace 0.37 miles of ACSR conductor on the Tap Line between 005/205 and CISCO Grove, due to high probability of failure • Replace 8 switches with SCADA-operable switches on the Spaulding - Summit 60 kV Line • Replace 1 switch with SCADA-operable switch on the CISCO Grove Tap 60 kV Line • Identify any distribution under-build and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-03-26 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Zone 1 - HHZ, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | 1. Work that prevents fire ignition | 5 | RBPPF - TBD | Yes | 5790358 | T.0005849 | Spaulding-Summit 60 kV | 3 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-07-08 | NA | 2031-07-29 | NA | FALSE | NA | NA | 53.0806 | 30999.8149 | 0 | 0 | 25.1732 | 6.3416 | 20.945 | 3.8448 | 0 | 0 | 0 | 0 | 0 | 52.4598 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1498 | Spaulding Summit 60kV Replacement - Ph 2 |  |  | Kingvale CDP, Nevada ¦ Nevada ¦ Placer ¦ Soda Springs CDP, Nevada | The Spaulding – Summit 60 kV Line is located in Placer and Nevada counties. The Line is 19.65 miles long and is supported by 594 non-steel structures and 31 steel structures, a total of 626 structures. 460 of these structures are located in high fire threat districts (HFTD). The project will increase system performance and reduce fire ignition risk in Placer and Nevada counties by performing the following work: • Replace 574 Structures on the Spaulding - Summit 60 kV Line2 • Review 7.86 miles of AAC, ACSR and CU conductor on the Spaulding - Summit 60 kV Line, due to age, to determine if replacement is required • Replace 0.97 miles of ACSR conductor on the Spaulding - Summit 60 kV Line, due to high probability of failure • Replace 0.37 miles of ACSR conductor on the Tap Line between 005/205 and CISCO Grove, due to high probability of failure • Replace 8 switches with SCADA-operable switches on the Spaulding - Summit 60 kV Line • Replace 1 switch with SCADA-operable switch on the CISCO Grove Tap 60 kV Line • Identify any distribution under-build and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. | Transmission Line - Pole/Tower | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-03-26 | 79 | Lifecycle Replacement Analysis | TBD | TBD | Zone 1 - HHZ, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 19.65 | NA | 60 | NA | Not Available | 1. Work that prevents fire ignition | 5 | RBPPF - TBD | Yes | 5790359 | T.0005849 | Spaulding-Summit 60 kV | 3 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-04-25 | NA | 2030-05-06 | NA | FALSE | NA | NA | 403.2846 | 30914.8876 | 0 | 23.3205 | 100.1058 | 146.8998 | 126.8071 | 30.6459 | 0 | 0 | 0 | 0 | 0 | 397.1332 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1499 | Spaulding Summit 60kV Replacement - Ph 3 |  |  | Kingvale CDP, Nevada ¦ Nevada ¦ Placer ¦ Soda Springs CDP, Nevada | The Spaulding – Summit 60 kV Line is located in Placer and Nevada counties. The Line is 19.65 miles long and is supported by 594 non-steel structures and 31 steel structures, a total of 626 structures. 460 of these structures are located in high fire threat districts (HFTD). The project will increase system performance and reduce fire ignition risk in Placer and Nevada counties by performing the following work: • Replace 574 Structures on the Spaulding - Summit 60 kV Line2 • Review 7.86 miles of AAC, ACSR and CU conductor on the Spaulding - Summit 60 kV Line, due to age, to determine if replacement is required • Replace 0.97 miles of ACSR conductor on the Spaulding - Summit 60 kV Line, due to high probability of failure • Replace 0.37 miles of ACSR conductor on the Tap Line between 005/205 and CISCO Grove, due to high probability of failure • Replace 8 switches with SCADA-operable switches on the Spaulding - Summit 60 kV Line • Replace 1 switch with SCADA-operable switch on the CISCO Grove Tap 60 kV Line • Identify any distribution under-build and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. | Transmission Line - Multiple | Replace | TBD | Asset Condition | Age/Condition - Replace Conductor | NA | 2024-03-26 | 82 | Lifecycle Replacement Analysis | TBD | TBD | Zone 1 - HHZ, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 7.86 | NA | 60 | NA | Not Available | 1. Work that prevents fire ignition | 5 | RBPPF - TBD | Yes | 5790360 | T.0005849 | Spaulding-Summit 60 kV | 3 | 93 | NA | 2020 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-03-04 | NA | 2030-10-21 | NA | FALSE | NA | NA | 0 | 29245.5796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1500 | Mission-Larkin #2 115 kV Cable (X-Y 2) |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Transmission Line - Multiple | Replace | T.0002705 ¦ T.0000557 ¦ T.0000934 | Asset Condition | Seismic Upgrade - Replace Conductor | NA | 2024-03-13 | 74 | Lifecycle Replacement Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 7 | NA | 115 | NA | 434 | 4. Underground / Network (Strong Safety Link) | 1126 | RBPPF - TBD | Yes | 5765140 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 93 | NA | 2015 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2032-04-23 | 2025-06-20 | 2032-10-28 | Project Design | FALSE | 191100 | NA | 3006.3534 | 29497.7477 | 124.1704 | 424.1616 | 385.7743 | 386.2823 | 213.6454 | 217.2084 | 0 | 0 | 0 | 0 | 0 | 2971.1943 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1501 | Potrero-Larkin #3 115 kV Cable (A-Y 3) |  |  | Brisbane, San Mateo ¦ Daly City, San Mateo ¦ San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Transmission Line - Multiple | Replace | T.0002705 ¦ T.0000557 ¦ T.0000934 | Asset Condition | Seismic Upgrade - Replace Conductor | NA | 2024-03-13 | 54 | Lifecycle Replacement Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 2.8 | NA | 115 | NA | 434 | 4. Underground / Network (Strong Safety Link) | 1204 | RBPPF - TBD | Yes | 5765139 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 93 | NA | 2015 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2032-08-25 | 2025-06-20 | 2033-05-12 | Project Design | FALSE | 191100 | NA | 3495.9325 | 81109.873 | 354.1041 | 214.8132 | 286.1352 | 941.1621 | 221.1905 | 252.6283 | 0 | 0 | 0 | 0 | 0 | 3455.0478 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1502 | TLine USFS-SteelSpeciesProtection(North) |  |  | NA | Bucket for replacement for raptor protection involves reframing structures, replacement of insulators, conversion of insulator configurations and installation of guano shields in the US Forest Services Northern Area on steel towers. These capital related improvements have been identified during annual patrols as critical work needing to be corrected. Correction of these findings will assist in optimize the integrity of our transmission lines and to reduce the risk of unplanned outages. | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Raptor Protection - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 180 | 1. Work that prevents fire ignition | 408 | RBPPF - TBD | Yes | 5510401 | NA | NA | NA | 93 | NA | NA | 2013 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 4996.0991 | 4996.0991 | -55.0714 | 64.0078 | 54.8013 | -48.881 | 23.2185 | 12.3061 | 0 | 0 | 0 | 0 | 0 | 4983.793 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | -44.5643 | 54.6403 | 0.91685 | 3.8322 | 1.6988 | 0.62612 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1503 | Vineyard Transition Station- Switch 265 and 245 |  |  | Alameda ¦ Livermore, Alameda ¦ Pleasanton, Alameda | Switches 265 and 245 at Vineyard Transition Station have bottles with low SF6 gas and need to be replaced before failure. In last two years, we have had similar problem with Lone Tree – Cayetano switch 295, which resulted replacement of the switch by OH crew /contractor. | Transmission Line - Switch | Replace | TBD | Asset Condition | Age/Condition - Switch Replacement - Steel | NA | 2024-01-09 | 21 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | Tier 5 | No | EX112189 | TBD | TBD | TBD | 93 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2029-12-01 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1504 | Switch Rplcmnts - Steel - Program |  |  | NA | Bucket for Switch Replacements on steel structures | Transmission Line - Switch | Replace | NA | Asset Condition | Age/Condition - Switch Replacement - Steel | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | 1. Work that prevents fire ignition | Not Available | NA | NA | 5507681 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2013 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2960.3412 | 2960.3412 | 0 | 0 | 0 | 8.7948 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 2960.3412 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 8.7948 | 0.3 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1505 | GO95 Steel N - Low Cond Proj |  |  | NA | Bucket for GO95 compliance on conductors | Transmission Line - Multiple | Replace | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 197 | 5. Compliance/Commitments With Strong Safety Link | Not Available | RBPPF - TBD | No | 5510404 | NA | NA | NA | 93 | NA | NA | 2013 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 11732.4188 | 11732.4188 | 200.5187 | 2780.3889 | 27.4866 | -687.3718 | 290.0371 | 192.831 | 0 | 0 | 0 | 0 | 0 | 11539.5878 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 200.5104 | 2780.3889 | 27.4866 | -688.3251 | 244.7947 | 95.7232 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1506 | 93T: GO-95 Mitigation |  |  | NA | Forecast placeholder for potential mitigation needed for GO-95 mitigation on HFTD Lines. This work will be developed after line assessments/LiDAR analysis. Represents mitigation on steel structure lines. | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | EX112095 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7125 | 12000 | 12000 | 12000 | 12000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1507 | GO95 Steel N - Low Cond Proj (Sac) |  |  | NA | Bucket for GO95 low conductor work on steel poles in Sacramento area. | Transmission Line - Multiple | Replace | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | NA | NA | 5511321 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 1094.4278 | 1094.4278 | 0 | 0 | 0 | 19.2812 | 4.7045 | 0 | 0 | 0 | 0 | 0 | 0 | 1094.4278 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1508 | EO-SYSPLN 93T - ET Prev Work |  |  | NA | Forecast placeholder for replacement due to 3rd party damage | Transmission Line - Multiple | Replace | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 380 | Not Available | Not Available | RBPPF - TBD | No | 5533335 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 2940 | 0 | 0 | 0 | 0 | 0 | 2940 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1509 | DEL MONTE - FORT ORD#1 |  |  | Del Rey Oaks, Monterey ¦ Monterey, Monterey ¦ Seaside, Monterey | The project will rebuild the 4.2- and 4.1-mile sections of the lines with 397.5 kcmil all-aluminum conductor (AAC) mounted on new LSP’s. Completion of the project will ensure reliable service to the existing 14,200 and future customers served from Fort Ord Substation. The expected in-service date is May 2020. The total project cost for the project is estimated at roughly $8.00M based on preliminary cost estimates (AACE Class 5). | Transmission Line - Multiple | Replace | TBD | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | 2024-03-27 | 89 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | $20 Mil - $30 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 8.3 | NA | 60 | NA | 380 | 1. Work that prevents fire ignition | 105 | Tier 5 | No | 5781040 | T.0004114 | DEL MONTE - FORT ORD#1 | 1 | 93 | NA | 2018 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | On Hold | 4 | 2027-01-19 | 2025-02-07 | 2027-03-30 | Prioritization | FALSE | 12698 | NA | 2858.3652 | 6611.4516 | 246.8643 | 455.0065 | 550.1414 | 553.5948 | 450.2994 | 173.9666 | 0 | 0 | 0 | 0 | 4153 | 2858.3702 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 1510 | MWC 93: Coatings – Tags |  |  | NA | Forecast placeholder for Completion of priority E/F paint tags (within the 12mo-60 mo time frame) to mitigate asset conditions that may pose a safety or wildfire risk. Also includes backlogged tags. This backlog must be cleared in order to reach steady-state compliance with GO-95. | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | No | Ex112983 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10974.1984 | 15684.3632 | 29037.9232 | 26998.4704 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1511 | Early Fault Detectors - Transmission |  |  | NA | Forecast placeholder for Early Fault Detectors (EFD) for use in wildfire risk reduction(~$10.6k per unit) | Transmission Line - Other Equipment | New | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 1 | No | EX112096 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1512 | MWC 93: Coatings – Strategy |  |  | NA | Forecast placeholder for tower coating work | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 4 | No | Ex112982 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9135.04 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1513 | Arc Fault Mitigation Program |  |  | NA | Bucket for Arc Fault Mitigation Program | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 3 | No | 5546935 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 5079.7795 | 10079.7805 | 0 | 0 | 0 | 4441.7348 | 567.143 | 5070.9029 | 0 | 2834 | 0 | 0 | 0 | 5008.8776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 4431.9466 | 556.3311 | 52.7028 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1514 | Tower Coating Program Capital |  |  | NA | Bucket for capital tower coating work | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 5 | No | 5549743 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 34729.6058 | 34729.6058 | 0 | 4.107 | 2.0766 | 18293.9132 | 13756.8399 | 2672.6698 | 0 | 0 | 0 | 0 | 0 | 32056.936 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 6.1836 | 17801.3851 | 14120.7676 | 3605.46 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1515 | 2022 Cathodic Protection Installs |  |  | NA | Bucket for cathodic protection improvements for overhead transmission circuits | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 3 | No | 5547633 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 30631.4609 | 30631.4609 | 0 | 0 | 4245.4934 | 14580.7134 | 10446.4008 | 1358.8537 | 0 | 0 | 0 | 0 | 0 | 29272.6072 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 2966.2691 | 15151.4411 | 7803.8465 | -87.6832 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1516 | TO TLine (93P) - Insulator Replacements |  |  | NA | Bucket for insulator replacement on wood poles | Transmission Line - Other Equipment | Replace | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | 10 | NA | NA | 5526200 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2426.2501 | 2426.2501 | 75.3471 | 57.3504 | 9.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2426.2501 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 68.8526 | 57.3504 | 4.4577 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1517 | Tower Cathodic Protection -Mitigation |  |  | NA | Forecast placeholder for Tower cathodic protection | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | Tier 3 | No | 5542903 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | TRUE | NA | NA | 0 | 21468.2855 | 0 | 0 | 0 | 0 | 0 | 11468.2855 | 5000 | 8677.2871 | 8677.2871 | 8677.2871 | 8677.2871 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1518 | Corrosion Control MWC 93 |  |  | NA | Forecast placeholder for tower coating work | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5542459 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | NA | NA | NA | OAI | NA | TRUE | NA | NA | 0 | 114948.574 | 0 | 0 | 0 | 0 | 0 | 20948.574 | 54000 | 19630.0377 | 21611.5396 | 6506.5507 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1519 | Lattice Steel Pole Guarding/Marking |  |  | NA | Bucket for installing 707 anti climb guards / mesh on Lattice Steel Poles on various 500, 230, 115 & 70KV T/Lines so that PG&E will be in compliance with GO95. This was performed on 31 different line names over 7 counties. | Transmission Line - Multiple | Replace | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 380 | Not Available | Not Available | NA | NA | 5515925 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2707.5341 | 2707.5341 | 0 | 0 | 57.8968 | 121.3378 | 2.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 2707.5341 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 47.4336 | 121.4404 | 2.5494 | 0 | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1520 | WSIP - Steel Pole Reframe |  |  | NA | Bucket for steel pole reframes in HFTD | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | 18 | RBPPF - TBD | Yes | 5534699 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | TRUE | NA | NA | 13450.2887 | 13450.2887 | 48.6758 | 907.4107 | 436.8283 | 12046.849 | 1.1763 | 9.3489 | 0 | 0 | 0 | 0 | 0 | 13440.9398 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 37.4382 | 840.8536 | 443.3849 | 196.956 | 11728.2241 | 1.4715 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1521 | Steel Pole Reframe |  |  | NA | Bucket for steel pole reframing | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5555068 | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 2161.5243 | 2161.5243 | 53.3048 | 115.4166 | 450.2193 | 339.4799 | 1137.9503 | 65.8534 | 0 | 0 | 0 | 0 | 0 | 2095.6709 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 50.685 | 92.143 | 449.6679 | 273.2255 | 1038.5941 | 99.6335 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1522 | NORTH BUNDLE N-15 |  |  | Humboldt ¦ Junction City CDP, Trinity ¦ Trinity ¦ Weaverville CDP, Trinity | Add SCADA capability to Motor Operated Air Switches (MOAS) Nos. 29, 19, 25, 37, 39, 137, 139, and 59 on the Essex Jct. – Arcata – Fairhaven 60 kV, Bridgeville – Garberville 60 kV, Ultra Power Tap 60 kV, Trinity – Maple Creek 60 kV, Humboldt – Trinity 115 kV, and Rio Dell Jct. – Bridgeville 60 kV Lines. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-12 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5735163 | T.0000033 | NORTH BUNDLE N-15 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-20 | 2018-12-03 | 2020-06-15 | Prioritization | FALSE | 5519 | NA | 3447 | 3447 | 1388 | 1176 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 | 1340.5671 | 1133.4782 | -2.0507 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1523 | Central Bundle C-19 |  |  | Burlingame, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ San Mateo, San Mateo ¦ South San Francisco, San Mateo | This project proposes to replace the following manually operated switches and existing structures with SCADA- operable switches and Engineered Direct Embedded Poles (Steel): Switch Nos. 137 & 139 on the East Grand – San Mateo 115 kV Line, Switch No. 147 at Millbrae Junction on the on Millbrae – San Mateo No. 1 115 kV Line and Switch No. 69 on the San Mateo – Bair 60 kV Line. The project is needed to improve electric transmission service reliability by reducing customer outage minutes for emergency conditions to customers served in San Mateo County, California. The expected benefit of this program is a reduction of safety risks and improvement in reliability levels on transmission lines prone to outages. The remote control features of SCADA switches will eliminate the need to provide on-site, manual operation. This will reduce traveling safety risks during non-ideal weather conditions and to remote, off-road locations. In parallel, SCADA enables faster fault isolation and restoration possibilities as well as improved clearance planning | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2020-10-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 ¦ 60 | NA | 180 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | No | 5526516 | T.0003181 | Central Bundle C-19 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2024-01-04 | 2019-10-31 | 2024-01-23 | Prioritization | FALSE | 3970 | NA | 1286.0128 | 1286.0128 | 202.1175 | 508.5492 | 10.2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1286.0128 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 174.4876 | 490.2339 | 9.911 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements.
| 1524 | South Bundle S-32 |  |  | Chowchilla, Madera ¦ Fresno ¦ Madera | Wave 3 Transmission Line SCADA Switch Program: Replace SWs 177 & 179 with SCADA SWs on CHOWCHILLA-KERCKHOFF 115 kV Line | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-10 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | No | 5541997 | T.0006538 | South Bundle S-32 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2022-02-01 | 2024-12-15 | 2025-03-11 | NA | TRUE | 154700 | NA | 902.8407 | 902.8407 | 0 | 0 | 162.4279 | 719.5456 | 20.8672 | 0 | 0 | 0 | 0 | 0 | 651.2583 | 902.8407 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 | 0 | 0 | 158.031 | 700.0477 | 20.3024 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1525 | South Bundle S-34 |  |  | Kern ¦ San Luis Obispo | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: ARCO-CHOLAME 70 kV (SW 65 & New Switch on 003/041) ARCO-POLONIO PASS PP 70 kV (SW 85) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-11 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541999 | T.0006540 | South Bundle S-34 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2025-10-06 | 2024-12-15 | 2025-11-19 | Prioritization | TRUE | 154700 | NA | 363.9707 | 372.0866 | 0 | 8.0656 | 56.9055 | 295.4161 | 4 | 0 | 0 | 0 | 0 | 0 | 119.8671 | 363.9707 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 0 | 64.9711 | 295.4161 | 3.5834 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1526 | North Bundle N-35 |  |  | Chester CDP, Plumas | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: HAMILTON BRANCH-CHESTER 60 kV (SW 99) COLLINS PINE TAP 60 kV (SW 25 | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-08-17 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541988 | T.0006527 | North Bundle N-35 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-06-12 | 2024-12-15 | 2025-06-12 | NA | FALSE | 149600 | NA | 10.7086 | 1005.5658 | 0 | 0 | 8.0528 | 2.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7086 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 ¦ 2026 | 0 | 0 | 8.0528 | 2.6558 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1527 | Husted Jct SW 47 and 49 Switch Capability Upgrades |  |  | Colusa ¦ Colusa, Colusa ¦ Williams, Colusa | Replace switch 47 and 49 with SCADA operable upgrades that have loop breaking and line dropping capabilities on Cortina #2 60kV. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-10 | 70 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | Tier 4 | No | EX112702 | TBD | TBD | TBD | 94 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-06-01 | NA | 2030-02-28 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1528 | Merced #1 El Nido Customer Switch Installation |  |  | Fresno ¦ Madera ¦ Merced | Install two new switches along the Merced #1 70 kV line to improve the reliability and cost of service to El Nido Customer. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-08 | 94 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 70 | NA | Not Available | Not Available | Not Available | Tier 4 | No | EX112701 | TBD | TBD | TBD | 94 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-06-01 | NA | 2030-03-04 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4988 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1529 | Re-locate and Replace Ripon Switch 339 and 337 |  |  | Ripon, San Joaquin ¦ San Joaquin ¦ Stanislaus | Relocate switch 337 and 339 to a more accessible location for safe and reliable operation. Replace both switches with SCADA operable upgrades. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2021-10-01 | 88 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | Tier 3 | No | EX112703 | TBD | TBD | TBD | 94 | NA | TBD | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-06-01 | NA | 2031-02-28 | NA | FALSE | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2073 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1530 | South Bundle S-27 |  |  | Fresno ¦ Hanford, Kings ¦ Kings | Add SCADA capability to Contadina Junction SWs 137 and 139 in the GWF – Kingsburg 115 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-09 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | Not Available | NA | NA | NA | 5526503 | T.0003168 | South Bundle S-27 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-03-03 | 2018-12-31 | 2019-04-01 | NA | FALSE | 1560 | NA | 1369.5792 | 1369.5792 | 559.6034 | 57.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1369.5792 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 512.3387 | 55.1493 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1531 | Central Bundle C-06 |  |  | Clearlake Oaks CDP, Lake ¦ Clearlake, Lake ¦ Lake ¦ Lower Lake CDP, Lake ¦ Sonoma | Add SCADA capability to Motor Operated Air Switches (MOAS) Nos. 17, 139, 67, 19, and 67 on the Potter Valley – Willits 60 kV, Eagle Rock – Redbud 115 kV, Elk – Gualala 60 kV, Philo Jct. – Elk 60 kV, Laytonville – Willits 60 kV Lines. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-12 | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 ¦ 60 | NA | 180 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5526506 | T.0003171 | Central Bundle C-06 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-05 | 2018-12-31 | 2020-05-07 | Prioritization | FALSE | 3010 | NA | 1524.5457 | 1524.5457 | 800.5084 | 108.4797 | -263.9041 | 16.0109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1524.5457 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 740.5812 | 104.5728 | -254.3996 | -127.8693 | -3e-05 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1532 | North Bundle N-17 |  |  | Greenfield, Monterey ¦ King City, Monterey ¦ Monterey ¦ Soledad, Monterey | Add SCADA capability to Motor Operated Air Switches (MOAS) Nos. 39, 47, and 49 on the Kilarc – Deschutes 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-09 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | Not Available | NA | NA | NA | 5527390 | T.0003394 | North Bundle N-17 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-23 | 2019-07-30 | 2019-10-08 | NA | FALSE | 4570 | NA | 1763.9572 | 1763.9572 | 983.6362 | 401.4693 | -0.9549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1763.9572 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 948.2107 | 387.0104 | -0.92051 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1533 | North Bundle N-14 |  |  | Gerber CDP, Tehama ¦ Los Molinos CDP, Tehama ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama ¦ Tehama, Tehama | Add SCADA capability to Motor Operated Air Switches (MOAS) Nos. 39, 51, 57, 59, 227, 229, 37, and 17 on the Coleman – Red Bluff 60 kV, Bridgeville – Cottonwood 115 kV, Cottonwood #1 60 kV, and Kilarc – Cedar Creek 60 kV Lines. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-12-20 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | 180 | Not Available | NA | NA | NA | 5526767 | T.0003242 | North Bundle N-14 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-03 | 2019-05-30 | 2019-12-23 | Prioritization | FALSE | 1871 | NA | 4503.9747 | 4503.9747 | 2614.9194 | 832.4064 | -0.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4503.9747 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 2482.9669 | 802.4273 | -0.92598 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1534 | SOUTH BUNDLE S-23 |  |  | Chowchilla, Madera ¦ Fresno ¦ Madera | Add SCADA capability to Oakhurst Junction Motor Operated Air Switches (MOAS) Nos. 147 and 149 on the Chowchilla - Kerckhoff No. 2 115 kV Line, | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-10 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 76 | Not Available | NA | NA | NA | 5772325 | T.0002254 | SOUTH BUNDLE S-23 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-03-19 | 2020-06-19 | 2019-03-29 | NA | FALSE | 1380 | NA | 1313.0147 | 1313.0147 | 762.603 | 106.2053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1313.0147 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 723.2765 | 102.3803 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1535 | South Bundle S-11 |  |  | King City, Monterey ¦ Monterey ¦ San Lucas CDP, Monterey | Add SCADA capability to Switch Nos. 17 and 19 on the Coburn – Oil Fields No. 1 60 kV Line and Switch Nos. 27 and 29 on the Coburn – Oil Fields No. 2 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-08 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | Not Available | NA | NA | NA | 5526492 | T.0003157 | South Bundle S-11 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-02 | 2018-09-30 | 2019-04-11 | Prioritization | TRUE | 1499 | NA | 1850.6604 | 1850.6604 | 124.9265 | 127.9186 | 0.536 | 0 | 56.3819 | 0 | 0 | 0 | 0 | 0 | 0 | 1850.6604 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2023 ¦ 2024 | 64.932 | 123.3116 | 0.5167 | 0 | 54.3513 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1536 | South Bundle S-13 |  |  | Aromas CDP, Monterey ¦ Aromas CDP, San Benito ¦ Monterey ¦ Prunedale CDP, Monterey ¦ Prunedale CDP, San Benito ¦ Salinas, Monterey ¦ San Benito ¦ Santa Cruz ¦ Watsonville, Santa Cruz | Add SCADA capability to Switch Nos. 27, 37 and 39 on the Watsonville – Salinas 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-09 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | Not Available | NA | NA | NA | 5526494 | T.0003159 | South Bundle S-13 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-05-01 | 2018-10-31 | 2019-06-05 | Workforce | FALSE | 1630 | NA | 1639.8601 | 1639.8601 | 1011.3502 | 295.1107 | 4.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1639.8601 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 963.0652 | 284.4823 | 3.9039 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1537 | South Bundle S-12 |  |  | Monterey ¦ Salinas, Monterey | Add SCADA capability to Switch Nos. 67 and 69 on the Salinas – Firestone No. 1 60 kV Line and Switch Nos. 19, 25 and 49 on the Salinas – Firestone No. 2 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-09-21 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5526493 | T.0003158 | South Bundle S-12 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-23 | 2018-12-31 | 2021-01-28 | Prioritization | FALSE | 2607 | NA | 3012.4946 | 3012.4946 | 414.799 | 1797.105 | 231.5874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3012.4946 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 319.8765 | 1385.8568 | 178.591 | 580.8828 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1538 | Central Bundle C-15 |  |  | Alameda ¦ Fremont, Alameda ¦ Livermore, Alameda ¦ Sunol CDP, Alameda | Add SCADA capability to Switch Nos. 67, 69, and 57 on Newark – Vallecitos, and Newark – Livermore 60 kV Lines at Sunol and San Ramon Junctions. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-09 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Heat Wave |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | 249 | NA | NA | 5526512 | T.0003177 | Central Bundle C-15 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-10 | 2019-05-30 | 2021-05-12 | Prioritization | FALSE | 1422 | NA | 1878.2055 | 1878.2055 | 671.3149 | 591.0623 | 332.7495 | 0.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1878.2055 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 636.9459 | 569.7753 | 320.7656 | 0.08758 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1539 | 94A-Trans Line SCADA Switch Program |  |  | NA | Bucket for transmission line SCADA switch upgrades | Transmission Line - Switch | Upgrade/Retrofit | NA | Reliability | SCADA Switch Installation | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 58 | Not Available | Not Available | NA | NA | 5507910 | NA | NA | NA | 94 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | FALSE | NA | NA | 4599.0936 | 4599.0936 | 1.115 | -23.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4599.0936 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 1.2119 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1540 | MIDWAY SUB: T-LINE WORK WITHIN SUB |  |  | Bakersfield, Kern ¦ Buttonwillow CDP, Kern ¦ Greenacres CDP, Kern ¦ Kern ¦ Rosedale CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Termination | NA | 2024-04-09 | 63 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | NA | 230 | NA | 705 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5782605 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-07 | 2022-04-01 | 2023-05-29 | Prioritization | TRUE | 105100 | NA | 9592.6952 | 11861.2422 | 1272.4959 | 642.4049 | 4893.3729 | 1054.2462 | 1715.9264 | 0 | 2268.547 | 0 | 0 | 0 | 0 | 9592.6952 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 8729.2598 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1541 | Midway: Upgrade 230KV Tline Phase 2 |  |  | Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Termination | NA | 2023-11-02 | 57 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | NA | 230 | NA | 705 | Not Available | Not Available | RBPPF - TBD | Yes | 5788381 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-06-30 | 2022-04-01 | 2026-07-16 | Prioritization | FALSE | 105100 | NA | 1.1076 | 2241.4233 | 0 | 0 | 0.1791 | 0.8428 | 0.0755 | 0.0774 | 682.5784 | 0 | 0 | 0 | 0 | 1.0974 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1542 | Midway: Upgrade 230KV Tline Phase 3 |  |  | Bakersfield, Kern ¦ Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Transmission Line - Conductor | Relocate | NA | Reliability | SCADA Switch Installation | NA | 2024-02-01 | 57 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5788382 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-03-30 | 2022-04-01 | 2026-08-21 | Prioritization | TRUE | 105100 | NA | 0 | 4316.7044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1543 | Midway: Upgrade 230KV Tline Phase 4 |  |  | Bakersfield, Kern ¦ Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Transmission Line - Conductor | Relocate | NA | Reliability | SCADA Switch Installation | NA | 2024-02-01 | 57 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5788383 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-06-28 | 2022-04-01 | 2027-12-15 | Prioritization | FALSE | 105100 | NA | 0.2846 | 4087.6607 | 0 | 0 | 0 | 0.2629 | 0.0194 | 0.0196 | 4171.7912 | 0 | 0 | 0 | 0 | 0.2823 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1544 | Midway: Upgrade 230KV Tline Phase 5 |  |  | Bakersfield, Kern ¦ Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Transmission Line - Conductor | Relocate | NA | Reliability | SCADA Switch Installation | NA | 2024-02-01 | 57 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | NA | 230 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5788384 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-12-29 | 2022-04-01 | 2030-05-28 | Prioritization | FALSE | 105100 | NA | 0 | 4196.3266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1545 | SOUTH BUNDLE S-22 |  |  | Merced | Install two new 70 kV SCADA-operable switches at Wright Junction, on the Los Banos – Mercy Springs SW STA 70 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-02-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.92862 | 70 | NA | 58 | Not Available | NA | NA | NA | 5768809 | T.0001214 | South Bundle S-22 | 1 | 94 | 5738883 | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-01 | 2019-02-05 | 2019-04-12 | NA | FALSE | 1345 | NA | 1247.862 | 1247.862 | 538.2237 | 38.8548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.862 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 518.8397 | 37.4554 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1546 | Clay Martell 60kV SCADA |  |  | Amador ¦ Amador City, Amador ¦ Drytown CDP, Amador ¦ Ione, Amador ¦ Martell CDP, Amador ¦ Plymouth, Amador ¦ Sutter Creek, Amador | Phase 1 of this project will replace 6 manually operated switches with SCADA-operable switches on the Valley Springs-Martell No. 1, Valley Springs – Clay, and the Pardee No. 2 Tap 60kV lines. The associated wood poles will be replaced with 4 Tubular Steel Poles (TSP) and 2 Engineered Direct Embedded Poles (EDEP) as required. This project will improve customer electric service reliability by reducing outage durations and allowing greater operational flexibility. Phase 2 of this project will replace 4 manually operated switches with SCADA-operable switches on the Clay - Martell 60kV line. The associated wood poles will be replaced with 3 Fiberglass Poles and one Engineered Direct Embedded Poles (EDEP) as required. The manual switches will be replaced with either Cleveland/Price or SEECO switches. The project is being constructed in 2 phases due to testing required for the new fiberglass pole design. | Transmission Line - Switch | Upgrade/Retrofit | NA | Reliability | SCADA Switch Installation | NA | 2024-04-10 | 50 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5798378 | T.0003024 | ValleySprings-Martell No.2 SCADA | 3 | 94 | NA | 2010 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5801-E | 2020-04-03 | Approved | 2020 | Engineering less than 50% complete | 5 | 2026-11-26 | 2021-10-31 | 2027-01-18 | Prioritization | FALSE | 10500 | NA | 428.1226 | 3455.2411 | 0 | 0 | 0 | 275.5444 | 142.6107 | 35.421 | 0 | 0 | 0 | 0 | 2203 | 418.1551 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ $50 Mil – $75 Mil
| 1547 | Val Springs-Clay60kV, Pardee Tap 5 SCADA |  |  | Amador ¦ Buena Vista CDP, Amador ¦ Calaveras ¦ Ione, Amador | Phase 1 of this project will replace 6 manually operated switches with SCADA-operable switches on the Valley Springs-Martell No. 1, Valley Springs – Clay, and the Pardee No. 2 Tap 60kV lines. The associated wood poles will be replaced with 4 Tubular Steel Poles (TSP) and 2 Engineered Direct Embedded Poles (EDEP) as required. This project will improve customer electric service reliability by reducing outage durations and allowing greater operational flexibility. Phase 2 of this project will replace 4 manually operated switches with SCADA-operable switches on the Clay - Martell 60kV line. The associated wood poles will be replaced with 3 Fiberglass Poles and one Engineered Direct Embedded Poles (EDEP) as required. The manual switches will be replaced with either Cleveland/Price or SEECO switches. The project is being constructed in 2 phases due to testing required for the new fiberglass pole design. | Transmission Line - Switch | Upgrade/Retrofit | NA | Reliability | SCADA Switch Installation | NA | 2023-09-29 | 49 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 58 | Not Available | Not Available | NA | NA | 5792368 | T.0003024 | ValleySprings-Martell No.2 SCADA | 3 | 94 | NA | 2010 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5801-E | 2020-04-03 | Approved | 2020 | Operational | 2 | 2021-12-06 | 2021-10-31 | 2021-12-15 | NA | FALSE | 10500 | NA | 2329.8047 | 2329.8047 | 0 | 19.4643 | 2194.7393 | 134.2638 | -18.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 2329.8047 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 2054.9363 | 124.5199 | -17.3084 | 0 | 0% | NA | NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ $50 Mil – $75 Mil
| 1548 | South Bundle S-15 |  |  | Chualar CDP, Monterey ¦ Gonzales, Monterey ¦ Monterey ¦ Soledad, Monterey | Remove Switch No. 55 on the Gonzales No. 1 Tap Line and add SCADA capability to Switch Nos. 51 and 53 on the Soledad No. 1 Line, Switch No. 29 on the Soledad No. 2 Line, Switch Nos. 67 and 87 on the Gonzales No. 1 Tap Line and Switch No. 25 on the Gonzales No. 2 Tap Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | Not Available | NA | NA | NA | 5526765 | T.0003240 | SOUTH BUNDLE S-15 | 1 | 94 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-24 | 2019-05-30 | 2019-12-13 | Clearances | FALSE | 3239 | NA | 3371.8706 | 3371.8706 | 718.703 | 254.1345 | -0.0143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3371.8706 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 606.4177 | 244.9819 | -0.01374 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1549 | South Bundle S-24 |  |  | Lompoc, Santa Barbara ¦ Santa Barbara | Replace manually operated switch No. 169 on the City No. 2 Tap 115 kV Line at the Lompoc Junction, switch No. 115 on the Manville Tap 115 kV at the Manville Junction, switch No. 149 on the Cabrillo – Santa Ynez SW STA 115 kV at the Manville Junction, switch No. 135 on the Surf Tap 115 kV Line at the Surf Junction, and switch Nos. 137 and 139 on the Divide – Cabrillo No. 1 115 kV Line at the Surf Junction with SCADA-operable switches and Tubular Steel Poles (TSP). | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5526500 | T.0003165 | South Bundle S-24 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-02-14 | 2019-06-30 | 2020-01-27 | Workforce | FALSE | 4140 | NA | 5201.6986 | 5201.6986 | 2212.8518 | 1893.9526 | 0.0053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5201.6986 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 2093.7242 | 1825.7422 | 0.00507 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1550 | South Bundle S-10 |  |  | Monterey, Monterey | Replace manually operated Switch No. 17 on the Del Monte – Monterey 60 kV Line and Switch No. 37 on the Del Monte – Viejo 60 kV Line and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel). Also install a new SCADA operable Switch No. 19 on the Del Monte – Monterey Line at the Navy School tap connection. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5526491 | T.0003156 | South Bundle S-10 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-01-28 | 2018-05-01 | 2020-02-03 | Prioritization | FALSE | 1620 | NA | 1405.064 | 1405.064 | 233.0911 | 803.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1405.064 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 211.4218 | 774.4525 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1551 | North Bundle N-09 |  |  | Butte ¦ Forbestown CDP, Butte ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte | Replace manually operated switch No. 47 on the Garberville – Laytonville 60 kV Line at Bell Springs with SCADA-operable switch and Engineered Direct Embedded Pole (Steel) and add SCADA to existing SCADA-ready switches Nos. 145, 147, and 149 on the Woodleaf – Palermo 115 kV Line at Kanaka Tap. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-04 | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | Not Available | NA | NA | NA | 5526486 | T.0003149 | NORTH BUNDLE N-09 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-10-02 | 2019-08-30 | 2019-11-25 | NA | FALSE | 2020 | NA | 1764.7469 | 1764.7469 | 902.4396 | 506.5279 | -0.3474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1764.7469 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 857.1126 | 488.2854 | -0.33489 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1552 | South Bundle S-25 |  |  | Santa Barbara ¦ Sisquoc CDP, Santa Barbara | Replace manually operated switch Nos. 127 and 129 on the Sisquoc – Santa Ynez Sw Sta 115 kV Line at Palmer Substation with SCADA-operable switches and Tubular Steel Poles (TSP). | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-10 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 180 | Not Available | NA | NA | NA | 5526501 | T.0003166 | South Bundle S-25 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-11-08 | 2018-12-31 | 2019-11-19 | Prioritization | FALSE | 1390 | NA | 1312.6 | 1312.6 | 922.6629 | 5.9076 | 0.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.6 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 875.6219 | 5.6948 | 0.5167 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1553 | NORTH BUNDLE N-13 |  |  | Canyondam CDP, Plumas ¦ Clear Creek CDP, Lassen ¦ East Shore CDP, Plumas ¦ Lassen ¦ Plumas ¦ Westwood CDP, Lassen | Replace manually operated switch Nos. 29, and 37 on the Hat Creek No. 1 – Westwood 60 kV Line, switch No. 27 on the Hat Creek No. 1 – Pit No. 1 60 kV Line and switch Nos. 37, 39, and 97 on the Caribou – Westwood 60 kV Line with SCADA-operable switches and Engineered Direct Embedded Pole (Steel), | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-11 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5772362 | T.0002268 | NORTH BUNDLE N-13 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-05-13 | 2020-04-24 | 2019-02-28 | NA | FALSE | 1300 | NA | 2608.5979 | 2608.5979 | 608.271 | 1084.8833 | 308.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608.5979 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 588.287 | 1045.8115 | 297.1175 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1554 | South Bundle S-18 |  |  | San Luis Obispo | Replace manually operated switch Nos. 57 and 59 on the San Luis Obispo – Cayucos 70 kV Line at Mustang Junction and Switch Nos. 135 and 145 on the Goldtree 115 kV Tap Line at Goldtree Junction with SCADA-operable switches and new steel structures. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-09 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 ¦ 70 | NA | 180 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5526497 | T.0003162 | South Bundle S-18 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-14 | 2020-03-01 | 2020-06-03 | NA | FALSE | 2120 | NA | 2452.5724 | 2452.5724 | 1532.9738 | 303.4495 | 3.5201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2452.5724 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 1455.7003 | 292.5209 | 3.3933 | -0.00018 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1555 | CENTRAL BUNDLE C-02 |  |  | Garden Acres CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel). Seven manually operated transmission line switches (SWITCH 17, SWITCH 19, SWITCH 67, SWITCH 37, SWITCH 65, SWITCH 39, SWITCH 37 with SCADA-operable switches on the Stockton ‘A’ – Weber No. 3, Weber – Mormon Junction, and the Lockeford No. 1 60 kV lines. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-12-20 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5764511 | T.0001521 | CENTRAL BUNDLE C-02 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-10-30 | 2019-11-12 | 2022-03-14 | Prioritization | FALSE | 2727 | NA | 4624.2205 | 4624.2205 | 667.2874 | 194.2171 | 172.7908 | 632.4922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4624.2205 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 652.597 | 187.2224 | 166.5677 | 609.713 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1556 | CENTRAL BUNDLE C-01 |  |  | Healdsburg, Sonoma | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel). There have been several outages on the Monte Rio-Fulton 60 kV line. One of the most recent outages affected over 14,000 customers for over eight hours with a SAIDI contribution of 0.27. Upgrading Wohler JCT SWs 67 and 69, Trenton JCT SW 59 to SCADA-operable switches will significantly reduce the outage duration for this line and customers affected. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-07-10 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5774082 | T.0002753 | CENTRAL BUNDLE C-01 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-01-08 | 2017-10-18 | 2019-02-28 | Prioritization | FALSE | 2940 | NA | 4073.6459 | 4073.6459 | 117.9403 | 510.7282 | 342.7549 | 0.3221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4073.6459 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 5.5143 | 492.3344 | 330.4106 | 0.31053 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1557 | Central Bundle C-17 |  |  | Fulton CDP, Sonoma ¦ Santa Rosa, Sonoma ¦ Sonoma | Replace the Switch Nos. 67 and 69 on Fulton – Molino – Cotati 60 kV Line at Laguna Junction transmission line switch with SCADA-operable switch. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-08 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | 9 | NA | NA | 5526514 | T.0003179 | Central Bundle C-17 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-27 | 2018-12-31 | 2021-05-03 | Prioritization | FALSE | 1660 | NA | 1622.0476 | 1622.0476 | 656.9735 | 59.0405 | 707.5077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1622.0476 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 626.1629 | 56.9142 | 682.027 | -0.00017 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1558 | NORTH BUNDLE N-21 |  |  | Marysville, Yuba ¦ Smartsville CDP, Yuba ¦ Yuba | Replace three manually-operated switches on the Cottonwood #1 and Palermo-Oroville #1 60 kV lines with SCADA-operable switches and install four new SCADA-operable switches on the Cottonwood #2 60 kV Line, with the associated structures replaced with Engineered Direct Embedded Poles (Steel). | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-12-08 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5530512 | T.0004085 | North Bundle N-21 | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-11-16 | 2020-12-31 | 2020-12-21 | NA | FALSE | 5170 | NA | 4255.809 | 4255.809 | 4.3156 | 3948.8488 | 292.3135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4255.809 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 14.6466 | 3948.8488 | 292.3135 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1559 | South Bundle S-16 |  |  | Monterey ¦ Prunedale CDP, Monterey ¦ Salinas, Monterey ¦ Soledad, Monterey | Replace transmission line Switch Nos. 37 and 39 at Gabilan Substation on the Salinas – Lagunitas 60 kV Line and Switch Nos. 117 and 119 at Natividad Junction on the Crazy Horse Canyon – Salinas – Soledad 115 kV Lines with SCADA-operable switches and install new Switch Nos. 127, 129, 137 and 139 at Natividad Junction on the 115 kV lines. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-05-19 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 ¦ 60 | NA | 180 | Not Available | NA | NA | NA | 5526496 | T.0003161 | South Bundle S-16 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-17 | 2018-12-31 | 2019-06-05 | NA | FALSE | 2663 | NA | 4072.5266 | 4072.5266 | 858.4026 | 326.5163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4072.5266 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 723.4905 | 314.7568 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1560 | South Bundle S-28 |  |  | Corcoran, Kings ¦ Kings | Retrofit seven manually operated switches on the Balch-Sanger, Kings River-Sanger-Reedley, Cascade-Cottonwood, and Eagle Rock-Cortina 115kV lines, to be SCADA-operable switches | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-14 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5530369 | T.0004092 | South Bundle S-28 | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-03-18 | 2020-05-31 | 2020-05-06 | NA | FALSE | 3830 | NA | 2341.1204 | 2341.1204 | 5.8421 | 2288.299 | 30.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2341.1204 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 22.5344 | 2225.747 | 29.4672 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1561 | NORTH BUNDLE N-11 |  |  | Butte Valley CDP, Butte | The following work scope is required to complete the North Bundle N-11 project:•Replace manually operated switch Nos. 77 and 79 on the Centerville – Table Mountain – Oroville 60 kV Line at Clark Road Substation with SCADA-operable switches •Install three new SCADA-operable switches on the Centerville – Table Mountain – Oroville 60 kV Line at Miocene Junction•Install new steel structures as required Engineering, procurement and construction will be performed by contract resources. Design oversight and construction safety and quality inspection activities for this project will be performed by PG&E internal resources. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-02-05 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.40715 | 60 | NA | 69 | 3. Emergency Preparedness | NA | NA | NA | 5738847 | T.0000035 | NORTH BUNDLE N-11 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-08 | 2019-05-03 | 2019-02-28 | NA | FALSE | 1835 | NA | 2938.1894 | 2938.1894 | 769.0382 | 1065.7934 | 76.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2938.1894 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 744.5651 | 1027.409 | 73.3554 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1562 | NORTH BUNDLE N-23 |  |  | Arbuckle CDP, Colusa ¦ Colusa ¦ Yolo | The project objective is to replace and install the following structures with new SCADA operable switch structure: • 004/030 SW 317 & SW 327 on the El Dorado-Missouri Flat 1&2 115kV line. • 004/032 SW 319 & SW 329 on the El Dorado-Missouri Flat 1&2 115kV Line. • 010/092A SW 337 & SW 347 on the El Dorado-Missouri Flat 1&2 115kV Line. • 010/095A SW 339 & SW 349 on the El Dorado-Missouri Flat 1&2 115kV Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-20 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530514 | T.0004087 | North Bundle N-23 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-09-17 | 2024-12-15 | 2025-10-03 | Prioritization | TRUE | 154700 | NA | 1853.9176 | 5199.6062 | 10.9955 | 11.8153 | 356.1187 | 1414.8231 | 51.9034 | 2.7312 | 3345.6886 | 0 | 0 | 0 | 3757.8863 | 1851.1864 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 16.526 | 11.8153 | 356.1187 | 1414.8231 | 51.9034 | 2.7312 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1563 | South Bundle S-37 |  |  | Chowchilla, Madera ¦ Fresno ¦ Madera | The project objective is to replace transmission line switch 175 on Sharon Prison Tap with SCADA operable switches as following: (1) To install new SCADA operable switch 175 on str.000/002(new TSP) on Sharon Prison Tap 115 kV line. (2) Remove existing KPF manual switch 175 on str.000/002 and remove existing wood pole str.000/002 on Sharon Prison Tap 115 kV line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-10 | 35 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5548960 | T.0008201 | South Bundle S-37 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-09-19 | 2024-12-15 | 2025-04-03 | NA | TRUE | 154700 | NA | 412.0957 | 3648.3086 | 0 | 0 | 0 | 326.2802 | 83.2155 | 2.6 | 3236.2129 | 0 | 0 | 0 | 280.3217 | 409.4957 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 326.2802 | 83.2155 | -75.4721 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1564 | Central Bundle C-23 |  |  | Alameda ¦ Lathrop, San Joaquin ¦ Manteca, San Joaquin ¦ Ripon, San Joaquin ¦ San Joaquin ¦ Tracy, San Joaquin | The project proposes to replace three manually operated switches and their associated structures, on the Tesla – Stockton Cogen Junction 115 kV Line with SCADA-operable switches and Engineered Direct Embedded Poles (Steel). | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-12-20 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | Not Available | NA | NA | NA | 5526520 | T.0003185 | Central Bundle C-23 | 1 | 94 | NA | 2017 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-05-22 | 2019-06-30 | 2019-12-13 | NA | FALSE | 2000 | NA | 1726.342 | 1726.342 | 959.0021 | 122.105 | 0.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1726.342 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 901.2325 | 117.7073 | 0.1834 | -2e-05 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1565 | NICOLAUS WILKINS SLOUGH SW REPLACEMENT |  |  | East Nicolaus CDP, Sutter ¦ Knights Landing CDP, Yolo ¦ Nicolaus CDP, Sutter ¦ Sutter ¦ Yolo | The purpose of this project is to improve the resistance of this line to failures caused by extreme wind speeds (in excess of 70mph) and to minimize future outages to Wilkins Slough Substation and 4 Reclamation District Substations. This project proposes to relocate/replace 274 wood transmission poles with light duty steel poles on the Nicolaus – Wilkins Slough 60kV Line, and Replace 2 manual switches on the District 1001 tap line. | Transmission Line - Switch | Upgrade/Retrofit | NA | Reliability | SCADA Switch Installation | NA | 2023-11-20 | 74 | NA | Wires - Reconductor/Line Rebuild Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5784327 | T.0003076 | Nicolaus-Wilkins Slough 60kV line Pole | 3 | 94 | NA | 2017 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-06-23 | 2022-10-11 | 2027-07-02 | Prioritization | FALSE | 13482 | NA | 0 | 1559.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12103 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1566 | North Bundle N-19 |  |  | East Quincy CDP, Plumas ¦ Plumas ¦ Quincy CDP, Plumas ¦ Twain CDP, Plumas | This project proposes to replace a total of five manually operated switches with SCADA-operable switches and replace associated existing structures with Engineered Direct Embedded Poles (Steels). The switches include: • Smartville-Marysville 60 kV Line Switch #37 and 39 • Caribou-Plumas Jct 60 kV Line Switch #15, #25, and #95 | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-12 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5530506 | T.0004077 | North Bundle N-19 | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-04-19 | 2020-12-31 | 2021-02-04 | NA | FALSE | 4240 | NA | 3308.2161 | 3308.2161 | 29.0764 | 2924.1054 | 335.2428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3308.2161 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 48.8679 | 2843.6298 | 326.168 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1567 | Central Bundle C-24 |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Manteca, San Joaquin ¦ Murphys CDP, Calaveras ¦ San Joaquin ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | This project proposes to replace a total of seven manually-operated switches with SCADA-operable switches, install one new SCADA-operable switch and replace associated existing structures with Engineered Direct Embedded Poles (Steels). The switches include: Ignacio-Bolinas 60 kV Line Number (No.) 2 Switches (SWs) 25, 27, 29, 57, 59 (SW 25 is new), Valley Springs 60 kV Line No. 1 SW 17, Valley Springs-Martell 60 kV Line No. 1 SW 75 and Valley Springs 60 kV Line No. 2 SW 19. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-09 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5530439 | T.0004062 | Central Bundle C-24 | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-04-15 | 2020-10-31 | 2020-10-26 | NA | FALSE | 5190 | NA | 4430.5256 | 4430.5256 | 79.4083 | 4296.4034 | 43.4024 | 0.2809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4430.5256 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 90.4388 | 4177.6573 | 42.2276 | 0.27332 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1568 | SUMMIT: Repl 60 KV SW 37 & SW Operator |  |  | Nevada | This project proposes to replace Summit Switch No. 37 with a SCADA-operable circuit switcher. | Transmission Line - Switch | Upgrade/Retrofit | NA | Reliability | SCADA Switch Installation | NA | 2024-02-06 | 27 | NA | Wires - Replacement Alternative | $3 Mil -$5 Mil | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 0.028737 | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5736613 | T.0001377 | SUMMIT - SW 37 - SCADA | 1 | 94 | NA | 2006 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2024-01-04 | 2018-08-31 | 2024-05-13 | Project Design | TRUE | 2261 | NA | 2319.8737 | 2511.9439 | 76.0749 | 163.468 | 130.6317 | 145.2111 | 0 | 130.4142 | 61.6561 | 0 | 0 | 0 | 0 | 2319.8737 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1569 | North Bundle N-18 |  |  | Palermo CDP, Butte ¦ Plumas | This project proposes to replace the following four manually operated switches and the associated existing structures with SCADA-operable switches and Engineered Direct Embedded Poles (Steel): • Coleman-Red Bluff 60 kV Line Switch #67 and #69 • Cottonwood #2 60 kV Line Switch #57 and #69 The project will also install four, new SCADA-operable switches mounted on Steel poles: • Cottonwood #2 60 kV Line Switch #59 • Red Bank 60 kV Tap Switch #67 • Bridgeville-Cottonwood 115 kV Line Switch #239 • Cascade-Cottonwood 115 kV Line Switch #137 | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-20 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5530505 | T.0004076 | North Bundle N-18 | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-04-19 | 2020-12-31 | 2021-01-16 | NA | FALSE | 6600 | NA | 4411.0674 | 4411.0674 | 40.2738 | 4041.7954 | 255.1438 | 5.1239 | 49.3054 | 0 | 0 | 0 | 0 | 0 | 0 | 4411.0674 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 59.6988 | 3958.5288 | 249.9641 | 5.0199 | 48.3044 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1570 | Central Bundle C-09 |  |  | Bay Point CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa | This project proposes to replace the following manually operated switch and its existing structures with a SCADA- operable switch and an Engineered Direct Embedded Pole (Steel): Switch No. 57 at Pole No. 06/09 on Christie – Willow Pass 60 kV Line at Stauffer Junction. The project is needed to improve electric transmission service reliability by reducing customer outage minutes for emergency conditions to customers served in Contra Costa County, California. The expected benefit of this program is a reduction of safety risks and improvement in reliability levels on transmission lines prone to outages. The remote control features of SCADA switches will eliminate the need to provide on-site, manual operation. This will reduce traveling safety risks during non-ideal weather conditions and to remote, off-road locations. In parallel, SCADA enables faster fault isolation and restoration possibilities as well as improved clearance planning | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-05 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5526509 | T.0003174 | Central Bundle C-09 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-10-05 | 2019-06-30 | 2020-10-06 | Project Design | FALSE | 790 | NA | 1066.906 | 1066.906 | 314.2854 | 639.9171 | 13.4537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1066.906 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 299.392 | 616.8705 | 12.9692 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1571 | Central Bundle C-10 |  |  | Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma ¦ Yolo | This project proposes to replace the following manually operated switch and its existing structures with a SCADA- operable switch and an Engineered Direct Embedded Pole (Steel): Switch Nos. 27, 37, and 47 at Pole Nos. 33/14, 20/00, and 16/03 on Fulton – Calistoga 60 kV Line at St. Helena Junction. The project is needed to improve electric transmission service reliability by reducing customer outage minutes for emergency conditions to customers served in Napa and Sonoma Counties, California. The expected benefit of this program is a reduction of safety risks and improvement in reliability levels on transmission lines prone to outages. The remote control features of SCADA switches will eliminate the need to provide on-site, manual operation. This will reduce traveling safety risks during non-ideal weather conditions and to remote, off-road locations. In parallel, SCADA enables faster fault isolation and restoration possibilities as well as improved clearance planning | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-10 | NA | NA | Other - Status Quo | NA | Zone 1 - HHZ, Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | 70 | NA | NA | 5526510 | T.0003175 | Central Bundle C-10 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6291-E | 2021-08-10 | Approved | 2021 | Operational | 2 | 2021-11-29 | 2019-12-31 | 2021-12-10 | Prioritization | FALSE | 2240 | NA | 2758.7166 | 2758.7166 | 198.8519 | 382.8894 | 1827.945 | 75.2232 | 4.4951 | 0 | 0 | 0 | 0 | 0 | 0 | 2758.7166 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 181.9911 | 369.0996 | 1762.1118 | 72.5139 | 4.3332 | 0 | 0% | NA | NA | NA | 44% | 56%
| 1572 | Central Bundle C-18 |  |  | Clearlake Oaks CDP, Lake ¦ Colusa ¦ Lake ¦ Lucerne CDP, Lake ¦ Mendocino ¦ Nice CDP, Lake | This project proposes to replace the following manually operated switch and its existing structures with a SCADA- operable switch and an Engineered Direct Embedded Pole (Steel): Switch No. 117 at Pole No. 26/125 on Cortina – Mendocino # 1 115 kV Line at Redbud Junction. The project is needed to improve electric transmission service reliability by reducing customer outage minutes for emergency conditions to customers served in Lake County, California. The expected benefit of this program is a reduction of safety risks and improvement in reliability levels on transmission lines prone to outages. The remote control features of SCADA switches will eliminate the need to provide on-site, manual operation. This will reduce traveling safety risks during non-ideal weather conditions and to remote, off-road locations. In parallel, SCADA enables faster fault isolation and restoration possibilities as well as improved clearance planning. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-12 | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5526515 | T.0003180 | Central Bundle C-18 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-05-16 | 2018-12-31 | 2022-05-19 | Prioritization | FALSE | 1030 | NA | 1095.0949 | 1095.0949 | 152.8931 | 298.3279 | 219.1148 | 381.5897 | -21.1045 | 0 | 0 | 0 | 0 | 0 | 0 | 1095.0949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 145.0719 | 287.5838 | 211.2234 | 367.8468 | -20.3444 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1573 | Central Bundle C-25 |  |  | Calaveras ¦ Linden CDP, San Joaquin ¦ Rancho Calaveras CDP, Calaveras ¦ San Joaquin ¦ Valley Springs CDP, Calaveras | This project proposes to replace the following manually operated switches and existing structures with SCADA- operable switches and Engineered Direct Embedded Poles (Steel): Fort Ross-Gualala 60kV Line Switch Nos. 47 and 49, and Mendocino-Hartley 60kV Line Switch Nos. 17 and 19. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-10 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5530440 | T.0004063 | Central Bundle C-25 | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-11 | 2020-10-31 | 2020-05-28 | NA | FALSE | 3005 | NA | 2298.3071 | 2298.3071 | 24.5969 | 2200.6497 | 57.7483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2298.3071 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 39.9091 | 2140.001 | 56.1852 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1574 | NORTH BUNDLE N-16 |  |  | Bangor CDP, Butte ¦ Butte ¦ Nevada ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte ¦ Yuba | This project proposes to replace the following manually operated switches and its existing structures with a SCADA- operable switches and Engineered Direct Embedded Poles (Steel): Switch Nos. 15, 17 and 19 on the Spaulding – Summit 60 kV Line, at Cisco Grove Junction, Switch No. 19 on the Drum – Grass Valley – Weimar 60 kV Line, at Colfax Junction, and Switch Nos. 15 and 47 on the Drum – Grass Valley – Weimar 60 kV Line, at Shady Glen Substation. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-08 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | 76 | Not Available | NA | NA | NA | 5772363 | T.0002269 | NORTH BUNDLE N-16 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-30 | 2020-03-18 | 2019-02-28 | NA | FALSE | 4198 | NA | 2574.5084 | 2574.5084 | 1202.5826 | -161.6699 | -0.8655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2574.5084 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1164.128 | -155.8474 | -0.8343 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1575 | Central Bundle C-22 |  |  | San Joaquin ¦ Stanislaus ¦ Valley Home CDP, Stanislaus | This project proposes to replace the following manually operated switches and its existing structures with SCADA- operable switches and an Engineered Direct Embedded Poles (Steel): Switch No. 113, at Stockton Junction, on the Tesla – Tracy 115 kV Line, Switch Nos. 117 and 119, at the Stockton Co-gen Junction, on the Stockton ‘A’ – Lockeford – Bellota No. 1 115 kV Line, and Switch No. 169, at Melones Junction, on the Stanislaus – Melones Sw Sta – Riverbank Junction Sw Sta 115 kV Line, and Switch No. 179, at Riverbank Junction, on the Bellota – Riverbank 115 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 9. Reliability (Low Safety Risk) | 611 | RBPPF - TBD | Yes | 5526519 | T.0003184 | Central Bundle C-22 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-11-15 | 2019-06-30 | 2026-02-13 | Prioritization | TRUE | 2386 | NA | 3080.7362 | 3981.3022 | -660.1265 | 708.4316 | 679.7869 | 114.4838 | 56.3819 | 0 | 900.5661 | 0 | 0 | 0 | 1010.2415 | 3080.7362 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2026 | -714.9287 | 682.9175 | 655.3044 | 110.3607 | 54.3513 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1576 | North Bundle N-02 |  |  | Dixon, Solano ¦ Elmira CDP, Solano ¦ Fairfield, Solano ¦ Solano ¦ Vacaville, Solano | This project proposes to replace the following manually operated switches and its existing structures with SCADA- operable switches and Engineered Direct Embedded Pole (Steel): Switch Nos. 27 and 29 on the Dixon – Vaca No. 2 60 kV Line at Dixon Substation, Switch No. 27, on the Dixon – Vaca No. 2 60 kV Line at Travis Junction, and Switch Nos. 47 and 49 on the Dixon – Vaca No. 2 60 kV Line at Vaca Junction. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-15 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5526482 | T.0003143 | North Bundle N-02 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-19 | 2018-12-31 | 2021-05-13 | Prioritization | FALSE | 1895 | NA | 2185.3793 | 2185.3793 | 165.7532 | 276.4124 | 4.1474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2185.3793 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 97.1513 | 266.4574 | 3.998 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1577 | North Bundle N-10 |  |  | Fairfield, Solano ¦ Green Valley CDP, Napa ¦ Green Valley CDP, Solano ¦ Napa ¦ Solano | This project proposes to replace the following manually operated switches and its existing structures with SCADA- operable switches and Engineered Direct Embedded Poles (Steel): Switch Nos. 135 and 137 on the Brighton – Davis 115 kV Line at Barker Slough Junction, Switch Nos. 155, 157 and 159 on the Cordelia No.2 115 kV Tap Line near the Cordelia Pumping Plant. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-19 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5526487 | T.0003152 | North Bundle N-10 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5455-E | 2018-12-26 | Approved | 2019 | Operational | 2 | 2020-03-03 | 2019-03-30 | 2021-03-23 | Prioritization | FALSE | 3298 | NA | 3268.5921 | 3268.5921 | 582.5369 | 1444.2062 | 759.9213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3268.5921 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 544.2003 | 1392.1933 | 732.5527 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56%
| 1578 | North Bundle N-01 |  |  | Dixon, Solano ¦ Elmira CDP, Solano ¦ Fairfield, Solano ¦ Solano ¦ Vacaville, Solano | This project proposes to replace the following manually operated switches and its existing structures with SCADA- operable switches and Engineered Direct Embedded Poles (Steel): Switch Nos. 87 and 89 on the Dixon-Vaca No. 1 60 kV Line at Dixon Canning Junction, Switch No. 19 on the Dixon – Vaca No. 1 60 kV Line at Travis Junction, and Switch Nos. 37, 39, and 59 on the Dixon – Vaca No. 1 60 kV Line at Vaca Junction. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-09 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5526481 | T.0003142 | North Bundle N-01 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-16 | 2018-12-31 | 2020-02-04 | Prioritization | FALSE | 2374 | NA | 2117.0602 | 2117.0602 | 557.9714 | 806.6498 | -321.3684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2117.0602 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 499.2031 | 777.5985 | -309.7944 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1579 | Central Bundle C-26 |  |  | San Joaquin ¦ Stockton, San Joaquin | This project proposes to replace the following manually operated switches and the existing structures with SCADA- operable switches mounted on Engineered Direct Embedded Poles (Steel): Ignacio-Alto-Sausalito No. 1 60 kV Line Switch Nos. 67 and 69, Ignacio-Bolinas No. 1 60 kV Line Switch Nos. 47 and 49, and Christie-Willow Pass 60 kV Line Switch Nos. 47 and 59. The project will also install two, new SCADA-operable switches mount on Steel poles: Ignacio-Alto-Sausalito No. 2 60 kV Line Switch Nos. 84 and 85. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-07 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5530441 | T.0004064 | Central Bundle C-26 | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6186-E | 2021-05-04 | Approved | 2022 | Operational | 2 | 2020-10-06 | 2020-12-31 | 2022-08-12 | Prioritization | TRUE | 5650 | NA | 13971.8927 | 14361.8927 | 50.5112 | 2234.6679 | 1557.5436 | 7014.2463 | 3070.2906 | 416.6659 | 0 | 0 | 0 | 0 | 0 | 13945.2268 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 68.4783 | 2172.3243 | 1515.3825 | 6824.3788 | 2987.1812 | 40.1329 | 0% | NA | NA | NA | 0% | 100%
| 1580 | NORTH BUNDLE N-08 |  |  | Anderson, Shasta ¦ Cottonwood CDP, Shasta ¦ Redding, Shasta ¦ Shasta | This project proposes to replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel): Anderson Substation SWs 17 and 19, Girvan Substation SWs 47 and 49, and Oregon Trail Substation SWs 147 and 149. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-09 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 ¦ 60 | NA | 76 | Not Available | NA | NA | NA | 5772360 | T.0002266 | NORTH BUNDLE N-08 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-12-06 | 2020-04-27 | 2019-04-07 | NA | FALSE | 2127 | NA | 3015.911 | 3015.911 | 885.8159 | 496.593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3015.911 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 859.0806 | 478.7083 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1581 | NORTH BUNDLE N-07 |  |  | Cottonwood CDP, Shasta | This project proposes to replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel): Coleman Hatchery SW 65, Hamilton JCT SWs 27 and 29, Loomis JCT SW 49 and 59 and Wintu JCT SWs 37 and 39. In addition this project proposes to add two SWs (approximately close to structure 0/18 and 1/21) on the Coleman-Cottonwood 60 kV line close to Coleman-Hatchery 60 kV tap line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 26.1945 | 60 | NA | 180 | 1. Work that prevents fire ignition | NA | NA | NA | 5772867 | T.0002402 | NORTH BUNDLE N-07 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-04-10 | 2019-12-09 | 2019-02-28 | NA | FALSE | 2664 | NA | 3454.9414 | 3454.9414 | -8.7989 | 867.5629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3454.9414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | -0.28982 | 836.3178 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1582 | SOUTH BUNDLE S-29 |  |  | Fresno ¦ Sanger, Fresno | This project proposes to replace the following three manually operated switches and the associated existing structures with SCADA-operable switches mounted on Engineered Direct Embedded Poles (Steel): • Balch-Sanger 115 kV Line Switch #127, #129, and #147 The project will also install the following four new SCADA-operable switches mounted on Steel poles: • Divide-Cabrillo #2 115 kV Line Switch #127 and #129 • One new switch on the Kings River-Sanger-Reedley 115 kV Line at Piedra Junction • One new switch on the Exchequer-Yosemite 70 kV Line near Saxon Creek Tap | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-15 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5530374 | T.0004097 | South Bundle S-29 | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-20 | 2020-12-31 | 2021-07-19 | Prioritization | FALSE | 5370 | NA | 4176.1264 | 4176.1264 | 7.1394 | 3445.0504 | 711.0113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4176.1264 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 20.0647 | 3378.0527 | 697.264 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1583 | NORTH BUNDLE N-20 |  |  | Cameron Park CDP, El Dorado ¦ Diamond Springs CDP, El Dorado ¦ El Dorado ¦ El Dorado Hills CDP, El Dorado ¦ Folsom, Sacramento ¦ Shingle Springs CDP, El Dorado | This project proposes to replace the following two manually operated switches and the associated existing structures with SCADA-operable switches mounted on Engineered Direct Embedded Poles (Steel): • Maple Creek-Hoopa 60 kV Line Switch #17 • Kilarc-Cedar Creek 60 kV Line Switch #29 The project will also install five, new SCADA-operable switches mounted on Steel poles: • Hat Creek #1-Westwood 60 kV Line Switch #17, #19, #27 and #39 • Garberville-Laytonville 60 kV Line Switch north of Kekawaka Tap | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2022-09-30 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5530510 | T.0004082 | North Bundle N-20 | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-06 | 2020-11-30 | 2021-04-21 | NA | FALSE | 5590 | NA | 4034.2098 | 4034.2098 | 10.9955 | 3882.4391 | 130.7238 | 1.6166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4034.2098 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 19.4303 | 3847.2331 | 129.5444 | 1.6021 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1584 | Central Bundle C-27 |  |  | French Camp CDP, San Joaquin ¦ Lathrop, San Joaquin ¦ Manteca, San Joaquin ¦ San Joaquin | This project proposes to retrofit the following manually operated switches to be SCADA-operable switches: Santa Rosa-Corona 115 kV Line Switch Nos.127, 129, 147, and 149 and add two (2) new SCADA-operable switches on the Cortina-Mendocino No. l 115 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-12-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530442 | T.0004065 | Central Bundle C-27 | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2020-10-29 | 2020-12-31 | 2026-09-18 | Prioritization | TRUE | 4670 | NA | 4890.4989 | 5381.8649 | 45.2006 | 2546.3342 | 1213.0014 | 1061.8977 | 14.1841 | 0 | 491.366 | 0 | 0 | 0 | 546.5336 | 4890.4989 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 55.0814 | 2499.3894 | 1191.1117 | 1042.7348 | 13.9281 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1585 | North Bundle N-12 |  |  | Keddie CDP, Plumas ¦ Paxton CDP, Plumas ¦ Plumas ¦ Quincy CDP, Plumas ¦ Twain CDP, Plumas | This project will reduce safety risk, improve service reliability and provide additional transmission capacity for the customers served by the Caribou Power House Substation by providing remote sectionalizing capability to the Caribou No. 2 60 kV Line. This project will also reduce the duration of momentary and sustained outages for the customers served by the Caribou No. 2 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-12 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | 180 | Not Available | NA | NA | NA | 5526488 | T.0003153 | North Bundle N-12 | 1 | 94 | NA | 2017 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-27 | 2018-11-30 | 2019-11-27 | Prioritization | FALSE | 1490 | NA | 1817.3352 | 1817.3352 | 844.6039 | 393.0654 | -77.4108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1817.3352 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 790.521 | 378.9092 | -74.6228 | 0 | 0 | 0 | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1586 | Gold Hill Sub: Install 230kV Tline work |  |  | Folsom, Sacramento ¦ Granite Bay CDP, Placer ¦ Granite Bay CDP, Sacramento ¦ Orangevale CDP, Sacramento ¦ Roseville, Placer ¦ Sacramento | This project will replace 230kV circuit breakers 212, 222, 242, 252, 712 and associated equipment at Gold Hill Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Termination | NA | 2021-11-18 | 58 | NA | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 230 | NA | 80 | Not Available | Not Available | NA | NA | 5790353 | T.0000466 | GOLD HILL: REPL CBS 252,212,222,242,712 | 5 | 94 | NA | 2011 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-10-15 | 2020-12-18 | 2022-03-30 | Prioritization | FALSE | 10585 | NA | 1329.9296 | 1329.9296 | 0 | 820.5106 | 84.5325 | 424.8834 | 0.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 1329.9296 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1329.9264 | 0.00312 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1587 | Ashlan: Reroute 230kV T-Lines |  |  | Fresno, Fresno | This project will upgrade the existing 230kV bus from looped design to a ring bus design as well as install an MPAC building and upgrade protection at Ashlan, Herndon, Gregg, and Figarden substations. These upgrades will improve reliability, safety, and maintenance at Ashlan substation and the 230kV protection in the local area. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Line Termination | NA | 2023-11-16 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | 270 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5776978 | T.0002362 | Ashlan Ave 230kV Bus Reliability | 7 | 94 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-01-22 | 2019-04-10 | 2020-03-24 | Project Design | FALSE | 40900 | NA | 2124.8942 | 2124.8942 | 819.0642 | 179.651 | 4.1697 | 0.5922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2124.8942 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 2087.514 | 4.0998 | 0.58231 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1588 | HERNDON-MANCHESTER 115KV OPGW |  |  | Fresno, Fresno ¦ Madera ¦ Old Fig Garden CDP, Fresno | This project will upgrade the existing 230kV bus from looped design to a ring bus design as well as install an MPAC building and upgrade protection at Ashlan, Herndon, Gregg, and Figarden substations. These upgrades will improve reliability, safety, and maintenance at Ashlan substation and the 230kV protection in the local area. | Transmission Line - Other Equipment | Upgrade/Retrofit | NA | Reliability | SCADA Switch Installation | NA | 2023-11-17 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 270 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5779821 | T.0002362 | Ashlan Ave 230kV Bus Reliability | 7 | 94 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5310-E | 2018-06-13 | Approved | 2018 | Operational | 2 | 2019-08-12 | 2019-04-08 | 2020-04-08 | Workforce | FALSE | 40900 | NA | 7224.675 | 7224.675 | 5962.7096 | 887.3967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7224.675 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2024 | 0 | 7170.8974 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1589 | Kern PP 115kV Tline |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Transmission Line - Switch | Upgrade/Retrofit | T.0000204 | Reliability | SCADA Switch Installation | NA | 2024-04-12 | 34 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 37.7504 | 115 | NA | 705 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5771732 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-03-08 | 2022-10-12 | 2025-06-02 | Prioritization | TRUE | 77400 | NA | 7146.3102 | 14534.3911 | 46.5077 | 1516.0921 | 1591.0401 | 2301.9607 | 808.563 | 4066.7426 | 3396.4065 | 0 | 0 | 0 | 0 | 7071.2421 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil
| 1590 | Kern PP 115kV Tline Reroute Phase 3 |  |  | Bakersfield, Kern ¦ Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Transmission Line - Conductor | Upgrade/Retrofit | T.0000204 | Reliability | Line Termination | NA | 2024-02-01 | 72 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | NA | 115 | NA | 705 | Not Available | Not Available | RBPPF - TBD | Yes | 5788178 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-05-01 | 2022-10-12 | 2026-07-23 | Prioritization | FALSE | 77400 | NA | 7.147 | 2730.2276 | 0 | 0 | 2.1524 | 4.4873 | 0.4334 | 353.0574 | 1181.7601 | 1700.6274 | 0 | 0 | 0 | 7.0731 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil
| 1591 | Kern PP 115kV Tline Reroute Phase 4 |  |  | Bakersfield, Kern ¦ Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Transmission Line - Conductor | Upgrade/Retrofit | T.0000204 | Reliability | Line Termination | NA | 2024-02-01 | 72 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | NA | 115 | NA | 705 | Not Available | Not Available | RBPPF - TBD | Yes | 5788179 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-05-25 | 2022-10-12 | 2027-07-29 | Prioritization | FALSE | 77400 | NA | 4.8044 | 4891.1462 | 0 | 0 | 3.3038 | 0.2028 | 0.223 | 1.3673 | 0.2956 | 3035.9988 | 1665.4537 | 0 | 0 | 3.7295 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil
| 1592 | NORTH BUNDLE N-22 |  |  | Allendale CDP, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Yolo | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: BRUNSWICK #1 TAP 115 kV (SW 315) BRUNSWICK #2 TAP 115 kV (SW 325) COLGATE-ALLEGHANY 60 kV (SW 75) DRUM-GRASS VALLEY-WEIMAR 115 kV (SW 27 & 29) DRUM-HIGGINS 115 kV (SW 127) DRUM-RIO OSO #1 115 kV (SW 317 & 319) DRUM-RIO OSO #2 115 kV (SW 327 & 329) DRUM-SPAULDING 60 kV (SW 47 & 49) DUTCH FLAT #2 TAP 115 kV (SW 129) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-14 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530513 | T.0004086 | North Bundle N-22 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-07-26 | 2023-04-11 | 2026-09-18 | Prioritization | TRUE | 154700 | NA | 3502.0064 | 6239.696 | 4.4667 | 27.6842 | 1904.648 | 1257.5346 | 294.7781 | 31.371 | 2617.8239 | 0 | 0 | 0 | 4923.4109 | 3498.9644 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 14.3195 | 27.6842 | 1710.9579 | 1132.4111 | 265.448 | 28.4511 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1593 | NORTH BUNDLE N-26 |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: CLOVER CREEK TAP 115 kV (SW 25) KILARC-CEDAR CREEK 115 kV (SW 27) Trinity-Cottonwood 115 kV (2 New SWs) VOLTA-DESCHUTES 60 kV (SW 51, 57, & 59) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-01 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530517 | T.0004090 | North Bundle N-26 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2024-11-25 | 2022-03-21 | 2025-12-26 | Prioritization | TRUE | 154700 | NA | 3252.0761 | 4435.1533 | 10.9955 | 20.5594 | 1781.9137 | 1426.0494 | 6.6786 | 28.329 | 1154.7482 | 0 | 0 | 0 | 1287.0999 | 3252.0761 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 16.8751 | 20.5594 | 1781.9137 | 1426.0494 | 6.6786 | 28.3291 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1594 | NORTH BUNDLE N-27 |  |  | Auburn, Placer ¦ North Auburn CDP, Placer ¦ Placer | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: CORDELIA #2 TAP 60 kV (SW 17) TULUCAY-NAPA #1 115 kV (SW 19) VACA-SUISUN 115 kV (177 & 179) VACA-SUISUN-JAMESON 115 kV (SW 167 & 169) VACA-VACAVILLE-CORDELIA 115 kV (SW 137 & 139) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-22 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530518 | T.0004091 | North Bundle N-27 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2025-03-03 | 2022-08-08 | 2025-12-26 | Prioritization | TRUE | 154700 | NA | 1239.9439 | 2336.7661 | 16.5293 | 5.7582 | 93.9775 | 1055.7685 | 62.619 | 28.4393 | 1068.4932 | 0 | 0 | 0 | 1312.431 | 1239.8336 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 21.7105 | 5.7582 | 93.9775 | 1055.7685 | 62.619 | 28.4512 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1595 | North Bundle N-24 |  |  | Chester CDP, Plumas ¦ East Shore CDP, Plumas ¦ Plumas | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: DRUM-SUMMIT #1 115 kV (SW 139) DRUM-SUMMIT #2 115 kV (SW 239) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-02 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530515 | T.0004088 | North Bundle N-24 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-07-31 | 2022-09-08 | 2025-11-13 | Prioritization | TRUE | 154700 | NA | 710.8612 | 1457.7774 | 10.9955 | 11.0498 | 102.7599 | 536.1481 | 40.2499 | 2.6 | 746.9163 | 0 | 0 | 0 | 842.7066 | 708.2612 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 18.0535 | 11.0498 | 102.7599 | 536.1481 | 40.2499 | 2.6669 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1596 | CENTRAL BUNDLE C-32 |  |  | Mendocino ¦ Sea Ranch CDP, Mendocino ¦ Sea Ranch CDP, Sonoma ¦ Sonoma ¦ Timber Cove CDP, Sonoma | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: ELK-GUALALA 60 kV (SW 69) FULTON-HOPLAND 60 kV (SW 47, 55, 57, & 89) WINDSOR-FITCH MOUNTAIN 60 kV (SW 67, 69, 77, & 87) GEYSERS #3-CLOVERDALE 115 kV (SWs 157 & 159) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530501 | T.0004071 | Central Bundle C-32 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2022-07-07 | 2023-04-28 | 2026-09-21 | Prioritization | TRUE | 154700 | NA | 1893.5648 | 5677.1581 | 26.4518 | 4.0572 | 248.6214 | 1604.9242 | -51.5113 | 81.6189 | 1535.2941 | 0 | 0 | 0 | 4185.3683 | 1840.2749 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 34.1834 | 4.0572 | 248.6214 | 1604.9242 | -51.5113 | 81.6279 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1597 | CENTRAL BUNDLE C-45 |  |  | Fresno ¦ Sanger, Fresno | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: FULTON-PUEBLO 115 kV (SW 135, 145, & 177) EAGLE ROCK-FULTON-SILVERADO 115 kV (SW 157, 167, & 177) IONE TAP 60 kV (SW 29) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-15 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530375 | T.0004098 | Central Bundle C-45 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-12-18 | 2022-09-08 | 2026-01-05 | Prioritization | TRUE | 154700 | NA | 1183.4923 | 4678.5091 | 11.0439 | 10.3562 | 343.2171 | 645.294 | 167.605 | 2.6 | 1365.6346 | 0 | 0 | 0 | 2180.4237 | 1180.8923 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 ¦ 2027 | 14.42 | 10.3562 | 343.2171 | 645.294 | 167.605 | 2.6 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1598 | North Bundle N-31 |  |  | Humboldt ¦ Junction City CDP, Trinity ¦ Trinity ¦ Weaverville CDP, Trinity | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: JANES CREEK TAP 60 kV (SW 71) BRIDGEVILLE-COTTONWOOD 115 kV (SW 237) TRINITY-MAPLE CREEK 60 kV (SW 67 & 69) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-11 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 ¦ 60 | NA | 180 | Not Available | Not Available | RBPPF - TBD | Yes | 5541984 | T.0006523 | North Bundle N-31 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (over 75%) | 3 | 2022-04-19 | 2022-03-18 | 2025-12-26 | Prioritization | TRUE | 154700 | NA | 2250.5383 | 2278.1133 | 0 | 13.1642 | 283.5755 | 1888.4175 | 65.3758 | 0.0052 | 0 | 0 | 0 | 0 | 808.4898 | 2250.5331 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 296.7397 | 1888.4175 | 65.3758 | 0.00782 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1599 | CENTRAL BUNDLE C-30 |  |  | Alameda ¦ Contra Costa | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: MONTA VISTA-BURNS 60 kV (SW 27) PERMANENTE #2 TAP 60 kV (SW 39) PERMANENTE #1 TAP 60 kV (SW 47) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-09-28 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530445 | T.0004069 | Central Bundle C-30 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-11-18 | 2023-02-16 | 2025-12-03 | Prioritization | TRUE | 154700 | NA | 383.1438 | 2829.6822 | 31.8583 | -9.3679 | 57.2326 | 254.2546 | 38.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 383.1438 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 ¦ 2026 ¦ 2027 | 43.0028 | -9.3679 | 57.2326 | 254.2546 | 38.0217 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1600 | NORTH BUNDLE N-25 |  |  | Shasta | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: PALERMO-OROVILLE #2 60 kV (SW 47 & 65) PALERMO-OROVILLE #1 60 kV (SW 39) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-05 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530516 | T.0004089 | North Bundle N-25 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2025-12-24 | 2022-05-31 | 2025-12-26 | Prioritization | TRUE | 154700 | NA | 1315.9609 | 2011.839 | 11.3853 | 39.6276 | 178.7571 | 1028.001 | 50.7055 | 0.3205 | 693.3881 | 0 | 0 | 0 | 765.4656 | 1315.6404 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 18.5492 | 39.6276 | 178.7571 | 1028.001 | 50.7055 | 0.32313 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1601 | CENTRAL BUNDLE C-31 |  |  | Contra Costa ¦ El Cerrito, Contra Costa ¦ El Sobrante CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Pinole, Contra Costa ¦ Richmond, Contra Costa ¦ Rodeo CDP, Contra Costa | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: Pine Grove Tap 60 kV (SW 25) Beardsley Tap 115 kV (SW 139) Donnells-MiWuk 115 kV (SW 137) Melones-Curtis 115 kV (SWs 147, 149, & 137) Fulton-Molino-Cotati 60 kV (SW 15 & 2 new SWs) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-11 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather, Heat Wave |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530499 | T.0004070 | Central Bundle C-31 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-01-13 | 2023-04-11 | 2026-03-11 | Prioritization | TRUE | 154700 | NA | 858.4897 | 5844.4095 | 0.0483 | 0.6028 | 382.325 | 621.1282 | -166.286 | 10 | 4760.7139 | 0 | 0 | 0 | 5497.058 | 848.4897 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 10.7197 | 0.60279 | 382.325 | 621.1282 | -166.286 | 19.1126 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1602 | Central Bundle C-28 |  |  | Dogtown CDP, San Joaquin ¦ Lockeford CDP, San Joaquin ¦ Lodi, San Joaquin ¦ San Joaquin ¦ Thornton CDP, San Joaquin ¦ Woodbridge CDP, San Joaquin | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: SILVERADO-FULTON JCT 115 kV (SW 165, 187, & 189) FULTON-PUEBLO 115 kV (SW 117, 137, 155, & 179) EAGLE ROCK-FULTON-SILVERADO 115 kV (SW 129) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-18 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530443 | T.0004066 | Central Bundle C-28 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-01-14 | 2023-01-27 | 2026-01-29 | Prioritization | TRUE | 154700 | NA | 1880.1456 | 4934.9529 | 67.2583 | -9.8454 | 370.317 | 1351.1885 | 78.3205 | 2.6 | 1983.4522 | 0 | 0 | 0 | 0 | 1877.5456 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 87.565 | -9.8454 | 370.317 | 1351.1885 | 78.3205 | 2.6 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1603 | SOUTH BUNDLE S-30 |  |  | Kern ¦ South Taft CDP, Kern ¦ Taft, Kern | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: WISHON-SAN JOAQUIN #3 70 kV (SW 27 & 29) OAKHURST TAP 115 kV (SW 159) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-03 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 70 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530378 | T.0004101 | South Bundle S-30 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-09-16 | 2024-12-15 | 2027-03-05 | Prioritization | TRUE | 154700 | NA | 1028.3791 | 1573.4065 | 11.0439 | 12.1851 | 137.9343 | 952.0396 | -93.2128 | 2.6014 | 225.6742 | 0 | 0 | 0 | 331.6407 | 1025.7777 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 16.8314 | 12.1851 | 137.9343 | 952.0396 | -120.9808 | 2.5642 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1604 | North Bundle N-29 |  |  | Butte ¦ Forbestown CDP, Butte ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: WOODLEAF-PALERMO 115 kV (SW 137) Sly Creek Tap 115 kV (SW 117) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-04 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541982 | T.0006521 | North Bundle N-29 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 3 | 2025-02-26 | 2022-01-21 | 2025-12-26 | Prioritization | TRUE | 154700 | NA | 829.7524 | 1500.5995 | 0 | 0 | 67.8142 | 650.764 | 108.5742 | 2.6 | 670.8471 | 0 | 0 | 0 | 836.0833 | 827.1524 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 67.8232 | 631.3037 | 105.6351 | 2.5296 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1605 | South Bundle S-36 |  |  | Fresno ¦ Sanger, Fresno | Wave 3 Transmission Line SCADA Switch Program: Replace SWs 135 & 145 with SCADA SWs on ARVIN EDISON TAP 115 kV Line | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-15 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5542001 | T.0006542 | South Bundle S-36 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-01-22 | 2024-12-15 | 2026-02-06 | Prioritization | TRUE | 154700 | NA | 676.3789 | 1632.4858 | 0 | 0 | 31.9222 | 504.6422 | 137.2145 | 2.6 | 880.0125 | 0 | 0 | 0 | 1014.3597 | 673.7789 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 0 | 522.0401 | 133.5002 | 2.5296 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1606 | Central Bundle C-29 |  |  | Fremont, Alameda ¦ Milpitas, Santa Clara ¦ San Jose, Santa Clara | Wave 3 Transmission Line SCADA Switch Program: Replace SWs 199, 137, & 139 with SCADA SWs on SAN JOSE B-STONE-EVERGREEN 115 kV line. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2020-08-07 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 180 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5530444 | T.0004068 | CENTRAL BUNDLE C-29 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-05-06 | 2023-04-19 | 2026-05-22 | Prioritization | TRUE | 154700 | NA | 570.7873 | 2257.0233 | 70.5665 | 30.2411 | 310.3838 | 107.2813 | 22.9129 | 0 | 1535.7811 | 0 | 0 | 0 | 279.151 | 570.7873 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 99.9683 | 30.2411 | 310.3838 | 107.2813 | 22.9129 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1607 | Central Bundle C-33 |  |  | Mendocino ¦ Sea Ranch CDP, Mendocino ¦ Sea Ranch CDP, Sonoma ¦ Sonoma ¦ Timber Cove CDP, Sonoma | Wave 3 Transmission Line SCADA Switch Program: Replace SWs 355 & 365 with SCADA SWs on Monticello PH 115 kV Tap | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530500 | T.0004072 | Central Bundle C-33 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-04-02 | 2023-02-22 | 2026-04-02 | Prioritization | TRUE | 154700 | NA | 618.5884 | 1202.8009 | 50.8855 | -12.0646 | 140.7289 | 414.062 | 12.99 | 0 | 574.0725 | 0 | 0 | 0 | 661.9466 | 618.5884 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2026 | 62.8722 | -12.0646 | 140.7289 | 414.062 | 12.99 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1608 | South Bundle S-33 |  |  | Kern ¦ Lebec CDP, Kern | Wave 3 Transmission Line SCADA Switch Program: Replace SWs 47 & 69 with SCADA SWs on TEJON-LEBEC 70 kV Line | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-09 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541998 | T.0006539 | South Bundle S-33 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-08-12 | 2024-12-15 | 2025-12-17 | Prioritization | TRUE | 154700 | NA | 432.8035 | 1248.718 | 0 | 0.6378 | 72.8251 | 318.7319 | 40.6086 | 0 | 599.5614 | 0 | 0 | 0 | 0 | 432.8035 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 ¦ 2026 | 0 | 0 | 71.4744 | 310.1042 | 39.5094 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1609 | CENTRAL BUNDLE C-36 |  |  | Fort Bragg, Mendocino ¦ Mendocino ¦ Redwood Valley CDP, Mendocino ¦ Willits, Mendocino | Wave 3 Transmission Line SCADA Switch Program: Replace SWs 85, 87, & 89 with SCADA SWs on MENDOCINO-WILLITS-FORT BRAGG 60 kV Line & SW 17 for Laytonville-Willits 60 kV Line | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-11 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530504 | T.0004075 | Central Bundle C-36 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2022-08-12 | 2022-07-06 | 2026-04-29 | Prioritization | TRUE | 154700 | NA | 936.3187 | 1545.3396 | 25.2552 | 7.6366 | 48.8387 | 832.017 | 12.5727 | 28.329 | 539.4934 | 0 | 0 | 0 | 603.8655 | 936.3187 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 35.2537 | 7.6366 | 48.8387 | 832.017 | 12.5727 | 4.7081 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1610 | CENTRAL BUNDLE C-35 |  |  | Lake ¦ Mendocino | Wave 3 Transmission Line SCADA Switch Program: • Retrofit existing structure 006/128 SW 17 on Cordelia Tap #2 60 kV line to be SCADA operable. • Replace existing structure 006/015 SW 19 on Tulucay-Napa #1 60 kV line with a SCADA operable switch structure. • Retrofit existing structure 001/011C 3-Way SW 155, 157, & 159 on Mission Power Tap 115kV and Geyers #3-Cloverdale 115kV lines to be SCADA operable. • Replace existing structure 004/097 SW 39 on Palermo-Oroville #1 60 kV line with a SCADA operable switch structure. • Replace existing structure 005/126 SW 27 on Kilarc-Cedar Creek 60 kV line with a SCADA operable switch structure. • 004/036 SW 327 (New) on the Trinity-Cottonwood 115 kV line • 004/038 SW 329 (New) on the Trinity-Cottonwood 115 kV line • 003/093 SW 39 on the Colgate-Allegany 60kV line • 003/089 SW 47 on the Colgate-Grass Valley 60 kV line • 008/212 SW 47 on the Drum-Spaulding 60 kV line • 008/214 SW 49 on the Drum-Spaulding 60 kV line | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-05 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | NA | NA | 5530503 | T.0004074 | Central Bundle C-35 | 1 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-06-01 | 2021-11-15 | 2021-11-15 | NA | FALSE | 154700 | NA | 6784.8662 | 6784.8662 | 25.6831 | -2.7361 | 6716.3922 | 38.0746 | -0.0005 | 0 | 0 | 0 | 0 | 0 | 0 | 6784.8662 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 33.1359 | -2.7361 | 6533.7653 | 37.044 | -0.00049 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1611 | CENTRAL BUNDLE C-39 |  |  | Meridian CDP, Sutter ¦ Sutter ¦ Sutter CDP, Sutter ¦ Yuba City, Sutter | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: BELLOTA-RIVERBANK-MELONES SW STA 115 kV (SW 157 & 159) STANISLAUS-MELONES SW STA-MANTECA #1 115 kV (SW 147 & 149) STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA 115 kV (SW 165) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-27 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530509 | T.0004080 | Central Bundle C-39 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-01-27 | 2024-12-15 | 2026-04-13 | Prioritization | FALSE | 149600 | NA | 47.0345 | 2699.391 | 20.971 | 5.4897 | 7.3547 | 2.6558 | 0 | 0 | 573.8885 | 0 | 0 | 0 | 0 | 47.0345 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2026 | 31.5342 | 5.4897 | 7.3547 | 2.6558 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1612 | North Bundle N-36 |  |  | East Quincy CDP, Plumas ¦ Plumas ¦ Quincy CDP, Plumas ¦ Twain CDP, Plumas | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: CARIBOU-PLUMAS JCT 60 kV (SW 65, 69, 79, & 91) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541989 | T.0006528 | North Bundle N-36 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-06-12 | 2024-12-15 | 2025-06-12 | NA | FALSE | 149600 | NA | 13.0367 | 2185.3375 | 0 | 0 | 10.3809 | 2.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0367 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 ¦ 2026 | 0 | 0 | 10.3809 | 2.6558 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1613 | CENTRAL BUNDLE C-38 |  |  | Arcata, Humboldt ¦ Humboldt ¦ Indianola CDP, Humboldt ¦ Manila CDP, Humboldt ¦ Samoa CDP, Humboldt | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: Christie-Franklin #1 60 kV (SW 57 & 59) OLEUM-G #1 115 kV (SW 117 & 119) OLEUM-G #2 115 kV (SW 127 & 129) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-21 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530508 | T.0004079 | Central Bundle C-38 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-11-23 | 2024-12-15 | 2026-12-08 | Prioritization | FALSE | 149600 | NA | 83.9328 | 3296.5333 | 8.4942 | 48.0825 | 7.6406 | 7.7383 | 0 | 0 | 942.2179 | 0 | 0 | 0 | 0 | 83.9328 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2026 | 20.4713 | 48.0825 | 7.6406 | 7.7383 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1614 | North Bundle N-34 |  |  | Corning, Tehama ¦ Cottonwood CDP, Shasta ¦ Gerber CDP, Tehama ¦ Las Flores CDP, Tehama ¦ Proberta CDP, Tehama ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: COLEMAN-RED BLUFF 60 kV (SW 69) COTTONWOOD #1 60 kV (SW 3, 15, & 59) ORO FINO TAP 60 kV (SW 25) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-18 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541987 | T.0006526 | North Bundle N-34 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-04-04 | 2024-12-15 | 2025-04-04 | NA | FALSE | 149600 | NA | 410.1534 | 2512.2293 | 0 | 0.4385 | 108.9524 | 293.7463 | 7.0161 | 0 | 0 | 0 | 0 | 0 | 0 | 410.1534 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 ¦ 2026 | 0 | 0 | 109.391 | 293.7463 | 7.0161 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1615 | North Bundle N-39 |  |  | Colusa ¦ Colusa, Colusa ¦ Princeton CDP, Colusa ¦ Williams, Colusa | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: CORTINA #4 60 kV (SW 19 & 27) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-12-20 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541992 | T.0006533 | North Bundle N-39 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-06-26 | 2024-12-15 | 2025-07-14 | Prioritization | FALSE | 149600 | NA | 14.1366 | 1008.9938 | 0 | 0 | 7.7807 | 6.3559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.1366 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 ¦ 2026 | 0 | 0 | 7.7807 | 6.3559 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1616 | North Bundle N-33 |  |  | Auburn, Placer ¦ Folsom, Sacramento ¦ Granite Bay CDP, Placer ¦ Placer | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: FLINT TAP 115 kV (SW 115 & 125) HALSEY-PLACER 60 kV (SW 49) PLACER-GOLD HILL #1 115 kV (SW 117, 119, 337, & 339) PLACER-GOLD HILL #2 115 kV (127, 129, 347, & 349) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-03 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 ¦ 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541986 | T.0006525 | North Bundle N-33 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-06-11 | 2024-12-15 | 2025-06-11 | NA | TRUE | 149600 | NA | 14.9138 | 6907.2788 | 0 | 0.4385 | 9.4754 | 4.9999 | 0 | 0 | 3720.5754 | 0 | 0 | 0 | 0 | 14.9138 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 9.9139 | 4.9999 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1617 | North Bundle N-41 |  |  | Cassel CDP, Shasta ¦ Shasta | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: HAT CREEK #1-PIT #1 60 kV (SW 69) PIT #3-PIT #1 230 kV (SW 217 & 219) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-11 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 230 ¦ 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541994 | T.0006535 | North Bundle N-41 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-04-25 | 2024-12-15 | 2025-04-25 | NA | TRUE | 149600 | NA | 12.3635 | 2699.9759 | 0 | 0 | 7.7057 | 4.6578 | 0 | 0 | 1620.575 | 0 | 0 | 0 | 0 | 12.3635 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 7.7057 | 4.6578 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1618 | South Bundle S-31 |  |  | Clovis, Fresno ¦ Fresno | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: KERCKHOFF-CLOVIS-SANGER #1 115 kV (SW 137, 139, 155, 157, 159, & 335) KERCKHOFF-CLOVIS-SANGER #2 115 kV (SW 147, 149, & 345) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541996 | T.0006537 | South Bundle S-31 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-01-13 | 2024-12-15 | 2026-02-10 | Prioritization | TRUE | 154700 | NA | 61.3915 | 5910.9911 | 0 | 18.4474 | 27.6671 | 15.277 | 0 | 0 | 476.6318 | 0 | 0 | 0 | 0 | 61.3915 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 ¦ 2027 | 0 | 0 | 46.1145 | 15.277 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1619 | CENTRAL BUNDLE C-47 |  |  | Fresno ¦ Fresno, Fresno ¦ Madera ¦ Madera Ranchos CDP, Madera ¦ Rolling Hills CDP, Madera | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: Lakewood-Meadow Lane-Clayton 115 kV (2 New SWs) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-09-20 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530377 | T.0004100 | Central Bundle C-47 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2028-03-24 | 2024-12-15 | 2028-04-07 | Prioritization | FALSE | 149600 | NA | 53.9506 | 1106.6536 | 10.9955 | 23.61 | 9.4388 | 2.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.9506 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2028 | 18.246 | 23.61 | 9.4388 | 2.6558 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1620 | North Bundle N-30 |  |  | Allendale CDP, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Yolo | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: MADISON-VACA 115 kV (SW 159) Fulton JCT-Vaca 115 kV (SW 137 & 139) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2021-08-25 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 115 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541983 | T.0006522 | North Bundle N-30 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-08-07 | 2024-12-15 | 2026-10-15 | Prioritization | FALSE | 149600 | NA | 14.3906 | 2656.119 | 0 | 0.2193 | 11.5155 | 2.6558 | 0 | 0 | 246.3043 | 0 | 0 | 0 | 0 | 14.3906 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 ¦ 2027 | 0 | 0 | 11.7348 | 2.6558 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1621 | North Bundle N-42 |  |  | Manton CDP, Tehama ¦ Shasta ¦ Tehama | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: MTN GATE JCT-CASCADE 60 kV (SW 39) COLEMAN-SOUTH 60 kV (SW 15 & 45) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-12 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541995 | T.0006536 | North Bundle N-42 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-04-25 | 2024-12-15 | 2025-04-25 | NA | FALSE | 149600 | NA | 11.7505 | 1543.9913 | 0 | 0 | 9.0947 | 2.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7505 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 ¦ 2026 | 0 | 0 | 9.0947 | 2.6558 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1622 | CENTRAL BUNDLE C-37 |  |  | Colusa ¦ Glenn ¦ Orland, Glenn ¦ Willows, Glenn | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: Pittsburg-Martinez #1 115 kV (SW 139) Pittsburg-Martinez #2 115 kV (SW 167, 169, 187, & 189) Oleum-Martinez 115 kV (SW 127 & 129) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-12-05 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530507 | T.0004078 | Central Bundle C-37 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-11-20 | 2024-12-15 | 2026-12-08 | Prioritization | FALSE | 149600 | NA | 57.7095 | 6622.6789 | 11.4741 | 19.718 | 16.2448 | 2.6558 | 0 | 0 | 835.7966 | 0 | 0 | 0 | 0 | 57.7095 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2026 ¦ 2027 ¦ 2028 | 19.0909 | 19.718 | 16.2448 | 2.6558 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1623 | North Bundle N-38 |  |  | Beale AFB CDP, Yuba ¦ East Nicolaus CDP, Sutter ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Smartsville CDP, Yuba ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ Wheatland, Yuba ¦ Yuba | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: SMARTVILLE TAP 60 kV (SW 97) SMARTVILLE-CAMP FAR WEST 60 kV (SW 99) SMARTVILLE-NICOLAUS #1 60 kV (SW 59) SMARTVILLE-NICOLAUS #2 60 kV (SW 67 & 71) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-04-04 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | NA | 60 | NA | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5541991 | T.0006530 | North Bundle N-38 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-06-11 | 2024-12-15 | 2025-06-11 | NA | TRUE | 149600 | NA | 182.6629 | 3857.5296 | 0 | 0 | 180.0071 | 2.6558 | 0 | 0 | 246.5517 | 0 | 0 | 0 | 0 | 182.6629 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 180.0071 | 2.6558 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1624 | CENTRAL BUNDLE C-40 |  |  | East Nicolaus CDP, Sutter ¦ Madison CDP, Yolo ¦ Nicolaus CDP, Sutter ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ Woodland, Yolo ¦ Yolo | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: SOBRANTE-G #1 115 kV (SW 119) SOBRANTE-GRIZZLY-CLAREMONT #1 115 kV (SW 159 & 1 New SW) SOBRANTE-GRIZZLY-CLAREMONT #2 115 kV (SW 149 & 165) SOBRANTE-R #1 115 kV (SW 137) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-12-08 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530511 | T.0004084 | Central Bundle C-40 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-04-16 | 2024-12-15 | 2026-05-15 | Prioritization | TRUE | 149600 | NA | 45.4495 | 4281.6856 | 10.9955 | 12.9437 | 10.9501 | 2.6558 | 0 | 0 | 192.7384 | 0 | 0 | 0 | 0 | 45.4495 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2026 ¦ 2027 ¦ 2028 | 18.8998 | 12.9437 | 10.9501 | 2.6558 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1625 | CENTRAL BUNDLE C-41 |  |  | Kern ¦ South Taft CDP, Kern ¦ Taft, Kern | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: STOCKTON "A" #1 60 kV (SW 27 & 47) NEW HOGAN TAP 60 kV (SW 35) TESLA-SALADO-MANTECA 115 kV (SW 179) VALLEY SPRINGS #2 60 kV (SW 87) VALLEY SPRINGS-CALAVERAS CEMENT 60 kV (SW 67, 69, & 1 New SW) WEST POINT-VALLEY SPRINGS 60 kV (SW 29) | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2023-11-03 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | Not Available | RBPPF - TBD | Yes | 5530370 | T.0004093 | Central Bundle C-41 | 1 | 94 | NA | NA | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2019-11-05 | 2024-12-15 | 2026-12-09 | Prioritization | TRUE | 149600 | NA | 966.3979 | 3096.6539 | 11.5196 | 35.4896 | 835.0477 | 66.6196 | 9.2692 | 0 | 965.8296 | 0 | 0 | 0 | 152.9197 | 966.3979 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2026 ¦ 2027 | 19.9718 | 35.4896 | 835.0477 | 66.6196 | 9.2692 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements. [Original Projected Cost] Original projected cost reflects Wave 3/4 Gate 2 Business Case. [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA
| 1626 | UKIAH: Upgrade 115 KV Reliability |  |  | Mendocino | In an effort to reduce the customer outage duration for the customers at Ukiah Substation, it is recommended to replace Switch (Sw.) Nos. 175 and 185 on Distribution Bank Nos. 1 and 2 witch circuit switchers, replace Sw. No. 177 with a circuit breaker, and replace Sw. No. 195 on City of Ukiah tap with a circuit breaker. The installation of circuit breakers and circuit switchers are needed to improve service reliability to the customers served by Ukiah Substation and is expected to reduce customer minutes. | Substation - Circuit Breaker | New | TBD | Reliability | Substation Reliability | NA | 2024-02-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.92364 | NA | 115 kV | 270 | 9. Reliability (Low Safety Risk) | 9 | RBPPF - TBD | Yes | 5769362 | T.0001467 | Ukiah Sub 115 kV Reliability Project | 1 | 94 | NA | 2016 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-03-30 | NA | 2030-02-12 | NA | FALSE | NA | NA | 661.8184 | 9231.7525 | 279.0456 | 243.1633 | 48.2242 | 44.8783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 661.8184 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1627 | COLUMBUS: Install 2-115 KV CBs |  |  | Bakersfield, Kern | Install two 115 kV circuit breakers with SCADA at Columbus Substation. | Substation - Circuit Breaker | New | NA | Reliability | Substation Reliability | NA | 2024-02-08 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.3875 | NA | 115 kV | 247 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5768808 | T.0001209 | COLUMBUS SUB: INSTALL 2-115KV CIRCUIT | 3 | 94 | 5738859 | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-01 | 2019-02-05 | 2019-03-15 | NA | FALSE | 8660 | NA | 5196.0527 | 5196.0527 | 944.9853 | 336.3658 | 34.4701 | 0.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5196.0527 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 4579.8698 | 455.983 | 33.6026 | 0.33632 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1628 | COLUMBUS: INSTALL CB 122 |  |  | Bakersfield, Kern | Install two 115 kV circuit breakers with SCADA at Columbus Substation. | Substation - Circuit Breaker | New | NA | Reliability | Substation Reliability | NA | 2024-02-08 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.3875 | NA | 115 kV | 247 | Not Available | Not Available | NA | NA | 5787178 | T.0001209 | COLUMBUS SUB: INSTALL 2-115KV CIRCUIT | 3 | 94 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-01 | 2020-02-01 | 2020-04-20 | NA | FALSE | 8660 | NA | 1556.9533 | 1556.9533 | 381.26 | 1183.0167 | -7.2533 | -0.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1556.9533 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 1412.2051 | -6.5409 | -0.06329 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1629 | PURISIMA: Install 115 KV SCADA SW |  |  | Santa Barbara | It is recommended that the existing Purisima Switch Nos. 125 and 115 be replaced with SCADA-operable Motor Operated Air Switch (MOAS) switches. The installation of 115kV MOAS switches is needed to improve service reliability to customers served by Purisima and is expected to reduce sustained customer outage minutes by 214,383 annually. | Substation - Switch | New | TBD | Reliability | Substation Reliability | NA | 2024-02-07 | NA | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.86746 | NA | 115 kV | 107 | 9. Reliability (Low Safety Risk) | 12 | RBPPF - TBD | Yes | 5772327 | T.0002252 | Purisima 115 kV SCADA Switch Project | 1 | 94 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-08-06 | NA | 2027-12-08 | NA | FALSE | NA | NA | 15.8279 | 2289.407 | 0.5744 | 0.9255 | 1.2417 | 0.9871 | 1.0856 | 1.1437 | 0 | 0 | 0 | 0 | 0 | 15.6428 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1630 | Humb Sub:Instl 115kV section CB& 2nd CB |  |  | Humboldt | The project scope of work includes following: Install 115 kV Bus Sectionalizing circuit breaker and associated equipment as required. Install second Aux circuit breaker and associated equipment as required. | Substation - Circuit Breaker | New | TBD | Reliability | Substation Reliability | NA | 2024-03-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.569 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5796758 | T.0006372 | Humboldt - Install 115kv Sec & AUX CB | 1 | 94 | NA | 2021 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-09-11 | NA | 2026-01-30 | NA | FALSE | NA | NA | 1002.4486 | 6735.0177 | 0 | 0 | 428.2879 | 498.345 | 59.3518 | 77.4769 | 0 | 0 | 0 | 0 | 5171.3616 | 985.9847 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 0 | 428.2879 | 498.345 | 59.3518 | 16.3642 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1631 | PALERMO SUB: INSTALL 115KV AUX CB |  |  | Palermo CDP, Butte | The project scope of work includes following: • Install 115kV a Bus Tie Breaker and associated structure and switches • Install 115kV Breaker and associated structure and switches • Install new foundations • Install controls and protection equipment • Upgrade ground grid as required • Extending 115kV Bus • Extend Fence | Substation - Circuit Breaker | New | NA | Reliability | Substation Reliability | NA | 2024-03-04 | NA | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 8.0464 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5799371 | T.0006252 | Palermo Sub: Install 115KV Aux CB | 1 | 94 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-07-11 | 2023-05-31 | 2022-11-17 | NA | TRUE | 7170 | NA | 3919.7465 | 3919.7465 | 0 | 11.1327 | 373.0903 | 3163.363 | 372.1604 | 0 | 0 | 0 | 0 | 0 | 0 | 3919.7465 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 384.223 | 2968.731 | 351.7425 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1632 | Chester Substation |  |  | East Shore CDP, Plumas | The purpose of the project is to improve the reliability performance of the Hamilton Branch-Chester 60kV transmission line. The scope of the project is to rebuild 12 miles of the Hamilton Branch-Chester 60kV line with a combination of direct embedded engineered steel poles (EDEP) and tubular steel poles (TSP) with galvanize finish for the majority of the route. Five locations where a distribution service is attached will require a fiber glass pole. The project will install new 397ACSR conductor for the transmission circuit and replace all existing distribution underbuild with 1/0ACSR tree wire. In addition, a new OPGW will be installed between structures 000/002 and 012/250. A new ADSS cable will be installed between structures 000/002 and 000/001 as well as between 012/250 and 012/251. The ADSS will then be routed to the control building at Hamilton Branch and Chester substations via a riser at structure 000/001 and 012/251 respectively. Also included in the scope is the external generation of Chester Substation during the 6-8 month construction schedule. This generation is necessary due to the 60kv circuit being the only feed to Chester Substation and providing Distribution service. The generator’s location will be at Collins Pine Lumber Company property and the Collins Pine 60kV Tap will act as a Distribution shoofly back to the Chester Substation main Distribution Feeder. The project will include upgrading or replacing 30 poles on this tap to upgrade the 60kv circuit to 397 in-lieu of the existing 2-6/1 ACSR. Scope: replace or upgrade poles 000/001 to 000/029. | Substation - Line Termination | Upgrade/Retrofit | TBD | Reliability | Substation Reliability | NA | 2024-03-13 | 67 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.1317 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5792884 | T.0003637 | Hamilton Branch - Chester Conductor Repl | 3 | 94 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2026-01-06 | NA | 2028-09-01 | NA | FALSE | NA | NA | 33.4659 | 1464.7122 | 0 | 0 | 12.0383 | 21.4276 | 0 | 2.0441 | 0 | 0 | 0 | 0 | 0 | 33.4659 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1633 | Redbud: Install Bus Sect CB |  |  | Clearlake Oaks CDP, Lake | These projects will replace the fused disconnect switches on Banks 1 & 3 with a sectionalizing breaker and upgrade the relays and controls at Redbud Substation to enable rapid shut-off and restoration of customers triggered by a PSPS event. This project is needed to maintain safe and reliable power to electric customers served from Redbud Substation and provides the following benefits: • Mitigates impacts to customers during a PSPS event by increasing operating flexibility and by facilitating more rapid shut off and restoration of electric substation equipment • Improve employee safety by enhancing visibility, control, and coordination of devices in the electric transmission system • Help achieve goals of the Wildfire Safety Program; namely reduce the risk and customer impacts of wildfires | Substation - Circuit Breaker | New | NA | Reliability | Substation Reliability | NA | 2024-02-16 | NA | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.1825 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801329 | T.0005771 | Redbud - Replace Bank 3 Fuse PSPS Relay | 1 | 94 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-10-02 | 2022-12-03 | 2026-01-07 | Prioritization | FALSE | 5530 | NA | 19.589 | 3745.7305 | 0 | 0 | 0 | 11.6018 | 7.7701 | 1.4095 | 0 | 0 | 0 | 0 | 3462.0046 | 19.3718 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1634 | WEST SACRAMENTO: Add CB or Sectionalizer |  |  | West Sacramento, Yolo | This project plans to replace SW 347 and Circuit Switcher 349 with 115kV circuit breakers, associated structures and disconnect switches. This project is part of Substation Asset Strategy’s Transmission Bus Reliability Improvement Program. It proposes to improve the 115kV bus reliability at West Sacramento Substation by December 2026. West Sacramento Substation is a Distribution Substation that serves over 12,000 customers. The 115kV bus is arranged as an eight (8) element single bus configuration. The 115kV bus is comprised of three (3) distribution banks, three (3) 115kV transmission lines, and two (2) capacitors banks. During normal operation the distribution banks are separated by SW 347 and Circuit Switcher 349 keeping two banks connected to one bus section. That means any bank fault or faults in the bus could trip two banks, causing the sustained outage to about 7,000 customers. This arrangement does not provide protection for individual distribution transformer and makes it very difficult to get clearances. | Substation - Circuit Breaker | New | TBD | Reliability | Substation Reliability | NA | 2024-02-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.303 | NA | 115 kV | 171 | 9. Reliability (Low Safety Risk) | 16 | RBPPF - TBD | Yes | 5777340 | T.0003462 | W Sac. 115 kV: Add CB or Sectionalizer | 1 | 94 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2026-07-06 | NA | 2028-04-04 | NA | FALSE | NA | NA | 0 | 9371.8884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1635 | Paradise Term Upg - Wyn Reconfig |  |  | Paradise, Butte | This project proposes to complete the removal of the Caribou-Palermo 115kV Line by removing abandoned lattice steel tower structures and assessing the remaining towers supporting other transmission lines and replacing or strengthening these towers if needed. To mitigate the risk of Wyandotte being single sourced, this project proposes to reconfigure Wyandotte Substation to utilize the Paradise-Table Mountain 115kV circuit as a backup source. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Reliability | NA | 2024-02-06 | 21 | NA | Other - Deferral | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.79098 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5796196 | T.0006251 | Caribou-Palermo 10391 Remove Structures | 8 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-02-01 | 2021-12-31 | 2022-05-27 | NA | TRUE | 20700 | NA | 2352.1648 | 2352.1648 | 0 | 0 | 292.1829 | 1573.6231 | 480.6199 | 5.7389 | 0 | 0 | 0 | 0 | 0 | 2346.4259 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1762.5868 | 453.7975 | 9.1025 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1636 | WyandotteTerm Upg - Wyn Reconfig |  |  | South Oroville CDP, Butte | This project proposes to complete the removal of the Caribou-Palermo 115kV Line by removing abandoned lattice steel tower structures and assessing the remaining towers supporting other transmission lines and replacing or strengthening these towers if needed. To mitigate the risk of Wyandotte being single sourced, this project proposes to reconfigure Wyandotte Substation to utilize the Paradise-Table Mountain 115kV circuit as a backup source. | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Substation Reliability | NA | 2024-02-12 | 14 | NA | Other - Deferral | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.2226 | NA | 115 kV | Not Available | Not Available | Not Available | NA | NA | 5796195 | T.0006251 | Caribou-Palermo 10391 Remove Structures | 8 | 94 | NA | 2020 | 2021 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-12-06 | 2021-12-31 | 2022-05-27 | NA | FALSE | 20700 | NA | 1146.8025 | 1146.8025 | 0 | 0 | 509.1436 | 635.3481 | 2.3108 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.8025 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 1066.5583 | 2.15 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1637 | BELLEVUE: Install CBs - SANTA ROSA END |  |  | Santa Rosa, Sonoma | This project proposes to install two new SCADA-operable 115 kV circuit breakers at Bellevue Substation. This project is needed to improve electric service reliability by reducing customer outage time and frequency at Bellevue, Penngrove and Stony Point substations. | Substation - Circuit Breaker | New | TBD | Reliability | Substation Reliability | NA | 2024-03-08 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.91804 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5793877 | T.0000555 | BELLEVUE SUB: INSTALL: 115KV CB | 4 | 94 | NA | 2011 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-07-17 | NA | 2026-07-17 | NA | FALSE | NA | NA | 3.746 | 2560.2528 | 0 | 1.7802 | 1.4314 | 0.2336 | 0.257 | 0.2707 | 0 | 0 | 0 | 0 | 0 | 3.7022 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1638 | BELLVUE: Install 2-115 KV CB |  |  | Sonoma | This project proposes to install two new SCADA-operable 115 kV circuit breakers at Bellevue Substation. This project is needed to improve electric service reliability by reducing customer outage time and frequency at Bellevue, Penngrove and Stony Point substations. | Substation - Circuit Breaker | New | TBD | Reliability | Substation Reliability | NA | 2024-03-12 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.6531 | NA | 115 kV | 168 | 9. Reliability (Low Safety Risk) | 9 | RBPPF - TBD | Yes | 5743009 | T.0000555 | BELLEVUE SUB: INSTALL: 115KV CB | 4 | 94 | NA | 2011 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2025-11-10 | NA | 2026-02-06 | NA | FALSE | NA | NA | 170.0021 | 3880.0196 | 4.0309 | 73.4518 | 23.9617 | 10.6864 | 11.6599 | 12.2836 | 0 | 0 | 0 | 0 | 0 | 168.0139 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1639 | Valley Springs: 60kV BAAH |  |  | Calaveras | This project will Install a Distribution Bank 3 60/12 kV, a 60 kV Breaker and a half (BAAH) Bay 5, a 12 kV Double Bus Single Breaker (DBSB) at Valley Springs Substation so to decommission North Branch Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-02-02 | 50 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.8736 | NA | 60 kV | 362 | 9. Reliability (Low Safety Risk) | 9 | NA | NA | 5788199 | T.0002197 | Valley Springs: Install New Bank | 1 | 94 | NA | 2018 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-08-31 | 2021-11-01 | 2023-01-28 | Prioritization | TRUE | 10000 | NA | 4509.0386 | 4712.5789 | 0 | 348.144 | 2278.0371 | 1714.0302 | 156.486 | 215.8817 | 0 | 0 | 0 | 0 | 0 | 4496.6972 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 4463.6238 | 13.0691 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $5 Mil - $10 Mil ¦ NA
| 1640 | OROVILLE: Inst Sectionalizing CBs Bus |  |  | Oroville, Butte | This project will install bus sectionalizing circuit breakers on the Oroville Substation 60kV loop bus that serves the 60/12kV Banks 1, 2 and 3. The breakers will replace bus-tie switches 89 and 97. The control building cannot accommodate the additional panels required for the new breakers; therefore, it will need to be replaced (likely as part of an in-flight D-SCADA project). | Substation - Circuit Breaker | New | TBD | Reliability | Substation Reliability | NA | 2024-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 0.75208 | NA | 60 kV | 598 | 9. Reliability (Low Safety Risk) | 10 | RBPPF - TBD | Yes | 5769942 | T.0001569 | Oroville:Inst Sectionalizg CBs on60kVBus | 1 | 94 | NA | 2019 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-07-20 | NA | 2027-05-10 | NA | FALSE | NA | NA | 306.4147 | 6776.9297 | 7.5209 | 197.9642 | 30.9798 | 19.1486 | 21.016 | 22.14 | 0 | 0 | 0 | 0 | 0 | 302.8312 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1641 | VACA DIXON: Add Aux Breaker |  |  | Solano | Upgrade the existing 60kV Main and Auxiliary Bus configuration at Vaca-Dixon Sub by installing two new bays. The project plans to relocate the Vaca-Dixon #2 Line, CB 42 position to make space for a new Sectionalizing breaker. In addition a new 60kV bus parallel breaker will be installed to support the bus sectionalizing upgrade. The addition of the two new 60kV bays will be installed within PG&E property and should not require any fence relocation. | Substation - Circuit Breaker | New | TBD | Reliability | Substation Reliability | NA | 2024-03-12 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 60 kV | 270 | 9. Reliability (Low Safety Risk) | 4 | RBPPF - TBD | Yes | 5777339 | T.0003461 | Vaca Dixon 60 kV: Add Aux Breaker | 1 | 94 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-10-02 | NA | 2028-07-10 | NA | FALSE | NA | NA | 0 | 14649.2373 | 0 | 0 | 0 | 0 | 0 | 31.4663 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1642 | El Cerrito - Fencing/Grading |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Substation - Structure | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-20 | NA | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 8.2538 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799974 | T.0000636 | El Cerrito G Substation Rebuild | 8 | 94 | NA | 2011 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2024-10-30 | 2021-02-18 | 2025-03-24 | Prioritization | TRUE | 94600 | NA | 106.2302 | 109.7315 | 0 | 0 | 0 | 29.3095 | 2.8517 | 34.5265 | 2591.3159 | 0 | 0 | 0 | 0 | 74.4765 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1643 | SOBRANTE: Add & Repl 14-115 KV Breakers |  |  | Orinda, Contra Costa | Install 115 kV automation equipment and rebuild the 115 kV facilities (buses, breakers, switches, and structure foundations) at Sobrante Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-07 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Corrosion |  | NA | 11.0767 | NA | 115 kV | 127 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5770140 | T.0000654 | Sobrante Substation 115kV Upgrade | 2 | 94 | NA | 2008 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2016-03-01 | 2018-05-07 | 2019-04-05 | Workforce | FALSE | 34500 | NA | 16804.3475 | 16804.3475 | 3521.7098 | 338.7295 | 8.0778 | 33.1757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16804.3475 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 9081.3576 | 308.9492 | 7.3343 | 30.1223 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1644 | SANGER: Replace 115 KV Bus |  |  | Fresno | Install a new seven bay 115 kV BAAH bus, two MPAC buildings, and relocate all associated 115 kV lines at Sanger Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-02-07 | 20 | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 11.0513 | NA | 115 kV | 225 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5741360 | T.0000601 | Sanger Substation 115kV Bus Replacement | 4 | 94 | NA | 2014 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2017-07-13 | IS/MND | NA | CPUC | NA | PTC: A.15-09-012 | 2015-09-30 | Approved | 2017 | Operational | 2 | 2019-04-25 | 2019-12-31 | 2020-11-02 | Prioritization | FALSE | 55300 | NA | 38198.2485 | 38198.2485 | 15598.4019 | 9830.3857 | 5330.994 | 78.7486 | 0.3371 | 0 | 0 | 0 | 0 | 0 | 0 | 38198.2485 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 30598.2789 | 4940.8772 | 72.986 | 0.3124 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1645 | MIDWAY: UPGRADE 230 KV BUS SECT D PH 2 |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-15 | 48 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | 230 kV | 705 | 5a.Mitigates System Wide Failure Risk | 9 | NA | NA | 5787769 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-11-10 | 2022-04-01 | 2021-11-10 | NA | FALSE | 105100 | NA | 2163.4719 | 2163.4719 | 1.8832 | 0.1364 | 2084.0326 | 72.2453 | 5.1745 | 0 | 0 | 0 | 0 | 0 | 0 | 2163.4719 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 1987.3353 | 67.1413 | 4.9226 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1646 | MIDWAY: UPGRADE 230 KV BUS SECT D PH 3 |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-15 | 49 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | 230 kV | 705 | 5a.Mitigates System Wide Failure Risk | 9 | NA | NA | 5787770 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-10-11 | 2022-04-01 | 2023-04-24 | Prioritization | TRUE | 105100 | NA | 7824.6024 | 7824.6024 | 10.2932 | 19.9223 | 3968.6785 | 1545.6632 | 2214.6159 | 65.4293 | 0 | 0 | 0 | 0 | 0 | 7759.1731 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 7155.9371 | 84.15 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1647 | MIDWAY: UPGRADE 230 KV BUS SECT D PH 4 |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-15 | 49 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | 230 kV | 705 | 5a. Mitigates System Wide Failure Risk | 9 | RBPPF - TBD | Yes | 5787771 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-12-23 | 2022-04-01 | 2026-01-22 | Prioritization | FALSE | 105100 | NA | 113.9557 | 8293.3666 | 0 | 0 | 91.9827 | 10.0103 | 9.6601 | 316.9142 | 1577.9181 | 0 | 0 | 0 | 0 | 111.6531 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1648 | MIDWAY: UPGRADE 230 KV BUS SECT D PH 5 |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-15 | 49 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | 230 kV | 705 | 5a. Mitigates System Wide Failure Risk | 9 | RBPPF - TBD | Yes | 5787772 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-03-10 | 2022-04-01 | 2027-12-02 | Prioritization | FALSE | 105100 | NA | 32.5265 | 20808.4738 | 0 | 0 | 26.026 | 1.8932 | 4.2426 | 2.336 | 4472.0651 | 3701.8143 | 0 | 0 | 0 | 32.1619 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1649 | MIDWAY: Upgrade 230 KV Bus Section D |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-15 | 55 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Heat Wave |  | NA | 94.5324 | NA | 230 kV | 705 | 5a.Mitigates System Wide Failure Risk | 9 | RBPPF - TBD | Yes | 5768786 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA | 2016 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 3 | 2021-07-08 | 2022-04-01 | 2026-01-31 | Prioritization | TRUE | 105100 | NA | 50631.9564 | 67635.4901 | 3058.8812 | 4339.9589 | 24534.8253 | 14799.3581 | 909.5321 | 6074.9492 | 300 | 0 | 0 | 0 | 0 | 50631.9564 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1650 | EMBARCADERO: Cutover GIS BK 5 |  |  | San Francisco, San Francisco | Replace and upgrade the Embarcadero 230 kV bus. The new transmission bus will improve electric reliability in downtown San Francisco and reduce clearance restrictions for equipment maintenance, thereby eliminating abnormal conditions and instances where electric service to downtown San Francisco and the Financial District are at risk. The new bus will also be designed to accommodate future expansion. | Substation - Bus Arrangement | Upgrade/Retrofit | T.0003672 | Reliability | Bus Upgrade | NA | 2024-03-14 | NA | NA | Wires - Replacement Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.55624 | NA | 230 kV | 598 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5778322 | T.0003671 | SAN FRAN Z 230kV CONV\BAAH\REBUILD | 3 | 94 | NA | 2007 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-12-28 | 2019-07-31 | 2019-12-08 | NA | FALSE | 94500 | NA | 1656.8186 | 1656.8186 | 1146.0289 | 382.4117 | 67.1788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1656.8186 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 1170.2332 | 370.6854 | 92.9334 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1651 | EMBARCADERO: Cutover GIS BK3 & HZ-1 |  |  | San Francisco, San Francisco | Replace and upgrade the Embarcadero 230 kV bus. The new transmission bus will improve electric reliability in downtown San Francisco and reduce clearance restrictions for equipment maintenance, thereby eliminating abnormal conditions and instances where electric service to downtown San Francisco and the Financial District are at risk. The new bus will also be designed to accommodate future expansion. | Substation - Bus Arrangement | Upgrade/Retrofit | T.0003672 | Reliability | Bus Upgrade | NA | 2024-03-14 | NA | NA | Wires - Replacement Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.55624 | NA | 230 kV | 598 | Not Available | NA | NA | NA | 5778321 | T.0003671 | SAN FRAN Z 230kV CONV\BAAH\REBUILD | 3 | 94 | NA | 2007 | 2012 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-01-02 | 2018-12-28 | 2019-01-02 | NA | FALSE | 94500 | NA | 11882.0664 | 11882.0664 | 1372.3587 | 3.315 | 4.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11882.0664 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2021 ¦ 2024 | 11516.1792 | 3.2114 | 347.138 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1652 | Milpitas 115kV: Bus Reliability Improve. |  |  | Milpitas, Santa Clara | Replace circuit switchers 177 and 187 with circuit breakers in Milpitas. Install associated equipment as required. | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NA | 2024-02-08 | 37 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.3452 | NA | 115 kV | 171 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5777265 | T.0003451 | Milpitas 115kV: Bus Reliability Improve. | 2 | 94 | NA | 2015 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-07-21 | NA | 2028-09-06 | NA | FALSE | NA | NA | 0 | 2671.6011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1653 | POTRERO: CONVERT 115 KV BUS TO GIS BAAH |  |  | San Francisco, San Francisco | Replacement of 115/12kV, 45MVA Bank 2 with a 75MVA Bank and convert 115 KV Bus to GIS BAAH at Potrero Substation. This bank will be replaced as a part of the Potrero Substation rebuild project. The entire substation is recommended to be moved to north of Humboldt Street. | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NA | 2024-03-28 | 33 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 115 kV | 564 | 5a.Mitigates System Wide Failure Risk | 5 | Tier 4 | Yes | 5760988 | T.0000557 | POTRERO: CONVERT 115KV BUS TO GIS BAAH | 1 | 94 | NA | 2015 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2016 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2028-07-21 | NA | 2030-09-18 | NA | FALSE | NA | NA | 1880.9059 | 173575.344 | 124.923 | 109.1514 | 30.7987 | 656.4403 | 181.7928 | 138.5816 | 0 | 0 | 0 | 0 | 11000 | 1856.8038 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 1654 | LARKIN: Upgd 115 KV Reliability |  |  | San Francisco, San Francisco | Replacement of the existing 115 kV single bus to a five (5) bay Breaker-and-A-Half (BAAH) 115 kV Gas Insulated Switchgear ( GIS) configuration at Larkin Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NA | 2024-02-15 | 26 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 1.0478 | NA | 115 kV | 705 | 5a.Mitigates System Wide Failure Risk | 5 | RBPPF - TBD | Yes | 5768170 | T.0000934 | LARKIN: 115KV RELIABILITY | 1 | 94 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2028-05-12 | NA | 2030-07-17 | NA | FALSE | NA | NA | 239.3127 | 68883.6938 | 42.5194 | 60.403 | 28.7264 | 16.3149 | 16.4137 | 17.2916 | 0 | 0 | 0 | 0 | 500 | 236.5139 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1655 | MOUNT EDEN: Check 115 KV Bus Reliability |  |  | Hayward, Alameda | System Protection recommends that the backup relays at both ends be replaced with new SEL line differential relays with separate communication channel from the primary relay. Eastshore-Mt Eden #1 and #2 lines are short line slightly longer than 1.00 mile. For such a short line, one set of line differential relay plus another set of overcurrent relay configuration does not meet current PG&E protection standard and results in significant coordination problems when line differential protection is not available for any reason (e.g., relay or communication channel maintenance or failure). | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NA | 2024-03-05 | 64 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.6074 | NA | 115 kV | 270 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5757753 | T.0001212 | MT. EDEN 115 KV BUS RELIABILITY | 1 | 94 | NA | 2014 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-12-30 | NA | 2028-05-10 | NA | FALSE | NA | NA | 96.7072 | 4465.7093 | 11.5556 | 17.4092 | 16.9159 | 42.6206 | 6.6329 | 6.9876 | 0 | 0 | 0 | 0 | 0 | 95.5762 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1656 | HENRIETTA: Upgrade 230 KV Bus |  |  | Kings | The BAAH work scope under MWC 94 includes installation of three bays of 230 kV systems and its connection to the existing 230 kV bus at Henrietta Substation. The new 230 kV bus bus will include circuit breakers, disconnect switches, voltage transformers, current transformers, buses, bushings, structures, and connections of the equipment. Three bays with eight breakers will be installed to connect two lines and three transformer banks. T‐line re‐arrangement will be a required, but line relocation will depend on ultimate plan completion. | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NA | 2024-03-05 | 50 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 7.0079 | NA | 230 kV | 171 | Not Available | Not Available | RBPPF - TBD | Yes | 5777343 | T.0007174 | Henrietta 230kV Bus Upgrade | 1 | 94 | NA | 2017 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2027-11-08 | NA | 2028-09-08 | NA | FALSE | NA | NA | 0 | 16968.7957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0%
| 1657 | Placer: 115kV T-Line Work |  |  | Auburn, Placer ¦ Folsom, Sacramento ¦ Granite Bay CDP, Placer ¦ Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-04-03 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801600 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-12-19 | 2024-12-30 | 2027-08-20 | Prioritization | FALSE | 17200 | NA | 295.3234 | 4037.6841 | 0 | 0 | 0 | 30.2039 | 250.5653 | 32.5289 | 0 | 0 | 0 | 0 | 129.4567 | 280.7691 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1658 | Placer: 60kV T-Line Work |  |  | Auburn, Placer ¦ Loomis, Placer ¦ Newcastle CDP, Placer ¦ Penryn CDP, Placer ¦ Placer ¦ Rocklin, Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Line Termination | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-04-02 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated, Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801601 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-10-24 | 2024-12-30 | 2027-07-23 | Prioritization | FALSE | 17200 | NA | 164.4145 | 4273.1363 | 0 | 0 | 0 | 24.56 | 134.8232 | 15.0382 | 0 | 0 | 0 | 0 | 118.9613 | 159.3832 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1659 | Placer: Convert 115kV Bus Sec ""D"" |  |  | Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-12 | 64 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801701 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-08-03 | 2024-12-30 | 2027-04-30 | Prioritization | FALSE | 17200 | NA | 282.6962 | 7209.9143 | 0 | 0 | 0 | 33.1651 | 244.5069 | 22.2302 | 0 | 0 | 0 | 0 | 166.2947 | 277.6721 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1660 | Placer: Convert 115kV Bus Sec ""E"" |  |  | Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-12 | 64 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801700 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA | 2020 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-08-04 | 2024-12-30 | 2026-08-17 | Prioritization | FALSE | 17200 | NA | 432.1876 | 8553.0686 | 0 | 0 | 0 | 37.6157 | 390.5471 | 35.9041 | 0 | 0 | 0 | 0 | 145.5515 | 428.1628 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1661 | Placer: Convert 60kV Bus Sec ""D"" |  |  | Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-12 | 64 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5801702 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-08-03 | 2024-12-30 | 2027-04-30 | Prioritization | FALSE | 17200 | NA | 198.9853 | 6208.5935 | 0 | 0 | 0 | 27.7064 | 166.7087 | 26.7635 | 0 | 0 | 0 | 0 | 148.1433 | 194.415 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1662 | PLACER: CONVERT 60KV BUS SEC ""E"" |  |  | Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-12 | 61 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 60 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5796180 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | 5792685 | 2021 | 2022 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-08-04 | 2024-12-30 | 2026-07-31 | Prioritization | FALSE | 17200 | NA | 437.1258 | 8449.0769 | 0 | 0 | 113.3854 | 93.4396 | 223.9046 | 33.0015 | 0 | 0 | 0 | 0 | 169.3086 | 430.7295 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1663 | CLAYTON: Install 2-Sect-Breakers |  |  | Concord, Contra Costa | The proposed project will install two bus tie breakers and sectionalize the bus. As there is no space in the existing configuration, either the bus paralleling breaker or one of the line breaker spaces will be used to sectionalize the bus. Five new bays will be added to the 115 kV buses, which will require expanding the buses. Two bays will be used for bank high-side breakers, two bays will be used for the bus paralleling breaker and one bay will be used to unbundle Pittsburg – Clayton lines 1 & 2. In addition, Pittsburg – Clayton No. 3 line(source) will be swapped with Lakewood – Meadow Lane – Clayton line (load) to balance out source and load connection on the newly formed bus sections. This will allow us to serve our load even if we lose the entire bus section. The MPAC buildings will fully integrate new bus arrangement. Both MPAC and 115 kV Bus Reliability projects will be engineered and constructed concurrently. These projects will improve operational and maintenance flexibility, and service reliability in this area. | Substation - Bus Arrangement | New | TBD | Reliability | Bus Upgrade | NA | 2024-03-06 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.9731 | NA | 115 kV | 267 | 9. Reliability (Low Safety Risk) | 11 | RBPPF - TBD | Yes | 5770151 | T.0001640 | CLAYTON: 2SECT-BRK & MPAC | 2 | 94 | 5752303 | 2013 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2027-02-18 | NA | 2027-07-02 | NA | FALSE | NA | NA | 47.8456 | 6516.4673 | 12.6391 | 25.5828 | 2.7525 | 3.0301 | 3.2816 | 3.4715 | 0 | 0 | 0 | 0 | 0 | 47.2861 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1664 | Eagle Rock: Convert 115 kV Bus |  |  | Sonoma | This planned project will convert Eagle Rock 115 kV bus to DBSB, decommission Geysers 3 & 4, and build 1.5 miles between Eagle Rock and Cloverdale Substations | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NA | 2024-03-01 | NA | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.8266 | NA | 115 kV | Not Available | Not Available | Not Available | RBPPF - TBD | Yes | 5799300 | T.0007732 | Eagle Rock: Convert 115 kV Bus | 3 | 94 | NA | 2022 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-05-11 | NA | 2027-09-20 | NA | FALSE | NA | NA | 1081.9556 | 3394.7198 | 0 | 0 | 0 | 1081.9556 | 0 | 0 | 0 | 0 | 0 | 0 | 404.263 | 1081.9556 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1665 | ORO LOMA: Upgrade 70 KV Bus |  |  | Fresno | This project is part of Substation Asset Strategy’s Bus Reliability Improvement Program. It proposes to replace the 70kV single-bus with a ring-bus. | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000563 ¦ T.0000891 ¦ T.0001473 | Reliability | Bus Upgrade | NA | 2024-02-16 | NA | NA | Wires - Bus Upgrade Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.8637 | NA | 70 kV | 705 | 9. Reliability (Low Safety Risk) | Not Available | NA | NA | 5776078 | T.0003408 | UPGRADE ORO LOMA 70KV BUS | 1 | 94 | NA | 2016 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-11-19 | 2020-07-01 | 2020-04-05 | NA | FALSE | 5669 | NA | 7069.8241 | 7069.8241 | 1818.7163 | 3627.4005 | 211.2978 | 3.5127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7069.8241 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 6224.6676 | 191.1469 | 3.1777 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1666 | COTTONWOOD: Improve 60 KV Bus |  |  | Cottonwood CDP, Shasta | This project proposes to convert the existing Cottonwood 60 kV Main-Auxiliary Buses into Double-Bus-Single-Breaker (DBSB). This project is needed to improve the electric transmission service to customers served from Cottonwood Substation, and will and will eliminate a single point of failure for the 2 transformers that serve the 60 kV bus. | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NA | 2024-03-06 | 57 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | NA | 26.1945 | NA | 60 kV | 270 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5744979 | T.0000519 | COTTONWOOD SUB - 60KV BUS IMPROVEMENT | 1 | 94 | NA | 2011 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2029-02-05 | NA | 2030-02-11 | NA | FALSE | NA | NA | 163.9495 | 11487.5559 | 30.6767 | 59.3062 | 12.1165 | 14.8913 | 11.2448 | 11.8961 | 0 | 0 | 0 | 0 | 0 | 162.0321 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1667 | El Cerrito G: 115kV BAAH Bay 4 |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-20 | 73 | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 8.2538 | NA | 115 kV | 276 | Not Available | Not Available | RBPPF - TBD | Yes | 5795286 | T.0000636 | El Cerrito G Substation Rebuild | 8 | 94 | NA | 2011 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (10%-25%) | 3 | 2024-01-12 | 2021-02-18 | 2025-05-07 | Prioritization | TRUE | 94600 | NA | 5374.1369 | 19772.7223 | 0 | 0 | 147.8961 | 2345.6849 | 1261.0173 | 10730.6748 | 5287.4492 | 2320.9863 | 0 | 0 | 0 | 3754.5983 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1668 | EL CERRITO G: Upgrade 115 KV Bus |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-20 | 63 | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 8.2538 | NA | 115 kV | 276 | 5a.Mitigates System Wide Failure Risk | 4 | NA | NA | 5767962 | T.0000636 | El Cerrito G Substation Rebuild | 8 | 94 | 5746713 | 2011 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2016-12-06 | 2021-02-18 | 2022-01-23 | Prioritization | FALSE | 94600 | NA | 2176.8706 | 2176.8706 | 112.5444 | 158.2029 | 461.4965 | 6.7038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2176.8706 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2024 | 0 | 0 | 0 | 1923.6228 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1669 | EL CERRITO G: Upgrade 115 KV Bus Phase 1 |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-20 | NA | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 8.2538 | NA | 115 kV | 270 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5767958 | T.0000636 | El Cerrito G Substation Rebuild | 8 | 94 | 5746713 | 2011 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-04-25 | 2021-02-18 | 2020-01-27 | NA | FALSE | 94600 | NA | 26411.1108 | 26411.1108 | 3127.8738 | 788.9472 | 107.2289 | 0.0581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26411.1108 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 25750.3622 | -26.9981 | 0.05629 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1670 | EL CERRITO G: Upgrade 115 KV Bus Phase 2 |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-20 | 63 | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather, Subsidence |  | NA | 8.2538 | NA | 115 kV | 276 | 5a.Mitigates System Wide Failure Risk | 4 | NA | NA | 5767959 | T.0000636 | El Cerrito G Substation Rebuild | 8 | 94 | 5746713 | 2011 | 2016 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-11 | 2021-02-18 | 2022-01-23 | Prioritization | TRUE | 94600 | NA | 21376.1325 | 21376.1325 | 566.6517 | 7482.4677 | 6079.2606 | 3677.5325 | 563.8597 | 8.9144 | 0 | 0 | 0 | 0 | 0 | 21367.2181 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 18626.8158 | 499.2134 | 16.1486 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1671 | RIO OSO: Install 115 KV BAAH/GIS |  |  | Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-04 | 64 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.3219 | NA | 115 kV | 462 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5740958 | T.0000614 | Rio Oso Substation Upgrade | 12 | 94 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2022-10-28 | 2019-12-02 | 2024-12-13 | Prioritization | TRUE | 264900 | NA | 62278.4373 | 85071.6035 | -271.8953 | 3975.2109 | 13734.9676 | 15509.0442 | 14265.1842 | 16544.5786 | 9061.595 | 935.0311 | 0 | 0 | 0 | 58760.5186 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil
| 1672 | RIO OSO: Repl 230 KV BAAH/GIS |  |  | Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-04 | 64 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.3219 | NA | 230 kV | 462 | 9. Reliability (Low Safety Risk) | Not Available | RBPPF - TBD | Yes | 5732785 | T.0000614 | Rio Oso Substation Upgrade | 12 | 94 | NA | 2008 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2022-08-25 | 2019-12-02 | 2024-12-13 | Prioritization | TRUE | 264900 | NA | 92182.2939 | 124568.6895 | 1626.0807 | 5569.8569 | 19870.4131 | 30232.6822 | 17532.998 | 24298.9845 | 10851.2541 | 764.3506 | 0 | 0 | 0 | 86445.4895 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil
| 1673 | ASHLAN: Convert to 230 KV Ring Bus |  |  | Fresno, Fresno | This project will upgrade the existing 230kV bus from looped design to a ring bus design as well as install an MPAC building and upgrade protection at Ashlan, Herndon, Gregg, and Figarden substations. These upgrades will improve reliability, safety, and maintenance at Ashlan substation and the 230kV protection in the local area. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-05 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.6505 | NA | 230 kV | 270 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5772494 | T.0002362 | Ashlan Ave 230kV Bus Reliability | 7 | 94 | NA | 2014 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-09 | 2020-02-11 | 2020-02-20 | NA | FALSE | 40900 | NA | 15814.8639 | 15814.8639 | 9820.6557 | 3181.2482 | 33.4246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15814.8639 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2024 | 0 | 15077.0839 | 31.8651 | 0 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1674 | HUNTERS POINT: Repl 115 KV GIS BAAH |  |  | San Francisco, San Francisco | This proposed project will rebuild the entire Hunters Point Substation about 2,000 feet from its current location but is still within the existing PG&E parcel. Rebuilding at a new site has many benefits based on lessons learned from other substation rebuild projects. Specific scope of work includes: • A new 115 kV bus using gas-insulated switchgear (GIS) in a breaker-and-a-half (BAAH) configuration, • 115 kV modular protection, automation, and control (MPAC) panels, • New 12 kV switchgear in a double-bus-double-breaker configuration, • Two new 115/12 kV substation transformers, • Spill prevention control and countermeasure (SPCC) facilities, and • Relocation and potentially undergrounding of the 115 kV transmission and 12 kV outlets. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-03-14 | 28 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 2.9037 | NA | 115 kV | 181 | 5a.Mitigates System Wide Failure Risk | 9 | RBPPF - TBD | Yes | 5752496 | T.0000590 | Hunters Point Substation | 4 | 94 | NA | 2013 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5483-E | 2019-02-13 | Approved | 2019 | Engineering more than 50% complete | 4 | 2028-08-10 | 2017-12-15 | 2031-02-19 | Prioritization | FALSE | 190398 | NA | 36629.1951 | 254762.7803 | 1004.1648 | 5071.6679 | 5134.577 | 11801.7712 | 6997.0969 | 3999.3934 | 0 | 0 | 0 | 0 | 0 | 36108.1461 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $200 Mil - $250 Mil
| 1675 | HICKS: Improve 230 KV Bus Reliability |  |  | San Jose, Santa Clara | To reduce customer interruptions at Hicks Substation, it is recommended to re-connect existing T-Line and distribution bank connections and install four new 230kV circuit breakers to build a six-breaker ring bus in conjunction with a new MPAC building. This will reduce System Average Interruption Duration Index (SAIDI) impacts affecting these 44,000 customers. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | Reliability | Bus Upgrade | NA | 2024-02-08 | 46 | NA | Wires - Bus Upgrade Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.8635 | NA | 230 kV | 247 | 5a.Mitigates System Wide Failure Risk | Not Available | NA | NA | 5739142 | T.0001600 | HICKS SUB: 230 KV BUS REL IMPROV | 3 | 94 | NA | 2010 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-17 | 2017-08-29 | 2021-11-04 | Prioritization | FALSE | 21300 | NA | 15898.2897 | 15898.2897 | 3985.4136 | 4324.0054 | 4688.6254 | 564.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15898.2897 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 13990.2491 | 507.6014 | 0 | 0 | 0% | NA | NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1676 | BUTTE: Repl BK 2 and Upgrade Equipment |  |  | Chico, Butte | Upgrade the exisiting double-bus single-breaker set-up at Butte Substaton to a breaker-and-a-half (BAAH) layout. The new 115kV bus will include circuit breakers, disconnect switches, voltage transformers, current transformers, buses, bushings, structures, and connections of the equipment. A moudular control building (MPAC) will also be required. | Substation - Bus Arrangement | Upgrade/Retrofit | TBD | Reliability | Bus Upgrade | NA | 2024-02-12 | 11 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.1949 | NA | 115 kV | 270 | 9. Reliability (Low Safety Risk) | 3 | RBPPF - TBD | Yes | 5777333 | T.0003457 | Butte 115kV Sec MA BAAH DBSB | 1 | 94 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2026-09-25 | NA | 2028-07-31 | NA | FALSE | NA | NA | 0 | 24195.8713 | 0 | 0 | 0 | 0 | 0 | 31.4938 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1677 | KERN PP: CONV. 115kV BUS TO BAAH – Ph. 2 |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000204 | Reliability | Bus Upgrade | NA | 2024-04-12 | 72 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | 37.7504 | NA | 115 kV | 705 | 5a. Mitigates System Wide Failure Risk | 10 | RBPPF - TBD | Yes | 5787960 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-05-01 | 2022-10-12 | 2025-12-05 | Prioritization | TRUE | 77400 | NA | 0 | 5053.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 5053.6659 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil
| 1678 | KERN PP: CONV. 115kV BUS TO BAAH - Ph. 3 |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000204 | Reliability | Bus Upgrade | NA | 2024-04-12 | 72 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | 37.7504 | NA | 115 kV | Not Available | 5a. Mitigates System Wide Failure Risk | 10 | RBPPF - TBD | Yes | 5787961 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-01-08 | 2022-10-12 | 2026-12-04 | Prioritization | FALSE | 77400 | NA | 0 | 11112.5025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil
| 1679 | KERN PP: CONV. 115kV BUS TO BAAH - Ph. 4 |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000204 | Reliability | Bus Upgrade | NA | 2024-04-12 | 72 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | 37.7504 | NA | 115 kV | Not Available | 5a. Mitigates System Wide Failure Risk | 10 | RBPPF - TBD | Yes | 5787962 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA | 2014 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-11-01 | 2022-10-12 | 2027-12-13 | Prioritization | FALSE | 77400 | NA | 0 | 10701.6255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil
| 1680 | KERN PP: Convert 115 KV Bus to BAAH - Ph. 1 |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Bus Arrangement | Upgrade/Retrofit | T.0000204 | Reliability | Bus Upgrade | NA | 2024-04-12 | 72 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence, Extreme Heat |  | NA | 37.7504 | NA | 115 kV | 705 | 5a.Mitigates System Wide Failure Risk | 10 | RBPPF - TBD | Yes | 5770678 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | 5762085 | 2014 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-10-01 | 2022-10-12 | 2024-11-08 | Prioritization | TRUE | 77400 | NA | 32729.4365 | 41984.8425 | 788.1989 | 6357.9332 | 9588.7026 | 10170.0783 | 2280.4259 | 6299.2967 | 2397.3533 | 0 | 0 | 0 | 0 | 33288.1924 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-D NOC, PTC or CPCN requirements [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil
| 1681 | Monta Vista-Big Basin M.V. Sub to Sw 67 |  |  | Bonny Doon CDP, Santa Cruz ¦ Cupertino, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Address 15 miles of aging infrastructure on the Monta Vista – Burns 60 kV Line located in Tier 2 and 3 fire risk zones in Santa Clara and Santa Cruz Counties between Monta Vista and Big Basin Substations. The work includes the installation, replacement and reframing of poles, vibration dampers and insulators. The project will also address any line maintenance tags that are to be completed at that time, as well as completing the right-of-way (ROW) expansion tree trimming project for the line. During this timeframe the project scope was reduced to the 15-mile section from Monta Vista to Big Basin in order to better address risk mitigation and gain execution efficiencies. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Targeted Line Reliability | NA | 2024-04-10 | 60 | NA | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 5.5 | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 78 | RBPPF - TBD | Yes | 5767514 | T.0000262 | MONTA VISTA-BIG BASIN SW 67 TO SW 19 | 3 | 94 | 5747825 | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2029-04-18 | NA | 2029-11-13 | NA | FALSE | NA | NA | 475.4154 | 19702.9491 | 46.2362 | 39.6316 | 35.5333 | 14.0595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.4154 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1682 | Monta Vista-Big Basin Sw 19 to Big Basin |  |  | Bonny Doon CDP, Santa Cruz ¦ Cupertino, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Address 15 miles of aging infrastructure on the Monta Vista – Burns 60 kV Line located in Tier 2 and 3 fire risk zones in Santa Clara and Santa Cruz Counties between Monta Vista and Big Basin Substations. The work includes the installation, replacement and reframing of poles, vibration dampers and insulators. The project will also address any line maintenance tags that are to be completed at that time, as well as completing the right-of-way (ROW) expansion tree trimming project for the line. During this timeframe the project scope was reduced to the 15-mile section from Monta Vista to Big Basin in order to better address risk mitigation and gain execution efficiencies. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Targeted Line Reliability | NA | 2024-04-10 | 60 | NA | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 5.9 | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 78 | RBPPF - TBD | Yes | 5767513 | T.0000262 | MONTA VISTA-BIG BASIN SW 67 TO SW 19 | 3 | 94 | 5747825 | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2029-05-15 | NA | 2029-10-31 | NA | FALSE | NA | NA | 450.9624 | 19718.5549 | 76.7264 | 37.0443 | 33.526 | 13.2144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450.9624 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1683 | Monta Vista-Big Basin Sw 67 to Sw 19 |  |  | Bonny Doon CDP, Santa Cruz ¦ Cupertino, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Address 15 miles of aging infrastructure on the Monta Vista – Burns 60 kV Line located in Tier 2 and 3 fire risk zones in Santa Clara and Santa Cruz Counties between Monta Vista and Big Basin Substations. The work includes the installation, replacement and reframing of poles, vibration dampers and insulators. The project will also address any line maintenance tags that are to be completed at that time, as well as completing the right-of-way (ROW) expansion tree trimming project for the line. During this timeframe the project scope was reduced to the 15-mile section from Monta Vista to Big Basin in order to better address risk mitigation and gain execution efficiencies. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Targeted Line Reliability | NA | 2024-04-10 | 60 | NA | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 3.7 | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 78 | RBPPF - TBD | Yes | 5767318 | T.0000262 | MONTA VISTA-BIG BASIN SW 67 TO SW 19 | 3 | 94 | 5747825 | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-08-11 | NA | 2028-11-02 | NA | FALSE | NA | NA | 841.1969 | 19877.6192 | 109.3399 | 63.4792 | 60.2489 | 25.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841.1969 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1684 | Maple Creek#Willow Creek 60 kV Reliabili |  |  | Hoopa CDP, Humboldt ¦ Humboldt ¦ Willow Creek CDP, Humboldt | Increase reliability along the Maple Creek-Hoopa 60kV line by rebuilding a 20-mile section with new transmission poles and other reliability work. | Transmission Line - Switch | Upgrade/Retrofit | NA | Reliability | Targeted Line Reliability | NA | 2024-04-09 | 73 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 84 | NA | NA | 5747824 | T.0000609 | MAPLE CREEK-WILLOW CK 60KV RELIABILITY | 3 | 94 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5121-E | 2017-08-08 | Approved | 2017 | Operational | 2 | 2020-07-06 | 2018-01-29 | 2020-09-29 | Construction Delays | FALSE | 15900 | NA | 10919.4919 | 10919.4919 | 1361.9745 | 7133.4455 | 534.1956 | -55.5298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10919.4919 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 | 0 | 9989.7945 | 509.658 | -52.9791 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $20 Mil - $30 Mil ¦ $50 Mil – $75 Mil
| 1685 | Ph 2-Maple Ck- Willow Ck REL |  |  | Hoopa CDP, Humboldt ¦ Humboldt ¦ Willow Creek CDP, Humboldt | Increase reliability along the Maple Creek-Hoopa 60kV line by rebuilding a 20-mile section with new transmission poles and other reliability work. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Targeted Line Reliability | NA | 2024-04-09 | 64 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 10 | NA | 60 | NA | 534 | Not Available | Not Available | NA | NA | 5791525 | T.0000609 | MAPLE CREEK-WILLOW CK 60KV RELIABILITY | 3 | 94 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6161-E | 2021-04-16 | Approved | 2021 | Operational | 2 | 2021-07-23 | 2020-06-30 | 2021-10-05 | Permitting | FALSE | 15900 | NA | 16285.8328 | 16285.8328 | 0 | 73.7602 | 16446.2068 | -245.7801 | 11.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 16285.8328 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 12841.0551 | -190.7161 | 9.0367 | 0 | 0% | NA | NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $20 Mil - $30 Mil ¦ $50 Mil – $75 Mil
| 1686 | Ph 3-Maple Ck- Willow Ck REL |  |  | Hoopa CDP, Humboldt ¦ Humboldt ¦ Willow Creek CDP, Humboldt | Increase reliability along the Maple Creek-Hoopa 60kV line by rebuilding a 20-mile section with new transmission poles and other reliability work. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Targeted Line Reliability | NA | 2024-04-09 | 66 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 10.5 | NA | 60 | NA | 534 | Not Available | Not Available | NA | NA | 5791526 | T.0000609 | MAPLE CREEK-WILLOW CK 60KV RELIABILITY | 3 | 94 | NA | 2012 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6161-E | 2021-04-16 | Approved | 2021 | Operational | 2 | 2022-07-01 | 2020-06-30 | 2022-11-07 | Permitting | TRUE | 15900 | NA | 36277.7911 | 36277.7911 | 0 | 15.3634 | 485.1761 | 27920.8998 | 7856.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 36277.7911 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 23255.3304 | 6412.05 | 0.0756 | 0% | NA | NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $20 Mil - $30 Mil ¦ $50 Mil – $75 Mil
| 1687 | EXCHEQUER-YOSEMITE 70KV RELIABILITY - BEAR VALLEY SUB TO BRICEBURG SW |  |  | Mariposa | Replace/raise towers, install new lattice steel interset poles, replace insulators, add bird spikes, and re-tension and re-conductor identified portions of the Exchequer-Yosemite 70kV transmission line (~40 miles) to address California Public Utilities Commission (CPUC) General Order 95 (GO-95)1 infractions. Achieve Our Mission to safely and reliably deliver affordable and clean energy to our customers by striving to be the safest gas and electric company in the country and running an operationally excellent, resilient system: The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | T.0000270 | Reliability | Targeted Line Reliability | NA | 2024-04-10 | 119 | NA | Other - Status Quo | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 3.8 | NA | 70 | NA | 534 | 1. Work that prevents fire ignition | NA | NA | NA | 5774210 | T.0000322 | EXCHEQUER-YOSEMITE 70KV RELIABILITY | 5 | 94 | NA | 2011 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5486-E | 2019-02-28 | Approved | 2019 | Operational | 2 | 2019-09-16 | 2019-06-28 | 2019-12-23 | NA | FALSE | 24800 | NA | 10787.2648 | 10787.2648 | 12045.339 | -1280.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10787.2648 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 9614.4085 | -1016.6002 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1688 | EXCHEQUER-YOSEMITE 70KV RELIABILITY - BRICEBURG SW TO TOWER 024/99 |  |  | Mariposa | Replace/raise towers, install new lattice steel interset poles, replace insulators, add bird spikes, and re-tension and re-conductor identified portions of the Exchequer-Yosemite 70kV transmission line (~40 miles) to address California Public Utilities Commission (CPUC) General Order 95 (GO-95)1 infractions. Achieve Our Mission to safely and reliably deliver affordable and clean energy to our customers by striving to be the safest gas and electric company in the country and running an operationally excellent, resilient system: The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | T.0000270 | Reliability | Targeted Line Reliability | NA | 2024-04-10 | 71 | NA | Other - Deferral | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 3.1 | NA | 70 | NA | 534 | 1. Work that prevents fire ignition | 75 | NA | NA | 5774211 | T.0000322 | EXCHEQUER-YOSEMITE 70KV RELIABILITY | 5 | 94 | NA | 2011 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6085-E | 2021-02-11 | Approved | 2021 | Operational | 2 | 2021-06-08 | 2018-06-29 | 2021-09-27 | Scope Change | FALSE | 24800 | NA | 10427.1255 | 10427.1255 | 2.9507 | 149.1691 | 10267.1481 | -2.9577 | 1.2913 | 0 | 0 | 0 | 0 | 0 | 0 | 10427.1255 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 9480.0672 | -2.6853 | 1.1724 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1689 | EXCHEQUER-YOSEMITE 70KV RELIABILITY - EXCHEQUER SUB TO BEAR VALLEY SUB |  |  | Mariposa | Replace/raise towers, install new lattice steel interset poles, replace insulators, add bird spikes, and re-tension and re-conductor identified portions of the Exchequer-Yosemite 70kV transmission line (~40 miles) to address California Public Utilities Commission (CPUC) General Order 95 (GO-95)1 infractions. Achieve Our Mission to safely and reliably deliver affordable and clean energy to our customers by striving to be the safest gas and electric company in the country and running an operationally excellent, resilient system: The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | T.0000270 | Reliability | Targeted Line Reliability | NA | 2024-04-10 | 71 | NA | Other - Deferral | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 6.5 | NA | 70 | NA | 534 | 1. Work that prevents fire ignition | 75 | NA | NA | 5767391 | T.0000322 | EXCHEQUER-YOSEMITE 70KV RELIABILITY | 5 | 94 | 5745129 | 2011 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5766-E | 2020-02-20 | Approved | 2020 | Operational | 2 | 2020-11-03 | 2018-06-29 | 2021-01-13 | Bundling Dependencies | FALSE | 24800 | NA | 10201.73 | 10201.73 | 793.6104 | 6286.6648 | 275.2319 | -8.4123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10201.73 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 9343.732 | -7.6264 | 0 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1690 | EXCHEQUER-YOSEMITE 70KV RELIABILITY - INDIAN FLAT SUB 35/203 TO 40/243 (EOL) |  |  | Mariposa | Replace/raise towers, install new lattice steel interset poles, replace insulators, add bird spikes, and re-tension and re-conductor identified portions of the Exchequer-Yosemite 70kV transmission line (~40 miles) to address California Public Utilities Commission (CPUC) General Order 95 (GO-95)1 infractions. Achieve Our Mission to safely and reliably deliver affordable and clean energy to our customers by striving to be the safest gas and electric company in the country and running an operationally excellent, resilient system: The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | T.0000270 | Reliability | Targeted Line Reliability | NA | 2024-04-10 | 73 | NA | Other - Deferral | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 5.1 | NA | 70 | NA | 534 | 1. Work that prevents fire ignition | 75 | NA | NA | 5774213 | T.0000322 | EXCHEQUER-YOSEMITE 70KV RELIABILITY | 5 | 94 | NA | 2011 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6085-E | 2021-02-11 | Approved | 2021 | Operational | 2 | 2021-08-02 | 2018-06-29 | 2021-11-08 | Scope Change | FALSE | 24800 | NA | 10556.5712 | 10556.5712 | 68.8133 | 32.9962 | 10290.3673 | 149.3124 | 8.3975 | 0 | 0 | 0 | 0 | 0 | 0 | 10556.5712 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 9373.014 | 134.3816 | 7.5578 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1691 | EXCHEQUER-YOSEMITE 70KV RELIABILITY - TOWER 024/99 TO INDIAN FLAT SUB 35/203 |  |  | Mariposa | Replace/raise towers, install new lattice steel interset poles, replace insulators, add bird spikes, and re-tension and re-conductor identified portions of the Exchequer-Yosemite 70kV transmission line (~40 miles) to address California Public Utilities Commission (CPUC) General Order 95 (GO-95)1 infractions. Achieve Our Mission to safely and reliably deliver affordable and clean energy to our customers by striving to be the safest gas and electric company in the country and running an operationally excellent, resilient system: The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | T.0000270 | Reliability | Targeted Line Reliability | NA | 2024-04-10 | 71 | NA | Other - Deferral | NA | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 11.4 | NA | 70 | NA | 534 | 1. Work that prevents fire ignition | 75 | NA | NA | 5774212 | T.0000322 | EXCHEQUER-YOSEMITE 70KV RELIABILITY | 5 | 94 | NA | 2011 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6085-E | 2021-02-11 | Approved | 2021 | Operational | 2 | 2021-07-07 | 2018-06-29 | 2021-09-27 | Scope Change | FALSE | 24800 | NA | 20422.0252 | 20422.0252 | 0.9102 | 43.231 | 20567.8386 | -192.7324 | 1.2913 | 0 | 0 | 0 | 0 | 0 | 0 | 20422.0252 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 18734.6324 | -175.0337 | 1.1727 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1692 | Drum-Rio Oso 115 kV Re-Build (Phase 1) |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | The project proposes to abandon and rebuild the first 11 miles of the 45-mile long Drum-Rio Oso #1 and #2 circuits. Specifically, 241 lattice steel structures and conductors in the current 11 mile tower line (dual tower configuration) will be replaced with a double-circuit 115kV tower line (single tower configuration) using fire resistant, self-weathering steel poles and components, conductors in the centerline of the existing ROW.The project will also widen the existing ROW, where required, as the current ROW is only 70 feet wide. By replacing the existing dual tower configuration with a single, double-circuit tower line and siting them in the existing ROW centerline, the project will eliminate the need for a more rigorous permitting process, avoid costlier ROW land acquisition costs, and provide the new tower line greater clearance distances from the edges of the ROW. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | SCADA Switch Installation | NA | 2024-04-01 | 109 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 11 | NA | 115 | NA | 2032 | 1. Work that prevents fire ignition | 83 | NA | NA | 5747900 | T.0000036 | Drum-Rio Oso 115kV Reliability | 3 | 94 | NA | 2012 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6073-E | 2021-01-29 | Approved | 2021 | Operational | 2 | 2021-11-01 | 2022-02-09 | 2022-03-11 | NA | TRUE | 54700 | NA | 19746.32 | 19746.32 | 508.0346 | 802.6707 | 13798.9415 | 3862.5146 | 198.5989 | 26.1041 | 0 | 0 | 0 | 0 | 0 | 19720.2159 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 18741.3367 | 190.3411 | 54.6131 | 0% | NA | NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $50 Mil – $75 Mil
| 1693 | Drum-Rio Oso 115 kV Re-Build (Phase 2) |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | The project proposes to abandon and rebuild the first 11 miles of the 45-mile long Drum-Rio Oso #1 and #2 circuits. Specifically, 241 lattice steel structures and conductors in the current 11 mile tower line (dual tower configuration) will be replaced with a double-circuit 115kV tower line (single tower configuration) using fire resistant, self-weathering steel poles and components, conductors in the centerline of the existing ROW.The project will also widen the existing ROW, where required, as the current ROW is only 70 feet wide. By replacing the existing dual tower configuration with a single, double-circuit tower line and siting them in the existing ROW centerline, the project will eliminate the need for a more rigorous permitting process, avoid costlier ROW land acquisition costs, and provide the new tower line greater clearance distances from the edges of the ROW. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | SCADA Switch Installation | NA | 2024-04-01 | 109 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 11 | NA | 115 | NA | 534 | 1. Work that prevents fire ignition | Not Available | NA | NA | 5784525 | T.0000036 | Drum-Rio Oso 115kV Reliability | 3 | 94 | NA | 2012 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6073-E | 2021-01-29 | Approved | 2021 | Operational | 2 | 2022-04-01 | 2022-02-09 | 2022-05-23 | NA | FALSE | 54700 | NA | 4908.2315 | 4908.2315 | 181.8546 | 29.919 | 326.9828 | 4332.809 | 27.3854 | 9.2806 | 0 | 0 | 0 | 0 | 0 | 4898.9509 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 0 | 4029.8861 | 22.5681 | 8.0133 | 0% | NA | NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $50 Mil – $75 Mil
| 1694 | Drum-Rio Oso 115 kV Re-Build (Phase 3) |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | The project proposes to abandon and rebuild the first 11 miles of the 45-mile long Drum-Rio Oso #1 and #2 circuits. Specifically, 241 lattice steel structures and conductors in the current 11 mile tower line (dual tower configuration) will be replaced with a double-circuit 115kV tower line (single tower configuration) using fire resistant, self-weathering steel poles and components, conductors in the centerline of the existing ROW.The project will also widen the existing ROW, where required, as the current ROW is only 70 feet wide. By replacing the existing dual tower configuration with a single, double-circuit tower line and siting them in the existing ROW centerline, the project will eliminate the need for a more rigorous permitting process, avoid costlier ROW land acquisition costs, and provide the new tower line greater clearance distances from the edges of the ROW. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Targeted Line Reliability | NA | 2024-04-01 | 110 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | TRUE | Heat Wave, Weather |  | 22 | NA | 115 | NA | 2032 | Not Available | Not Available | NA | NA | 5788868 | T.0000036 | Drum-Rio Oso 115kV Reliability | 3 | 94 | NA | 2012 | 2019 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6073-E | 2021-01-29 | Approved | 2021 | Operational | 2 | 2022-10-03 | 2022-02-09 | 2023-10-23 | Prioritization | TRUE | 54700 | NA | 28918.3567 | 29211.5263 | 0 | 0 | 15.5678 | 17297.3409 | 11500.4379 | 398.1798 | 0 | 0 | 0 | 0 | 0 | 28813.3465 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 | 0 | 0 | 0 | 0 | 24879.368 | 107.3286 | 0% | NA | 2.3 ¦ Electric Operations Risk Management | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $50 Mil – $75 Mil
| 1695 | Colgate-Challenge 60kV Imprv TLine Relia |  |  | Challenge-Brownsville CDP, Yuba ¦ Yuba | The project proposes to upgrade approximately 13 miles of the Colgate-Challenge 60kV line. Reliability upgrades include rotten pole replacements, reframes, replacement or installation of damaged and missing hardware, and raptor mitigation on 183 Structures between the Colgate and Challenge Substations. A four mile transmission reconductor with #2 ACSR will also be completed from structure 8/151 to the Challenge Substation. KPF Switch #19, Located at structure 5/99, will be replaced with a Triangular SEECO 70kV SCADA Switch with Special Motor Operator and Vacuum Interrupter. Wood poles will be replaced with light duty steel poles (LDSP’s). Note: Some field drilling will be required for LDSP installation. Helicopter and crane set procedures will be used for 103 pole structures and 43 anchors. Electric Transmission General Construction will perform their own pre-drilled holes at the pole and anchor set locations. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Targeted Line Reliability | NA | 2024-04-02 | 21 | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 3 - Extreme, Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 4 | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 153 | NA | NA | 5747898 | T.0000112 | COLGATE-CHALLENGE RELIABILITY PROJEC | 1 | 94 | 5767640 | 2012 | 2017 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5114-E | 2017-07-14 | Approved | 2017 | Operational | 2 | 2018-09-17 | 2018-10-02 | 2021-06-30 | Weather | FALSE | 9971 | NA | 13283.8988 | 13283.8988 | 946.1373 | 1485.8532 | 1914.9444 | 35.5614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13283.8988 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2024 | 0 | 0 | 11765.7416 | 30.9094 | 0 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1696 | Bridgeville-Garberville Imprv Tline Reli |  |  | Garberville CDP, Humboldt ¦ Humboldt | The purpose of this project is to determine the scope of improving reliability on the Bridgeville-Garberville 60kV Line. The Bridgeville-Garberville 60kV Line was placed on the list of worst performing circuits. This line is approximately 36 miles long and has a total of 490 structures. This project proposes to do any of the following items that are deemed appropriate by a thorough patrol and inspection: tree trimming, replace insulators, replace bond connectors with AMPACT connectors, bridge all distribution cross arms, reframe structures, secure or replace static ground wires, remove links to shorten jumpers and increase clearance, repair/replace structures, replace quadrant clams, replace vibration dampers, and adjust or replace switches. | Transmission Line - Switch | Upgrade/Retrofit | TBD | Reliability | SCADA Switch Installation | NA | 2024-03-14 | 65 | NA | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 36 | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 115 | RBPPF - TBD | Yes | 5747823 | T.0000044 | Bridgeville-Garberville 60kV Reliability | 3 | 94 | NA | 2012 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2014 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-02-19 | NA | 2027-11-10 | NA | FALSE | NA | NA | 48.1206 | 5215.1278 | 1.7134 | 3.2674 | 2.685 | 4.2847 | 3.3005 | 3.4752 | 0 | 0 | 0 | 0 | 0 | 47.5578 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1697 | ESSEX JCT ORICK RELIABILITY |  |  | Fieldbrook CDP, Humboldt ¦ Humboldt ¦ McKinleyville CDP, Humboldt ¦ Orick CDP, Humboldt ¦ Westhaven-Moonstone CDP, Humboldt | The purpose of this project is to determine the scope of improving reliability on the Essex Junction-Orick 60kV. Essex Junction-Orick 60kV was placed on the list of worst performing circuits. This line is approximately 30 miles long and has a total of 371 structures. This project proposes to do any of the following items that are deemed appropriate by a thorough patrol and inspection: tree trimming, replace insulators, replace bond connectors with AMPACT connectors, bridge all distribution cross arms, reframe structures, secure or replace static ground wires, remove links to shorten jumpers and increase clearance, repair/replace structures, replace quadrant clams, replace vibration dampers, and adjust or replace switches. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Targeted Line Reliability | NA | 2024-04-09 | 72 | NA | TBD | TBD | Zone 1 - HHZ, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 31 | NA | 60 | NA | 258 | 1. Work that prevents fire ignition | 633 | RBPPF - TBD | Yes | 5767554 | T.0000451 | ESSEX JCT ORICK RELIABILITY | 2 | 94 | 5752218 | 2013 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-02-23 | NA | 2027-08-06 | NA | FALSE | NA | NA | 1853.6398 | 1853.6398 | 201.8932 | 163.6964 | -0.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1853.6398 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1698 | KESWICK-TRINITY RELIABILITY PROJECT |  |  | French Gulch CDP, Shasta ¦ Keswick CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | The purpose of this project is to improve the reliability of the Keswick-Trinity 60 kV line. The original 31-mile reconductor scope of work has been reduced to the replacement of the existing 60kV manual switches with SCADA remote-operable switches mounted on tubular steel poles (TSPs): The expedited restoration enabled by the new switches will reduce the outage duration. The reconductor part of the scope was deemed unnecessary from a component factor and would not be more effective at reducing the duration time. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Targeted Line Reliability | NA | 2023-06-24 | 19 | NA | Wires - Reconductor/Line Rebuild Alternative | $2 Mil - $3 Mil | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 0.06 | NA | 60 | NA | 58 | Not Available | NA | NA | NA | 5767097 | T.0000140 | KESWICK-TRINITY RELIABILITY PROJECT | 1 | 94 | 5743843 | 2011 | 2018 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-12-10 | 2019-07-03 | 2019-03-27 | NA | FALSE | 2209 | NA | 2367.7422 | 2367.7422 | 234.2329 | 4.2383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2367.7422 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2019 ¦ 2020 ¦ 2024 | 2221.7412 | 3.9943 | 0 | 0 | 0 | 0 | 0% | NA | NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-D NOC, PTC or CPCN requirements
| 1699 | Nicolaus-Wilkens Slough 60kV line Pole |  |  | East Nicolaus CDP, Sutter ¦ Knights Landing CDP, Yolo ¦ Nicolaus CDP, Sutter ¦ Sutter ¦ Yolo | The purpose of this project is to improve the resistance of this line to failures caused by extreme wind speeds (in excess of 70mph) and to minimize future outages to Wilkins Slough Substation and 4 Reclamation District Substations. This project proposes to relocate/replace 274 wood transmission poles with light duty steel poles on the Nicolaus – Wilkins Slough 60kV Line, and Replace 2 manual switches on the District 1001 tap line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Targeted Line Reliability | NA | 2023-11-20 | 74 | NA | Wires - Reconductor/Line Rebuild Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | 43 | NA | 60 | NA | 240 | 2. Overhead With Strong Safety Link | 630 | RBPPF - TBD | Yes | 5775319 | T.0003076 | Nicolaus-Wilkins Slough 60kV line Pole | 3 | 94 | NA | 2017 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5459-E | 2018-12-28 | Approved | 2018 | On Hold | 4 | 2025-06-02 | 2022-10-11 | 2026-10-22 | Prioritization | FALSE | 13482 | NA | 2281.4807 | 11031.97 | 188.7582 | 173.1446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2281.4807 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1700 | Nicolaus-Wilkens Slough 60kV line Pole#2 |  |  | East Nicolaus CDP, Sutter ¦ Knights Landing CDP, Yolo ¦ Nicolaus CDP, Sutter ¦ Sutter ¦ Yolo | The purpose of this project is to improve the resistance of this line to failures caused by extreme wind speeds (in excess of 70mph) and to minimize future outages to Wilkins Slough Substation and 4 Reclamation District Substations. This project proposes to relocate/replace 274 wood transmission poles with light duty steel poles on the Nicolaus – Wilkins Slough 60kV Line, and Replace 2 manual switches on the District 1001 tap line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Targeted Line Reliability | NA | 2023-11-20 | 74 | NA | Wires - Reconductor/Line Rebuild Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave, Weather |  | 43 | NA | 60 | NA | 240 | 2. Overhead With Strong Safety Link | 630 | RBPPF - TBD | Yes | 5782846 | T.0003076 | Nicolaus-Wilkins Slough 60kV line Pole | 3 | 94 | NA | 2017 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5459-E | 2018-12-28 | Approved | 2018 | On Hold | 4 | 2026-02-02 | 2022-10-11 | 2027-06-24 | Prioritization | FALSE | 13482 | NA | 58.3617 | 1068.7777 | 55.5849 | 1.9176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.3617 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1701 | Kilarc-Cedar Creek 60 kV Reliability |  |  | Round Mountain CDP, Shasta ¦ Shasta | This project proposes to Evaluate the line and complete targeted reliability improvements as recommended on the Kilarc – Cedar Creek 60kV Line. | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Targeted Line Reliability | NA | 2023-12-20 | 67 | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave, Weather |  | 13 | NA | 60 | NA | 412 | 1. Work that prevents fire ignition | 192 | RBPPF - TBD | Yes | 5772894 | T.0002386 | Kilarc-Cedar Creek 60 kV Reliability | 1 | 94 | NA | 2018 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2027-10-06 | NA | 2028-03-31 | NA | FALSE | NA | NA | 829.2506 | 32725.6253 | 0.607 | 1.9631 | 4.2489 | 206.6536 | 592.0733 | 69.9624 | 0 | 0 | 0 | 0 | 0 | 814.139 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 0% | 100%
| 1702 | ELECTRA-VLY SPNGS REL./RECOND |  |  | Amador ¦ Calaveras ¦ Mokelumne Hill CDP, Calaveras ¦ Pine Grove CDP, Amador ¦ Pioneer CDP, Amador ¦ Red Corral CDP, Amador | This project proposes to reconductor the West Point-Valley Springs 60kV Line between Electra Substation and Valley Springs Substation to provide additional system capability to the area that serves electric customers in Calaveras County. The project scope of work includes the following: • Replace 181 wood poles with Light Duty Steel Poles (LDSP) and composite poles • Reconductor 10.9 miles line section with 715 All Aluminum Conductor (AAC) • Raise existing Tower 7/58 by 10 feet on the Tiger Creek-Valley Springs/Electra-Bellota 230kV • Install one SCADA Line Switch | Transmission Line - Conductor | Upgrade/Retrofit | TBD | Reliability | Targeted Line Reliability | NA | 2024-04-12 | 59 | NA | TBD | TBD | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 10.9 | NA | 60 | NA | 564 | 1. Work that prevents fire ignition | 1 | RBPPF - TBD | Yes | 5767631 | T.0003726 | ELECTRA TO WEST PT SCADA SWT. | 1 | 94 | 5743838 | 2015 | TBD | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-08-25 | NA | 2027-12-01 | NA | FALSE | NA | NA | 1964.7287 | 8397.6702 | 60.9762 | 94.4834 | 172.5491 | 358.1085 | 255.985 | 140.6418 | 0 | 0 | 0 | 0 | 0 | 1943.1913 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA | TBD | NA | 44% | 56%
| 1703 | MERCED FALLS-EXCHEQUER REL PROJECT |  |  | Mariposa ¦ Merced | This project will replace existing Lattice Steel Poles/Steel Towers with new Lattice Steel Poles, replace insulators, and reconductor identified portions of the Merced Falls-Exchequer transmission line (~6 miles) | Transmission Line - Conductor | Upgrade/Retrofit | NA | Reliability | Targeted Line Reliability | NA | 2024-02-16 | 91 | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 2 - Elevated, Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 5.9 | NA | 70 | NA | 290 | 1. Work that prevents fire ignition | 342 | NA | NA | 5767308 | T.0000270 | MERCED FALLS-EXCHEQUER REL PROJECT | 1 | 94 | 5743840 | 2012 | 2020 | Please refer to Attachment A of the corresponding TPR Transmittal Letter | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5294-E | 2018-05-03 | Approved | 2018 | Operational | 2 | 2020-09-08 | 2020-10-04 | 2020-12-07 | NA | FALSE | 12300 | NA | 7801.9408 | 7801.9408 | 97.2397 | 6344.9774 | 526.9145 | 4.331 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 7801.9408 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 | 0 | 6529.6096 | 470.6393 | 3.8676 | 0.11077 | 0 | 0% | NA | NA | NA | 0% | 100%
| 1704 | MWC 05: Projects < $1M |  |  | NA | NA | Other | New | NA | Other [See Notes] | Tools | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 2.4131 | 27.9566 | 36.3361 | 94.0813 | 0 | 777.4741 | 0 | 0 | 0 | 0 | 0 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] Not applicable as this line item is not a project
| 1705 | MWC 21: Projects < $1M |  |  | NA | NA | Other | New | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 21 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 270.055 | 0 | 350.5384 | 100.1475 | 847.5731 | 0 | 0 | 0 | 0 | 0 | 0 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] Not applicable as this line item is not a project
| 1706 | MWC 23: Projects < $1M |  |  | NA | NA | Other | New | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 23 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | -9563.2997 | 653.062 | 1129.7584 | 0 | 39.4317 | 0.4666 | 0 | 0 | 0 | 0 | 0 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] Not applicable as this line item is not a project
| 1707 | MWC 60: Projects < $1M |  |  | NA | NA | Transmission Line - Multiple | New | NA | CAISO Transmission Planning Standards | T-Line Capacity | NERC TPL Standards | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 60 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 849.4204 | 528.5111 | 479.7157 | 771.921 | 1463.6234 | 3109.7928 | 309.6709 | 368.0878 | 695.269 | 90.6314 | 60.4108 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] Not applicable as this line item is not a project
| 1708 | MWC 61: Projects < $1M |  |  | NA | NA | Substation - Multiple | New | NA | CAISO Transmission Planning Standards | Substation Capacity | NERC TPL Standards | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 61 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 5486.2493 | 2132.1686 | 2611.4679 | 1633.7069 | -11405.8143 | 3803.5006 | 3272.8051 | 326.9057 | 103.9137 | 434.9678 | 1256.0836 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [NERC/WECC/CAISO Standard/Requirement/Contingency] TPL-001-4 R2-R5 [CPUC Status] Not applicable as this line item is not a project
| 1709 | MWC 63: Projects < $1M |  |  | NA | NA | Other - Operations Tech | Upgrade/Retrofit | NA | Other [See Notes] | System Operations | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 63 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 1246.0509 | 17835.1691 | 18440.1644 | 24845.2447 | 28144.6268 | 36742.9819 | 1102 | 8 | 0 | 0 | 0 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] Not applicable as this line item is not a project
| 1710 | MWC 64: Projects < $1M |  |  | NA | NA | Substation - Circuit Breaker | Replace | NA | Asset Condition | Age/Condition - Replace Breakers | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 64 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 589.0376 | 82.6986 | 82.9978 | 447.6468 | 127.3157 | 43.7364 | 389.8872 | 0 | 0 | 0 | 0 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1711 | MWC 65: Projects < $1M |  |  | NA | NA | Substation - Multiple | Replace | NA | Emergency Event | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 65 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 15517.5907 | 18694.289 | 16159.5611 | 14198.3172 | 16478.1694 | 12243.0078 | 788.717 | 29.1758 | 0 | 0 | 0 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1712 | MWC 66: Projects < $1M |  |  | NA | NA | Substation - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Other Substation Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 66 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 4515.6155 | 2917.1798 | 2717.0539 | 4419.5011 | 871.3977 | 618.6215 | 0 | 0 | 0 | 0 | 4813.0292 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1713 | MWC 67: Projects < $1M |  |  | NA | NA | Substation - Modular Protection and Automation Control Building | Upgrade/Retrofit | NA | Other [See Notes] | Modular Protection and Automation Control | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 67 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 3917.9467 | 4127.6179 | 3176.5574 | 1612.5692 | 2823.9432 | 9673.8772 | 5362.1371 | 4106.0948 | 2647.5484 | 999.609 | 1332.5447 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Infrastructure Enhancement [CPUC Status] Not applicable as this line item is not a project
| 1714 | MWC 68: Projects < $1M |  |  | NA | NA | Substation - Transformer | Replace | NA | Asset Condition | Age/Condition - Replace Transformers | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 68 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 274.9551 | 376.3064 | 454.0487 | 633.783 | 88.3782 | 28.3182 | 0 | 0 | 0 | 0 | 0 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1715 | MWC 70: Projects < $1M |  |  | NA | NA | Transmission Line - Pole/Tower | Replace | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 70 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 354.9852 | 412.8314 | 1437.5258 | 1469.7875 | 2238.5441 | 122.5635 | 0 | 0 | 0 | 0 | 2804.3214 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1716 | MWC 71: Projects < $1M |  |  | NA | NA | Transmission Line - Right of Way | Upgrade/Retrofit | NA | Reliability | Safety - Line Right of Way Access | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 71 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 53.8632 | 113.083 | 780.6991 | 137.2075 | 264.0556 | 0.9229 | 0 | 0 | 0 | 0 | 918 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1717 | MWC 72: Projects < $1M |  |  | NA | NA | Transmission Line - Underground | Replace | NA | Asset Condition | Age/Condition - Replace Underground System | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 72 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 0 | 0 | 32.0545 | 22.6864 | 33.0334 | 34.429 | 0 | 0 | 0 | 0 | 89 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1718 | MWC 82: Projects < $1M |  |  | NA | NA | Transmission Line/Substation | New | NA | Work Requested by Others | Generation Interconnection | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 82 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | TRUE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 2232.38 | 23846.425 | -3430.0805 | 11363.761 | 23337.3333 | 24853.0747 | 14775.0407 | 5735.7516 | 945.6816 | 133.6808 | 90.4102 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1719 | MWC 92: Projects < $1M |  |  | NA | NA | Transmission Line - Multiple | Replace | NA | Emergency Event | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 92 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 12.6772 | 0 | 410.5795 | 263.3458 | 550.1081 | 212.7391 | 0 | 0 | 0 | 0 | 0 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1720 | MWC 93: Projects < $1M |  |  | NA | NA | Transmission Line - Multiple | Replace | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 93 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 4355.31 | 4138.2336 | 7467.2273 | 5296.1256 | 5737.416 | 5183.349 | 279.0522 | 0 | 0 | 0 | 460.0394 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1721 | MWC 94: Projects < $1M |  |  | NA | NA | Transmission Line/Substation | Upgrade/Retrofit | NA | Reliability | Substation Reliability | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 94 | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 4358.1194 | 2843.5954 | 1007.5339 | 2284.467 | 294.2736 | 82.3483 | 682.5784 | 0 | 0 | 0 | 330.3217 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1722 | MWC 2F: Projects < $1M |  |  | NA | NA | Other - IT | Upgrade/Retrofit | NA | Other [See Notes] | IT | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 317.4732 | 702.4978 | 4149.2055 | 2256.5801 | 4658.7774 | 5173.3679 | 717 | 0 | 0 | 0 | 0 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [Primary Purpose] Operations Support [CPUC Status] Not applicable as this line item is not a project
| 1723 | MWC 3F: Projects < $1M |  |  | NA | NA | Substation - Protection Relay | Replace | NA | Asset Condition | Age/Condition - Replace Relays | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3F | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 17382.5349 | 26437.7753 | 14157.7226 | 18858.8277 | 18119.6118 | 12726.8207 | 276.336 | 0.4592 | 0 | 0 | 6150.0684 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project
| 1724 | MWC 3N: Projects < $1M |  |  | NA | NA | Other - Physical Security | Upgrade/Retrofit | NA | Physical Security | Security Upgrades | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3N | NA | NA | NA | Please refer to Attachment A of the corresponding TPR Transmittal Letter | NA | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | NA | NA | NA | NA | NA | NA | FALSE | NA | NA | NA | NA | 217.5907 | 139.4628 | 5.1489 | 0.0911 | 74.6994 | 2149.8725 | 0 | 0 | 0 | 0 | 0 | NA | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | NA | NA | NA | NA | NA | NA | 0% | NA | NA | NA | 44% | 56% | [CPUC Status] Not applicable as this line item is not a project

## Data Field Descriptions
Line | Transmission Project Data Field | Format | Example | Input Terms and Descriptions | PG&E Notes
1 | Row/Line No. | Number (whole number) | 4 | Row/line number in spreadsheet. Include separate project lines, as described and required in data fields 26-28, for all subparts, i.e., ID #1 of all FERC-jurisdictional electric transmission projects, including generator interconnection-related network upgrades: 1. the total cost of which At Unique ID #2 will at any point equal or exceed $1 million. In the event that there is no ID#2 to provide, the million-dollar threshold applies to ID #1. and 2. for which there were capital expenditures in the last five years OR for which any capital expenditures are anticipated in the current or next four years, regardless of the actual or anticipated operative date. Each project should have at least one Row/Line No. in this spreadsheet, as subparts of projects will require additional project lines.
Project Description
2 | Project Name | Text String, separated by " ¦ " as necessary | Manzanita Substation | Include Project Name at date of report filing. Identify all prior names of the project and other names currently used in different venues, including the name as approved and included in the CAISO's TPP. | Please refer to Unique Utility ID#2 for the CAISO TPP Project Name
3a | Latitude | Number (decimal), separated by " ¦ " for multiple locations; NA if no geolocation | 20.234 ¦ 19.983 | Positive number indicates north of equator. Subject to redaction in the public data.
3b | Longitude | Number (decimal), separated by " ¦ " for multiple locations; NA if no geolocation | -132.018 ¦ -132.231 | Negative number indicates west of Prime Meridian. Subject to redaction in the public data.
4 | Location 2 | Text String, with comma separator between City and County. Multiple entries separated by " ¦ ". Order of values to be consistent with latitude and longitude values * City1, County1 ¦ City2, County2 | Berkeley, Alameda ¦ Concord, Contra Costa | All Cities and Counties included in the scope of the project. | Please note some assets have locations in a given county that does not have a a city. This is the case where only one location is provided. "CDP" refers to Census Designated Place.
5 | Project Description | Text String | This project will repair the transmission line connecting 4th and Townsend to the East Northfork station which failed as consequence of the 2019 San Clemente Hedge Fire. Assets to be replaced include... at ....kV. | General project overview: what, where, and why. Discuss all assets to be installed and include all capacities (MVA) and voltages (kV).
6 | Project Description - What | Select text from drop-down menu | Substation - Circuit Breaker | Transmission line (new, reconductor, relocation), substation (breaker, transformer relay protection), etc.
7 | Project Description - Action Taken | Select text from drop-down menu(s) | Upgrade/Retrofit | See drop-down menu for options. If more than two options are required, select "Multiple Options" in second column and provide remaining responses, pipe-delimited, in "Notes" data field. If the primary or secondary purpose relates to complying with a NERC, WECC, or CAISO requirement, list the specific standard(s), requirement(s), and/or any contingencies that are being addressed.
8 | Project Dependencies | Number (whole) indicating required project or projects' Unique ID #(s), separated by " ¦ " as necessary | 235435 ¦ 432787 | Identify all other projects (Unique ID #1) in the spreadsheet that this project depends on and/or whose construction will be bundled with this project. | For a given PO, Project Dependencies are identified as T.Dots if part of a different T.Dot. While POs can be populated and would require including many POs in this field, the T.Dot is the most complete option as it captures the entire project. Projects within the same T.Dot are inherently dependent and therefore N/A is populated.
9 | Primary Purpose | Select text from drop-down menu | Reliability | May include, but not limited to: CAISO Transmission Planning Standards (NERC Compliance and contingency code, WECC Requirement (and the specific requirement)), Reliability, Load Growth, Local Capacity Requirement, Address Results of Power Flow Analysis, Address Results of Protection Studies, Physical Security, Policy, Economic, Generator Interconnection, Work Requested by Others, Age/End of Life, Wildfire Mitigation, Field Test Results, Emergency Event, Location, Environmental Conditions, Safety, Asset Condition, or Other. In the "Notes" data field, please explain a purpose identified as "Other" or provide additional details on the purpose identified.
10 | Secondary Purpose | Select text from drop-down menu | Age/Condition - Anti Climb Guards | May include, but not limited to: 3rd Party Damage, Age/Condition, Age/Condition - 230/115/70/60 kV Relay Replacement, Age/Condition - 500 kV Relay Replacement, Age/Condition - Anti Climb Guards, Age/Condition - Insulator Replacement - Steel, Age/Condition - Insulator Replacement - Wood, Age/Condition - Raptor Protection - Steel, Age/Condition - Replace 230/115/70/60 kV Breakers, Age/Condition - Replace 230/115/70/60 kV Transformers, Age/Condition - Replace 500 kV Breakers, Age/Condition - Replace 500 kV Transformers, Age/Condition - Replace Boardwalks, Age/Condition - Replace Breakers, Age/Condition - Replace Civil Structures, Age/Condition - Replace Conductor, Age/Condition - Replace Insulators, Age/Condition - Replace Other Substation Equipment, Age/Condition - Replace Other T-Line Equipment, Age/Condition - Replace Reactors, Age/Condition - Replace Relays, Age/Condition - Replace Relays, Age/Condition - Replace SCADA/RTU, Age/Condition - Replace Steel Poles, Age/Condition - Replace Switches, Age/Condition - Replace Transformers, Age/Condition - Replace Underground System, Age/Condition - Replace Wood Poles, Age/Condition - Switch Replacement - Steel, Age/Condition - Switch Replacement - Wood, Age/Condition - Targeted Relay Replacement, Age/Condition - Wood Pole Reframe, Animal Abatement, Automation, Bus Upgrade, Compliance - Remove Idle Facilities, Construct Roads/Gates/Culverts, Emergency Response - Fire Related, Emergency Response - Storm Related, Environmental, Facility Relocation, Fire Protection, Generation Interconnection, GO95 Mitigation - Steel, Install SCADA/RTU, Line Reconductoring, Line Termination, Load Interconnection, Modular Protection and Automation Control, NERC CIP Compliance, NERC Compliance - GO 95, New Substation, New T-Line, Priority 1 Steel Structure Replacement, Priority 1 Wood Structure Replacement, Protection NERC Compliance, Relay Upgrades, Replace Breakers, Replace Other Substation Equipment, Replace Transformers, Safety - Line Right of Way Access, SCADA Emergency Replacement, SCADA Switch Installation, Security Upgrades, Seismic Upgrade - Replace Conductor, Special Protection Scheme, Substation Capacity, Substation Reliability, System Design Upgrade, System Operations, Targeted Line Reliability, T-Line Capacity, T-Line Emergency, T-Line Reliability, Tools, Transformer Addition/Replacement, Underground Emergency, Voltage Conversion, Voltage Support. If the secondary purpose is to comply with a NERC, WECC, or CAISO requirement, list the standard, requirement, and/or any contingencies that are being addressed in the "Notes" data field.
11 | NERC/WECC/CAISO Standard/Requirement/Contingency | Select text from drop-down menu(s) | CIP-006 | See drop-down menu for options. If more than two options are required, select "Multiple Options" in second column and provide remaining responses, pipe-delimited, in "Notes" data field. If the primary or secondary purpose relates to complying with a NERC, WECC, or CAISO requirement, list the specific standard(s), requirement(s), and/or any contingencies that are being addressed in the "Notes" data field.
12 | Last Inspection | Date, formatted YYYY-MM-DD if text; NA if not yet inspected | 2019-12-10 | Specific date when the last inspection of the asset being repaired, replaced, or upgraded occurred. | The latest inspection date for overhead transmission lines is based on detailed ground and/or aerial inspections. These are done every 3 years for HFTD lines and 5 years for non-HFTD lines (3 years if 500 kV). Please note that transmission lines can be inspected via climbing as triggered, inspected by infrared (annually if Tier 3, 3 years if Tier 2 or Zone 1, and 5 years if non -HFTD), and are patrolled annually. “N/A” is noted for projects that do not impact assets that require inspections (e.g. technology or operational upgrades), or are programs that cover multiple assets in various locations (e.g. pole replacement). "TBD" is noted for projects that involve new assets that have yet to be installed.
13 | Age of Asset | Number (whole number) | 12 | Age in years from original in-service date of the asset being repaired, replaced, or upgraded. | The age of asset is a calculated value based on installation data of the asset at the functional location. For transmission lines, the assets on each line are not typically all the same age. Therefore, the age reflects an approximation of the oldest asset on the line for replacement projects. “N/A” is noted where there is no functional location for the project, programmatic work, or if the project is installing a new asset (e.g. new transmission line).
14 | Types of Analyses | Select text from drop-down menu | Load Flow | Types of analyses that have been performed on the asset being repaired, replaced, or upgraded (e.g., load flow, short circuit, corrosion). List all field test and results that indicated the need for the project, and include inspector ID, when available in the "Notes" data field. | For all Analyses listed, results of these analyses are included in the AAs & BCs. For Steady State Power Flow System Analysis, please also refer to annual CAISO Transmission Plan & corresponding attachments (Reliability Assessment Study Results, Detailed Policy Assessment, Production Cost Simulation and Economic Assessment Detailed Results) for these results.
15a | Alternative Solutions and Costs - Solutions | Select text from drop-down menu(s) | Dynamic System Analysis | See drop-down menu for options. If more than two options are required, select "Multiple Options" in second column and provide remaining responses, pipe-delimited, in "Notes" data field. Include all alternative solutions to the project that were considered and the costs of all alternatives considered. | In evaluating Projects, PG&E considers feasible alternatives and Status Quo is included as an alternative. Generally, a "YES" in the Status Quo column is defined as replacing a like-for-like asset to continue existing operations without providing for increases in capacity, reliability or functionality. In some cases, a "YES" in the Status Quo column might involve the deferral of a proposed project. Please refer to other columns in Item 15 for alternative descriptions and costs included in the business cases. Where "N/A" is indicated, that refers programmatic work. Where "TBD" is indicated, that refers to planning and/or where the Project does not have utility approval yet.
15b | Alternative Solutions and Costs - Costs | Select text from drop-down menu(s) | $5 Mil - $10 Mil | See drop-down menu for options. If more than two options are required, select "Multiple Options" in second column and provide remaining responses, pipe-delimited, in "Notes" data field. If multiple responses as included for the Sulutions and Costs fields, please provide costs in the same order as solutions.
16 | CPUC Fire Threat Zone/Rating | Text String, separated by " ¦ " as necessary, or NA | HFTD Tier 2 | Indicate whether the project is located in Tier1, Tier 2, or Tier 3 of CPUC's High Fire-Threat Districts (HFTD) or Zone 1 in CalFire/USFS High Hazard Zone (HHZ). | If a project footprint spans multiple Tiers/Zone, all are listed. Tier 1 is any location that is not Tiers 2 & 3 and Zone 1. Programmatic Work is assigned Tier 1 unless the program is work specifically related to Tiers 2 & 3.
17 | Wildfire Related | Boolean, TRUE or FALSE, divided by " ¦ " | TRUE ¦ TRUE ¦ FALSE | Indicate whether the project is 1. related to repairing wildfire damage, 2. a measure identified in the Wildfire Mitigation Plan, or 3. is related to wildfire in some other way. If #3, please explain in the "Notes" data field.
18 | RAMP | Boolean, TRUE or FALSE | TRUE | Indicate whether the project is a proposed mitigation measure in the utility's Risk Assessment & Mitigation Phase (RAMP).
19 | Other Environmental Factors | Text String, or NA | Project exists in CA Building Climate Zone 3 which presents a high risk of accelerated oxidation or steel structures due to coastal humidity and salt exposure. | Environmental factors in the project's location that may affect the length of the asset's service life.
20 | Project Manager | Text String: Last, First | Doe, John | Person in charge of the implementation of this project for the Utility.
21 | Transmission Project Size (length in miles) | Number (decimal), or NA | 42.66 | Miles of transmission power lines included in the project.
22 | Substation Project Footprint (acres) | Number (decimal), or NA | 12.25 | Acres of substation footprint included in the project.
23 | Transmission Voltage Level (kV) | Number (whole), separated by " ¦ " as necessary, or NA | 230 | Use kV for transmission power lines ratings.
24 | Substation or Transformer Capacity (MVA and/or kV) | Text String, separated by " ¦ " as necessary, or NA if unrelated | 115kV | Use MVA and/or kV for substations.
25 | Utility Prioritization Ranking | Number (whole), in reference to ranking system identified in field name | 1 | Using the Utility's prioritization ranking. If multiple metrics are used to prioritize projects, please include a separate data subfield for each. (Sub-columns can be created to accommodate multiple or tiered ranking methodologies.) | Loading Order was implemented in 2019 and applied to 2019 and beyond in the portfolio. Loading Order prioritization evaluates and prioritizes the work portfolio for Electric Operations in alignment with the reduction of both wildfire ignition and safety risk. RIBA scoring inputs (e.g. Safety, Environmental and Reliability) and Classifications (e.g. Required work flags) are used to aid in the assignment of Loading Order. Loading Order comprises of a scale from 1 to 9, with 1 being the highest priority and 9 being the lowest priority. "N/A" is listed for Projects before PG&E's usage of Loading Order or programmatic projects. Circuit Based Plan was implemented in 2020 and applied to 2020 and beyond in the portfolio. The CBP ranks each transmission circuit and substation 1-N, based on varying weighted risk values from a PSPS, safety, wildfire, reliability, and commitment/capacity driven perspective. CBP is used to identify critical circuits lines and substations, and also aid bundling of work occurring on the same line. "N/A" is listed for Projects before PG&E's usage of CBP. RBPPF was implemented in 2023 and applied to 2024 and beyond in the portfolio. Below is a description of the RBPPF Funding Tiers. o IGP: Electric distribution circuit, substation and transmission line capital investments that have been bundled and prioritized using PG&E’s Integrated Grid Planning approach. o Tier 5: Proposed non-IGP investment with the highest risk-reduction/compliance/capacity/reliability/other TNS objectives impact and highest urgency. Financial and/or opportunity losses due to inability to fund Tier 5 investments cannot be recovered in future periods. o Tier 4: Proposed non-IGP investment with high risk-reduction/compliance/capacity/reliability/other TNS objectives impact or high urgency. Financial and/or opportunity losses due to inability to fund Tier 4 investments are at high risk for non-recovery in future periods. o Tier 3: Proposed non-IGP investment with medium risk-reduction/compliance/capacity/reliability/other TNS objectives impact or medium urgency; financial and/or opportunity losses due to inability to fund Tier 3 investments are at medium risk for non-recovery in future periods. o Tier 2: Proposed non-IGP investment with low risk-reduction/compliance/capacity/reliability/other TNS objectives impact or low urgency; financial and/or opportunity losses due to inability to fund Tier 2 investments are recoverable in future periods. o Tier 1: Proposed non-IGP investment with no risk-reduction/compliance/capacity/reliability/other TNS objectives impact and no urgency; Financial and/or opportunity losses due to inability to fund Tier 1 investments are recoverable in future periods. o N/A: listed for Projects before PG&E’s usage of RBPPF o RBPPF - TBD: is listed for Projects that are in-flight but have not been included in the Investment Plan
26 | Utility Unique ID #1 | Text String | 78493 | Most specific (PG&E = Planning Order, SCE = SCE ID, SDG&E = Project ID)
27 | Utility Unique ID #2 | Text String | 432 | Less specific (PG&E = T.dot, SCE = Capital Work Breakdown Structure, SDG&E = Budget Code)
28 | Utility Unique ID #3 | Text String | 92 | Least specific (PG&E = Major Work Category, SCE = Project Identification Number , SDG&E = NA)
29 | Changes in Unique IDs | Date, formatted YYYY-MM-DD, and former identifiers: YYYY-MM-DD ¦ UID1 ¦ UID2 ¦ UID 3 If any components remain unchanged, use NA for those UIDs | 2022-05-05 ¦ NA ¦ NA ¦ 78322 | If any of the Unique IDs above changed at any time, please note the date of change and the former ID, using the presecribed format. | PG&E does not have a computerized method for tracking changes in unique IDs. However, PG&E took manual steps to provide the requested information for a portion of the Projects. PG&E is unable to provide the date of the change as well.
Utility/CAISO Approval and FERC Rate Cases
30 | Utility Approval | Boolean: TRUE or FALSE | TRUE | "TRUE" if the Utility self-approved the project; "FALSE" if not. | PG&E is treating this field as the Year of Advanced Authorization approval. Where "TBD" is indicated that means the Project has not yet advanced to the point at which the advanced authorization is presented to PG&E management for approval. Where "N/A" is indicated, an Advanced Authorization is not applicable.
AA Collected
31 | Year of Internal Utility Approval | Date, formatted YYYY-MM-DD, or NA | 2022-01-02 | If utility has approved the project, insert first year of internal approval. If not insert "NA." | PG&E is treating this field as the Year of the first approved Business Case. Where "TBD" is indicated that means the Project has not yet advanced to the point at which the first business case is presented to PG&E management for approval. Where "N/A" is indicated, a Business Case is not applicable.
BC Collected
32 | Process(es) for Utility Approval | Text String, or NA | Annual Capital Operating Plan Process | If utility has approved the project, insert utility approval process for which a description has been provided to the CPUC and Stakeholders. | Please refer to Attachment A of the Transmittal Letter
33 | Long term Transmission Investment Plan Inclusion | Year, formatted YYYY | 2022 | The year in which the project was first included in the utility's long-term transmission investment plan.
34 | CAISO Year | Year, formatted YYYY, or NA | 2019 | Insert the year when approved by CAISO. If not a CAISO-approved project, insert "NA".
35 | Transmission Planning Process ("TPP") Phase 3 | Boolean: TRUE or FALSE | FALSE | Please indicate with "TRUE" if any part of this project was subject to the competitive solicitation process in the TPP. In the "Notes" section briefly describe any portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. | Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
36 | Year(s) when considered in CAISO TPP | Years, formatted YYYY and separated by " ¦ ", or NA | 2020 ¦ 2021 | Indicate years in which the project was considered in the TPP. If considered in year(s) prior to CAISO approval, please indicate all years.
37 | Year when expected to be considered in CAISO TPP | Years, formatted YYYY and separated by " ¦ ", or NA | 2025 | If not yet considered in the CAISO TPP, indicate the year when it is expected to be considered in the CAISO TPP.
38 | Link to TPP where project has been considered, approved, and/or expected to be considered | URL | http://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | Insert active hyperlink to any TPP where project was considered, including years in which the project was not approved. | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request.
39 | Generator Interconnection and Deliverability Allocation Procedures (GIDAP) Related | Boolean: TRUE or FALSE | TRUE | Please indicate with TRUE or FALSE whether this transmission project is a transmission network upgrade related to generator interconnection(s).
CPUC Permit Status
40a | CEQA Status | Select text from drop-down menu | Final Certified | See drop-down menu for options. Include one of the following: Expected PEA Completion, PEA Deemed Complete, CEQA Draft Published, CEQA Final Published, Final Certified, TBD, Other [See Notes], or NA.
40b | CEQA Status - Date | Date, formatted YYYY-MM-DD, or NA | 2020-03-29 | Include the date that corresponds with the CEQA status.
41a | CEQA Document Type | Select text from drop-down menu | EIR | Examples include: IS/ND, IS/MND, EIR, Exempted, Other, or NA (If "Other," include explanation in the "Notes" data field.).
41b | NEPA Document Type | Select text from drop-down menu | EIS | Examples include: EIS, EA, Categorical Exclusion, Other, or NA (If "Other," include explanation in the "Notes" data field.).
42a | CEQA Lead Agency | Text String, separated by " ¦ " as necessary, or NA | CPUC | Examples include: CPUC, SWRCB, CSLC, NA etc. If more than two options are required, enter each, pipe-delimited.
42b | NEPA Lead Agency | Text String, separated by " ¦ " as necessary, or NA | USFS | Examples include: USFS, NA etc. If more than two options are required, enter each, pipe-delimited.
43 | CPUC Filing Type | Text String, or NA | PG&E AL 2355-E | NOC Advice Letter (AL), Application for 851, PTC, CPCN, or NA. If an AL, include the number. If an Application, include number.
44 | CPUC Date Filed | Date, formatted YYYY-MM-DD, or NA | 2022-04-08 | The year filed at the CPUC or insert "Not yet filed" with the expected filing date.
45 | CPUC Status | Select text from drop-down menu | Approved | Indicate "Approved", "Rejected", "To be Filed", "Filed and Under Review," "Other," or "NA" (If "Other" or "NA", include explanation in the "Notes" data field.).
46 | CPUC Status - Year | Year, formatted YYYY, or NA | 2019 | Insert the year this CPUC Status was determined.
Project Status
47 | Project Status | Select text from drop-down menu | Construction (10%-25%) | See drop-down menu for options. Examples include: Planning, Engineering less than 50% complete, Engineering more than 50% complete, Permitting, Construction (include percentage of construction completed at the time this data spreadsheet is provided (i.e., less than 10%, 10%-25%, 25%-50%, 50%-75%, greater than 75%), Operational, On Hold, Canceled, or Abandoned (if On Hold, Canceled, or Abandoned, include explanation in the "Notes" data field.). | PG&E is using the Project Status of Programmatic Work for buckets and Planning for forecast placeholders. PG&E’s current systems have no way to track engineering & construction percentages. The % provided for Engineering and Construction Project Statuses are a function of the day the data was pulled from PG&E systems and milestone start and end dates or both Engineering and Construction.
48 | AACE Class | Select text from drop-down menu | 3 | The current Estimate Class in AACE International's Cost Estimate Classification System at the time this data spreadsheet is provided.
49 | Construction Start Date | Date, formatted YYYY-MM-DD, or NA | 2025-06-01 | The date on which construction began or is expected to begin.
50 | Original Planned In-Service Date | Date, formatted YYYY-MM-DD, or NA* | 2025-06-01 | What was the expected in-service date when the project was first approved by the CAISO? If not a CAISO-approved project, provide the expected in-service date when the project was approved internally by the Utility.
51 | Current Projected or Actual In-Service Date | Date, formatted YYYY-MM-DD, followed by OAI indicator if applicable (or NA) | 2021-01-01 ¦ NA 2021-01-01 ¦ OAI | At the time the data was extracted from the Utility’s Database(s) as provided in Section 2.1.5 of the Transmission Project Review Process Description. Projects without identified in-service dates that are "Operative as Installed" should be identified as "OAI".
52 | Reason for Change in In-Service Date | Select text from drop-down menu(s) | Customer Action | See drop-down menu for options. If the current projected or actual in-service date varies more than six months from the original in-service date, please select all reasons for this change. If more than two options are required, select "Multiple Options" in second column and provide remaining responses, pipe-delimited, in "Notes" data field.
53 | In-Flight Projects | Boolean: TRUE or FALSE | TRUE | For projects with costs expected to go into rate base in the current rate year or in the following rate year at FERC, please indicate with "TRUE." If there will be no additions to rate base in either year, indicate with "FALSE."
Costs
54 | Original Projected Cost or Cost Range ($000) | Dollar value, or dollar value range, separated by " ¦ " | 2100 ¦ 2500 | Forecast cost or forecast cost range for Utility Unique ID #2, i.e., the totality of the project, at the earliest of CAISO, CPUC, or utility internal approval.
55 | Cost Cap ($000) | Dollar value and Text String, separated by " ¦ ", or NA | 2500 ¦ CAISO TPP | Insert Cost Cap on project if available, as well as the authority imposing the cost cap. This shall include any maximum cost determined to be reasonable and prudent in a CPUC proceeding or a cost cap set for a competitively bid project in the CAISO's Transmission Planning Process.
56 | Current Projected Total or Actual Final Cost ($000) | Dollar value | 78 | Updated projected fully-loaded total or actual fully loaded final cost of project. Projected total should be the anticipated sum of all capital expenditures, overhead,and AFUDC. Actual cost should be the total expenditures, overhead and AFUDC in the addition to rate base. Operational projects and all data must remain in this report for at least five (5) years after the last of the project's expenditures and capital additions.
57 | Actual Capital Expenditures ($000) | Dollar value | 12 | Please include separate columns for each of the previous five (5) years and one for actual expenditures for the current year as of the date the data was extracted. If these expenditures do not include overheads and AFUDC, please provide those year-by-year.
58 | Projected Capital Expenditures ($000) | Dollar value | 4650 | For the current year and four (4) future years, provide the year-by-year fully-loaded forecast capital expenditures for the project. Please include separate columns for each year. If these expenditures do not include overheads and AFUDC, please provide those year-by-year.
59 | Construction Work in Progress Expenditures ($000) | Dollar value | 2350 | Total amount of money that has been spent so far for the project through the last calendar year.
60 | Accrued Overhead ($000) | Dollar value | 12 | If the capital expenditures provided in Data Field #57 do not include Overhead, please provide the accrued Overhead through the last calendar year.
61 | Accrued AFUDC ($000) | Dollar value | 0 | If the capital expenditures provided in Data Field #57 do not include AFUDC, please provide the accrued AFUDC through the last calendar year.
62 | FERC: Year(s) | Years, separated by " ¦ ", or NA | 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | Insert ALL rate years when any costs of this project went - or are forecast to go - into FERC jurisdictional transmission rate base.
63 | Dollars Put into FERC Rate Base ($000) | Dollar Value, per year column e.g., FERC_dollars_in_rate_base_2022 | 500000 | Insert the year(s) and actual dollars added to FERC jursidictional transmission rate base on the project for each of the four prior years and the present year. This should include additional costs added to rate base in years after operation first occurred.
64 | Percentage of Bid | Percentage to two decimals, and Text String, separated by " ¦ " | 33.33% ¦ "SuperPower LLC is developing a third of the project as part of its "TransValley Electrification" project. See http://.... | Percentage (or actual cost) of project implemented by outside developer, as opposed to the incumbent utility. If there is a project being developed by a non-incumbent utility that relates to this project, please indicate the name of the project as approved in the CAISO TPP. | 0% of the projects included in the TPR data spreadsheet are not being implemented by an outside developer. However, there are projects being developed by a non-incumbent utility that relates to some of these projects. Please refer to Unique Utility ID #2 for the name of the project as approved in the CAISO TPP.
65 | Percentage and Value ($000) of Work Requested by Others Passed onto Ratepayers | Percentage to two decimals and/or dollar value. If both, separate by " ¦ ". If either is not provided, please enter NA. | 25.00% ¦ 2300 35% ¦ NA NA ¦ 50000 | If the project is work requested by others or customer-driven, what percentage of the projects costs has been - or is expected to be - passed onto ratepayers? If the dollar amount being passed onto ratepayers is fixed, then this number can be expressed as a dollar amount. Please provide the values in order, using an NA placeholder if either is not provided.
66 | Cost-Benefit Analysis | Percentage to two decimals, and ranking system identifier, separated by " ¦ " | 25.00% ¦ EnergyRank | The Cost-to-Benefit ratio. If the Utility's Cost-Benefit analysis related to its Risk-Based Decision-Making Framework (RDF) has not already been included in the "Utility Prioritization Ranking" data field above, please include it here. | N/A is populated for Operational projects. TBD is provided for in-flight projects that do not have a project specific CBR score yet.
67 | FERC Incentives | Test Strings, separated by " ¦ ", or NA | Abandoned Plant ¦ CWIP | List any project-specific transmission incentives granted under any FERC Orders. | FERC Incentives are in addition to ROE adder that PG&E may receive as a result of its participation in the CAISO. PG&E did not include the CAISO-adder incentive in the PDS.
68 | Percentage of Cost in High Voltage TAC | Percentage to two decimals | 23.05% | Insert % of project cost recovered in the high-voltage TAC.
69 | Percentage of Cost in Low Voltage TAC | Percentage to two decimals | 0% | Insert % of project cost recovered in the low-voltage TAC.
Notes
70 | Notes | Strings, inclusive of field identifiers in brackets, separated by 3 linebreaks ("\n\n\n"), or NA [ID1] String1 [ID2] String2 | [CEQA/NEPA Document Type] Form STD762 [CPUC Status] Approved in part following bifurcation. Details indeterminate as of 5/6/2024. Expected update and clarification by 8/1/2024. | Any additionally requested information or other needed details about the project that were not otherwise covered.

## Options Lists
06. Project Description - What | 07. Project Description - Action taken | 09. Primary Purpose | 10. Secondary Purpose | 11. NERC/WECC/CAISO Standard/Requirement/Contingency | 14. Types of Analyses | 15a. Alternative Solutions and Costs - Solutions | 15b. Alternative Solutions and Costs - Costs | 40. CEQA Status | 41a. CEQA Document Type | 41b. NEPA Document Type | 45. CPUC Status | 47. Project Status | 48. AACE Class | 52. Reason for Change in In-Service Date
Substation - Transformer | Upgrade/Retrofit | Load Growth | Age/Condition - 230/115/70/60 kV Relay Replacement | NERC FAC Compliance | Dynamic System Analysis | Wires - Reconductor/Line Rebuild Alternative | $2 Mil - $3 Mil | CEQA Draft Published | EIR | Categorical Exclusion | Administratively Complete and Under Technical Review | Engineering more than 50% complete | 3 | Clearances
Substation - Other Equipment | Replace | Reliability | Age/Condition | NERC BAL Compliance | Steady State Power Flow System Analysis | Wires - Location/Route Alternative | $1 Mil - $2 Mil | PEA Deemed Complete | IS/MND | EA | Filed and Under Administrative Review | Engineering less than 50% complete | 2 | Permitting
Substation - Multiple | New | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | 3rd Party Damage | NERC CIP Compliance | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | $0 Mil – $1 Mil | Expected PEA Completion | IS/ND | EIS | To be Filed | Planning | 1 | Weather
Substation - Line Termination | Removal | Address Results of Power Flow Analysis | Age/Condition - Anti Climb Guards | NERC PRC Compliance | Protection Studies | Wires - Minimum Required Scope (spot repair) Alternative | $5 Mil - $10 Mil | Final Certified | Other [See Notes] | NA | Rejected | Construction (under 10%) | 5 | Workforce
Substation - Circuit Breaker | Relocate | Local Capacity Requirement | Age/Condition - 500 kV Relay Replacement | WECC Audit Findings | Short Circuit Duty Analysis | Wires - Replacement Alternative | $3 Mil -$5 Mil | CEQA Final Published | Exempted | Other [See Notes] | Approved | Permitting | 4 | Material
Substation - Voltage Support Equipment | NA | Address Results of Protection Studies | Age/Condition - Insulator Replacement - Steel | NERC TPL Standards | Interconnection System Impact/Facilities Studies | Wires - Voltage Support/Reactive Support Alternative | $10 Mil -$15 Mil | TBD | NA |  | Advice Letter Filed and In-Process | Construction (10%-25%) | NA | Prioritization
Substation - Bus Arrangement | Multiple Options [See Notes] | Physical Security | Age/Condition - Insulator Replacement - Wood | CAISO Requirement | Other [See Notes] | Wires - New Substation Alternative | $15 Mil - $20 Mil | Other [See Notes] |  |  | Other [See Notes] | Construction (25%-50%) |  | Bundling Dependencies
Substation - Switch |  | Policy | Age/Condition - Raptor Protection - Steel | Other [See Notes] | Multiple Options [See Notes] | Wires - Bus Upgrade Alternative | $20 Mil - $30 Mil | NA |  |  | NA [See Notes] | Construction (50%-75%) |  | Customer Action
Substation - Protection Relay |  | Generator Interconnection | Age/Condition - Replace 230/115/70/60 kV Transformers | Multiple Options [See Notes] | NA | Non-Wires - Large Scale Energy Alternative | $40 Mil - $50 Mil |  |  |  |  | Operational |  | Completed Early
Substation - Modular Protection and Automation Control Building |  | Economic | Age/Condition - Replace 230/115/70/60 kV Breakers | NA |  | Wires - New T-Line Alternative | $30 Mil - $40 Mil |  |  |  |  | Construction (over 75%) |  | ISO Action
Other - IT |  | Wildfire Mitigation | Age/Condition - Replace Boardwalks |  |  | Other - Deferral | $100 Mil – $125 Mil |  |  |  |  | Abandoned |  | Project Design
Substation - Structure |  | Age/End of Life | Age/Condition - Replace 500 kV Transformers |  |  | Other - Status Quo | $75 Mil – $100 Mil |  |  |  |  | Canceled |  | Outage
Substation - Reactive Equipment |  | Work Requested by Others | Age/Condition - Replace 500 kV Breakers |  |  | Non-Wires - System DER Alternative | $50 Mil – $75 Mil |  |  |  |  | On Hold |  | Construction Delays
Other - Physical Security |  | Field Test Results | Age/Condition - Replace Breakers |  |  | TBD | $125 Mil - $150 Mil | [6 empty] | Input Error
Other - Remedial Action Scheme/Special Protection Scheme |  | Safety | Age/Condition - Replace Insulators |  |  | NA | $200 Mil - $250 Mil | [6 empty] | Land Rights
Other - Civil |  | Other [See Notes] | Age/Condition - Replace Reactors, Age/Condition - Replace Relays |  |  |  | $350 Mil – $400 Mil | [6 empty] | Multiple Options [See Notes]
Other - Environmental |  | Asset Condition | Age/Condition - Replace Other T-Line Equipment |  |  |  | $300 Mil - $350 Mil | [6 empty] | NA
Other |  | Location, Environmental Conditions | Age/Condition - Replace Other Substation Equipment |  |  |  | $250 Mil – $300 Mil | [6 empty] | Other [See Notes]
Other - Cybersecurity |  | Emergency Event | Age/Condition - Replace Conductor |  |  |  | $175 Mil - $200 Mil | [6 empty] | Scope Change
Other - Operations Tech |  |  | Age/Condition - Replace Civil Structures |  |  |  | $150 Mil - $175 Mil | [6 empty] | Vendor Quality/Delays
Transmission Line/Substation |  |  | Age/Condition - Replace Relays |  |  |  | $400 Mil - $500 Mil
Transmission Line - Switch |  |  | Age/Condition - Replace Steel Poles |  |  |  | Multiple Options [See Notes]
Transmission Line - Underground |  |  | Age/Condition - Replace Switches, Age/Condition - Replace Transformers |  |  |  | NA
Transmission Line - Multiple |  |  | Age/Condition - Replace SCADA/RTU |  |  |  | Over $500 Mil
Multiple Options [See Notes] |  |  | Age/Condition - Targeted Relay Replacement
Transmission Line - Conductor |  |  | Age/Condition - Replace Wood Poles
Transmission Line - Other Equipment |  |  | Age/Condition - Switch Replacement - Steel
Transmission Line - Pole/Tower |  |  | Age/Condition - Replace Underground System
Transmission Line - Right of Way |  |  | Age/Condition - Switch Replacement - Wood
Age/Condition - Wood Pole Reframe
Animal Abatement
Automation
Bus Upgrade
Compliance - Remove Idle Facilities
Construct Roads/Gates/Culverts
Emergency Response - Fire Related
Emergency Response - Storm Related
Environmental
Facility Relocation
Fire Protection
Generation Interconnection
GO95 Mitigation - Steel
Install SCADA/RTU
Line Reconductoring
Line Termination
Load Interconnection
Modular Protection and Automation Control
NERC CIP Compliance
NERC Compliance - GO 95
New Substation
New T-Line
Priority 1 Steel Structure Replacement
Priority 1 Wood Structure Replacement
Protection NERC Compliance
Relay Upgrades
Replace Breakers
Replace Other Substation Equipment
Replace Transformer
Safety - Line Right of Way Access
SCADA Emergency Replacement
SCADA Switch Installation
Security Upgrades
Seismic Upgrade - Replace Conductor
Special Protection Scheme
Substation Capacity
Substation Reliability
System Design Upgrade
System Operations
Targeted Line Reliability
T-Line Capacity
T-Line Emergency
T-Line Reliability
Tools, Transformer Addition/Replacement
Underground Emergency
Voltage Conversion
Voltage Support

## Data Template Example
| Project Description | [31 empty] | Utility/CAISO Approval and FERC Rate Cases | [9 empty] | CPUC Permit Status | [9 empty] | Project Status | [7 empty] | Costs | [27 empty] | Notes
1 | 2 | 3a | 3b | 4 | 5 | 6 | 7 | 7 | 8 | 9 | 10 | 11 | 11 | 12 | 13 | 14 | 15a | 15b | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40a | 40b | 41a | 41b | 42a | 42b | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 52 | 53 | 54 | 55 | 56 | 57 | 57 | 57 | 57 | 57 | 58 | 58 | 58 | 58 | 58 | 59 | 60 | 61 | 62 | 63 | 63 | 63 | 63 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70
Row/Line No. | Project Name(s) | Latitude | Longitude | Location2 | Project Description | Project Description - What | Project Description - Action Taken | Project Description - Action Taken (2) | Project Dependencies | Primary Purpose | Secondary Purpose | NERC/WECC/CAISO Standard/Requirement/Contingency | NERC/WECC/CAISO Standard/Requirement/Contingency (2) | Last Inspection | Age of Asset | Types of Analyses | Alternative Solutions and Costs - Solutions | Alternative Solutions and Costs - Costs | CPUC Fire Threat Zone/Rating | Wildfire Related | RAMP | Other Environmental Factors | Project Manager | Transmission Project Size (length in miles) | Substation Project Footprint (acres) | Transmission Voltage Level (kV) | Substation or Transformer Capacity (MVA and/or kV) | Utility Prioritization Ranking | Utility Unique ID #1 (Most Specific) | Utility Unique ID #2 (Less Specific) | Utility Unique ID #3 (Least Specific) | Changes in Unique IDs | Utility Approval | Year of Internal Utility Approval | Process(es) for Utility Approval | Long term Transmission Investment Plan Inclusion | CAISO Year | TPP Phase 3 | Year(s) when considered in CAISO TPP | Year when expected to be considered in CAISO TPP | Link to TPP where project has been considered, approved, and/or expected to be considered | GIDAP-Related | CEQA Status | CEQA Status - Date | CEQA Document Type | NEPA Document Type | CEQA Lead Agency | NEPA Lead Agency | CPUC Filing Type | CPUC Date Filed | CPUC Status | CPUC Status - Year | Project Status | AACE Class | Construction Start Date | Original Planned In-Service Date | Current Projected or Actual In-Service Date | Reason for Change in In-Service Date | Reason for Change in In-Service Date (2) | In-Flight Projects | Original Projected Cost or Cost Range ($000) | Cost Cap ($000) | Current Projected Total or Actual Final Cost ($000) | Actual Capital Expenditures 2019 ($000) | Actual Capital Expenditures 2020 ($000) | Actual Capital Expenditures 2021 ($000) | Actual Capital Expenditures 2022 ($000) | Actual Capital Expenditures 2023 ($000) | Actual and Forecast Capital Expenditures 2024 ($000) | Projected Capital Expenditures 2025 ($000) | Projected Capital Expenditures 2026 ($000) | Projected Capital Expenditures 2027 ($000) | Projected Capital Expenditures 2028 ($000) | Construction Work in Progress ($000) | Accrued Overhead ($000) | Accrued AFUDC ($000) | FERC: Year(s) | Dollars Put into FERC Rate Base 2020 ($000) | Dollars Put into FERC Rate Base 2021 ($000) | Dollars Put into FERC Rate Base 2022 ($000) | Dollars Put into FERC Rate Base 2023 ($000) | Dollars Put into FERC Rate Base 2024 ($000) | Percentage of Bid | Percentage and Value ($000) of Work Requested by Others Passed onto Ratepayers | Cost-Benefit Analysis | FERC Incentives | Percentage of Cost in High Voltage TAC | Percentage of Cost in Low Voltage TAC | Notes
1 | Manzanita Substation | 20.123 | 34.543 | Berkeley, Alameda County | This project will replace the substation breaker at LBNL. | Substation - Transformer | Replace | NA | 12352 ¦ 78998 | Reliability | Age/Condition | NERC BAL-003 | TPL-001-4R2-R4 | 2019-09-30 | 44 | Load Flow | Protection Studies | NA | HFTD Tier 2 | TRUE ¦ TRUE ¦ FALSE | TRUE | Extreme Heat | Cooper, Dale | 43.25 | 0 | 112 | 60kV | 43 | 11111 | 433 | 22 | 2022-05-05 ¦ NA ¦ NA ¦ 78322 | FALSE | 1812 | Annual Capital Operating Plan Process | 2018 | 1929 | FALSE | NA | NA | NA | FALSE | PEA Deemed Complete | 2018-09-01 | IS/ND | EIS | CPUC | NA | NA | NA | NA | NA | Construction (10%-25%) | 2 | 2007-12-01 | 2010-01-01 | 2025-06-01 | Weather | Material | TRUE | 2500 | 3000 ¦ TPP | 5000 | 50 | 1000 | 1000 | 1000 | 456 | 345 | 34 | 0 | 0 | 0 | 3676 | 23 | 234 | 2022 ¦ 2024 | 432 | 432 | 432 | 432 | 432 | 34% | 40% ¦ 5000 | 23% ¦ EnergyRank | NA | 5% | 15%
2 | Sycamore-Calaveras 115kV Line | 23.765 ¦ 43.542 | -132.018 ¦ -132.231 | Concord, Contra Costa County ¦ San Mateo, San Mateo County | This project will effect repairs upon the transmission line connecting 4th and Townsend to the East Northfork station. | Other - IT ¦ Other - Operations Tech | Removal | Relocate | 11111 | Load Growth | New T-line | TPL-001-4R2-R4 | NA | 2017-06-01 | 34 | NA | Lifecycle Replacement Analysis | $1M - $2M | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Project exists in CA Building Climate Zone 3 which presents a high risk of accelerated oxidation or steel structures due to coastal humidity and salt exposure. | Booth, Frank | 65.5 | 12.66 | 230 | 115kV | NA | 22222 | 532 | 22 | NA | TRUE | 2006 | NA | 2020 | 2012 | TRUE | 2008 ¦ 2009 ¦ 2010 | 2011 | http://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | TRUE | Final Certified | 2022-01-01 | EIR | Categoical Exclusion | CPUC | USFS | PC&E AL 2355-E | 2020-01-02 | Approved | 2020 | On Hold | 3 | 2024-01-01 | 2025-01-01 | 2030-01-01 | ISO Action | NA | FALSE | 349 ¦ 789 | 800 ¦ NA | 1000 | 23 | 54 | 123 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 787 | 0 | 0 | 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 643 | 643 | 643 | 643 | 643 | 33.33% ¦ "SuperPower LLC is developing a third of the project as part of its "TransValley Electrification" project. See http://.... | NA ¦ 230 | 23% ¦ EnergyRank | AFL 10 point project adder ¦ CPA | 12.33% | 0% | [CEQA/NEPA Document Type] Form STD762
Note on B4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TOs will probably find it easier to export if this is the corner cell. To import, we'll need to strip above and left as well.