| 2177 | DRUM-SPAULDING SHUNT SPLICE RPL |  |  | Nevada ¦ Placer | A short-term mitigation program to harden our transmission system by installing shunt splices on smaller sized conductors within High Fire Threat Districts (HFTD’s). Splice failure in an HFTD can result in a wildfire ignition. The difficulty in predicting a splice failure has prompted the need to add an extra layer of reliability (by shunting) to conventional splices with a high failure rate. A splice can fail because of numerous factors such as workmanship, manufacturing defect, or corrosive environmental conditions to name a few. Shunt splices are estimated to last up to 40 years, and it is anticipated that they add 15-25 years of life extension for the conductor and original splice.In efforts to bolster the 2023 Wildfire Mitigation Plan (WMP), it has been proposed to proactively reinforce the integrity of small size conductors through the addition of shunt splices. This program proposes to shunt splices using either preformed or bolted shunt splices. Desktop reviews revealed 37 circuits traversing HFTD areas within our transmission system have been identified to be utilizing twist sleeves. To reduce the risk of failure due to twist splices, this program will attempt to shunt as many twists sleeves as it safely can, to maximize risk reduction across as many of these 37 circuits as is feasible, with a minimum target of 20 circuits. The project team will coordinate with key stakeholders in Engineering to develop design packages, Land and Environmental to secure the appropriate land rights, permits and permissions and Internal/External Construction resources to validate field conditions and install shunt splices. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-07-12 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | NA | NA | 5550809 | T.0008666 | VARIOUS SHUNT SPLICE RPL | 35 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-06-05 | 2024-12-31 | 2023-06-05 | NA | NA | FALSE | 4700 | NA ¦ NA | 53.9292 | 53.9292 | 0 | 0 | 3.8081 | 40.3568 | 9.7642 | 0 | 0 | 0 | 0 | 0 | 53.9292 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 53.9292 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Other - Status Quo ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $5 Mil - $10 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2178 | GOLD HILL #1 SHUNT SPLICE RPL |  |  | Amador ¦ Cameron Park CDP, El Dorado ¦ Diamond Springs CDP, El Dorado ¦ El Dorado ¦ El Dorado Hills CDP, El Dorado ¦ Folsom, Sacramento ¦ Plymouth, Amador ¦ Shingle Springs CDP, El Dorado | A short-term mitigation program to harden our transmission system by installing shunt splices on smaller sized conductors within High Fire Threat Districts (HFTD’s). Splice failure in an HFTD can result in a wildfire ignition. The difficulty in predicting a splice failure has prompted the need to add an extra layer of reliability (by shunting) to conventional splices with a high failure rate. A splice can fail because of numerous factors such as workmanship, manufacturing defect, or corrosive environmental conditions to name a few. Shunt splices are estimated to last up to 40 years, and it is anticipated that they add 15-25 years of life extension for the conductor and original splice.In efforts to bolster the 2023 Wildfire Mitigation Plan (WMP), it has been proposed to proactively reinforce the integrity of small size conductors through the addition of shunt splices. This program proposes to shunt splices using either preformed or bolted shunt splices. Desktop reviews revealed 37 circuits traversing HFTD areas within our transmission system have been identified to be utilizing twist sleeves. To reduce the risk of failure due to twist splices, this program will attempt to shunt as many twists sleeves as it safely can, to maximize risk reduction across as many of these 37 circuits as is feasible, with a minimum target of 20 circuits. The project team will coordinate with key stakeholders in Engineering to develop design packages, Land and Environmental to secure the appropriate land rights, permits and permissions and Internal/External Construction resources to validate field conditions and install shunt splices. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-01-29 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | NA | NA | 5550814 | T.0008666 | VARIOUS SHUNT SPLICE RPL | 35 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-04-18 | 2024-12-31 | 2023-04-28 | NA | NA | FALSE | 4700 | NA ¦ NA | 30.3525 | 30.3525 | 0 | 0 | 0 | 31.9357 | -1.5833 | 0 | 0 | 0 | 0 | 0 | 30.3525 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 30.3525 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Other - Status Quo ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $5 Mil - $10 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2179 | VOLTA-DESCHUTES SHUNT SPLICE RPL |  |  | Millville CDP, Shasta ¦ Palo Cedro CDP, Shasta ¦ Shasta ¦ Shingletown CDP, Shasta | A short-term mitigation program to harden our transmission system by installing shunt splices on smaller sized conductors within High Fire Threat Districts (HFTD’s). Splice failure in an HFTD can result in a wildfire ignition. The difficulty in predicting a splice failure has prompted the need to add an extra layer of reliability (by shunting) to conventional splices with a high failure rate. A splice can fail because of numerous factors such as workmanship, manufacturing defect, or corrosive environmental conditions to name a few. Shunt splices are estimated to last up to 40 years, and it is anticipated that they add 15-25 years of life extension for the conductor and original splice.In efforts to bolster the 2023 Wildfire Mitigation Plan (WMP), it has been proposed to proactively reinforce the integrity of small size conductors through the addition of shunt splices. This program proposes to shunt splices using either preformed or bolted shunt splices. Desktop reviews revealed 37 circuits traversing HFTD areas within our transmission system have been identified to be utilizing twist sleeves. To reduce the risk of failure due to twist splices, this program will attempt to shunt as many twists sleeves as it safely can, to maximize risk reduction across as many of these 37 circuits as is feasible, with a minimum target of 20 circuits. The project team will coordinate with key stakeholders in Engineering to develop design packages, Land and Environmental to secure the appropriate land rights, permits and permissions and Internal/External Construction resources to validate field conditions and install shunt splices. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-03-20 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | NA | NA | 5550834 | T.0008666 | VARIOUS SHUNT SPLICE RPL | 35 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-05-24 | 2024-12-31 | 2023-05-26 | NA | NA | FALSE | 4700 | NA ¦ NA | 31.8116 | 31.8116 | 0 | 0 | 0.1788 | 32.7582 | -1.1253 | 0 | 0 | 0 | 0 | 0 | 31.8116 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 31.8116 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Other - Status Quo ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $5 Mil - $10 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2180 | COLGATE-SMARTVILLE COND SEG RPL |  |  | Nevada ¦ Smartsville CDP, Yuba ¦ Yuba | The program will replace all associated insulators and hardware where appropriate and coordinate all tag work to minimize clearance time. Please note that the following scope of work was determined per desktop review and needs to be validated by Transmission Line Engineering. The scope and cost estimates may change if there are discrepancies found with data available and actual field conditions. • Colgate-Smartville #2 60 kV: Reconductor 4/0-7 Cu conductor from Colgate substation to 000/002, 000/008 to 001/022, 003/038 to 005/062. Length – approximately 4 circuit miles Please note that Transmission Planning has identified a capacity need for this line (P3 at 2035) therefore please check with Transmission Planning before determining the conductor size. • Volta-South 60 kV: Reconductor 2/0-7 Cu conductor from Volta #1 PH substation to 000/001, reconductor 1/0-7 Cu conductor from 000/001 to 000/003, reconductor 1-1 Cu conductor from 000/003 to 000/009. Length – approximately 0.5 circuit miles Replace 000/009 with a dead-end structure. • Hat Creek #1-Westwood 60 kV: Reconductor 4/0-7 Cu conductor from Hat Creek #1 substation to 008/169, 014/275 to 015/304. Length – approximately 10 circuit miles Replace 008/169, 014/275, 015/304 with dead-end structures. • Salt Springs-Tiger Creek 115 kV: Reconductor 4/0-7 Cu conductor from Salt Springs PH substation to 003/030, 011/091 to 012/094, 015/113 to Tiger Creek substation. Length – approximately 5.5 circuit miles Replace 015/133 with a dead-end structure. • Gold Hill #1 60kV: Reconductor 2/0-7 Cu conductor from 021/325 to 022/331 Length – approximately 0.5 miles Replace 022/331 with a dead-end structure. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-03-11 | 68 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 4 | NA | 60 | NA | NA | NA | NA | 5.4 | In-flight Future Scope | 5555243 | T.0009721 | COLGATE-SMARTVILLE COND SEG RPL | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-05-06 | NA | 2026-06-16 | NA | NA | TRUE | NA | NA ¦ NA | 193.7014 | 5168.0089 | 0 | 0 | 0 | 0 | 127.3473 | 1000.0488 | 4040.6128 | 0 | 0 | 0 | 127.3472 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 127.3473 | 66.3542 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2181 | Hat creek #1-Westwood 60kV Span Replc |  |  | Cassel CDP, Shasta ¦ Lassen ¦ Shasta ¦ Westwood CDP, Lassen | The program will replace all associated insulators and hardware where appropriate and coordinate all tag work to minimize clearance time. Please note that the following scope of work was determined per desktop review and needs to be validated by Transmission Line Engineering. The scope and cost estimates may change if there are discrepancies found with data available and actual field conditions. • Colgate-Smartville #2 60 kV: Reconductor 4/0-7 Cu conductor from Colgate substation to 000/002, 000/008 to 001/022, 003/038 to 005/062. Length – approximately 4 circuit miles Please note that Transmission Planning has identified a capacity need for this line (P3 at 2035) therefore please check with Transmission Planning before determining the conductor size. • Volta-South 60 kV: Reconductor 2/0-7 Cu conductor from Volta #1 PH substation to 000/001, reconductor 1/0-7 Cu conductor from 000/001 to 000/003, reconductor 1-1 Cu conductor from 000/003 to 000/009. Length – approximately 0.5 circuit miles Replace 000/009 with a dead-end structure. • Hat Creek #1-Westwood 60 kV: Reconductor 4/0-7 Cu conductor from Hat Creek #1 substation to 008/169, 014/275 to 015/304. Length – approximately 10 circuit miles Replace 008/169, 014/275, 015/304 with dead-end structures. • Salt Springs-Tiger Creek 115 kV: Reconductor 4/0-7 Cu conductor from Salt Springs PH substation to 003/030, 011/091 to 012/094, 015/113 to Tiger Creek substation. Length – approximately 5.5 circuit miles Replace 015/133 with a dead-end structure. • Gold Hill #1 60kV: Reconductor 2/0-7 Cu conductor from 021/325 to 022/331 Length – approximately 0.5 miles Replace 022/331 with a dead-end structure. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-04-04 | 77 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 10 | NA | 60 | NA | NA | NA | NA | 5.4 | In-flight Future Scope | 5808439 | T.0009921 | Hat creek #1-Westwood 60kV Span Replc | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering less than 50% complete | 5 | 2028-09-13 | NA | 2028-10-10 | NA | NA | FALSE | NA | NA ¦ NA | 13.9905 | 8101.4096 | 0 | 0 | 0 | 0 | 0 | 528.7036 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2182 | Cond. Segment Replacement |  |  | NA | Forecast placeholder for conductor segment replacement (typically ruling spans) | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | NA | NA | Lifecycle Replacement Analysis | TBD | TBD | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Future IGP Scope | 5812671 | T.0010715 | Cond. Segment Replacement | 1 | 93 | NA ¦ Ex112953 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 70000.788 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 10000 | 10000 | 10000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2183 | 2025-BRIDGEVILLE-GARBERVILLE SHUNT SPLIC |  |  | Garberville CDP, Humboldt ¦ Humboldt | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-04-07 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5812670 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2025-05-05 | NA | 2025-05-05 | NA | NA | TRUE | NA | NA ¦ NA | 34.7166 | 29078.3293 | 0 | 0 | 0 | 0 | 0 | 74.357 | 10.4906 | 4003.9723 | 5000 | 5000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2184 | 2025-GEYSERS #3-EAGLE ROCK SHUNT SPLICE |  |  | Sonoma | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2024-05-01 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813107 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-08-01 | NA | 2025-08-14 | NA | NA | TRUE | NA | NA ¦ NA | 4.1259 | 76.9497 | 0 | 0 | 0 | 0 | 0 | 66.4591 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2185 | 2025-STANISLAUS-MANTECA #2 SHUNT SPLICE |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Manteca, San Joaquin ¦ San Joaquin ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2024-08-16 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813122 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-11-12 | NA | 2025-11-13 | NA | NA | TRUE | NA | NA ¦ NA | 10.5489 | 61.4796 | 0 | 0 | 0 | 0 | 0 | 50.989 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2186 | 2025-STANISLAUS-MELONES MANTECA #1 SHUNT |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Manteca, San Joaquin ¦ Murphys CDP, Calaveras ¦ San Joaquin ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2024-07-08 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813124 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-11-12 | NA | 2025-11-13 | NA | NA | TRUE | NA | NA ¦ NA | 6.5182 | 57.2406 | 0 | 0 | 0 | 0 | 0 | 46.7501 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2187 | 2025-STANISLAUS-MELONES RIVERBANK SHUNT |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2023-04-19 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813123 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-11-12 | NA | 2025-11-13 | NA | NA | TRUE | NA | NA ¦ NA | 4.1259 | 54.7248 | 0 | 0 | 0 | 0 | 0 | 44.2343 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2188 | 2025-PARADISE-TABLE MTN SHUNT SPLICE |  |  | Butte ¦ Butte Valley CDP, Butte ¦ Oroville East CDP, Butte ¦ Oroville, Butte ¦ Paradise, Butte ¦ South Oroville CDP, Butte ¦ Yankee Hill CDP, Butte | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2024-04-22 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813117 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-07-01 | NA | 2025-07-15 | NA | NA | TRUE | NA | NA ¦ NA | 13.3848 | 63.5189 | 0 | 0 | 0 | 0 | 0 | 53.0283 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2189 | 2025-CARIBOU - TABLE MTN SHUNT SPLICE |  |  | Belden CDP, Plumas ¦ Butte ¦ Caribou CDP, Plumas ¦ Concow CDP, Butte ¦ Plumas ¦ Yankee Hill CDP, Butte | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2024-05-01 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813125 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (under 10%) | 3 | 2025-03-24 | NA | 2025-04-07 | NA | NA | TRUE | NA | NA ¦ NA | 14.9245 | 64.6242 | 0 | 0 | 0 | 0 | 0 | 54.1337 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2190 | 2025-CENTERVILLE-TABLE MTN-OROVILLE SHUN |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Butte Valley CDP, Butte ¦ Oroville, Butte ¦ Paradise, Butte ¦ Thermalito CDP, Butte | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-03-31 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813100 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-07-01 | NA | 2025-07-01 | NA | NA | TRUE | NA | NA ¦ NA | 21.7545 | 72.1151 | 0 | 0 | 0 | 0 | 0 | 61.6246 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2191 | 2025-COLGATE-PALERMO SHUNT SPLICE |  |  | Bangor CDP, Butte ¦ Butte ¦ Nevada ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte ¦ Yuba | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2024-07-09 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813101 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-08-01 | NA | 2025-08-14 | NA | NA | TRUE | NA | NA ¦ NA | 35.2753 | 86.3361 | 0 | 0 | 0 | 0 | 0 | 75.8455 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2192 | 2025-ELK CREEK TAP SHUNT SPLICE |  |  | Elk Creek CDP, Glenn ¦ Glenn | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-03-10 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813103 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-08-01 | NA | 2025-08-14 | NA | NA | TRUE | NA | NA ¦ NA | 11.3453 | 61.6112 | 0 | 0 | 0 | 0 | 0 | 51.1207 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2193 | 2025-FORT ROSS-GUALALA SHUNT SPLICE |  |  | Mendocino ¦ Sea Ranch CDP, Mendocino ¦ Sea Ranch CDP, Sonoma ¦ Sonoma ¦ Timber Cove CDP, Sonoma | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-04-02 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813105 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-07-01 | NA | 2025-07-15 | NA | NA | TRUE | NA | NA ¦ NA | 39.8991 | 90.7509 | 0 | 0 | 0 | 0 | 0 | 80.2604 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2194 | 2025-HAMILTON BRANCH- CHESTER SHUNT SPLI |  |  | Chester CDP, Plumas ¦ East Shore CDP, Plumas ¦ Plumas | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-03-04 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813642 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2025-03-18 | NA | 2025-03-24 | NA | NA | TRUE | NA | NA ¦ NA | 16.6141 | 106.3378 | 0 | 0 | 0 | 0 | 0 | 95.8027 | 10.5351 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2195 | 2025-HAT CREEK #1-WESTWOOD SHUNT SPLICE |  |  | Cassel CDP, Shasta ¦ Lassen ¦ Shasta ¦ Westwood CDP, Lassen | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-04-04 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813108 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-06-02 | NA | 2025-06-13 | NA | NA | TRUE | NA | NA ¦ NA | 23.1806 | 73.6689 | 0 | 0 | 0 | 0 | 0 | 63.1783 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2196 | 2025-POE - RIO OSO SHUNT SPLICE |  |  | Butte ¦ Oroville East CDP, Butte ¦ Oroville, Butte ¦ Palermo CDP, Butte ¦ South Oroville CDP, Butte ¦ Sutter ¦ Yuba | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-01-21 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave |  | NA | NA | 230 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813126 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-09-01 | NA | 2025-09-12 | NA | NA | TRUE | NA | NA ¦ NA | 34.1638 | 85.8674 | 0 | 0 | 0 | 0 | 0 | 75.3768 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2197 | 2025-IGNACIO-BOLINAS #1 SHUNT SPLICE |  |  | Bolinas CDP, Marin ¦ Lucas Valley-Marinwood CDP, Marin ¦ Marin ¦ Novato, Marin ¦ San Geronimo CDP, Marin ¦ Woodacre CDP, Marin | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-01-16 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813110 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-05-01 | NA | 2025-05-14 | NA | NA | TRUE | NA | NA ¦ NA | 12.341 | 62.3882 | 0 | 0 | 0 | 0 | 0 | 51.8977 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2198 | 2025-IGNACIO-ALTO-SAUSALITO #1 SHUNT SPL |  |  | Alto CDP, Marin ¦ Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin ¦ Sausalito, Marin ¦ Tamalpais-Homestead Valley CDP, Marin | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-03-31 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813109 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-04-11 | NA | 2025-04-14 | NA | NA | TRUE | NA | NA ¦ NA | 4.1259 | 76.3108 | 0 | 0 | 0 | 0 | 0 | 65.8202 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2199 | 2025-IGNACIO-BOLINAS #2 SHUNT SPLICE |  |  | Bolinas CDP, Marin ¦ Marin ¦ Novato, Marin | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-04-07 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813111 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-05-01 | NA | 2025-05-14 | NA | NA | TRUE | NA | NA ¦ NA | 19.2391 | 512.0156 | 0 | 0 | 0 | 0 | 0 | 387.3586 | 124.657 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2200 | 2025-SNEATH LANE-HALF MOON BAY SHUNT SPL |  |  | Half Moon Bay, San Mateo ¦ Montara CDP, San Mateo ¦ Pacifica, San Mateo ¦ San Bruno, San Mateo ¦ San Mateo | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-04-04 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813119 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-05-01 | NA | 2025-05-14 | NA | NA | TRUE | NA | NA ¦ NA | 29.5341 | 79.5873 | 0 | 0 | 0 | 0 | 0 | 69.0967 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2201 | 2025-JOLON TAP SHUNT SPLICE |  |  | Monterey ¦ Pine Canyon CDP, Monterey | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-03-27 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813112 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-05-01 | NA | 2025-05-14 | NA | NA | TRUE | NA | NA ¦ NA | 95.0221 | 146.0577 | 0 | 0 | 0 | 0 | 0 | 135.5671 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2202 | 2025-LAURELES-OTTER SHUNT SPLICE |  |  | Carmel Valley Village CDP, Monterey ¦ Monterey | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-04-07 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813113 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-06-02 | NA | 2025-06-13 | NA | NA | TRUE | NA | NA ¦ NA | 4.1259 | 53.8915 | 0 | 0 | 0 | 0 | 0 | 43.4009 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2203 | 2025-SNEATH LANE-PACIFICA SHUNT SPLICE |  |  | Pacifica, San Mateo ¦ San Bruno, San Mateo ¦ San Mateo | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2024-05-16 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813120 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-05-01 | NA | 2025-05-14 | NA | NA | TRUE | NA | NA ¦ NA | 13.8511 | 63.6691 | 0 | 0 | 0 | 0 | 0 | 53.1785 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2204 | 2025-MONTA VISTA-BURNS SHUNT SPLICE |  |  | Bonny Doon CDP, Santa Cruz ¦ Cupertino, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2023-06-23 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813116 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-10-01 | NA | 2025-10-02 | NA | NA | TRUE | NA | NA ¦ NA | 7.8357 | 58.3885 | 0 | 0 | 0 | 0 | 0 | 47.898 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2205 | 2025-SALINAS-LAURELES SHUNT SPLICE |  |  | Boronda CDP, Monterey ¦ Carmel Valley Village CDP, Monterey ¦ Monterey ¦ Monterey, Monterey ¦ Salinas, Monterey | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-04-04 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813118 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-04-01 | NA | 2025-04-11 | NA | NA | TRUE | NA | NA ¦ NA | 17.9266 | 67.6532 | 0 | 0 | 0 | 0 | 0 | 57.1626 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2206 | 2025-TULUCAY-NAPA #1 SHUNT SPLICE |  |  | Green Valley CDP, Napa ¦ Green Valley CDP, Solano ¦ Napa ¦ Napa, Napa ¦ Solano | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-03-27 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813121 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-06-02 | NA | 2025-06-13 | NA | NA | TRUE | NA | NA ¦ NA | 4.1259 | 76.419 | 0 | 0 | 0 | 0 | 0 | 65.9284 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2207 | 2025-CORDELIA #1 TAP SHUNT SPLICE |  |  | Fairfield, Solano ¦ Napa ¦ Solano | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2024-05-08 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813102 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-06-02 | NA | 2025-06-13 | NA | NA | TRUE | NA | NA ¦ NA | 26.37 | 99.1306 | 0 | 0 | 0 | 0 | 0 | 88.64 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2208 | 2025-ELK-GUALALA SHUNT SPLICE |  |  | Anchor Bay CDP, Mendocino ¦ Manchester CDP, Mendocino ¦ Mendocino ¦ Point Arena, Mendocino | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2025-04-07 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813104 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-07-01 | NA | 2025-07-15 | NA | NA | TRUE | NA | NA ¦ NA | 22.8147 | 73.204 | 0 | 0 | 0 | 0 | 2.4722 | 60.2412 | 10.4906 | 0 | 0 | 0 | 2.4723 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2209 | 2025-LOS BANOS-PACHECO SHUNT SPLICE |  |  | Merced | Installation of shunted splices to prevent single point of failure on certain splice types. Tied to WMP GH-07 target between 2023-2025. | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2024-10-16 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | NA | NA | NA | 5.101 | In-flight Future Scope | 5813114 | T.0010716 | Shunt Splice Program | 30 | 93 | NA ¦ Ex112977 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering less than 50% complete | 5 | 2025-06-02 | NA | 2025-06-13 | NA | NA | TRUE | NA | NA ¦ NA | 4.1259 | 53.8915 | 0 | 0 | 0 | 0 | 0 | 43.4009 | 10.4906 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2210 | Targeted Conductor Mitigation |  |  | NA | Forecast Placeholder for Targeted Conductor Mitigation - Addressing Conductor Spans in H-H, H-M and M-H in both HFTD and Non HFTD locations | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.301 | Future IGP Scope | EX130294 | TBD | TBD | TBD | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 109154.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3250.555 | 35295.606 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2211 | Pole Reframing - Wood (North) |  |  | NA | Bucket for wood pole reframing in the North region | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 211 | NA | 3 | 5.201 | In-flight Future Scope | 5513326 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 60684.8765 | 60684.8765 | 3695.1246 | 6605.9641 | 9993.2673 | 11173.6638 | 15747.0431 | 1184.4077 | 0 | 0 | 0 | 0 | 59500.4688 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 3009.5823 | 4613.4642 | 8424.053 | 9080.9245 | 13081.8994 | 1374.1897 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2212 | Pole Reframing - Wood (Central) |  |  | NA | Bucket for wood pole reframing in the South region | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | 13 | 5.201 | NA | 5513327 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 4041.1851 | 4041.1851 | -12.6883 | 35.1064 | 471.5376 | 1030.9265 | 534.5347 | 1.1571 | 0 | 0 | 0 | 0 | 4040.028 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | -3.8188 | 17.0436 | 419.0353 | 937.9762 | 314.0666 | 29.7909 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2213 | T Line Wood Pole Reframe - Fresno |  |  | NA | Bucket for wood pole reframing in the Fresno area. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 211 | 2. Overhead With Strong Safety Link | 304 | NA | NA | 5517321 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1500.6725 | 1500.6725 | 42.3384 | 8.8374 | -0.7939 | 3.3792 | 2.0472 | -22.9597 | 0 | 0 | 0 | 0 | 1523.6322 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 41.1247 | 4.5169 | 7.1077 | -5.8439 | 1.7261 | -18.6237 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2214 | T Line Wood Pole Reframe - Moss Landing |  |  | NA | Bucket for wood pole reframing in the Moss Landing area. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 211 | 2. Overhead With Strong Safety Link | 13 | NA | NA | 5517326 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1925.4976 | 1925.4976 | 116.5503 | 7.4198 | -49.3011 | -2.3548 | -51.5919 | 0 | 0 | 0 | 0 | 0 | 1925.4976 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 100.0752 | 6.817 | -42.3474 | -2.6008 | -56.6983 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2215 | T Line Wood Pole Reframe - Sac |  |  | NA | Bucket for wood pole reframing in the Sacramento area. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 211 | 2. Overhead With Strong Safety Link | 6 | NA | NA | 5517328 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 4401.8386 | 4401.8386 | 1.0973 | 5.1703 | -48.5563 | 1.4008 | 1.0531 | 1.0673 | 0 | 0 | 0 | 0 | 4400.7713 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 1.351 | 4.5962 | -42.7842 | 1.2525 | 0.94161 | 0.95426 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2216 | Wood Pole Reframe - Victor |  |  | NA | Bucket for wood pole reframing in the Victor area. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 211 | 2. Overhead With Strong Safety Link | 41 | NA | NA | 5517329 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1501.6577 | 1501.6577 | -58.2687 | 19.5475 | 7.1062 | 22.6025 | 0.0105 | 0 | 0 | 0 | 0 | 0 | 1501.6577 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | -31.8783 | 17.1275 | 0.13381 | 28.6097 | -4.8386 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2217 | WSIP - Wood Pole Reframe |  |  | NA | Bucket for wood pole reframing in HFTD Tier 2 & 3 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 3557 | 2. Overhead With Strong Safety Link | 1 | 5.201 | NA | 5533589 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 52431.4044 | 52431.4044 | 14406.5318 | 9690.1568 | 3104.0267 | 1229.1498 | 260.6287 | -18.6178 | 0 | 0 | 0 | 0 | 52450.0222 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 11633.1955 | 8500.3514 | 3755.5558 | 929.0476 | 263.559 | -26.9952 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2218 | T Line Wood Pole Reframe - Table Mountai |  |  | NA | Bucket for wood pole reframing in the Table Mountain area. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 211 | 2. Overhead With Strong Safety Link | 14 | NA | NA | 5517314 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 5777.0929 | 5777.0929 | 82.0343 | 54.2973 | 9.5692 | 6.6109 | 0 | 0 | 0 | 0 | 0 | 0 | 5777.0929 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 46.716 | 68.4405 | 4.8886 | 56.9592 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2219 | GO95 Low Wire - Wood |  |  | NA | Bucket for GO95 Low Wire work on wood poles | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | 38 | 5.101 | Non-IGP | 5505379 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 45729.1599 | 45729.1599 | 455.0307 | 1048.5186 | 868.6095 | 13946.8436 | 25750.7618 | 2077.638 | 0 | 0 | 0 | 0 | 43651.5219 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 422.0885 | 855.7157 | 660.4594 | 9847.4798 | 22324.5735 | 1350.507 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2220 | GO95 Wood - Low Cond Proj (North) |  |  | NA | Bucket for GO95 Low conductor work on wood poles in Northern region | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | 70 | 5.101 | Non-IGP | 5510405 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2013 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 21189.4334 | 21189.4334 | 0 | 5.4442 | 1259.5741 | 9762.4321 | 9016.686 | 325.3991 | 0 | 0 | 0 | 0 | 20864.0343 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 2.65 | 1101.1241 | 9565.2789 | 8910.6364 | 261.1133 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2221 | GO95 Mitigation - Wood - Lakeville |  |  | NA | Bucket for GO95 Mitigation work on wood poles in Lakeville area | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | NA | 197 | 5. Compliance/Commitments With Strong Safety Link | 7 | NA | NA | 5517249 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1202.9791 | 1202.9791 | 8.8342 | 7.6557 | 5.7276 | 0.5309 | 0 | 0 | 0 | 0 | 0 | 0 | 1202.9791 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 40.965 | 32.2323 | 60.665 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2222 | 93G: GO-95 Mitigation |  |  | NA | Forecast placeholder for potential mitigation needed for GO-95 mitigation on HFTD Lines. This work will be developed after line assessments/LiDAR analysis. Represents mitigation on wood pole lines. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.101 | Future IGP Scope | EX112094 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 243185.6117 | 0 | 0 | 0 | 0 | 0 | 0 | 40800 | 20400 | 40800 | 20400 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2223 | WSIP - Switch Replacement (Wood) |  |  | NA | Bucket for switch replacements on wood poles as part of WSIP program | Transmission Line - Switch | Replace | NA | NA | Asset Condition | Age/condition - Switch Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3574 | 1. Work that prevents fire ignition | 117 | 3.0011 | In-flight Future Scope | 5533591 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 2718.955 | 2718.955 | 177.9933 | 148.865 | 137.5196 | 462.8257 | 1489.0595 | 127.5898 | 0 | 0 | 0 | 0 | 2591.3652 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 168.9395 | 142.3691 | 117.5527 | 399.1243 | 1282.4866 | 115.994 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2224 | Switch Repl - Wood - Fresno BL |  |  | NA | Bucket for switch replacement on wood poles in the Fresno area | Transmission Line - Switch | Replace | NA | NA | Asset Condition | Age/condition - Switch Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5519269 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 5944.5831 | 5944.5831 | 0 | 13.4185 | 5928.5348 | 2.1374 | 0.4925 | 0 | 0 | 0 | 0 | 0 | 5944.5831 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 5518.7722 | 1.9851 | 0.45743 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2225 | Gerber Jct Switch 23 Capability Upgrade |  |  | Corning, Tehama ¦ Cottonwood CDP, Shasta ¦ Gerber CDP, Tehama ¦ Las Flores CDP, Tehama ¦ Proberta CDP, Tehama ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama | Replace switch 23 with an upgrade that has loop breaking and line dropping capability on Cottonwood #1 60kV. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Asset Condition | Age/condition - Switch Replacement - Wood | NA | NA | 2025-04-07 | 89 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | EX112704 | TBD | TBD | TBD | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2029-01-01 | NA | 2030-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1999.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2226 | Insulator Replacement - Wood - Fresno |  |  | NA | Bucket for insulator replacement on wood poles in the Fresno area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 52 | NA | NA | 5517292 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2802.4491 | 2802.4491 | 39.6233 | 60.8802 | 2.6114 | 0.6406 | 0.1874 | 0 | 0 | 0 | 0 | 0 | 2802.4491 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 34.648 | 53.5008 | 2.4002 | -9.1288 | -1.811 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2227 | Insulator Replacement - Wood - Midway |  |  | NA | Bucket for insulator replacement on wood poles in the Midway area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 40 | NA | NA | 5517296 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1150.6644 | 1150.6644 | -10.7248 | 0.915 | 3.0263 | 1.6267 | -5.6938 | 0 | 0 | 0 | 0 | 0 | 1150.6644 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | -7.9208 | -1.1401 | 2.8141 | -1.8284 | -5.8378 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2228 | Insulator Replacement - Wood-Sacramento |  |  | NA | Bucket for insulator replacement on wood poles in the Sacramento area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 6 | NA | NA | 5517299 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2700.0154 | 2700.0154 | 51.8592 | 75.4269 | 15.5914 | 0.5477 | 0.0434 | 0 | 0 | 0 | 0 | 0 | 2700.0154 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 46.5517 | 70.3912 | 12.7555 | 0.48457 | 0.04113 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2229 | WSIP - Insulator Replacement - Wood |  |  | NA | Bucket for insulator replacement on wood poles in HFTD Tier 2 & 3 | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3566 | 1. Work that prevents fire ignition | 1 | 3.0011 | In-flight Future Scope | 5533592 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 32676.5481 | 32676.5481 | 9853.2447 | 8030.5235 | 3755.0787 | 2662.7913 | 424.8944 | 108.5545 | 0 | 0 | 0 | 0 | 32567.9936 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 6950.9314 | 6378.0871 | 5611.8283 | 2539.3483 | 273.9135 | 90.6785 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2230 | Insulator Replacements - Wood (North) |  |  | NA | Bucket for insulator replacement on wood poles in the North region | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 220 | NA | 1 | 3.0011 | In-flight Future Scope | 5505339 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 175085.9284 | 175085.9284 | 4383.7989 | 10110.2625 | 22422.3519 | 28872.4231 | 14515.149 | 1234.5166 | 0 | 0 | 0 | 0 | 173851.4118 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 3500.4358 | 7637.5499 | 18568.8313 | 25637.6612 | 11467.3597 | 1274.3312 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2231 | Insulator Replacement - Wood - Eureka |  |  | NA | Bucket for insulator replacement on wood poles in the Eureka area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 84 | NA | NA | 5517291 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1320.2413 | 1320.2413 | 12.4986 | 13.1477 | -9.0899 | 0.7192 | 0 | 0.1971 | 0 | 0 | 0 | 0 | 1320.0442 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 11.3201 | 11.2953 | -9.3142 | 0.66212 | 0 | 0.18421 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2232 | Insulator Replacement - Wood - Lakeville |  |  | NA | Bucket for insulator replacement on wood poles in the Lakeville area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 8 | NA | NA | 5517293 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1376.6434 | 1376.6434 | 28.2712 | 6.7425 | -17.0999 | -2.8812 | 0 | 0 | 0 | 0 | 0 | 0 | 1376.6434 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 24.1318 | 36.8058 | -16.0423 | -2.6305 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2233 | Insulator ReplacementWood-Table Mountain |  |  | NA | Bucket for insulator replacement on wood poles in the Table Mountain area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 4 | NA | NA | 5517301 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2593.8665 | 2593.8665 | 22.6977 | 0.7904 | -11.3181 | 1.4883 | 0 | 0 | 0 | 0 | 0 | 0 | 2593.8665 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 21.1371 | 3.6391 | -9.4163 | -2.9719 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2234 | Insulator Replacement - Wood-Pismo Beach |  |  | NA | Bucket for insulator replacement on wood poles in the Pismo Beach area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 220 | 2. Overhead With Strong Safety Link | 229 | NA | NA | 5517298 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 3457.8759 | 3457.8759 | 0.4073 | 0 | 5.3717 | 24.8999 | 2.1585 | 0.1971 | 0 | 0 | 0 | 0 | 3457.6788 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0.36929 | 0 | 4.8346 | 11.187 | 1.8368 | 0.17852 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2235 | Insulator Replacements - Wood (Central) |  |  | NA | Bucket for Insulator Replacements on Wood poles in the Central region | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 220 | NA | 99 | NA | NA | 5513325 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2070.7873 | 2070.7873 | 0 | 0 | -6.7076 | 4.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 2070.7873 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2025 | 0 | 0 | -5.4969 | -9.364 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2236 | Insulator Replacements-Non-HFTD-Wood |  |  | NA | Forecast placeholder for Insulator Replacements-Non-HFTD-Wood | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Future IGP Scope | EX111866 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8000.1878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2237 | Insulator Replacements-HFTD-Wood |  |  | NA | Forecast placeholder for Insulator Replacements-HFTD-Wood | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Future IGP Scope | EX112185 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8000.1878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2238 | Woodleaf-Palermo 115kV - Insulator |  |  | Butte ¦ Forbestown CDP, Butte ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte | This project proposes to replace aging structures and insulators on the Woodleaf – Palermo 115 kV Line and associated 115 kV Tap lines to help mitigate high-risk components on these line. Scope in details: • Replace 124 of the 232 structures on the Woodleaf – Palermo 115 kV Line with steel structures; • Replace 69 insulators on the Woodleaf – Palermo 115 kV Line; • Perform field analysis on existing structures, Nos. 000/005, 006/053, and 013/128 on the Woodleaf – Palermo 115 kV Line to verify if replacements are needed; • Perform field analysis on 0.02 miles of Sly Creek Tap 115 kV from pole no. 000/006 to 000/008 to verify the age of the conductor and to determine if reconductor is needed; • Replace 3 structures, pole nos. 003/031A, 003/031B, and 003/031C and perform field analysis on 3 structures, pole nos. 002/019, 003/032, and 004/038 to determine if structure and insulator replacements are needed on the Sly Creek Tap 115 kV; • Replace all insulators on the Sly Creek Tap 115 kV; • Replace 1 structure, pole no. 004/039 and conduct field analysis on 3 structures, pole nos. 000/001A, 000/001B, and 000/001C to determine if structure and insulator replacements are needed on the Forbestown Tap 115 kV; • Perform field analysis on 9 structures, pole nos. 000/002, 001/008B, 001/008C, 001/010C, 001/011, 002/015, 002/016, 002/018A, and 002/018C, to verify if structure and insulator replacements are needed on the Kanaka Tap 115 kV; • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | 2024-06-13 | 63 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 4703 | 2. Overhead With Strong Safety Link | 151 | 4.01 | In-flight Future Scope | 5789805 | T.0005758 | Woodleaf-Palermo 115kV-Structure & Insul | 3 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2032-11-16 | NA | 2033-02-14 | NA | NA | FALSE | NA | NA ¦ NA | 2.8987 | 5536.3974 | 0 | 1.0249 | 1.5802 | 0.1943 | 0.0994 | 0.1798 | 0 | 0 | 0 | 184.9065 | 2.8987 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2239 | WSIP - Remove Idle Facilities |  |  | NA | Bucket for removal of t-line idle facilities in HFTD | Transmission Line - Multiple | Removal | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | 1. Work that prevents fire ignition | 4 | NA | NA | 5536740 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1798.3215 | 1798.3215 | 176.0611 | 788.1281 | 702.0956 | 6.5939 | -1.2199 | 2.5104 | 0 | 0 | 0 | 0 | 1795.8111 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 102.9843 | 479.6883 | 319.6659 | -12.597 | -40.6542 | 0.21506 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2240 | Caribou-Palermo Idle Facility Removal |  |  | Palermo CDP, Butte ¦ Plumas | Bucket for removal of idle transmission lines in Caribou-Palermo area | Transmission Line - Multiple | Removal | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | 2023-06-28 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 55 | NA | 115 | NA | NA | NA | NA | NA | NA | 5541326 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 8494.9774 | 8494.9774 | 4507.6861 | 4002.2839 | -16.1137 | 0.5775 | 0.5437 | 0 | 0 | 0 | 0 | 0 | 8494.9774 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 4507.6861 | -638.139 | 252.9809 | 0.57749 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2241 | Remove Idle Facilities |  |  | NA | Bucket for removal of idle transmission lines. | Transmission Line - Multiple | Removal | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 124 | 9. Reliability (Low Safety Risk) | 1179 | 5.1001 | Non-IGP | 5725566 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2005.7459 | 2005.7459 | 8.1889 | 87.8839 | 296.3678 | 71.9159 | 5.7362 | 0.1475 | 0 | 0 | 0 | 0 | 2005.5984 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 85.9517 | 226.3481 | 39.6668 | 33.8474 | -1.8298 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2242 | Systemwide Idle Line Removal |  |  | NA | Foreast placeholder for Idle Line Removal Program | Transmission Line - Multiple | Removal | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.1001 | Future IGP Scope | 5510559 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 23830.5215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2024 | 0 | -57.7212 | 0 | 0 | -40.1533 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2243 | IDLE FACILITIES REMOVAL TAGS |  |  | NA | Bucket for idle facilitiy removal tag work | Transmission Line - Multiple | Removal | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5757461 | T.0000046 | Homestake Tap Idle Line Removal | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1094.0236 | 1094.0236 | 5.5006 | 509.1687 | 26.1888 | 4.9744 | 538.924 | 8.0929 | 0 | 0 | 0 | 0 | 1085.9307 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 3.3681 | 311.3933 | 0.25758 | 5.2408 | 30.8349 | 0.45591 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2244 | BIG BEND-CLAYTON #1 NERC PROJECT |  |  | Antioch, Contra Costa ¦ Clayton, Contra Costa ¦ Pittsburg, Contra Costa | In October of 2016 the Big Bend-Clayton (Idle) circuit was determined to be Permanently Abandon as defined in Utility Standard: TD-1003S. As required within the Utility Standard the facility must be removed. Removal of the Permanently Abandon facilities supports CPUC GO 95 “Rules for Overhead Electric Line Construction”. The Big Bend-Clayton #1 and #2 double circuit tower line is an idle circuit which starts at Tower 074/551 and ends at Tower 086/643. The two transmission lines are 11.95 miles long with 3/0 cu conductor. The project scope includes removing 11.95 miles of 3/0 copper on Big Bend Clayton #1 & #2 idle circuit from Tower 074/551 to Tower 086/643. Removal of lattice steel double circuit towers from Tower 074/552 to Tower 086/643. Removal of foundations from Tower 074/552 to Tower 086/643. Six (6) Towers will not be removed due to the existence of revenue generating cell service atop the structure. | Transmission Line - Conductor | Removal | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | NA | 113 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 11.95 | NA | 115 | NA | 235 | NA | NA | NA | NA | 5550410 | T.0000068 | BIG BEND-CLAYTON #1 NERC PROJECT | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-11-01 | 2018-02-08 | 2018-03-31 | NA | NA | FALSE | 16219 | NA ¦ NA | 7927.8849 | 7927.8849 | 327.1105 | 1.5834 | 0.209 | -16.6148 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.8849 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2245 | BRIGHTON-CLAYTON #2 IDLE CIRCUIT REMOVAL |  |  | Antioch, Contra Costa ¦ Clayton, Contra Costa ¦ Pittsburg, Contra Costa | The project scope includes removing the double lattice steel tower line from Tower A00/001 to Tower 050/376. The tower line will be left in place from Tower 050/377 to Tower 051/386. Tower A00/001 was analyzed and determined to require replacement, which has extended our completion date. | Transmission Line - Multiple | Removal | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | NA | 89 | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 10.6 | NA | 115 | NA | 4 | NA | NA | NA | NA | 5760868 | T.0000413 | BRIGHTON-CLAYTON #2 NERC PROJECT | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-07-18 | 2017-12-29 | 2018-02-12 | NA | NA | FALSE | 4125 | NA ¦ NA | 5913.6593 | 5913.6593 | 105.2633 | 1927.698 | -92.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5913.6593 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 21.2336 | 388.8524 | -18.5834 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2246 | Brighton-Grand Island Idle Removal Proj |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | The project scope includes removing 16.42 miles of 3/0 copper and 118 lattice steel towers on Brighton-Grand Island #1 & #2 idle circuit from Tower 024/189 to Tower 041/307. All towers with cell service will be removed on Ph. 2 of this project. In October of 2016 the Brighton-Grand Island (Idle) circuit was determined to be Permanently Abandon as defined in Utility Standard: TD-1003S. As required within the Utility Standard the facility must be removed. Removal of the Permanently Abandon facilities supports CPUC GO 95 “Rules for Overhead Electric Line Construction”. | Transmission Line - Conductor | Removal | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | 2024-10-29 | 25 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | 16.4 | NA | 115 | NA | 4 | NA | NA | NA | NA | 5774041 | T.0002714 | Brighton-Grand Island Idle Removal Proj | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-02-20 | 2018-03-31 | 2018-03-31 | NA | NA | FALSE | 19078 | NA ¦ NA | 6635.8782 | 6635.8782 | 100.3486 | 430.7061 | 20.9086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6635.8782 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 15.7405 | 67.5594 | 3.2797 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2247 | Caribou-Palermo 10391 Remove Structures |  |  | Palermo CDP, Butte ¦ Plumas | This project proposes to complete the removal of the Caribou-Palermo 115kV Line by removing abandoned lattice steel tower structures and assessing the remaining towers supporting other transmission lines and replacing or strengthening these towers if needed. To mitigate the risk of Wyandotte being single sourced, this project proposes to reconfigure Wyandotte Substation to utilize the Paradise-Table Mountain 115kV circuit as a backup source. | Transmission Line - Pole/Tower | Removal | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | 2023-06-28 | NA | Lifecycle Replacement Analysis | Other - Deferral | $20 Mil - $30 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | 55 | NA | 115 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5545724 | T.0006251 | Caribou-Palermo 10391 Remove Structures | 5 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-11-01 | 2021-12-31 | 2024-12-19 | Prioritization | NA | FALSE | 20700 | NA ¦ NA | 3258.087 | 3383.1342 | 0 | 875.6611 | 8.9581 | 0 | 2210.1346 | 288.3803 | 0 | 0 | 0 | 0 | 3094.7539 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2248 | MENDOCINO # 1 60KV CONDUCTOR REMOVAL |  |  | Mendocino ¦ Ukiah, Mendocino | This project proposes to remove the idle transmission line and associated attached equipment to permanently mitigate any future wildfire catastrophes. 9 miles of the line being removed is located in tier 2 HFTD. Remove 9 miles of 60kV conductor, remove insulators, remove wood poles & steel poles and install tower modifications. • Remove 9 miles of conductor o Starting at 005/001 framing configuration will change to a delta set up due to loading concerns on the towers o Double circuit towers from 005/001 – 008/006 o Doing this will also fix and GO 95 infractions between spans 6/0 – 6/1 • Remove 46 wood poles • Remove 18 LDSPs • Remove 1 TSP | Transmission Line - Multiple | Removal | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | 2023-06-02 | 47 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 0.9 | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5548785 | T.0008162 | MENDOCINO # 1 60KV CONDUCTOR REMOVAL | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-08-14 | 2023-06-30 | 2023-09-01 | NA | NA | FALSE | 7900 | NA ¦ NA | 49.0696 | 49.0696 | 0 | 0 | 48.6681 | 0 | 0 | 0.4015 | 0 | 0 | 0 | 0 | 48.6681 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2025 | 0 | 0 | 15.7234 | -15.7234 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2249 | Mendocino #1 (Engineering) |  |  | Mendocino ¦ Ukiah, Mendocino | This project proposes to remove the idle transmission line and associated attached equipment to permanently mitigate any future wildfire catastrophes. 9 miles of the line being removed is located in tier 2 HFTD. Remove 9 miles of 60kV conductor, remove insulators, remove wood poles & steel poles and install tower modifications. • Remove 9 miles of conductor o Starting at 005/001 framing configuration will change to a delta set up due to loading concerns on the towers o Double circuit towers from 005/001 – 008/006 o Doing this will also fix and GO 95 infractions between spans 6/0 – 6/1 • Remove 46 wood poles • Remove 18 LDSPs • Remove 1 TSP | Other | NA | NA | NA | Asset Condition | Compliance - Remove Idle Facilities | NA | NA | 2023-06-02 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 5.1001 | Non-IGP | 5549441 | T.0008162 | MENDOCINO # 1 60KV CONDUCTOR REMOVAL | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2023 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2024-06-24 | 2023-06-30 | 2024-11-19 | Project Design | NA | FALSE | 7900 | NA ¦ NA | 854.3751 | 998.1336 | 0 | 0 | 0.5746 | 0 | 620.7475 | 376.8116 | 0 | 0 | 0 | 0 | 621.3221 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 539.038 | 202.1889 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2250 | Insulator Rep Steel - Concord |  |  | NA | Bucket for insulator replacement on steel towers in the Concord area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 144 | 5.2 | In-flight Future Scope | 5517258 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 3424.0566 | 3424.0566 | 227.5766 | 411.0943 | 157.188 | 30.3119 | 167.0468 | 587.3731 | 0 | 0 | 0 | 0 | 2836.6835 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 180.0298 | 334.6172 | 157.4702 | -13.1324 | 7.9939 | 234.5302 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2251 | Insulator Rep Steel - Lakeville |  |  | NA | Bucket for insulator replacement on steel towers in the Lakeville area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 2 | 5.2 | In-flight Future Scope | 5517281 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 4095.7189 | 4095.7189 | 606.1142 | 1125.7015 | 441.7104 | 311.6833 | 117.0901 | 415.5361 | 0 | 0 | 0 | 0 | 3680.1828 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 507.3303 | 989.8502 | 494.8826 | 235.0502 | 28.6843 | 123.0149 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2252 | Insulator Rep Steel - Metcalf |  |  | NA | Bucket for insulator replacement on steel towers in the Metcalf area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 91 | 5.2 | In-flight Future Scope | 5517283 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 7501.4851 | 7501.4851 | 1126.1084 | 693.8711 | 2555.9988 | 1236.8078 | 654.718 | 443.2632 | 0 | 0 | 0 | 0 | 7058.2219 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 1006.3393 | 668.8773 | 2435.2425 | 934.5566 | 99.2874 | 229.0374 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2253 | Insulator Rep Steel - Midway |  |  | NA | Bucket for insulator replacement on steel towers in the Midway area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 21 | NA | NA | 5517284 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 6917.4036 | 6917.4036 | 1053.8248 | 439.5356 | 95.4361 | 11.605 | 0.8747 | 0 | 0 | 0 | 0 | 0 | 6917.4036 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 856.4418 | 404.862 | 61.9091 | 4.8052 | 0.76678 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2254 | Insulator Rep Steel - Moss Landing |  |  | NA | Bucket for insulator replacement on steel poles in the Moss Landing area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 13 | 5.2 | In-flight Future Scope | 5517285 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 4418.643 | 4418.643 | 1709.7876 | 163.6703 | 4.1096 | 10.2143 | 51.7135 | 14.9622 | 0 | 0 | 0 | 0 | 4403.6808 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 1476.6674 | 138.1884 | 26.4347 | 3.8598 | 6.8927 | 0.23035 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2255 | Insulator Rep Steel - Pismo Beach |  |  | NA | Bucket for insulator replacement on steel towers in the Pismo Beach area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 21 | 5.2 | In-flight Future Scope | 5517286 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 15402.9846 | 15402.9846 | 3768.2976 | 1386.2011 | 182.3998 | 47.7507 | 20.2935 | 304.8783 | 0 | 0 | 0 | 0 | 15098.1063 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 3748.0224 | 1369.681 | 428.218 | -256.4932 | 15.406 | 305.6717 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2256 | Insulator Rep Steel - Sacramento |  |  | NA | Bucket for insulator replacement on steel towers in the Sacramento area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 37 | 5.2 | In-flight Future Scope | 5517287 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 8117.7289 | 8117.7289 | 962.5164 | 140.1312 | 423.1585 | 11.0918 | 902.5696 | 554.3726 | 0 | 0 | 0 | 0 | 7563.3563 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 965.3193 | 139.2267 | 271.5358 | -11.0925 | 745.0669 | 326.3271 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2257 | Insul Repl - Steel - Sacramento BL |  |  | NA | Bucket for insulator replacement on steel towers in the Sacramento area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | 652 | NA | NA | 5519143 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1029.862 | 1029.862 | 0.923 | 275.7318 | 655.1789 | 37.1106 | 59.3602 | 1.3186 | 0 | 0 | 0 | 0 | 1028.5434 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 1.162 | 250.5947 | 578.6736 | 17.0968 | 48.1604 | 1.1221 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2258 | WSIP - Insulator Replacement - Steel |  |  | NA | Bucket for replacement or installation of insulators on steel structures in HFTD Tier 2 & 3 | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 3562 | 1. Work that prevents fire ignition | 2 | 5.2 | In-flight Future Scope | 5533593 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 291694.0498 | 291694.0498 | 20879.8816 | 40269.3919 | 72568.6868 | 92293.2078 | 34391.3086 | 4980.1257 | 0 | 0 | 0 | 0 | 286713.9241 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 17403.0907 | 36900.0179 | 64848.2378 | 70590.7354 | 25931.5337 | 4353.302 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2259 | Insulator Rep Steel - Table Mountain |  |  | NA | Bucket for insulator replacement on steel towers in the Table Mountain area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 4 | 5.2 | In-flight Future Scope | 5517288 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 13026.1705 | 13026.1705 | 1133.3386 | 2233.1709 | 565.5939 | 166.511 | 2022.3134 | 1885.0403 | 0 | 0 | 0 | 0 | 11141.1302 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 1108.9304 | 2177.4012 | 436.6733 | 29.9616 | 1863.7682 | 1592.5371 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2260 | Insulator Rep Steel - Eureka |  |  | NA | Bucket for insulator replacement on steel towers in the Eureka area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 202 | 2. Overhead With Strong Safety Link | 4 | 5.2 | In-flight Future Scope | 5517279 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1479.8834 | 1479.8834 | 268.5121 | 160.7183 | 57.8466 | 11.1741 | 204.8001 | 290.6866 | 0 | 0 | 0 | 0 | 1189.1968 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 267.1968 | 160.7183 | 34.9497 | 7.721 | 64.6375 | 339.3995 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2261 | 60/70/115kV N Insulators & Struc - Steel |  |  | NA | Bucket for replacement or installation of 60/70/115 kV insulators on steel structures in North region | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | 115 ¦ 70 ¦ 60 | NA | 202 | NA | 12 | 5.2 | In-flight Future Scope | 5510406 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 13432.6152 | 13432.6152 | 4.9185 | 542.7533 | 6233.1944 | 911.1598 | 365.5589 | 139.9129 | 0 | 0 | 0 | 0 | 13292.7023 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 431.5574 | 5728.8885 | 405.5179 | 269.0738 | 108.6965 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2262 | Insul Repl - Steel - Table Mountain BL |  |  | NA | Bucket for insulator replacement on steel towers in the Table Mountain area. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Subsidence |  | NA | NA | NA | NA | NA | NA | NA | 5.2 | In-flight Future Scope | 5519144 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2720.3338 | 2720.3338 | 0 | 128.3294 | 2472.0564 | 88.158 | 30.0852 | 1.7047 | 0 | 0 | 0 | 0 | 2718.6291 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 116.1819 | 2484.2039 | -504.7767 | 29.8592 | 1.7047 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2263 | 500/230kV Insulators & Struct - S Steel |  |  | NA | Bucket for replacement or installation of 500/230 kV insulators on steel structures in South region | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | 500 ¦ 230 | NA | 202 | NA | 27 | 5.2 | In-flight Future Scope | 5506219 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 20933.6574 | 20933.6574 | 0 | 693.0058 | 4295.234 | 169.5545 | 259.1622 | 113.0124 | 0 | 0 | 0 | 0 | 20820.645 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 600.4612 | 4034.8058 | -252.4614 | 198.6467 | 24.144 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2264 | 500/230kV Insulators&Struct-N Steel |  |  | NA | Bucket for replacement or installation of 500/230 kV insulators on steel structures in North region | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | NA | 500 ¦ 230 | NA | 202 | NA | 67 | NA | NA | 5510403 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 10341.503 | 10341.503 | 0 | 0 | 0 | 0 | 42.1886 | 0.666 | 0 | 0 | 0 | 0 | 10340.837 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 39.0151 | 0.6058 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2265 | Insulator Replacements-HFTD-Steel |  |  | NA | Forecast placeholder for Insulator Replacements-HFTD-Steel | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.012 | Future IGP Scope | EX111869 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 12000.2432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2266 | Insulator Replacements-Non-HFTD-Steel |  |  | NA | Forecast placeholder for Insulator Replacements-Non-HFTD-Steel | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.012 | Future IGP Scope | EX111871 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 12000.2432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2267 | Gates-Midway 500 kV Line Ins Replacement |  |  | Avenal, Kings ¦ Buttonwillow CDP, Kern ¦ Fresno ¦ Kern ¦ Kings | The majority of the structures have the original ceramic insulators. Over the decades the insulators and steel members have been exposed to avian nesting, guano, streamers, and other type of contamination. Although there have been relatively few failures, the consequences have been and can be significant due to the inherit risk associated with 500 kV lines. The objective is to replace existing insulators and associated hardware on 22 towers on the Gates – Midway 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2020-08-10 | 56 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | NA | 500 | NA | 202 | 2. Overhead With Strong Safety Link | 801 | NA | NA | 5772889 | T.0002381 | Gates-Midway 500kV Line Insulator Replac | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-19 | 2019-10-20 | 2021-05-13 | Prioritization | NA | FALSE | 1600 | NA ¦ NA | 4611.9052 | 4611.9052 | 1632.5232 | 2061.0183 | 3.7807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4611.9052 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 3728.9896 | 95.047 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $2 Mil - $3 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2268 | Malin-Round Mountain #2-500 kV Ins Repl |  |  | Montgomery Creek CDP, Shasta ¦ Round Mountain CDP, Shasta ¦ Shasta ¦ Siskiyou | The purpose of this project is to replace the 500kV insulators on the Malin-Round Mountain #2 transmission line. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2025-04-07 | 56 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 35 | NA | NA | 5772895 | T.0002387 | Malin-Round Mountain #2-500 kV Ins Repl | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-08-24 | 2020-12-31 | 2021-06-30 | Clearances | NA | FALSE | 8000 | NA ¦ NA | 14040.9279 | 14040.9279 | 8874.2781 | 4856.571 | -0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14040.9279 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 14041.0922 | -0.3 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2269 | Los Banos-Gates #1 500 kV Line Ins Repl |  |  | Fresno ¦ Merced | The majority of the structures have the original ceramic insulators. Over the decades, the insulators and steel members have been exposed to avian nesting, guano, streamers, and other types of contamination. Although there have been relatively few failures, the consequences have been and can be significant due to the inherit risk associated with 500 kV lines. The objective is to replace existing insulators and associated hardware on 200 structures on the Los Banos - Gates No. 1 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-10-29 | 61 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | NA | 500 | NA | 202 | 2. Overhead With Strong Safety Link | 450 | NA | NA | 5772896 | T.0002388 | Los Banos-Gates #1 500kV Line Insulator | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-07-06 | 2019-12-31 | 2020-12-15 | Prioritization | NA | FALSE | 4911 | NA ¦ NA | 6710.918 | 6710.918 | 3979.4539 | 430.9735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6710.918 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 5379.005 | 367.6322 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2270 | Los Banos-Midway #2 Line Ins Repl |  |  | Avenal, Kings ¦ Buttonwillow CDP, Kern ¦ Fresno ¦ Kern ¦ Kings ¦ Merced | The majority of the structures have the original ceramic insulators. Over the decades, the insulators and steel members have been exposed to avian nesting, guano, streamers, and other types of contamination. Although there have been relatively few failures, the consequences have been and can be significant due to the inherit risk associated with 500 kV lines. The objective is to replace existing insulators and associated hardware on 151 structures on the Los Banos - Midway No. 2 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-12-07 | 54 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | NA | 500 | NA | 202 | 2. Overhead With Strong Safety Link | 398 | NA | NA | 5772897 | T.0002389 | Los Banos-Midway #2 500kV Line Insulator | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-08-20 | 2019-12-31 | 2021-05-27 | Prioritization | NA | FALSE | 10590 | NA ¦ NA | 8875.6179 | 8875.6179 | 5175.7461 | 1865.6855 | 4.8613 | 0.3156 | 0 | 0 | 0 | 0 | 0 | 0 | 8875.6179 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 7840.7449 | 4.2715 | -120.5751 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2271 | Pit#3-Pit#1 230 kV Insulators |  |  | Burney CDP, Shasta ¦ Johnson Park CDP, Shasta ¦ Shasta | Increase reliability by replacing insulators and hardware on 183 structures on Pit #3-Pit #1 230kV circuit | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-03-20 | 97 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | NA | 230 | NA | 202 | 1. Work that prevents fire ignition | 150 | NA | NA | 5772999 | T.0002405 | Pit#3-Pit#1 230 kV Insulators | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-09-21 | 2019-09-05 | 2020-10-11 | Material | NA | FALSE | 6300 | NA ¦ NA | 2681.4471 | 2681.4471 | 1950.9112 | 274.9382 | 9.0566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2681.4471 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 2672.3903 | 9.0566 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2272 | Pit #3-Carberry Sta Insulators |  |  | Shasta | Increase reliability by replacing insulators and hardware on 89 structures on Pit #3-Carberry SW Station 230kV circuit. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-05-10 | 97 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | NA | 230 | NA | 202 | 1. Work that prevents fire ignition | 313 | NA | NA | 5773000 | T.0002406 | Pit #3-Carberry Sta Insulators | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-10-12 | 2020-10-09 | 2020-10-20 | NA | NA | FALSE | 3900 | NA ¦ NA | 2649.7402 | 2649.7402 | 1923.7992 | 442.3136 | 41.1972 | 1.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 2649.7402 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 2606.6495 | 41.1972 | 1.8932 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2273 | Pit#1-Cottonwood 230kV Insulators |  |  | Burney CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Johnson Park CDP, Shasta ¦ Millville CDP, Shasta ¦ Oak Run CDP, Shasta ¦ Round Mountain CDP, Shasta ¦ Shasta | Over the decades the insulators and steel members have been exposed to avian nesting, guano and streamers. There have been relatively few failures, however with this prolonged exposure and age consideration. The project is to increase reliability by replacing insulators and hardware on 530 structures on Pit #1-Cottonwood 230kV circuit. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2025-03-25 | 96 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | NA | 230 | NA | 446 | 1. Work that prevents fire ignition | 19 | NA | NA | 5782138 | T.0002407 | Pit#1-Cottonwood 230kV Insulators | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-08-13 | 2019-11-21 | 2020-09-13 | Prioritization | NA | FALSE | 8671 | NA ¦ NA | 8584.6851 | 8584.6851 | 6286.2354 | 823.3386 | 95.9985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8584.6851 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 5881.6132 | 65.3722 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2274 | Tesla-Metcalf 500 kV Insulator Replace |  |  | Alameda ¦ San Jose, Santa Clara ¦ Santa Clara | Insulators on 28 towers of the line have already been replaced after the insulators flashed and failed. The Tesla – Metcalf 500 kV Line Insulator Replacement Project (Project) will replace the insulators on the remaining 120 transmission line structures. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-09-09 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 253 | NA | NA | 5774626 | T.0002836 | Tesla-Metcalf 500 kV Insulator Replace | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-06-20 | 2020-02-28 | 2022-07-19 | Bundling Dependencies | NA | FALSE | 6647 | NA ¦ NA | 14398.6853 | 14398.6853 | 4936.9055 | 3546.0945 | 5663.5324 | 12.8614 | 0 | 0 | 0 | 0 | 0 | 0 | 14398.6853 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2025 | 0 | 0 | 13576.4456 | 12.0836 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2275 | Moss Landing-Los Banos 500 kV Insl Rep |  |  | Merced ¦ Monterey ¦ Prunedale CDP, Monterey ¦ Ridgemark CDP, San Benito ¦ San Benito ¦ Tres Pinos CDP, San Benito | This project proposes to replace insulators on 185 structures on the Moss Landing – Los Banos 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-08-23 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 248 | NA | NA | 5774627 | T.0002837 | Moss Landing-Los Banos 500 kV Insl Rep | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-08-08 | 2021-12-24 | 2022-08-26 | Clearances | NA | FALSE | 6530 | NA ¦ NA | 7675.0542 | 7675.0542 | 204.2028 | 4820.9758 | 2641.6551 | 4.3882 | 0 | 0 | 0 | 0 | 0 | 0 | 7675.0542 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2025 | 0 | 0 | 7076.0488 | -213.0732 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2276 | Moss Landing-Metcalf 500 kV Insl Rep |  |  | Elkhorn CDP, Monterey ¦ Monterey ¦ Prunedale CDP, Monterey ¦ San Jose, Santa Clara ¦ Santa Clara ¦ Santa Cruz | This project proposes to replace insulators on 125 structures on the Moss Landing – Metcalf 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-12-05 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 73 | NA | NA | 5774628 | T.0002838 | Moss Landing-Metcalf 500 kV Insl Rep | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-12-27 | 2021-11-05 | 2022-02-14 | NA | NA | FALSE | 6430 | NA ¦ NA | 7228.1033 | 7228.1033 | 203.5149 | 3350.7045 | 3669.0605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7228.1033 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2025 | 0 | 0 | 6659.1636 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2277 | Diablo-Gates #1 500 kV Insl Replace |  |  | Atascadero, San Luis Obispo ¦ El Paso de Robles, San Luis Obispo ¦ Fresno ¦ Kings ¦ Los Osos CDP, San Luis Obispo ¦ Monterey ¦ San Luis Obispo | This project proposes to replace insulators and associated hardware on 311 structures within the Diablo – Gates No. 1 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2025-03-21 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 33 | NA | NA | 5774629 | T.0002839 | Diablo-Gates #1 500 kV Insl Replace | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-10-01 | 2021-11-30 | 2021-11-22 | NA | NA | FALSE | 10200 | NA ¦ NA | 13674.6909 | 13674.6909 | 264.9886 | 13625.5507 | -215.8484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13674.6909 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 12720.3236 | -197.5497 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2278 | Diablo-Midway #3 500 kV Insl Replace |  |  | Avila Beach CDP, San Luis Obispo ¦ Buttonwillow CDP, Kern ¦ Kern ¦ San Luis Obispo | This project proposes to replace insulators and associated hardware on 362 structures on the Diablo – Midway No. 3 500 kV Line. The main type of insulator for replacement are first generation Sediver as these have experience failures from years of contamination which ATS and the vendor have analyzed and confirm replacement. In addition, the associated corona rings, or lack there of, are being replaced/installed accordingly primarily due to corrosion. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2025-04-07 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 27 | NA | NA | 5774630 | T.0002840 | Diablo-Midway #3 500 kV Insl Replace | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-01-11 | 2022-02-18 | 2022-04-06 | NA | NA | FALSE | 6520 | NA ¦ NA | 9051.1528 | 9051.1528 | 228.7847 | 3883.952 | 4937.5629 | 0.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 9051.1528 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2025 | 0 | 0 | 8876.9136 | 0.83648 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2279 | Diablo-Midway #2 500 kV Insl Replace |  |  | Avila Beach CDP, San Luis Obispo ¦ Buttonwillow CDP, Kern ¦ Kern ¦ San Luis Obispo | This project proposes to replace insulators and associated hardware on 350 structures on the Diablo – Midway No. 2 500 kV Line. The main type of insulator for replacement are first generation Sediver as these have experience failures from years of contamination which ATS and the vendor have analyzed and confirm replacement. In addition, the associated corona rings, or lack there of, are being replaced/installed accordingly primarily due to corrosion. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2025-04-07 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 500 | NA | 202 | 1. Work that prevents fire ignition | 21 | NA | NA | 5774631 | T.0002841 | Diablo-Midway #2 500 kV Insl Replace | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-02-17 | 2022-04-08 | 2022-03-21 | NA | NA | FALSE | 8650 | NA ¦ NA | 11037.4705 | 11037.4705 | 240.4445 | 1357.6026 | 9439.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11037.4705 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2025 | 0 | 0 | 10141.2262 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2280 | Replace Insulators - Vaca-Tesla 500kV |  |  | Alameda ¦ Byron CDP, Contra Costa ¦ Contra Costa ¦ Discovery Bay CDP, Contra Costa ¦ Knightsen CDP, Contra Costa ¦ Oakley, Contra Costa ¦ Sacramento ¦ Solano ¦ Vacaville, Solano | This project proposes to replace insulators and associated hardware on 39 structures on the Vaca – Tesla 500 kV Line. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2025-01-15 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | NA | 500 | NA | NA | NA | NA | 5.2 | In-flight Future Scope | 5782299 | T.0004299 | Replace Insulators - Vaca-Tesla 500kV | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-04-07 | 2022-12-31 | 2026-10-02 | Prioritization | NA | TRUE | 7400 | NA ¦ NA | 2957.4207 | 14329.5999 | 0 | 61.5021 | 2830.1299 | 4.421 | 26.9965 | 2406.368 | 2645.2647 | 0 | 0 | 4000 | 2923.0495 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2281 | Round Mtn-Table Mtn #1 500kV Insulators |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Chico, Butte ¦ Cohasset CDP, Butte ¦ Round Mountain CDP, Shasta ¦ Shasta ¦ Tehama ¦ Whitmore CDP, Shasta | A previous project replaced the insulators on 121 of the 368 total structures. Following an outage on the Tesla-Los Banos 500kV line and subsequent inspections, The Round Mountain-Table Mountain #1 500kV line was found to have insulators of the same type in a deteriorated condition with damage at some locations. This project proposes to replace the insulators, hardware and install corona rings on the remaining 247 structures to prevent failures resulting in outages or possible fire ignition. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-06-11 | 60 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | NA | 500 | NA | NA | NA | NA | 5.2 | In-flight Future Scope | 5786185 | T.0004860 | Round Mtn-Table Mtn #1 500kV Insulators | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-01-01 | NA | 2031-05-15 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8500.1723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2282 | Round Mtn-Table Mtn #2 500kV Insulators |  |  | Butte ¦ Butte Creek Canyon CDP, Butte ¦ Butte Valley CDP, Butte ¦ Chico, Butte ¦ Cohasset CDP, Butte ¦ Manton CDP, Shasta ¦ Manton CDP, Tehama ¦ Paynes Creek CDP, Tehama ¦ Round Mountain CDP, Shasta ¦ Shasta ¦ Tehama ¦ Whitmore CDP, Shasta | A previous project replaced the insulators on 79 of the 366 total structures. Following an outage on the Tesla-Los Banos 500kV line and subsequent inspections, The Round Mountain-Table Mountain #2 500kV line was found to have insulators of the same type in a deteriorated condition with damage at some locations. This project proposes to replace the insulators, hardware and install corona rings on the remaining 287 structures to prevent failures resulting in outages or possible fire ignition. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-07-25 | 60 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | NA | 500 | NA | NA | NA | NA | 5.2 | In-flight Future Scope | 5786186 | T.0004862 | Round Mtn-Table Mtn #2 500kV Insulators | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2030-01-01 | NA | 2031-05-15 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8500.1723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2283 | CH-S-S # 1 115 kV Insulator Replacement |  |  | Monterey ¦ Prunedale CDP, Monterey ¦ Salinas, Monterey ¦ Soledad, Monterey | Replace Polymer insulators on 45 Structures with glass in an inverted V configuration to meet the 51” clearance requirement. These lines have experienced multiple insulator related outages due to contamination. Replacing the polymer insulators with glass will facilitate the mitigation of future outages related to contamination. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-10-26 | 101 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 4.02 | Future IGP Scope | 5801819 | T.0009090 | CH-S-S # 1 & # 2 115 kV Insulator Repl | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-11-01 | NA | 2030-03-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2000.0405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2284 | CH-S-S # 2 115 kV Insulator Replacement |  |  | Monterey ¦ Prunedale CDP, Monterey ¦ Salinas, Monterey ¦ Soledad, Monterey | Replace Polymer insulators on 45 Structures with glass in an inverted V configuration to meet the 51” clearance requirement. These lines have experienced multiple insulator related outages due to contamination. Replacing the polymer insulators with glass will facilitate the mitigation of future outages related to contamination. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2021-08-24 | 101 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 4.02 | Future IGP Scope | 5801820 | T.0009090 | CH-S-S # 1 & # 2 115 kV Insulator Repl | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-11-01 | NA | 2030-03-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2000.0405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2285 | System NERC Mitigation Project (North) |  |  | NA | Bucket for System NERC Mitigation Project in Northern Service Territory | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 228 | NA | 5 | NA | NA | 5510301 | NA | NA | NA | 93 | NA ¦ 5520745 ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 72268.1492 | 72268.1492 | 530.7272 | -232.4718 | -340.3501 | 329.5932 | 117.8845 | -7.0528 | 0 | 0 | 0 | 0 | 72275.202 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 397.9866 | -167.5529 | -341.3523 | 329.4723 | 117.7538 | -7.0528 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2286 | Metcalf-Green Valley (Wood) 115kV (NERC) |  |  | Elkhorn CDP, Monterey ¦ Interlaken CDP, Santa Cruz ¦ Monterey ¦ Prunedale CDP, Monterey ¦ Santa Cruz | Work included:-Replacement of wood poles with light duty steel poles Wood pole re-frames Vegetation Removal Helicopter / Crane Equipment utilized Hand Digging Excavation required at numerous pole locations Notification to property owners regarding maintenance activities.Biological and cultural review of work locations. Verification of CPUC Permitting requirements. Implementation of Best Management Practices regarding water pollution. No SWPP required.Engineering as-builts. Work not included:-Substation upgrades. Telecommunication upgrades. Reconductoring Switch Replacement. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2021-11-23 | 38 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1.5 | NA | 115 | NA | NA | NA | NA | NA | NA | 5757771 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2016-05-02 | 2015-11-25 | 2016-06-10 | Weather | NA | FALSE | 1456.3796 | NA ¦ NA | 1486.8112 | 1486.8112 | 14.6694 | 0.6042 | 14.6849 | 0.4203 | 0 | 0 | 0 | 0 | 0 | 0 | 1486.8112 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 12.0289 | 0.49545 | 55.8471 | 0.35729 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2287 | System NERC Mitigation Project (South) |  |  | NA | Bucket for System NERC Mitigation Project in Southern Service Territory | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 228 | NA | NA | NA | NA | 5513299 | NA | NA | NA | 93 | NA ¦ 5520748 ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 87169.6355 | 87169.6355 | 3.7803 | 37.4304 | 6.3073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87169.6355 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | -95.9343 | -373.7507 | 23.0793 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2288 | BRIDGEVILLE-COTTONWOOD NERC PROJECT |  |  | Cottonwood CDP, Shasta ¦ Humboldt ¦ Mad River CDP, Trinity ¦ Platina CDP, Shasta ¦ Post Mountain CDP, Trinity ¦ Shasta ¦ Tehama ¦ Trinity | Address clearance issues identified on the Bridgeville-Cottonwood 115kV Transmission Lines. This project proposes to address the CPUC G.O. 95 clearance issues by replacing 27 H-Frame with 27 H-Frame LDSP’s, 8 Dead-end Conversions of Tangent Towers, multiple Re-Tensions, 6 Top Cage Extensions including insulator replacements, 1 Lattice Steel Pole Replacement, and 9 H-Frame replacements to address distribution under-build and crossings. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-03-11 | 72 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 6 | NA | 115 | NA | NA | NA | NA | NA | NA | 5760865 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2015 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2016-07-05 | 2015-10-30 | 2016-10-10 | Prioritization | NA | FALSE | 5700 | NA ¦ NA | 6706.7347 | 6706.7347 | 0.2092 | 30.1337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6706.7347 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 0.17555 | 25.4713 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2289 | Brighton Grand Island 115kV Land Order |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Other | New | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-29 | NA | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 4.0221 | In-flight Future Scope | 5800687 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2021-10-31 | OAI | NA | NA | TRUE | 150900 | NA ¦ NA | 833.9486 | 833.9486 | 0 | 0 | 212.9718 | 194.0362 | 398.5272 | 28.4133 | 0 | 0 | 0 | 0 | 805.5353 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2290 | Brighton-Grand Island: PH2 I-5 W Piling |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-29 | 26 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 228 | NA | NA | 4.0221 | In-flight Future Scope | 5794779 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | NA ¦ 5750422 ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6463-E | 2022-01-18 | Approved | 2022 | On Hold | 4 | 2022-05-10 | 2022-12-31 | 2026-09-30 | Prioritization | NA | TRUE | 150900 | NA ¦ NA | 27324.9299 | 36565.5083 | 0 | 947.7301 | 17799.6456 | 8625.6253 | -48.071 | -26.8955 | 0 | 0 | 0 | 0 | 27324.9299 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil [Project Status] Project is On Hold due to prioritization and placed in deferred status
| 2291 | BRIGHTON-GRAND ISLAND PH4 I-5 W LAST SEC |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-29 | 26 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 26 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 388 | 4.0401 | In-flight Future Scope | 5750422 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7270-E | 2024-05-13 | Approved | 2024 | Engineering more than 50% complete | 4 | 2027-08-16 | 2025-11-30 | 2027-11-30 | Prioritization | NA | FALSE | 150900 | NA ¦ NA | 2857.1506 | 22321.9442 | 32.8292 | 272.2067 | 472.3685 | 739.6845 | 53.8591 | 29.1331 | 1758.677 | 17582.616 | 0 | 0 | 2827.3151 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | 12.94% ¦ Electric Operations Risk Management | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil
| 2292 | Brighton-Grand Island: PH1 I-5 W Twr |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-29 | 24 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 228 | NA | NA | NA | NA | 5794778 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | NA ¦ 5750422 ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-08-24 | 2021-10-31 | 2021-12-10 | NA | NA | FALSE | 150900 | NA ¦ NA | 2581.5579 | 2581.5579 | 4.267 | 2526.9939 | 50.2969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2581.5579 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 2261.3243 | 44.1972 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2293 | Brighton-Grand Islan PH 5 - River Towers |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-29 | 25 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 4.0301 | In-flight Future Scope | 5797638 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7270-E | 2024-05-13 | Approved | 2024 | Operational | 2 | 2024-09-07 | 2024-07-30 | 2024-12-09 | NA | NA | TRUE | 150900 | NA ¦ NA | 9440.8908 | 9731.0926 | 0 | 12.4586 | 193.6601 | 169.4152 | 8936.704 | 418.8548 | 0 | 0 | 0 | 0 | 9312.2379 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 8433.1103 | 116.2615 | 0% | NA ¦ NA | 0.17% ¦ Electric Operations Risk Management | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil
| 2294 | BRIGHTON-GRAND ISLAND PH3 I-5 E DEVELOPE |  |  | Elk Grove, Sacramento ¦ Florin CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento | This project proposes to mitigate the 124 remaining California Public Utilities Commission (CPUC) General Order (GO) 95 clearance discrepancies as well as strengthen the structural integrity of both the Brighton-Grand Island 115 kV #1 and #2 lines by replacing all of the lattice steel towers from Brighton Substation to Grand Island Substation. This project will also reconductor the entire length of both circuits, replacing the existing 3/0 American Wire Guage (AWG) 7-strand Medium Hard-Drawn (MHD) copper (CU) conductor with new 715 All Aluminum Conductor (AAC). In doing so, this project will achieve compliance with CPUC GO 95 requirements and increase the structural integrity of the system to provide safe and reliable electric service to the customers in Sacramento County. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-29 | 98 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 228 | NA | NA | 4.0121 | In-flight Future Scope | 5794780 | T.0000070 | BRIGHTON-GRAND ISLAND #1 & #2 115KV NERC | 7 | 93 | NA ¦ 5750422 ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7270-E | 2024-05-13 | Approved | 2024 | On Hold | 4 | 2028-09-01 | 2024-12-31 | 2029-11-30 | Prioritization | NA | FALSE | 150900 | NA ¦ NA | 789.4643 | 59393.5853 | 0 | 242.5574 | 589.6488 | -42.7419 | 0 | -2.15 | 1093.066 | 1933.5 | 24102.207 | 31161.966 | 789.4643 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | 4.97% ¦ Electric Operations Risk Management | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] NA ¦ $100 Mil – $125 Mil [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2295 | Brighton-Davis 115kV (Steel) - Construc1 |  |  | Davis, Yolo ¦ Fairfield, Solano ¦ Florin CDP, Sacramento ¦ Freeport CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento ¦ Solano ¦ Suisun City, Solano ¦ Yolo | Replace 51 towers and install four top cage extensions on the Brighton-Davis 115kV (Steel) circuit. This mitigation work will eliminate clearance issues and allow operation of the line at full capacity | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-11-15 | 104 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 7 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5767138 | T.0000104 | BRIGHTON-DAVIS 115KV NERC STEEL | 1 | 93 | NA ¦ 5750599 ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-09-10 | 2017-03-31 | 2018-04-18 | Permitting | NA | FALSE | 9696 | NA ¦ NA | 13156.9748 | 13156.9748 | 333.0832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13156.9748 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 292.3389 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2296 | COLGATE-RIO OSO 230KV NERC PROJECT |  |  | Loma Rica CDP, Yuba ¦ Sutter ¦ Yuba | This project involves installing 1 - Dead End Conversion; 2 - TCE; 15 - Damper Replacements; 4 - Replace Insulators on the Colgate-Rio Oso 230kV circuit to eliminate blow-out issues related to right-of-way and operate the line at full capacity. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2023-11-16 | 66 | Lifecycle Replacement Analysis | Other - Deferral | $1 Mil - $2 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 6 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 42 | NA | NA | 5767083 | T.0000117 | COLGATE-RIO OSO 230KV NERC PROJECT | 1 | 93 | NA ¦ 5510301 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-01 | 2017-05-30 | 2020-01-18 | Weather | NA | FALSE | 850 | NA ¦ NA | 1204.4877 | 1204.4877 | 12.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1204.4877 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 10.4907 | 9e-05 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2297 | PALERMO-COLGATE+ 230KV NERC PROJECT |  |  | Butte ¦ Loma Rica CDP, Yuba ¦ Palermo CDP, Butte ¦ Yuba | This project involves installing one Top Cage Extension, one Tubular Steel Pole, and 21 Dampers on the PALERMO-COLGATE 230KV circuit. This will eliminate clearance issues and operate the line at full capacity. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-06-03 | 66 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 0.4 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 97 | NA | NA | 5767084 | T.0000118 | PALERMO-COLGATE+ 230KV NERC PROJECT | 1 | 93 | NA ¦ 5510301 ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-01 | 2017-01-19 | 2020-03-03 | Workforce | NA | FALSE | 886 | NA ¦ NA | 1610.3436 | 1610.3436 | 179.0235 | -0.0177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1610.3436 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 161.1214 | -0.0159 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2298 | TRINITY-COTTONWOOD 115kV Ph 2 |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Multiple | Replace | NA | T.0000126 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-03-06 | 71 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 7.1 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 61 | NA | NA | 5784199 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 7 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5685-E | 2019-11-13 | Approved | 2019 | Operational | 2 | 2020-07-01 | 2020-12-31 | 2020-09-23 | NA | NA | FALSE | 18400 | NA ¦ NA | 7663.9766 | 7663.9766 | 6853.2044 | 51.4385 | -56.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7663.9766 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 6407.1073 | 42.8736 | -46.9406 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2299 | TRINITY-COTTONWOOD NERC PROJECT |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Pole/Tower | Replace | NA | T.0000126 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-03-06 | 71 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 228 | NA | NA | NA | NA | 5760929 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 7 | 93 | NA ¦ 5767318 ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5685-E | 2019-11-13 | Approved | 2019 | Operational | 2 | 2019-06-25 | 2020-12-31 | 2019-07-17 | NA | NA | FALSE | 18400 | NA ¦ NA | 6616.3147 | 6616.3147 | 27.6445 | -10.8535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6616.3147 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 25.4504 | -9.2684 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2300 | Trinity-Cottonwood Land Acquisition |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Other | New | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-03-06 | NA | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | NA | NA | NA | 5.121 | In-flight Future Scope | 5545327 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 7 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | 2022-11-30 | OAI | NA | NA | TRUE | 18400 | NA ¦ NA | 1004.4277 | 1004.4277 | 0 | 10.5 | 212.3126 | 607.9813 | 157.3841 | 16.2497 | 0 | 0 | 0 | 0 | 988.178 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 222.8126 | 607.9813 | 157.3841 | 16.2497 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Non-electric work; not subject to GO 131-E NOC, PTC or CPCN requirements
| 2301 | Trinity-Cottonwood 115kV Ph. 3 |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Multiple | Replace | NA | T.0000126 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-03-06 | 74 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 6.2 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5790355 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 7 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6191-E | 2021-05-12 | Approved | 2021 | Operational | 2 | 2021-08-09 | 2021-11-30 | 2022-01-07 | NA | NA | FALSE | 18400 | NA ¦ NA | 6873.5314 | 6873.5314 | 247.8077 | 6784.2537 | -158.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6873.5314 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2025 | 0 | 0 | 6070.3633 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2302 | Trinity-Cottonwood 115kV Ph. 4 |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Multiple | Replace | NA | T.0000126 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-03-06 | 75 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 9.34 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 61 | 5.121 | In-flight Future Scope | 5792158 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 7 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6602-E | 2022-05-19 | Approved | 2022 | Operational | 2 | 2022-09-06 | 2022-11-30 | 2024-11-07 | Prioritization | NA | TRUE | 18400 | NA ¦ NA | 15502.411 | 15562.411 | 91.8992 | 1241.8912 | 10098.8328 | -367.221 | 4407.3364 | 89.6724 | 0 | 0 | 0 | 0 | 15472.7386 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 15472.7386 | 29.6724 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2303 | TRINITY-COTTONWOOD 115KV PH. 5 |  |  | Anderson, Shasta ¦ Centerville CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Douglas City CDP, Trinity ¦ Happy Valley CDP, Shasta ¦ Lewiston CDP, Trinity ¦ Redding, Shasta ¦ Shasta ¦ Shasta CDP, Shasta ¦ Trinity ¦ Weaverville CDP, Trinity | Phase 1-2: The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 139 structure replacements and modifications, 7.1 miles of conductor replacement (21 spans), and 56 discrepancies. Phase 3-4: Replace approximately 23 miles of conductor from sections on pole no. 000/001 - 015/117, pole no. 020/147 - 022/163 and pole no. 039/255 - 045/301 on the Trinity – Cottonwood 115 kV Line with a conductor capable of handling 563 amps summer emergency; Replace all wood poles with light duty steel (LDS) poles on the Trinity – Cottonwood 115 kV Line; Replace all wood poles with light duty steel (LDS) poles on the Jessup Tap 115kV; and Replace existing switch no. 107 (Texas Spring Road) with SCADA-operable switch and move switch closer to the Jessup Tap 115 kV. | Transmission Line - Multiple | Replace | NA | T.0000126 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-03-06 | 76 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 9.1 | NA | 115 | NA | 228 | NA | NA | 5.121 | In-flight Future Scope | 5807422 | T.0000120 | TRINITY-COTTONWOOD 115kV NERC | 7 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2025-09-01 | 2022-11-30 | 2025-12-29 | Prioritization | NA | TRUE | 18400 | NA ¦ NA | 59.8438 | 8375.0265 | 0 | 0 | 0 | 0 | 0 | 8210.7765 | 164.25 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2304 | TABLE MOUNTAIN-BUTTE #1 NERC PROJECT |  |  | Butte ¦ Chico, Butte ¦ Durham CDP, Butte | The project will replace 61 wood poles with 59 LDSPs and 2 new wood poles, complete 6 reframes and install 1 LSP extension to address ground clearance issues on the Table Mtn-Butte #1 115kV Transmission Lines to allow operation at full capacity. In addition, the remaining idle section of the guest circuit Chico A – Dayton 60kV will be removed from the Table Mtn – Butte #1 structures (14 spans). | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-11-12 | 25 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 5 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5760926 | T.0000125 | Table Mountain-Butte #1 | 2 | 93 | NA ¦ 5520749 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2015-05-14 | 2017-05-31 | 2016-02-28 | NA | NA | FALSE | 2556 | NA ¦ NA | 3176.4837 | 3176.4837 | 683.4071 | -99.1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3176.4837 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 631.4202 | -91.6018 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2305 | TABLE MOUNTAIN-BUTTE #1 Land Acquisition |  |  | Butte ¦ Chico, Butte ¦ Durham CDP, Butte | The project will replace 61 wood poles with 59 LDSPs and 2 new wood poles, complete 6 reframes and install 1 LSP extension to address ground clearance issues on the Table Mtn-Butte #1 115kV Transmission Lines to allow operation at full capacity. In addition, the remaining idle section of the guest circuit Chico A – Dayton 60kV will be removed from the Table Mtn – Butte #1 structures (14 spans). | Other | New | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-11-12 | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5546469 | T.0000125 | Table Mountain-Butte #1 | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2017-05-31 | OAI | NA | NA | FALSE | 2556 | NA ¦ NA | 92.6366 | 92.6366 | 0 | 92.6366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6366 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2025 | 0 | 92.6366 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2306 | HUMBOLDT-TRINITY NERC PROJECT |  |  | Humboldt ¦ Junction City CDP, Trinity ¦ Trinity ¦ Weaverville CDP, Trinity | The total project proposes to addresses the GO-95 clearance issues associated with the Humboldt-Trinity 115kV line. There are a total of 175 structures and locations that are included in this scope as a few areas in the circuit require construction at two structures to mitigate a single discrepancy. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-06-10 | 71 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 13 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 48 | NA | NA | 5760883 | T.0000126 | HUMBOLDT-TRINITY NERC PROJECT | 2 | 93 | NA ¦ 5767321 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-01 | 2017-09-30 | 2020-11-20 | Workforce | NA | FALSE | 44600 | NA ¦ NA | 18563.0177 | 18563.0177 | 589.7582 | 14.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18563.0177 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 553.9711 | 14.038 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2307 | Humboldt - Trinity 115kV NERC |  |  | Humboldt ¦ Junction City CDP, Trinity ¦ Trinity ¦ Weaverville CDP, Trinity | The total project proposes to addresses the GO-95 clearance issues associated with the Humboldt-Trinity 115kV line. There are a total of 175 structures and locations that are included in this scope as a few areas in the circuit require construction at two structures to mitigate a single discrepancy. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-06-10 | 71 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 12 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 48 | NA | NA | 5776099 | T.0000126 | HUMBOLDT-TRINITY NERC PROJECT | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-01 | 2018-12-31 | 2020-11-20 | Workforce | NA | FALSE | 44600 | NA ¦ NA | 12378.6482 | 12378.6482 | 1843.4774 | 74.7291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12378.6482 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 1720.1231 | 69.7287 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - Replacement Alternative [Alternative Solutions and Costs - Costs] $100 Mil – $125 Mil ¦ $30 Mil - $40 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2308 | EAGLE ROCK-CORTINA 115KV NERC PRJ |  |  | Clearlake, Lake ¦ Colusa ¦ Lake ¦ Lower Lake CDP, Lake ¦ Sonoma | Modify four towers with one waist cage extension and three re-tensions on the Eagle Rock-Cortina 115kV line to eliminate clearance issues and operate the line at full capacity. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-06-20 | 46 | Lifecycle Replacement Analysis | Other - Deferral | $0 Mil – $1 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5754764 | T.0000336 | EAGLE ROCK-CORTINA 115KV NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2015 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2015-08-01 | 2015-04-30 | 2015-10-16 | NA | NA | FALSE | 628 | NA ¦ NA | 788.1163 | 788.1163 | 0 | 0.1796 | 65.9539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788.1163 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 0.1625 | 113.6167 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2309 | SANTA ROSA-CORONA NERC PROJECT |  |  | Cotati, Sonoma ¦ Penngrove CDP, Sonoma ¦ Petaluma, Sonoma ¦ Rohnert Park, Sonoma ¦ Santa Rosa, Sonoma ¦ Sonoma | This project will address (16) CPUC G.O. 95 clearance issues by replacing (7) wood poles with wood poles, replacing (1) wood pole with Light Duty Steel Pole, reframing (4) wood poles, and replacing (1) manual switch pole with (1) new manual switch on a Laminate Wood Pole. This mitigation work will eliminate clearance issues and allow operation of the line at full capacity. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-08-02 | 71 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 1 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5767442 | T.0000351 | SANTA ROSA-CORONA NERC PROJECT | 1 | 93 | NA ¦ 5510301 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2015-05-08 | 2017-09-27 | 2016-02-28 | NA | NA | FALSE | 1365 | NA ¦ NA | 1731.676 | 1731.676 | -10.7036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1731.676 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | -8.6743 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2310 | RAVENSWOOD-SAN MATEO 115KV (HC) NERC |  |  | Foster City, San Mateo ¦ Menlo Park, San Mateo ¦ Redwood City, San Mateo ¦ San Mateo, San Mateo | Install six top cage extensions and one waist cage extension to address GO95 cleareance issuesand operate the line at full capacity. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-01-23 | 55 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5767450 | T.0000379 | RAVENSWOOD-SAN MATEO 115KV (HC) NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2014 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-01-24 | 2018-12-23 | 2017-02-23 | NA | NA | FALSE | 925 | NA ¦ NA | 1084.4206 | 1084.4206 | 0 | 52.0251 | -4.5137 | 2.092 | 0 | 0 | 0 | 0 | 0 | 0 | 1084.4206 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 44.2213 | -3.8366 | 1.7782 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2311 | MONTA VISTA-JEFFERSON #2 230KV NERC |  |  | Cupertino, Santa Clara ¦ Palo Alto, Santa Clara ¦ San Mateo ¦ Santa Clara ¦ Woodside, San Mateo | This project will install 1 top cage extension and replace hardware on 1 tower hardware to address GO95 clearance issues and operate the line at full capacity | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-08-08 | 61 | Lifecycle Replacement Analysis | Other - Deferral | $0 Mil – $1 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 0.05 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 181 | NA | NA | 5520750 | T.0000402 | MONTA VISTA-JEFFERSON #2 230KV NERC | 1 | 93 | NA ¦ 5510301 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-02-26 | 2017-04-01 | 2021-03-04 | Prioritization | NA | FALSE | 534 | NA ¦ NA | 1096.1916 | 1096.1916 | 226.2842 | 458.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1096.1916 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 209.621 | 420.8152 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2312 | Ignacio-Mare-Island Land Rights Acq |  |  | American Canyon, Napa ¦ Benicia, Solano ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The Ignacio-Mare Island #1 and #2 115kV NERC project team will be performing work from the Highway Substation to Cordelia Substation to replace and install structures, install cage extensions, and reconductor approximately 16.0 miles due to over-tension issues. It will also perform work from Jameson Substation to the North Tower and Mare Island Substations to replace and install structures and reconductor approximately 5.2 miles due to over-tension issues. The project team will improve system performance and reduce extended outage risk on the Ignacio-Mare Island 115kV transmission line by completing the scopes shown below. | Other | New | NA | T.0002886 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2020-07-20 | NA | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $350 Mil – $400 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 4.021 | In-flight Future Scope | 5547940 | T.0000415 | IGNACIO-MARE ISLD Jameson/Hwy - Cordelia | 5 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6601-E | 2022-05-18 | Approved | 2022 | Operational | 2 | NA | 2023-09-30 | OAI | NA | NA | TRUE | 28300 | NA ¦ NA | 750.2511 | 787.764 | 0 | 0 | 187.5591 | 262.4128 | 255.491 | 82.3011 | 0 | 0 | 0 | 0 | 705.4629 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 187.5591 | 262.4128 | 255.491 | 44.7882 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2313 | Ignacio-Mare Island Hwy Sub-Jameson Shoo |  |  | American Canyon, Napa ¦ Benicia, Solano ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The Ignacio-Mare Island #1 and #2 115kV NERC project team will be performing work from the Highway Substation to Cordelia Substation to replace and install structures, install cage extensions, and reconductor approximately 16.0 miles due to over-tension issues. It will also perform work from Jameson Substation to the North Tower and Mare Island Substations to replace and install structures and reconductor approximately 5.2 miles due to over-tension issues. The project team will improve system performance and reduce extended outage risk on the Ignacio-Mare Island 115kV transmission line by completing the scopes shown below. | Transmission Line - Multiple | Replace | NA | T.0002886 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2020-07-20 | 73 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $350 Mil – $400 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 0.1 | NA | 115 | NA | NA | NA | NA | NA | NA | 5801318 | T.0000415 | IGNACIO-MARE ISLD Jameson/Hwy - Cordelia | 5 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6601-E | 2022-05-18 | Approved | 2022 | Operational | 2 | 2022-10-01 | 2023-09-30 | 2022-10-20 | NA | NA | FALSE | 28300 | NA ¦ NA | 1836.1064 | 1836.1064 | 0 | 0 | 1698.6354 | 120.5067 | 16.7363 | 0.228 | 0 | 0 | 0 | 0 | 1835.8784 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 1533.5832 | 108.6655 | 15.0918 | 0.2056 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2314 | Ignacio-Mare Isld #1 - Support of Ignacio |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The Ignacio-Mare Island #1 and #2 115kV NERC project team will be performing work from the Highway Substation to Cordelia Substation to replace and install structures, install cage extensions, and reconductor approximately 16.0 miles due to over-tension issues. It will also perform work from Jameson Substation to the North Tower and Mare Island Substations to replace and install structures and reconductor approximately 5.2 miles due to over-tension issues. The project team will improve system performance and reduce extended outage risk on the Ignacio-Mare Island 115kV transmission line by completing the scopes shown below. | Transmission Line - Multiple | Replace | NA | T.0002886 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-11-13 | 73 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $350 Mil – $400 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5551781 | T.0000415 | IGNACIO-MARE ISLD Jameson/Hwy - Cordelia | 5 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-10-04 | 2023-09-30 | 2023-11-14 | NA | NA | FALSE | 28300 | NA ¦ NA | 1237.9755 | 1237.9755 | 0 | 0 | 0 | 1220.557 | 16.7889 | 0.6295 | 0 | 0 | 0 | 0 | 1237.346 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 1098.957 | 15.1163 | 0.56681 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2315 | IGNACIO-MARE ISLAND 1-2 115KV NERC |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The Ignacio-Mare Island #1 and #2 115kV NERC project team will be performing work from the Highway Substation to Cordelia Substation to replace and install structures, install cage extensions, and reconductor approximately 16.0 miles due to over-tension issues. It will also perform work from Jameson Substation to the North Tower and Mare Island Substations to replace and install structures and reconductor approximately 5.2 miles due to over-tension issues. The project team will improve system performance and reduce extended outage risk on the Ignacio-Mare Island 115kV transmission line by completing the scopes shown below. | Transmission Line - Multiple | Replace | NA | T.0002886 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-11-13 | 73 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $350 Mil – $400 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 5.2 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 295 | 4.021 | In-flight Future Scope | 5754759 | T.0000415 | IGNACIO-MARE ISLD Jameson/Hwy - Cordelia | 5 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6601-E | 2022-05-18 | Approved | 2022 | Operational | 2 | 2024-06-10 | 2023-09-30 | 2024-11-05 | Prioritization | NA | TRUE | 28300 | NA ¦ NA | 11556.9642 | 11587.9876 | 331.6946 | 1062.6375 | 2363.0564 | 52.9869 | 6546.5834 | 195.9795 | 0 | 0 | 0 | 0 | 11370.8981 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 10299.4257 | 169.5477 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2316 | IGNACIO-MARE ISL 115KV (HWY SUB/COR SUB) |  |  | American Canyon, Napa ¦ Black Point-Green Point CDP, Marin ¦ Fairfield, Solano ¦ Marin ¦ Napa ¦ Novato, Marin ¦ Solano ¦ Sonoma ¦ Vallejo, Solano | The Ignacio-Mare Island #1 and #2 115kV NERC project team will be performing work from the Highway Substation to Cordelia Substation to replace and install structures, install cage extensions, and reconductor approximately 16.0 miles due to over-tension issues. It will also perform work from Jameson Substation to the North Tower and Mare Island Substations to replace and install structures and reconductor approximately 5.2 miles due to over-tension issues. The project team will improve system performance and reduce extended outage risk on the Ignacio-Mare Island 115kV transmission line by completing the scopes shown below. | Transmission Line - Multiple | Replace | NA | T.0002886 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-11-13 | 74 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $350 Mil – $400 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 16 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 295 | 4.021 | In-flight Future Scope | 5774831 | T.0000415 | IGNACIO-MARE ISLD Jameson/Hwy - Cordelia | 5 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7563-E | 2025-04-02 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2025-07-22 | 2023-09-30 | 2025-10-31 | Material | NA | TRUE | 28300 | NA ¦ NA | 7257.9485 | 17720.512 | 450.0761 | 1267.9409 | 2787.7935 | 206.1373 | 851.8628 | 10652.657 | 141.8 | 0 | 0 | 0 | 6926.055 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2317 | Corcoran-Smyrna 115kV NERC Alert |  |  | Corcoran, Kings ¦ Kings ¦ Tulare | Update the Corcoran-Smyrna 115kV NERC transmission line to comply with California Public Utilities Commission (CPUC) General Order 95 (GO-95) requirements by replacing 224 existing lattice steel pole structures, installing two Supervisory Control and Data Acquisition (SCADA)-operated switches, and replacing existing single circuit all-aluminum conductors on the 29.4-mile transmission line | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-04-01 | 91 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 29.4 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 529 | NA | NA | 5744341 | T.0000418 | CORCORAN SMYRNA 115KV NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5681-E | 2019-11-05 | Approved | 2019 | Operational | 2 | 2021-08-25 | 2020-03-31 | 2022-02-15 | Clearances | NA | FALSE | 41592 | NA ¦ NA | 40240.4732 | 40240.4732 | 3862.8687 | 25525.7285 | 3568.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40240.4732 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2025 | 0 | 0 | 31806.1913 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2318 | Temblor-San Luis Obispo 115kV NERC Prj |  |  | Kern ¦ San Luis Obispo | Replace single conductor on 38 miles, retension 8 spans, raise 8 towers via top cage extensions, install 3 interset Tubular Steel Poles, convert 6 suspension towers to dead-ends, replace 2 switches, and modify 64 tower foundations on the Temblor-San Luis Obispo 115kV line to comply with CPUC General Order 95 (GO-95) requirements. | Transmission Line - Multiple | Replace | NA | T.0004113 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-08 | 83 | Lifecycle Replacement Analysis | Other - Deferral | $20 Mil - $30 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 38 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 23 | 3.0011 | In-flight Future Scope | 5750606 | T.0000423 | TEMBLOR-SAN LUIS OBISPO 115KV NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-12-03 | 2020-11-07 | 2029-06-15 | Prioritization | NA | FALSE | 26061 | NA ¦ NA | 5593.507 | 46977.6769 | 881.7843 | 1158.6415 | 573.0664 | 89.1467 | 180.5454 | 406.6784 | 1381.1 | 5773.874 | 32137.217 | 63.376 | 5527.2718 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2319 | KINGSBURG CORCORAN 1 AND 2 115KV NERC |  |  | Corcoran, Kings ¦ Fresno ¦ Kings | The Kingsburg-Corcoran #1 & #2 115kV circuits were analyzed as part of the 2011 Priority 1 NERC Assessment. The analysis consisted of LiDAR surveying and PLS CADD modeling to identify non-compliant spans. The completed analysis identified 153 of the 199 spans (77%) with clearance issues on the Kingsburg-Corcoran #1 and 139 of the 200 spans (70%) with clearance issues on the Kingsburg-Corcoran #2 electric transmission lines. The Kingsburg-Corcoran #1 and #2 115kV NERC project will address the above discrepancies and return the line back to compliance. Of the total 200 spans and 201 structures being replaced, the Kingsburg-Corcoran #1 and #2 115kV NERC project is responsible for replacement and reconductoring of 137 structures and spans. The High Speed Rail (HSR) relocation program will replace and reconductor the balance of the scope. | Transmission Line - Multiple | Replace | NA | T.0000448 ¦ T.0000418 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-21 | 96 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 36.7 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 432 | 5.111 | In-flight Future Scope | 5767509 | T.0000434 | KINGSBURG CORCORAN 1 AND 2 115KV NERC | 1 | 93 | NA ¦ 5751061 ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2026-11-01 | 2022-03-31 | 2027-03-31 | Prioritization | NA | FALSE | 25658 | NA ¦ NA | 11751.7459 | 63016.212 | 34.4892 | 748.9744 | 5050.4626 | 1507.7703 | 3112.3578 | 3459.486 | 39200.825 | 8836.868 | 0 | 0 | 11519.033 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | 2.1% ¦ Electric Operations Risk Management | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2320 | Smyrna-Semitrop-Midway 115kV NERC Alert |  |  | Buttonwillow CDP, Kern ¦ Kern | The Smyrna-Semitropic-Midway 115kV NERC project will rebuild the line to meet NERC compliance. The major project scope items are as follows:•Replace 155 lattice steel pole (LSP) structures with a new-design LSP structure.•Replace 6 lattice steel towers with Tubular Steel Poles (TSPs); 5 of the 6 TSPs will be installed with SCADA operated switches – 3 at the Semitropic junction and 2 at the Ganso Substation. The 6th TSP is a replacement for an existing lattice steel tower.•Replace existing 266 kcmil AAC single circuit all-aluminum conductors on the 22.3-mile transmission line with 1,113 AAC conductor on the west side of the circuit. | Transmission Line - Multiple | Replace | NA | T.0000143 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2021-11-23 | 17 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 22.3 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5744339 | T.0000448 | SMYRNA-SEMITROP-MIDWAY 115KV NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5299-E | 2018-05-21 | Approved | 2018 | Operational | 2 | 2018-10-22 | 2018-02-14 | 2019-03-31 | Project Design | NA | FALSE | 22888 | NA ¦ NA | 27776.664 | 27776.664 | 129.3967 | 64.4631 | 4.1865 | -6.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 27776.664 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 107.6538 | 52.7282 | 3.4245 | -4.9646 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2321 | Llagas-Hollister 115kV |  |  | Gilroy, Santa Clara ¦ San Benito ¦ Santa Clara | This project scope includes the following: 4 tower replacements, 1 span re-tension (9 sections) circuit to address the ground clearance issues on the Llagas - Hollister 115kV line to address 3 identified ground clearance. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2023-11-21 | 20 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5769221 | T.0001417 | Llagas-Hollister 115kV | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2015-10-17 | 2018-12-31 | 2016-02-28 | NA | NA | FALSE | 1578 | NA ¦ NA | 2263.841 | 2263.841 | 1180.6737 | -18.6099 | 3.5109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2263.841 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 987.1457 | -15.5594 | 2.9354 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2322 | VAC-VACAVILLE-JAMESON-N TWR 115KVNERC |  |  | Benicia, Solano ¦ Fairfield, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | The project addresses the GO-95 clearance issues associated with the Vaca-Vacaville-Jameson North Tower 115kV line. The project’s key scope elements include: • Install 24 Top Cage Extensions • Replace 1 wood pole with a tubular steel pole • Replace conductor on both circuits for 18.4 miles • Install Federal Aviation Administration (FAA) Obstruction Lighting at one tower • Convert 3 tangent towers to dead-ends • Retension 7 spans • Install body modifications and cross arm extensions to 87 towers • Install 58 screw anchor foundations and one grade beam foundation | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-28 | 74 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 17.5 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 11 | NA | NA | 5769960 | T.0001546 | VAC-VACAVILLE-JAMESON-N TWR 115KVNERC | 2 | 93 | NA ¦ 5754763 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5120-E | 2017-08-02 | Approved | 2017 | Operational | 2 | 2018-01-03 | 2017-12-16 | 2020-06-21 | Clearances | NA | FALSE | 44000 | NA ¦ NA | 17111.8752 | 17111.8752 | 1258.7862 | -62.5707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17111.8752 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 936.8175 | -46.5665 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ NA
| 2323 | VACA-VACAVILLE-JMSN-N TWR 115KV NERC Ph2 |  |  | Benicia, Solano ¦ Fairfield, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Vallejo, Solano | The project addresses the GO-95 clearance issues associated with the Vaca-Vacaville-Jameson North Tower 115kV line. The project’s key scope elements include: • Install 24 Top Cage Extensions • Replace 1 wood pole with a tubular steel pole • Replace conductor on both circuits for 18.4 miles • Install Federal Aviation Administration (FAA) Obstruction Lighting at one tower • Convert 3 tangent towers to dead-ends • Retension 7 spans • Install body modifications and cross arm extensions to 87 towers • Install 58 screw anchor foundations and one grade beam foundation | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-28 | 54 | Lifecycle Replacement Analysis | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 19.3 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 11 | NA | NA | 5775602 | T.0001546 | VAC-VACAVILLE-JAMESON-N TWR 115KVNERC | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5120-E | 2017-08-02 | Approved | 2017 | Operational | 2 | 2018-05-19 | 2018-12-13 | 2021-05-30 | Clearances | NA | FALSE | 44000 | NA ¦ NA | 11373.5704 | 11373.5704 | 1545.2304 | 1579.9719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11373.5704 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 1126.9001 | 1152.2361 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Alternative Solutions and Costs - Solutions] Wires - Reconductor/Line Rebuild Alternative ¦ Wires - System Configuration Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ NA
| 2324 | EAGLE ROCK-FULTON-SILVERADO NERC PROJECT |  |  | Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma | The work on Eagle Rock-Fulton-Silverado 115kV NERC project will be completed by replacing all conductor on this circuit for total of 8.3 continuous miles, installing (3) Top Cage Extensions, modifying (32) towers, converting (1) towers to a Dead-End and re-tensioning (1) span and reinforcing (15) foundations. Once completed, the Eagle Rock-Fulton-Silverado 115kV circuit will be in compliance with G.O. 95 ground clearance requirements under emergency operating conditions. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-04-01 | 93 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 8.3 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5769963 | T.0001549 | EAGLE ROCK-FULTON-SILVERADO NERC PROJECT | 1 | 93 | NA ¦ 5510301 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5115-E | 2017-07-24 | Approved | 2017 | Operational | 2 | 2019-05-01 | 2017-11-22 | 2019-06-29 | Weather | NA | FALSE | 688 | NA ¦ NA | 10951.1562 | 10951.1562 | 85.3681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10951.1562 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 74.0663 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2325 | FULTON JCT-VACA NERC PROJECT |  |  | Allendale CDP, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Yolo | The Fulton-Junction-Vaca 115kV and Madison-Vaca 115kV NERC projects will be completed with installation of (13) top cage extensions, replacing conductor on both circuits for a total of 6.22 miles per circuit, (4) Vertical extensions, (3) Tower replacements and (12) screw anchor foundations. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2021-08-25 | 111 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 6.2 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5769964 | T.0001550 | FULTON JCT-VACA NERC PROJECT | 1 | 93 | NA ¦ 5510301 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5048-E | 2017-04-13 | Approved | 2017 | Operational | 2 | 2018-01-02 | 2017-05-26 | 2018-04-30 | Permitting | NA | FALSE | 15115 | NA ¦ NA | 8484.5698 | 8484.5698 | 8.0741 | 72.2625 | 48.5559 | 0.5859 | 0 | 0 | 0 | 0 | 0 | 0 | 8484.5698 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 7.6808 | 68.7429 | 46.1911 | 0.55737 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2326 | SILVERADO-FULTON JCT NERC PROJECT |  |  | Napa ¦ Saint Helena, Napa ¦ Yolo | The Silverado – Fulton Junction 115kV NERC project will be completed by reconductoring 24 spans (4.9 miles double circuit) and replacing impacted insulators (24 structures); installing 1 Interset (LSP); replacing 1 Lattice Steel Tower; converting 3 towers to dead-ends; installing 1 top cage extension; and restoring 14 foundations. Once completed, the Silverado – Fulton Junction 115kV circuit will comply with GO 95 ground clearance and conductor tension requirements. The North American Electric Reliability Corporation (NERC) will be notified that all discrepancies have been addressed which is a requirement of the NERC Alert – Electric Transmission Project. Operating restrictions will be eliminated which supports the NERC and Western Electricity Coordinating Council (WECC) reliability requirements. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2023-08-19 | 103 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 9.8 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5769966 | T.0001552 | SILVERADO-FULTON JCT NERC PROJECT | 1 | 93 | NA ¦ 5510301 ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5280-E | 2018-04-26 | Approved | 2018 | Operational | 2 | 2019-08-05 | 2018-05-31 | 2019-12-17 | Permitting | NA | FALSE | 9240 | NA ¦ NA | 10662.3275 | 10662.3275 | 243.1674 | -33.7655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10662.3275 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 237.644 | -32.8233 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2327 | FULTON-LAKEVILLE 230KV (P3) NERC |  |  | Fulton CDP, Sonoma ¦ Larkfield-Wikiup CDP, Sonoma ¦ Santa Rosa, Sonoma ¦ Sonoma | This project involves installing 1 Top Cage Extensions on the Fulton-Lakeville 230kV circuit. This will eliminate clearance issues and operate the line at full capacity. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-01-30 | 119 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 0.1 | NA | 230 | NA | 228 | NA | NA | NA | NA | 5769967 | T.0001553 | FULTON-LAKEVILLE 230KV (P3) NERC | 1 | 93 | NA ¦ 5510301 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2015-11-19 | 2017-11-22 | 2016-03-31 | NA | NA | FALSE | 553 | NA ¦ NA | 1776.1662 | 1776.1662 | 905.3344 | 0.9014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1776.1662 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 877.1084 | 47.7011 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2328 | METCALF-SALINAS #2 NERC PROJECT |  |  | Gilroy, Santa Clara ¦ San Benito ¦ Santa Clara | This project scope includes the following: 14 tower replacements, 41 span re-tensions (6 sections) circuit to address the 23 ground clearance issues on the Metcalf – Salinas #2 115kV line | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2023-11-21 | 91 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 4 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 1459 | NA | NA | 5771275 | T.0002054 | Metcalf-Salinas No. 2 (Idle) (P3) | 1 | 93 | NA ¦ 5760897 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-08-01 | 2018-01-31 | 2020-11-07 | Permitting | NA | FALSE | 3162 | NA ¦ NA | 5719.073 | 5719.073 | 1746.6958 | 13.9008 | 4.4471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5719.073 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 4858.2655 | 11.5553 | 15.4222 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2329 | MORRO BAY-GATES 230KV NERC PH2 |  |  | Atascadero, San Luis Obispo ¦ El Paso de Robles, San Luis Obispo ¦ Monterey ¦ Morro Bay, San Luis Obispo ¦ San Luis Obispo | This project proposes to address the CPUC G.O. 95 clearance issues by installing 2 top cage extensions, leg extensions on 1 tower, 1 interset tubular steel pole and 2 section (4 continuous spans) re-tensions on the Morro Bay – Gates 230kV Pedestrian Access circuit. This mitigation work will eliminate clearance and over-tension issues and allow operation of the line at full capacity with work. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-03-03 | 69 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 46 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 124 | NA | NA | 5523094 | T.0002059 | Morro Bay-Gates 230kV Pedestrian Acc | 1 | 93 | NA ¦ 5513299 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-06 | 2019-05-03 | 2020-05-20 | Project Design | NA | FALSE | 2010 | NA ¦ NA | 1628.8238 | 1628.8238 | 1086.438 | 2.4784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1628.8238 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 1058.4542 | 2.4146 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2330 | BIRDS LANDING SS CONTRA COSTA PP 230KV |  |  | Antioch, Contra Costa ¦ Contra Costa ¦ Sacramento ¦ Solano | This project will address the clearance issues associated with the Birds Landing SS-Contra Costa PP SS 230kV transmission line by increasing the height of the transmission crossing, to 161 ft. above MHW, over the Sacramento River. The project team will replace and increase the height of four towers / foundations, replace ~1.5 miles of double-circuit conductor, and perform tower modifications on two adjacent towers. | Transmission Line - Multiple | Replace | NA | T.0008048 | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2020-08-10 | 20 | Lifecycle Replacement Analysis | Other - Deferral | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | 1.5 | NA | 230 | NA | 228 | NA | NA | 4.041 | In-flight Future Scope | 5791742 | T.0002081 | Birds Landing SS-Contra Costa PP 230kV | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6131-E | 2021-03-26 | Approved | 2021 | Construction (over 75%) | 3 | 2021-09-17 | 2022-12-31 | 2025-04-30 | Material | NA | TRUE | 5700 | NA ¦ NA | 63220.9151 | 69071.4191 | 1235.9056 | 8741.535 | 13150.2336 | 7378.5052 | 24729.5571 | 12672.8977 | 0 | 0 | 0 | 0 | 56398.5214 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | -1076.0134 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | 1.04% ¦ Electric Operations Risk Management | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2331 | Vaca-Tulucay-Lakeville 230kV |  |  | Green Valley CDP, Napa ¦ Green Valley CDP, Solano ¦ Hartley CDP, Solano ¦ Napa ¦ Solano ¦ Vacaville, Solano | This project will address 27 spans with CPUC G.O. 95 clearance issues by replacing 21 Top Cage Extension with 2 Dead-end Structures and 1 Re-Sag. This mitigation work will eliminate clearance issues and allow operation of the line at full capacity. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-03-20 | 64 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 8 | NA | 230 | NA | 228 | NA | NA | NA | NA | 5773073 | T.0002425 | Vaca-Tulucay-Lakeville 230kV | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-08-06 | 2018-05-07 | 2019-10-15 | Bundling Dependencies | NA | FALSE | 5264 | NA ¦ NA | 7098.0864 | 7098.0864 | 19.3706 | 328.0234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7098.0864 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 19.293 | 311.1021 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2332 | Ignacio-San Rafael #3 115kV Phase 3 NERC |  |  | Marin ¦ Novato, Marin ¦ San Rafael, Marin | The project will replace 7 wood poles with new wood poles and re-frame 8 wood poles to eliminate 17 CPUC GO 95 clearance issues. The project is a result of assessment work completed as part of the NERC Alert – Electric Transmission Project. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-02-26 | 63 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 1 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5774042 | T.0002716 | Ignacio-San Rafael #3 115kV Phase 3 NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2016-10-03 | 2018-09-28 | 2017-01-31 | NA | NA | FALSE | 1108 | NA ¦ NA | 1143.8729 | 1143.8729 | 44.0353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1143.8729 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 36.1089 | 34.3178 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2333 | Mesa-Santa Maria 115kV NERC |  |  | Nipomo CDP, San Luis Obispo ¦ San Luis Obispo ¦ Santa Maria, Santa Barbara | Raise 9 Structures by installing 4 Waist Cage and 5 Top Cage Extensions, install 1 interset TSP and new shieldwire over 30 spans, and re-tension 2 parallel circuits for 29 spans each to address 6 GO 95 clearance issues, conductor over-tension issues and close gas line proximity to towers identified on the Mesa – Santa Maria 115kV Transmission Line to allow operation at full capacity. The project is a result of assessment work completed as part of the NERC Alert – Electric Transmission Project. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-01-23 | 68 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 4.3 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 22 | NA | NA | 5774250 | T.0002756 | Mesa-Santa Maria 115kV NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5874-E | 2020-07-09 | Approved | 2020 | Operational | 2 | 2020-10-26 | 2020-05-31 | 2021-02-15 | Prioritization | NA | FALSE | 5700 | NA ¦ NA | 8433.0597 | 8433.0597 | 5719.0974 | 1611.9231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8433.0597 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2025 | 0 | 8267.0407 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2334 | IGNACIO-SAN RAFAEL 3 115KV NERC WOOD P2 |  |  | Marin ¦ Novato, Marin ¦ San Rafael, Marin | The IGNACIO-SAN RAFAEL # 3 115kV project will replace 40 wood poles with new wood poles, 3 lower distribution, 8 cross-arm replacements, 3 reframes, and 2 switch replacements to allow operation of the line at full capacity. The project is a result of assessment work completed as part of the NERC Alert – Electric Transmission Project | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-02-26 | 63 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 2 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5774249 | T.0002764 | IGNACIO-SAN RAFAEL 3 115KV NERC WOOD P2 | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-07-05 | 2017-07-17 | 2021-03-19 | Prioritization | NA | FALSE | 5725 | NA ¦ NA | 5100.2998 | 5100.2998 | 547.6029 | 105.4248 | 0.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5100.2998 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 288.4061 | 94.5236 | 0.85101 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2335 | Rio Oso-West Sacramento 115kV NERC |  |  | Arden-Arcade CDP, Sacramento ¦ Elverta CDP, Sacramento ¦ Rio Linda CDP, Sacramento ¦ Sacramento ¦ Sacramento, Sacramento ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ West Sacramento, Yolo | Install 23 top cage extensions and replace 49 towers on the Rio Oso-West Sacramento 115kV circuit. This mitigation work will eliminate clearance issues and allow operation of the line at full capacity. The project is a result of assessment work completed as part of the NERC Alert – Electric Transmission Project. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-12-11 | 86 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 43.6 | NA | 115 | NA | 228 | NA | NA | NA | NA | 5774458 | T.0002765 | Rio Oso-West Sacramento 115kV NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-10 | 2017-06-17 | 2019-10-11 | Prioritization | NA | FALSE | 11135 | NA ¦ NA | 10738.0738 | 10738.0738 | 34.9623 | 9410.0384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10738.0738 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 31.4865 | 8148.4642 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2336 | CORTINA #1 60KV NERC PRJ |  |  | Arbuckle CDP, Colusa ¦ Colusa ¦ Yolo | The project is a result of assessment work completed as part of the NERC Alert – Electric Transmission Project. 112 of the 450 spans on the circuit had GO 95 clearance discrepancies. The scope was to include 77 wood pole reframes, 18 wood pole replacements and 1 wood pole interset. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-10-01 | 124 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 5.5 | NA | 60 | NA | 235 | NA | NA | NA | NA | 5760872 | T.0002766 | CORTINA #1 60KV WOOD NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2015-04-29 | 2016-12-20 | 2017-06-30 | Weather | NA | FALSE | 2010 | NA ¦ NA | 1963.7335 | 1963.7335 | -12.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1963.7335 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | -11.9919 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2337 | Pit #5-Round Mtn #1 230kV (Steel) NERC |  |  | Montgomery Creek CDP, Shasta ¦ Round Mountain CDP, Shasta ¦ Shasta | This project will modify 50 towers on the Pit 5-Round Mountain 1 230kV Transmission Lines to allow operation at full capacity. The project is a result of assessment work completed as part of the NERC Alert – Electric Transmission Project. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-04-03 | 82 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | 4.5 | NA | 230 | NA | 228 | NA | NA | NA | NA | 5774257 | T.0002771 | Pit #5-Round Mtn #1 230kV (Steel) NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-09-21 | 2017-09-30 | 2017-09-26 | NA | NA | FALSE | 5746 | NA ¦ NA | 3801.0954 | 3801.0954 | -0.4222 | 0 | 124.0631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3801.0954 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | -0.35478 | -1e-05 | 104.2571 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2338 | TES Tap 230kV (Steel) NERC |  |  | Danville, Contra Costa ¦ San Ramon, Contra Costa | The TES Tap 230kV NERC Project will replace 3 TSPs with 3 new TSPs and 1 span re-tension to address existing ground clearance issues. Once completed, the TES Tap 230kV circuit will be in compliance with G.O. 95 ground clearance requirements under emergency operating conditions. The North American Electric Reliability Corporation (NERC) will be notified that all discrepancies have been addressed which is a requirement of the NERC Alert – Electric Transmission Project. Operating restrictions will be eliminated which supports the NERC and Western Electricity in Coordinating Council (WECC) reliability requirements. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-11-18 | 100 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 3.3 | NA | 230 | NA | 228 | NA | NA | NA | NA | 5525496 | T.0002775 | TES Tap 230kV (Steel) NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-02-12 | 2018-03-19 | 2017-12-28 | NA | NA | FALSE | 1664 | NA ¦ NA | 1234.2943 | 1234.2943 | 213.1926 | 130.7098 | 4.3388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2943 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 185.197 | 113.5456 | 3.769 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2339 | Pit #5-Round Mtn #2 230kV (Steel) NERC |  |  | Montgomery Creek CDP, Shasta ¦ Round Mountain CDP, Shasta ¦ Shasta | This project will modify 50 towers on the Pit 5-Round Mountain 230kV Transmission Lines to allow operation at full capacity. The project is a result of assessment work completed as part of the NERC Alert – Electric Transmission Project. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-06-25 | 82 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | 4.5 | NA | 230 | NA | 228 | NA | NA | NA | NA | 5525486 | T.0002784 | Pit #5-Round Mtn #2 230kV (Steel) NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-08-26 | 2017-03-30 | 2018-09-21 | Project Design | NA | FALSE | 4914 | NA ¦ NA | 3646.6473 | 3646.6473 | 23.1828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3646.6473 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 21.9558 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2340 | West Fresno-California Avenue Phase 2 |  |  | Calwa CDP, Fresno ¦ Fresno ¦ Fresno, Fresno | In response to a NERC Recommendation to the Industry, PG&E LiDAR surveyed and prepared a PLS CADD model to assess GO 95 clearance compliance for the West Fresno-California Avenue 115kV Pole Replacement Project. This project will address the identified clearance issues. All design is complete. The West Fresno-California Avenue 115kV Pole Replacement Project consist of the replacement of structures 003/002 and 003/004 which has a distribution under-build circuit. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2023-09-08 | 73 | Lifecycle Replacement Analysis | Other - Deferral | $0 Mil – $1 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | 5. Compliance/Commitments With Strong Safety Link | 465 | NA | NA | 5537639 | T.0002808 | West Fresno-California Ave 115kV (Wood) | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-01-31 | 2021-11-19 | 2022-01-31 | NA | NA | FALSE | 478 | NA ¦ NA | 115.6566 | 115.6566 | 0 | 37.6067 | 78.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.6566 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2025 | 0 | 0 | 102.253 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2341 | Llagas-Hollister 115kV (Wood) |  |  | Gilroy, Santa Clara ¦ San Benito ¦ Santa Clara | This project scope includes the following: Replace 19 wood poles with Light Duty Steel Poles, replace 1 wood pole with 1 wood pole, re-frame 13 wood pole locations on the Llagas-Hollister circuit and remove 2 wood poles to address the ground clearance issues on the Llagas-Hollister Transmission Line to allow operation. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2023-11-21 | 48 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 21.6 | NA | 115 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 408 | NA | NA | 5778239 | T.0003249 | LLAGAS-HOLLISTER 115kV (Wood) | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-09-21 | 2019-08-31 | 2020-11-04 | Project Design | NA | FALSE | 3200 | NA ¦ NA | 1451.3294 | 1451.3294 | 1155.4132 | 6.3178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1451.3294 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 1239.877 | 31.9843 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2342 | Cresta-Rio Oso 230kV Ph. 2 |  |  | Butte ¦ Oroville East CDP, Butte ¦ Oroville, Butte ¦ Palermo CDP, Butte ¦ South Oroville CDP, Butte ¦ Sutter ¦ Yuba | This project scope involves 3 - Delta Cage Top Extensions, replacing 1 – Lattice Steel Tower (LST) with a 3-pole Tubular Steel Pole (TSP) structure with micro-pile foundations, and 4 – re-tension spans and associated hardware replacements. This mitigation work will eliminate clearance issues and allow operation of the line at full capacity with work | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-05-30 | 19 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 2 | NA | 230 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | NA | NA | NA | 5528379 | T.0003683 | Cresta-Rio Oso 230kV Ph. 2 NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-16 | 2019-09-30 | 2019-12-10 | NA | NA | FALSE | 2534 | NA ¦ NA | 2469.2445 | 2469.2445 | 115.5029 | 2.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2469.2445 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 287.28 | 1.968 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2343 | Silverado-Fulton 115kV Sw. No. 147 149 |  |  | Napa ¦ Saint Helena, Napa ¦ Yolo | The objective of this project is to design and replace the structures and switches at Silverado Jct. The new design will replace two (2) switches, two (2) wood structures with TSPs, and one wood tap pole to LDSP. This mitigation work will eliminate clearance issues and allow operation of the line at full capacity with work | Transmission Line - Switch | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2023-08-19 | 103 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 | NA | 228 | NA | NA | NA | NA | 5530982 | T.0004130 | Silverado Fulton 115kV Sw. No. 147/149E | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-20 | 2019-10-31 | 2019-11-23 | NA | NA | FALSE | 3061 | NA ¦ NA | 1361.9496 | 1361.9496 | 23.8178 | 0 | 103.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1361.9496 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2022 ¦ 2025 | -27.3257 | 0 | 99.3483 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2344 | Middle Fork #1 60kv |  |  | Placer | The project scope of work will mitigate 1 GO 95 clearance issues on the Middle Fork-Gold Hill 230kV circuit between structure number 008/118 and 008/114. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2023-07-08 | 58 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 0.4 | NA | 60 | NA | 228 | 5. Compliance/Commitments With Strong Safety Link | 16 | NA | NA | 5782183 | T.0004288 | Middle Fork #1 60kv NERC | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-09-13 | 2020-10-17 | 2021-10-17 | Project Design | NA | FALSE | 4780 | NA ¦ NA | 3749.0776 | 3749.0776 | 339.8639 | 3167.4645 | -1.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3749.0776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 52.7821 | 2971.5154 | -1.7242 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2345 | CRAGVIEW-CASCADE 115KV RECON P1 |  |  | Lakehead CDP, Shasta ¦ Mountain Gate CDP, Shasta ¦ Redding, Shasta ¦ Shasta | The project team will address CPUC GO-95 and PG&E standard requirements, in addition to increasing system performance and reducing fire ignition risk in Shasta County by performing the following work: • Replace 21.6 miles of existing conductor with 397 Aluminum Conductor Steel Reinforced (ACSR) conductor (Phase 1 = ~8.6 miles & Phase 2 = ~13 miles). • Replace 99 existing structures with new steel structures (Phase 1 = 37 structures & Phase 2 = 63). • Re-tension Optical Ground Wire (OPGW) In 2018 and 2019, PG&E’s Wildfire Safety Inspection Program (WSIP) identified 46 spans with transmission-line-to-fiber and six transmission-line-to-ground clearance discrepancies on the Crag View-Cascade 115kV Line. Engineering efforts commenced in June 2020 to develop the project scope to mitigate the identified discrepancies which resulted in 37 structure replacements. Between 30% and 60% engineering, the team identified overtension that exceeded CPUC GO-95 tension limits throughout the first 8.6 miles of the Crag View-Cascade 115kV Line. As a result of the identified overtension, it was deemed by the project team that the first 8.6 miles of conductor and 37 structures be replaced to address the identified overtension issues. If the overtension issues on the existing conductor is not corrected, more stress on the existing insulators and structures may occur, which potentially put the components at risk of failing. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-03-13 | 81 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $300 Mil - $350 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | TRUE | Heat Wave ¦ Weather |  | 21.6 | NA | 115 | NA | NA | 5. Compliance/Commitments With Strong Safety Link | 53 | NA | NA | 5790354 | T.0005874 | CRAG VIEW-CASCADE 115KV NERC PROJECT | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6547-E | 2022-03-31 | Approved | 2022 | Operational | 2 | 2022-06-21 | 2022-10-31 | 2023-02-23 | NA | NA | TRUE | 50200 | NA ¦ NA | 17444.9606 | 17444.9606 | 298.3826 | 765.2524 | 13173.995 | 2974.2485 | 231.1714 | 1.9106 | 0 | 0 | 0 | 0 | 17443.05 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 14777.2746 | 197.602 | 1.6331 | 0% | NA ¦ NA | 230% ¦ Electric Operations Risk Management | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2346 | CRAGVIEW-CASCADE 115KV RECON P2 |  |  | Lakehead CDP, Shasta ¦ Mountain Gate CDP, Shasta ¦ Redding, Shasta ¦ Shasta | The project team will address CPUC GO-95 and PG&E standard requirements, in addition to increasing system performance and reducing fire ignition risk in Shasta County by performing the following work: • Replace 21.6 miles of existing conductor with 397 Aluminum Conductor Steel Reinforced (ACSR) conductor (Phase 1 = ~8.6 miles & Phase 2 = ~13 miles). • Replace 99 existing structures with new steel structures (Phase 1 = 37 structures & Phase 2 = 63). • Re-tension Optical Ground Wire (OPGW) In 2018 and 2019, PG&E’s Wildfire Safety Inspection Program (WSIP) identified 46 spans with transmission-line-to-fiber and six transmission-line-to-ground clearance discrepancies on the Crag View-Cascade 115kV Line. Engineering efforts commenced in June 2020 to develop the project scope to mitigate the identified discrepancies which resulted in 37 structure replacements. Between 30% and 60% engineering, the team identified overtension that exceeded CPUC GO-95 tension limits throughout the first 8.6 miles of the Crag View-Cascade 115kV Line. As a result of the identified overtension, it was deemed by the project team that the first 8.6 miles of conductor and 37 structures be replaced to address the identified overtension issues. If the overtension issues on the existing conductor is not corrected, more stress on the existing insulators and structures may occur, which potentially put the components at risk of failing. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-03-13 | 82 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $300 Mil - $350 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 21.6 | NA | 115 | NA | NA | NA | NA | 4.013 | In-flight Future Scope | 5795434 | T.0005874 | CRAG VIEW-CASCADE 115KV NERC PROJECT | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 7571-E | 2025-04-11 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2025-07-22 | 2023-10-31 | 2025-10-31 | Prioritization | NA | TRUE | 50200 | NA ¦ NA | 2485.0268 | 26763.5332 | 0 | 289.9528 | 747.8073 | 9.8205 | 1196.8596 | 24384.8251 | 134.2679 | 0 | 0 | 0 | 2244.4403 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | 8.76% ¦ Electric Operations Risk Management | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2347 | Hetch Hetchy Wtr & Pwr Discrepancies |  |  | Fremont, Alameda | The project will address clearance issues that the Newark-Nummi 115 kV Line and the Newark-Livermore 60 kV Line have with the Moccasin Creek-Newark Nos. 3 and 4 115 kV Lines, which are operated by the Hetch Hetchy Water and Power Transmission System. The project scope of work includes following: • Install 10-foot top cage extensions on Towers 000/004 and 000/005 to increase the clearance separation between the lines; and • Replace the old copper conductor, insulators and other hardware on both PG&E lines between Towers 000/003 to 000/005. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-07-29 | 102 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | NA | 115 ¦ 60 | NA | NA | NA | NA | NA | NA | 5544747 | T.0007119 | Hetch Hetchy Wtr & Pwr Discrepancies | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-08-28 | 2022-08-12 | 2023-09-28 | Prioritization | NA | FALSE | 962 | NA ¦ NA | 1313.7887 | 1313.7887 | 0 | 124.928 | 538.2758 | 637.074 | 13.5109 | 0 | 0 | 0 | 0 | 0 | 1313.7887 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 110.8736 | 529.4618 | 598.0727 | 12.868 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2348 | Pittsburg 60kV Tap Project |  |  | Pittsburg, Contra Costa | This project will proactively replace 16 structures and replace all conductor on the Pittsburg 60kV Tap Line to address a deteriorating structure (000/001), mitigate induction risk due to an adjacent gas distribution line, remove idle distribution conductor, replace over-tensioned transmission conductor and mitigate 7 GO95 clearance infractions. To support PG&E top-level initiatives to manage asset risk for the benefit of public and employee safety, service reliability, operational flexibility, and cost reduction, the proposed Pittsburg 60kV Tap Line Project will proactively replace all structures and conductor on this line. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2024-05-15 | 51 | Lifecycle Replacement Analysis | Other - Deferral | $3 Mil -$5 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | 1.19 | NA | 60 | NA | NA | NA | NA | NA | NA | 5797938 | T.0007454 | Pittsburg 60kV Tap Project | 1 | 93 | NA ¦ 5544346 ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6446-E | 2021-12-28 | Approved | 2022 | Operational | 2 | 2022-03-29 | 2022-03-31 | 2022-05-18 | NA | NA | FALSE | 4500 | NA ¦ NA | 2690.5496 | 2690.5496 | 0 | 0 | 2669.2593 | 21.2903 | 0 | 0 | 0 | 0 | 0 | 0 | 2690.5496 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2025 | 0 | 0 | 2024.4256 | 16.1299 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2349 | Vasco-Herdlyn Clearance Mitigation |  |  | Alameda ¦ Contra Costa ¦ Livermore, Alameda | The project will address California Public Utilities Commission (CPUC) General Order 95 (GO-95) and Pacific Gas and Electric Company (PG&E) standard requirements, in addition increase system performance in Alameda and Contra Costa counties by performing the following work: • Replace sixty-one (61) wood structures on the Vasco-Herdlyn 60 kV Line; • Reframe one (1) wood structure • Install 19 bypass loops to mitigate magenetic heating effects • Reframe distribution underbuild at 25 locations with inadequate ground clearance • Install conductor temperature monitoring device • Replacement of old insulators, hardware, and equipment on the structure; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | NERC Compliance - GO 95 | Other [See Notes] | NA | 2025-02-27 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | 10.97 | NA | 60 | NA | NA | NA | NA | 5.121 | Non-IGP | 5798811 | T.0007628 | Vasco-Herdlyn NERC Mitigation | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6756-E | 2022-11-09 | Approved | 2023 | Operational | 2 | 2023-09-11 | 2023-07-31 | 2024-12-09 | Project Design | NA | TRUE | 13832 | NA ¦ NA | 7819.0493 | 7940.9232 | 0 | 75.9357 | 941.4075 | 4113.9778 | 2837.1326 | -27.5304 | 0 | 0 | 0 | 0 | 7968.4536 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 7315.5762 | -136.2197 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2350 | FAA Non-SCADA Beacon Replacements 2020 |  |  | NA | Bucket for FAA Non-SCADA Beacon Replacements 2020 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | 2. Overhead With Strong Safety Link | 880 | NA | NA | 5538267 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1150.4173 | 1150.4173 | 249.9601 | 822.6756 | 77.7817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150.4173 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 249.9601 | 822.6756 | -96.6964 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2351 | Wheatland-East Nicolaus #2-60kV Pole Rep |  |  | Beale AFB CDP, Yuba ¦ East Nicolaus CDP, Sutter ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Smartsville CDP, Yuba ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ Wheatland, Yuba ¦ Yuba | This project proposes to replace 232 wood poles with light duty steel poles in addition to reconductoring approximately 13 miles of obsolete 1/0 Cu transmission line in efforts to increase reliability on the Smartville-Nicolaus #2 line. Approximately 8 miles of #6 or 2/0 Cu conductor will be replaced on the 12 kV distribution system in the area with either 4/0 or 715 AAC. In addition a new transmission line switch will be installed at Wheatland Substation. The switch will be replaced in 2nd quarter 2016, with the poles planned for replacement and reconductoring. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-03-27 | 64 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 270 | NA | NA | 3.0011 | In-flight Future Scope | 5744742 | P.05271 | Wheatland to East Nicolaus | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 4778-E | 2016-01-20 | Approved | 2016 | Operational | 2 | NA | 2017-07-07 | OAI | NA | NA | FALSE | 7095.6018 | NA ¦ NA | 8358.6898 | 8358.6898 | 0 | 0 | 75.6838 | 83.7669 | 1181.4411 | 17.0364 | 0 | 0 | 0 | 0 | 8341.6534 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 75.6838 | 56.4781 | 1158.8465 | 16.8003 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2352 | MORAGA-OAKLAND X 115KV LINES 1-4 LAND |  |  | Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa ¦ Piedmont, Alameda | The project proposes to replace the structures, conductors, and hardware in the same overhead alignment between Moraga Substation and California State Highway 13 and also to relocate the line sections between Highway 13, and Oakland X underground (UG) within city streets. By replacing the aging facilities PG&E can improve wildfire safety and public safety and increase path capacity into the Oakland area. The project scope of work includes: • Removal of 78 existing lattice steel transmission towers • Removal of approximately 20 circuit miles of conductor • Installation of approximately 60 new lattice steel transmission towers • Installation of approximately 11 miles of Aluminum Conductor Composite Reinforced (ACCR) conductor • Installation of three 115kV underground duct banks with 115kV transmission cables totaling approximately six miles • Installation of new 115kV circuit breakers and air switches at Moraga Substation • Upgrade the 115kV bus at Oakland X Substation to complement the higher capacity ACCR conductor | Other | New | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-02-19 | NA | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | NA | 115 | NA | NA | NA | NA | 4.05 | In-flight Future Scope | 5551684 | T.0000349 | Moraga-Oakland #1-#4 Rebuild | 5 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2024-12-12 | EIR | NA | CPUC | NA | PTC: A. 24-11-005 | 2024-11-15 | Filed and Under Administrative Review | TBD | Planning | 5 | NA | 2025-07-31 | 2030-12-30 | Prioritization | NA | TRUE | 212000 | NA ¦ NA | 921.5749 | 1134.7936 | 0 | 169.1137 | 106.9085 | 163.9482 | 399.1569 | 225.6662 | 70 | 0 | 0 | 0 | 839.1274 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2030 | 0 | 169.1137 | 106.9085 | 163.9482 | 399.1569 | 82.4475 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2353 | MORAGA-OAKLAND X 115KV #1&2: RECOND |  |  | Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa ¦ Piedmont, Alameda | The project proposes to replace the structures, conductors, and hardware in the same overhead alignment between Moraga Substation and California State Highway 13 and also to relocate the line sections between Highway 13, and Oakland X underground (UG) within city streets. By replacing the aging facilities PG&E can improve wildfire safety and public safety and increase path capacity into the Oakland area. The project scope of work includes: • Removal of 78 existing lattice steel transmission towers • Removal of approximately 20 circuit miles of conductor • Installation of approximately 60 new lattice steel transmission towers • Installation of approximately 11 miles of Aluminum Conductor Composite Reinforced (ACCR) conductor • Installation of three 115kV underground duct banks with 115kV transmission cables totaling approximately six miles • Installation of new 115kV circuit breakers and air switches at Moraga Substation • Upgrade the 115kV bus at Oakland X Substation to complement the higher capacity ACCR conductor | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-08-22 | 94 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | 6 | NA | 115 | NA | 228 | NA | NA | 4.05 | In-flight Future Scope | 5793947 | T.0000349 | Moraga-Oakland #1-#4 Rebuild | 5 | 93 | NA ¦ 5789523 ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2024-12-12 | EIR | NA | CPUC | NA | PTC: A. 24-11-005 | 2024-11-15 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2029-05-01 | 2025-07-31 | 2030-12-30 | Prioritization | NA | FALSE | 212000 | NA ¦ NA | 11070.7333 | 132143.4702 | 2145.8684 | 4157.1539 | 1462.6327 | 1536.8403 | 1564.7673 | 1447.8165 | 20057.67 | 60479.042 | 26191.679 | 9100 | 10867.2627 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | 22.18% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2354 | MORAGA-OAKLAND X 115KV #3&4 RECOND |  |  | Contra Costa ¦ Oakland, Alameda ¦ Orinda, Contra Costa ¦ Piedmont, Alameda | The project proposes to replace the structures, conductors, and hardware in the same overhead alignment between Moraga Substation and California State Highway 13 and also to relocate the line sections between Highway 13, and Oakland X underground (UG) within city streets. By replacing the aging facilities PG&E can improve wildfire safety and public safety and increase path capacity into the Oakland area. The project scope of work includes: • Removal of 78 existing lattice steel transmission towers • Removal of approximately 20 circuit miles of conductor • Installation of approximately 60 new lattice steel transmission towers • Installation of approximately 11 miles of Aluminum Conductor Composite Reinforced (ACCR) conductor • Installation of three 115kV underground duct banks with 115kV transmission cables totaling approximately six miles • Installation of new 115kV circuit breakers and air switches at Moraga Substation • Upgrade the 115kV bus at Oakland X Substation to complement the higher capacity ACCR conductor | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-04-02 | 59 | Lifecycle Replacement Analysis | Wires - New T-Line Alternative | $250 Mil – $300 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | 6 | NA | 115 | NA | 228 | NA | NA | 4.05 | In-flight Future Scope | 5793948 | T.0000349 | Moraga-Oakland #1-#4 Rebuild | 5 | 93 | NA ¦ 5789524 ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2024-12-12 | EIR | NA | CPUC | NA | PTC: A. 24-11-005 | 2024-11-15 | Filed and Under Administrative Review | TBD | Engineering more than 50% complete | 4 | 2029-05-01 | 2025-07-31 | 2030-12-30 | Prioritization | NA | FALSE | 212000 | NA ¦ NA | 7339.7297 | 116875.9841 | 860.01 | 3044.8561 | 806.7845 | 1331.0454 | 1152.4773 | 978.4334 | 4773.7361 | 21876.2275 | 67167.3456 | 9100 | 7195.1732 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | 36.42% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2355 | COTTNWD-RED BLUFF INSTALL TSP'S |  |  | Cottonwood CDP, Shasta ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama | Rebuild the 16.5 miles-long Cottonwood-Red Bluff 60 kV Line and release the project to operations, The proposed project would rebuild the 16.5 mile Cottonwood-Red Bluff 60 kV line with new transmission poles and new conductor. The project scope of work includes the following:•Replace 304 transmission poles with 240 light duty steel poles (LDSPs), 7 tubular steel poles (TSPs), and 57 higher-class wood poles as identified by design.•Reconductor the Cottonwood-Red Bluff 60 kV line (16.5 miles) with 715 kcmil aluminum conductor.•Reroute a 3-pole section of the line to a new location and alignment. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-02-24 | 81 | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 197 | 1. Work that prevents fire ignition | 207 | NA | NA | 5767629 | T.0000456 | Cottonwood-Red Bluff Reconductor | 4 | 93 | NA ¦ 5732727 ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-11-01 | 2019-10-07 | 2020-05-18 | Permitting | NA | FALSE | 47000 | NA ¦ NA | 3933.4744 | 3933.4744 | 94.6131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3933.4744 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 3933.9724 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2356 | COTTNWD-RED BLUFF - REROUTE-CTTWD |  |  | Cottonwood CDP, Shasta ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama | Rebuild the 16.5 miles-long Cottonwood-Red Bluff 60 kV Line and release the project to operations, The proposed project would rebuild the 16.5 mile Cottonwood-Red Bluff 60 kV line with new transmission poles and new conductor. The project scope of work includes the following:•Replace 304 transmission poles with 240 light duty steel poles (LDSPs), 7 tubular steel poles (TSPs), and 57 higher-class wood poles as identified by design.•Reconductor the Cottonwood-Red Bluff 60 kV line (16.5 miles) with 715 kcmil aluminum conductor.•Reroute a 3-pole section of the line to a new location and alignment. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-02-24 | NA | Lifecycle Replacement Analysis | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 197 | 1. Work that prevents fire ignition | 207 | NA | NA | 5767630 | T.0000456 | Cottonwood-Red Bluff Reconductor | 4 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-07 | 2019-12-27 | 2020-05-18 | NA | NA | FALSE | 47000 | NA ¦ NA | 991.6202 | 991.6202 | 372.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 991.6202 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 920.8327 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2357 | Potrero-Larkin #3 115 kV Cable (A-Y 3) |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Transmission Line - Multiple | Replace | NA | T.0002705 ¦ T.0000557 ¦ T.0000934 | Asset Condition | Seismic Upgrade - Replace Conductor | NA | NA | 2025-04-04 | 55 | Lifecycle Replacement Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 2.8 | NA | 115 | NA | 434 | 4. Underground / Network (Strong Safety Link) | 1204 | 3.0011 | In-flight Future Scope | 5765139 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | On Hold | 5 | 2028-03-24 | 2025-06-20 | 2028-12-19 | Prioritization | NA | FALSE | 191100 | NA ¦ NA | 3577.7018 | 80348.5275 | 214.8132 | 286.1352 | 941.1621 | 221.1905 | 122.6541 | 227.1936 | 0 | 0 | 0 | 0 | 3577.7018 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2358 | Mission-Larkin #2 115 kV Cable (X-Y 2) |  |  | San Francisco, San Francisco | This project will build three new seismically resilient cables: two cables from Potrero to Mission and Larkin and one cable from Mission to Larkin. The project team will also determine other upgrades needed to cables serving Hunters Point, Potrero, and Bayshore, which will be initiated under a separate project. The San Francisco 115kV Seismic Upgrade project will: Construct new, seismically reinforced Potrero-Mission (A-X 2) cable, Mission-Larkin (X-Y 2) cable, and Potrero-Larkin (A-Y 3) cable using Triplex XLPE 115kV cable technology in duct banks which are located in franchised streets in a new alignment. | Transmission Line - Multiple | Replace | NA | T.0002705 ¦ T.0000557 ¦ T.0000934 | Asset Condition | Seismic Upgrade - Replace Conductor | NA | NA | 2025-04-02 | 75 | Lifecycle Replacement Analysis | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | 7 | NA | 115 | NA | 434 | 4. Underground / Network (Strong Safety Link) | 1126 | 3.0011 | In-flight Future Scope | 5765140 | T.0000603 | Seismic Upgrade: Potrero to Mission/Lark | 9 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC | TBD | TBD | TBD | On Hold | 5 | 2028-02-24 | 2025-06-20 | 2029-02-05 | Prioritization | NA | FALSE | 191100 | NA ¦ NA | 3076.6716 | 32512.2309 | 424.1616 | 385.7743 | 386.2823 | 213.6454 | 105.4774 | 195.3768 | 0 | 0 | 0 | 0 | 3076.6716 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2359 | Vaca Dixon shoofly work |  |  | Green Valley CDP, Napa ¦ Green Valley CDP, Solano ¦ Hartley CDP, Solano ¦ Napa ¦ Solano ¦ Vacaville, Solano | Replace overstressed 230kV CB 442, 452, 462 with 3000A CC, 63kA IC breakers and add new bus paralleling substitute breaker CB 402 as part of PG&E’s Deteriorated Breakers Replacement Program. | Transmission Line - Multiple | New | NA | NA | Asset Condition | T-Line Reliability | NA | NA | 2024-03-20 | NA | Lifecycle Replacement Analysis | Other - Status Quo | $10 Mil -$15 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 0.1 | NA | 230 | NA | NA | NA | NA | 5.11 | In-flight Future Scope | 5811558 | T.0001609 | Vaca Dixon - REPL 442, 452, 462 INST 402 | 5 | 93 | NA ¦ 5761196 ¦ NA ¦ NA | TRUE | 2024 | Project Management Governance Standard | 2025 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-02-24 | 2027-03-01 | 2026-06-16 | NA | NA | TRUE | 14900 | NA ¦ NA | 2.4638 | 3943.816 | 0 | 0 | 0 | 0 | 0.3354 | 1096.7182 | 2826.169 | 0 | 0 | 0 | 0.3354 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2360 | Eagle Rock-Cortina Struc Repl & Reinsul |  |  | Clearlake, Lake ¦ Colusa ¦ Lake ¦ Lower Lake CDP, Lake ¦ Sonoma | The Eagle Rock-Cortina 115 kV line is approximately 43.4 miles long with 322 structures that is located in the Northern region. Two hundred Ninety-Two (292) of these structures are in high fire tier districts (HFTD’s). In order to increase system performance and reduce fire ignition risk, asset components on the line are being performed with the following scope of work: • Replacement of 112 wood pole with steel structures; • Replacement of aging insulators on 119 structures; • Replacement of aging switch on structure 000/001; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring • Include all open maintenance tags within the project scope where applicable | Transmission Line - Pole/Tower | Replace | NA | T.0007732 | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-06-20 | 47 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 43.4 | NA | 115 | NA | 20067 | 2. Overhead With Strong Safety Link | 82 | 3.0011 | In-flight Future Scope | 5789712 | T.0005743 | Eagle Rock-Cortina Struc Repl & Reinsul | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2033-02-07 | NA | 2033-05-31 | NA | NA | FALSE | NA | NA ¦ NA | 141.0782 | 17429.035 | 58.576 | 10.7529 | 51.3533 | 15.5594 | 4.8366 | 8.8032 | 0 | 0 | 0 | 0 | 141.0782 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2361 | Eagle Rock-Cortina Struc Repl & Reinsul |  |  | Clearlake, Lake ¦ Colusa ¦ Lake ¦ Lower Lake CDP, Lake ¦ Sonoma | The Eagle Rock-Cortina 115 kV line is approximately 43.4 miles long with 322 structures that is located in the Northern region. Two hundred Ninety-Two (292) of these structures are in high fire tier districts (HFTD’s). In order to increase system performance and reduce fire ignition risk, asset components on the line are being performed with the following scope of work: • Replacement of 112 wood pole with steel structures; • Replacement of aging insulators on 119 structures; • Replacement of aging switch on structure 000/001; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring • Include all open maintenance tags within the project scope where applicable | Transmission Line - Multiple | Replace | NA | T.0007732 | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-06-20 | 74 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 | NA | 20067 | NA | 82 | 3.0011 | In-flight Future Scope | 5789714 | T.0005743 | Eagle Rock-Cortina Struc Repl & Reinsul | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2033-02-18 | NA | 2033-02-18 | NA | NA | FALSE | NA | NA ¦ NA | 7.8043 | 10402.8604 | 0 | 0 | 0.9093 | 6.6274 | 0.2676 | 0.487 | 0 | 0 | 0 | 0 | 7.8043 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2362 | Spaulding Summit 60kV Replacement - Ph 1 |  |  | Kingvale CDP, Nevada ¦ Nevada ¦ Placer ¦ Soda Springs CDP, Nevada | The Spaulding – Summit 60 kV Line is located in Placer and Nevada counties. The Line is 19.65 miles long and is supported by 594 non-steel structures and 31 steel structures, a total of 626 structures. 460 of these structures are located in high fire threat districts (HFTD). The project will increase system performance and reduce fire ignition risk in Placer and Nevada counties by performing the following work: • Replace 574 Structures on the Spaulding - Summit 60 kV Line2 • Review 7.86 miles of AAC, ACSR and CU conductor on the Spaulding - Summit 60 kV Line, due to age, to determine if replacement is required • Replace 0.97 miles of ACSR conductor on the Spaulding - Summit 60 kV Line, due to high probability of failure • Replace 0.37 miles of ACSR conductor on the Tap Line between 005/205 and CISCO Grove, due to high probability of failure • Replace 8 switches with SCADA-operable switches on the Spaulding - Summit 60 kV Line • Replace 1 switch with SCADA-operable switch on the CISCO Grove Tap 60 kV Line • Identify any distribution under-build and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. | Transmission Line - Pole/Tower | Replace | NA | T.0004951 | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-03-01 | 75 | Lifecycle Replacement Analysis | TBD | TBD | Zone 1 - HHZ ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | 1. Work that prevents fire ignition | 5 | 3.0011 | In-flight Future Scope | 5790358 | T.0005849 | Spaulding-Summit 60 kV | 3 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2034-09-21 | NA | 2035-10-18 | NA | NA | FALSE | NA | NA ¦ NA | 54.3221 | 31152.8904 | 0 | 25.1732 | 6.3416 | 20.945 | 1.8623 | 3.3697 | 0 | 0 | 0 | 0 | 54.3221 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2363 | Spaulding Summit 60kV Replacement - Ph 2 |  |  | Kingvale CDP, Nevada ¦ Nevada ¦ Placer ¦ Soda Springs CDP, Nevada | The Spaulding – Summit 60 kV Line is located in Placer and Nevada counties. The Line is 19.65 miles long and is supported by 594 non-steel structures and 31 steel structures, a total of 626 structures. 460 of these structures are located in high fire threat districts (HFTD). The project will increase system performance and reduce fire ignition risk in Placer and Nevada counties by performing the following work: • Replace 574 Structures on the Spaulding - Summit 60 kV Line2 • Review 7.86 miles of AAC, ACSR and CU conductor on the Spaulding - Summit 60 kV Line, due to age, to determine if replacement is required • Replace 0.97 miles of ACSR conductor on the Spaulding - Summit 60 kV Line, due to high probability of failure • Replace 0.37 miles of ACSR conductor on the Tap Line between 005/205 and CISCO Grove, due to high probability of failure • Replace 8 switches with SCADA-operable switches on the Spaulding - Summit 60 kV Line • Replace 1 switch with SCADA-operable switch on the CISCO Grove Tap 60 kV Line • Identify any distribution under-build and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. | Transmission Line - Pole/Tower | Replace | NA | T.0004951 | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-03-01 | 80 | Lifecycle Replacement Analysis | TBD | TBD | Zone 1 - HHZ ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 19.65 | NA | 60 | NA | NA | 1. Work that prevents fire ignition | 5 | 3.0011 | In-flight Future Scope | 5790359 | T.0005849 | Spaulding-Summit 60 kV | 3 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2032-06-04 | NA | 2034-07-19 | NA | NA | FALSE | NA | NA ¦ NA | 412.7175 | 31129.6308 | 23.3205 | 100.1058 | 146.8998 | 126.8071 | 15.5843 | 25.6015 | 0 | 0 | 0 | 0 | 412.7175 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2364 | Spaulding Summit 60kV Replacement - Ph 3 |  |  | Kingvale CDP, Nevada ¦ Nevada ¦ Placer ¦ Soda Springs CDP, Nevada | The Spaulding – Summit 60 kV Line is located in Placer and Nevada counties. The Line is 19.65 miles long and is supported by 594 non-steel structures and 31 steel structures, a total of 626 structures. 460 of these structures are located in high fire threat districts (HFTD). The project will increase system performance and reduce fire ignition risk in Placer and Nevada counties by performing the following work: • Replace 574 Structures on the Spaulding - Summit 60 kV Line2 • Review 7.86 miles of AAC, ACSR and CU conductor on the Spaulding - Summit 60 kV Line, due to age, to determine if replacement is required • Replace 0.97 miles of ACSR conductor on the Spaulding - Summit 60 kV Line, due to high probability of failure • Replace 0.37 miles of ACSR conductor on the Tap Line between 005/205 and CISCO Grove, due to high probability of failure • Replace 8 switches with SCADA-operable switches on the Spaulding - Summit 60 kV Line • Replace 1 switch with SCADA-operable switch on the CISCO Grove Tap 60 kV Line • Identify any distribution under-build and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. | Transmission Line - Multiple | Replace | NA | T.0004951 | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-03-01 | 83 | Lifecycle Replacement Analysis | TBD | TBD | Zone 1 - HHZ ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 7.86 | NA | 60 | NA | NA | 1. Work that prevents fire ignition | 5 | 3.0011 | In-flight Future Scope | 5790360 | T.0005849 | Spaulding-Summit 60 kV | 3 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2034-05-12 | NA | 2035-01-10 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 29387.7137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2365 | Colgate-Grass Valley 60kV Structure Repl |  |  | Grass Valley, Nevada ¦ Nevada ¦ Yuba | The Colgate-Grass Valley 60 kV Line is located in Nevada County. The Colgate-Grass Valley 60 kV Line is approximately 13.2 miles long and is supported by 326 structures, of which, 287 are in Tier 2 and Tier 3 high fire threat districts (HFTDs). The project will increase system performance and reduce fire ignition risk in Nevada County by performing the following work: • Replace 139 wood poles on the Colgate-Grass Valley 60 kV Line2 • Replace insulators on 8 structures not identified for repalcement • Replace Colgate-Grass Valley 60 kV Line Switch No. 47 • Review Colgate-Grass Valley 60 kV Line Switch No. 75 • Review Structure Nos. 000/003, A003/091, 010/232 and 012/303 for age and condition • Review all conductor for age and condition to determine if replacement is required • Identify any distribution underbuild and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring • Include all open maintenance tags within the project scope where applicable | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-03-17 | 100 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 13.2 | NA | 60 | NA | 11293 | 1. Work that prevents fire ignition | 81 | 3.0011 | In-flight Future Scope | 5790356 | T.0005865 | Colgate-Grass Valley 60kV | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2035-02-26 | NA | 2035-03-23 | NA | NA | FALSE | NA | NA ¦ NA | 67.9869 | 6734.9265 | 38.857 | 3.9256 | 13.1283 | 9.7452 | 2.3308 | 0 | 0 | 0 | 0 | 555.127 | 67.9869 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | 513.27% ¦ Electric Operations Risk Management | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2366 | Willow Creek-Hoopa 60 kV Str Project |  |  | Hoopa CDP, Humboldt ¦ Humboldt ¦ Willow Creek CDP, Humboldt | This project will replace structures, conductor and associated equipment between the Willow Creek and Hoopa substations. The project will increase system performance and reduce fire ignition risk in Humboldt County by performing the following work: • Replace 127 structures on the Willow Creek - Hoopa 60 kV Line2 section • Reconductor roughly 9 miles of conductor on the Willow Creek - Hoopa 60 kV Line section • Review 1 switch on the Willow Creek - Hoopa 60 kV Line section for possible upgrade to SCADA-operable switch • Review 14 structures on the Willow Creek - Hoopa 60 kV Line section for age information • Identify any distribution under-build and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | Age/Condition - Replace Steel Poles | NA | NA | 2024-07-20 | 67 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 9 | NA | 60 | NA | NA | 1. Work that prevents fire ignition | 84 | 3.0011 | In-flight Future Scope | 5790604 | T.0005899 | Willow Creek - Hoopa 60 kV Str | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2038-12-24 | NA | 2039-05-24 | NA | NA | FALSE | NA | NA ¦ NA | 500.3924 | 1228.9897 | 75.8841 | 238.149 | 127.1757 | 42.0286 | 17.1549 | 0 | 0 | 0 | 0 | 0 | 500.3924 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2367 | NARROWS #2 TAP REINF SW REPL |  |  | Nevada ¦ Smartsville CDP, Yuba ¦ Yuba | The Colgate-Smartville #2 60 kV Reinforcement Project is located in Yuba and Nevada Counties. The Colgate-Smartville #2 60 kV line is 11.13 miles long and is supported by 155 structures. The line is a single circuit that is supported on single wood poles. All the structures are in Tier 2 high fire tier districts (HFTDs). The assessment by Transmission Line Asset Strategy (TLAS) included the two 60 kV taps connected to the Colgate-Smartville #2 60 kV line. They are the Narrows #2 Tap at structure 010/127 and the Smartville Tap at structure 000/001. The project will increase system performance and reduce fire ignition risk in Yuba and Nevada Counties by performing the following work: ● Replace 98 non-steel structures on Colgate-Smartville #2 60 kV line that includes reviewing 11.13 miles of conductor and increase inspection because of aging asset. ● Replace 68 insulators on the Colgate-Smartville #2 line ● Replace 2 non-steel structures on Smartville Tap ● Replace 47 non-steel structures for Narrows #2 Tap ● Replace one (1) steel structure for Narrows #2 Tap ● Replace one (1) switch with SCADA on Colgate-Smartville #2 line; SW#29 ● Replace two (2) switches with SCADA on Smartville Tap; SW#97 & SW#99 ● Replace two (2) switches with SCADA on Narrows #2 Tap; SW#47 & SW#59 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-02-07 | 23 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 3.1 | NA | 60 | NA | NA | NA | NA | NA | NA | 5799144 | T.0005916 | Colgate-Smartville #2 | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-01-05 | NA | 2023-01-07 | NA | NA | FALSE | NA | NA ¦ NA | 19.4054 | 19.4054 | 0 | 0 | 13.0028 | 6.0412 | 0.3614 | 0 | 0 | 0 | 0 | 0 | 19.4054 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2368 | Colgate-Smartville #2 Reinf Sw Repl |  |  | Nevada ¦ Smartsville CDP, Yuba ¦ Yuba | The Colgate-Smartville #2 60 kV Reinforcement Project is located in Yuba and Nevada Counties. The Colgate-Smartville #2 60 kV line is 11.13 miles long and is supported by 155 structures. The line is a single circuit that is supported on single wood poles. All the structures are in Tier 2 high fire tier districts (HFTDs). The assessment by Transmission Line Asset Strategy (TLAS) included the two 60 kV taps connected to the Colgate-Smartville #2 60 kV line. They are the Narrows #2 Tap at structure 010/127 and the Smartville Tap at structure 000/001. The project will increase system performance and reduce fire ignition risk in Yuba and Nevada Counties by performing the following work: ● Replace 98 non-steel structures on Colgate-Smartville #2 60 kV line that includes reviewing 11.13 miles of conductor and increase inspection because of aging asset. ● Replace 68 insulators on the Colgate-Smartville #2 line ● Replace 2 non-steel structures on Smartville Tap ● Replace 47 non-steel structures for Narrows #2 Tap ● Replace one (1) steel structure for Narrows #2 Tap ● Replace one (1) switch with SCADA on Colgate-Smartville #2 line; SW#29 ● Replace two (2) switches with SCADA on Smartville Tap; SW#97 & SW#99 ● Replace two (2) switches with SCADA on Narrows #2 Tap; SW#47 & SW#59 | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-03-11 | 95 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 11.13 | NA | 60 | NA | NA | 1. Work that prevents fire ignition | 164 | 3.0011 | In-flight Future Scope | 5790663 | T.0005916 | Colgate-Smartville #2 | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2028-03-20 | NA | 2028-04-14 | NA | NA | FALSE | NA | NA ¦ NA | 506.5042 | 8866.2605 | 35.122 | 296.7894 | 105.5722 | 40.2618 | 28.7589 | 308.8857 | 0 | 0 | 0 | 307 | 506.5042 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2369 | Coleman Jct -Vina -Gerber 60 kV Str |  |  | Gerber CDP, Tehama ¦ Los Molinos CDP, Tehama ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama ¦ Tehama, Tehama | The Coleman Junction -Vina - Gerber 60 kV Line section is part of the Coleman - Red Bluff 60 kV Line located in Tehama County. The Coleman - Red Bluff 60 kV Line is approximately 48.1 miles long and is supported by 834 structures; 312 of these structures are in High Fire Threat Districts (HFTDs). There is an ongoing project to replace structures and conductor on the Coleman - Red Bluff 60 kV Line, between Coleman Power House and Red Bluff Substation. This new project will complete work on the remaining portions of the line between Coleman Junction, Vina and Gerber substations. | Transmission Line - Pole/Tower | Replace | NA | T.0000013 | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-04-04 | 92 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 10.6 | NA | 60 | NA | 20074 | 1. Work that prevents fire ignition | 65 | 3.0011 | In-flight Future Scope | 5790859 | T.0005935 | Coleman Jct -Vina -Gerber 60 kV Str | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2032-12-01 | NA | 2034-07-12 | NA | NA | FALSE | NA | NA ¦ NA | 3.5682 | 45132.6106 | 0 | 0 | 2.9055 | 0.5403 | 0.1223 | 0.2214 | 0 | 0 | 0 | 0 | 3.5682 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2370 | CALISTOGA-ST. HELENA 60 KV REINFORCEMENT |  |  | Deer Park CDP, Napa ¦ Fulton CDP, Sonoma ¦ Kenwood CDP, Sonoma ¦ Lake ¦ Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma | An emergency project was recently completed that replaced all of the structures, conductors and associated hardware on the 16.6-mile section of the line from Fulton to St. Helena Junction. This new project will further increase system performance and reduce fire ignition risk in Sonoma and Napa Counties by reconductoring the Fulton-Calistoga 60 kV line from St. Helena Junction up to Middletown Substation and from St. Helena Junction down to Dunbar Substation. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2023-07-25 | 94 | Lifecycle Replacement Analysis | Wires - Reconductor/Line Rebuild Alternative | $150 Mil - $175 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | TRUE | Weather |  | 13 | NA | 60 | NA | 20074 | 1. Work that prevents fire ignition | 70 | NA | NA | 5790867 | T.0005946 | Fulton-Calistoga 60 kV Line | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6429-E | 2021-12-08 | Approved | 2022 | Operational | 2 | 2022-02-01 | 2023-03-30 | 2023-04-17 | NA | NA | FALSE | 71400 | NA ¦ NA | 16385.3667 | 16385.3667 | 10.2758 | 723.0128 | 12815.4744 | 2807.2662 | 29.3375 | 0 | 0 | 0 | 0 | 0 | 16385.3667 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 15510.8186 | 27.7466 | 0 | 0% | NA ¦ NA | 230% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2371 | FULTON-CALISTOGA 60 KV REINFORCEMENT |  |  | Deer Park CDP, Napa ¦ Fulton CDP, Sonoma ¦ Kenwood CDP, Sonoma ¦ Lake ¦ Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma | An emergency project was recently completed that replaced all of the structures, conductors and associated hardware on the 16.6-mile section of the line from Fulton to St. Helena Junction. This new project will further increase system performance and reduce fire ignition risk in Sonoma and Napa Counties by reconductoring the Fulton-Calistoga 60 kV line from St. Helena Junction up to Middletown Substation and from St. Helena Junction down to Dunbar Substation. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2023-07-25 | 95 | Lifecycle Replacement Analysis | Wires - Reconductor/Line Rebuild Alternative | $150 Mil - $175 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | 11.3 | NA | 60 | NA | NA | 1. Work that prevents fire ignition | 70 | 3.0011 | In-flight Future Scope | 5790901 | T.0005946 | Fulton-Calistoga 60 kV Line | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6429-E | 2021-12-08 | Approved | 2022 | On Hold | 4 | 2032-10-15 | 2025-04-30 | 2033-05-26 | Prioritization | NA | FALSE | 71400 | NA ¦ NA | 649.5168 | 24775.1823 | 0 | 1.1961 | 333.8871 | 281.1146 | 33.319 | 40.5294 | 0 | 0 | 0 | 0 | 649.5168 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2372 | Ignacio-Alto 60kV Reinf Proj repl struc |  |  | Corte Madera, Marin ¦ Larkspur, Marin ¦ Marin ¦ Mill Valley, Marin ¦ Novato, Marin ¦ San Rafael, Marin ¦ Santa Venetia CDP, Marin | The assessment by Transmission Line Asset Strategy (TLAS) on Ignacio-Alto 60 kV Line was done on this line only. The associated Ignacio-San Rafael No. 1 115 kV Line that is supported by the DCTL was excluded from this assessment. The project will increase system performance and reduce fire ignition risk in Marin County by performing the following work: ● Replace nine (9) steel structures ● Replace 114 non-steel structures ● Replace 105 insulators ● Replace 5.7 miles of 397.5 all-aluminum conductor (AAC) and review the conductor on the other 12.1 miles of conductor for possible replacement ● Replace insulators and hardware on 16 steel towers ● Perform structure modification in four (4) lattice steel poles, 14 steel towers and two (2) tubular steel poles to accommodate new conductor replacement. ● Identify any distribution under-build and coordinate with distribution planning ● Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-10-08 | 63 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | 5.7 | NA | 60 | NA | NA | 1. Work that prevents fire ignition | 7 | 3.0011 | In-flight Future Scope | 5790910 | T.0005966 | Ignacio-Alto 60kV Reinf | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2035-06-25 | NA | 2035-08-17 | NA | NA | FALSE | NA | NA ¦ NA | 7.1301 | 8035.1274 | 0 | 0 | 6.4078 | 0.4778 | 0.2444 | 0.437 | 0 | 0 | 0 | 0 | 7.1301 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2373 | Tulucay-Napa #1-Repl Wood Poles |  |  | Green Valley CDP, Napa ¦ Green Valley CDP, Solano ¦ Napa ¦ Napa, Napa ¦ Solano | The project will increase system performance and reduce fire ignition risk in Napa County by performing the following work: • Replace 4 steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 8 steel structures on the Cordelia #2 Tap 60 kV; • Replace 126 existing wood poles with steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 19 existing wood poles with steel structures on the Cordelia #1 Tap 60 kV; • Replace 77 existing wood poles with steel structures on the Cordelia #2 Tap 60 kV; • Replace 2.33 miles of conductor from pole no. T001/006 to 006/107 on the Cordelia #1 Tap 60 kV; • Replace existing ceramic insulators on 26 structures with modern equivalent insulators; • Replace 5 existing switches with Supervisory Control and Data Acquisition (SCADA)-operable switches; • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-03-27 | 74 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 2.33 | NA | 60 | NA | 11313 | 2. Overhead With Strong Safety Link | 161 | NA | NA | 5791023 | T.0005976 | Tulucay-Napa #1 | 4 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-11-02 | NA | 2022-11-06 | NA | NA | FALSE | NA | NA ¦ NA | 20.3685 | 20.3685 | 0.6957 | 0.0501 | 17.5231 | 1.4013 | 0.6983 | 0 | 0 | 0 | 0 | 0 | 20.3685 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2374 | Cordelia #1 Structure Replacement |  |  | Fairfield, Solano ¦ Napa ¦ Solano | The project will increase system performance and reduce fire ignition risk in Napa County by performing the following work: • Replace 4 steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 8 steel structures on the Cordelia #2 Tap 60 kV; • Replace 126 existing wood poles with steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 19 existing wood poles with steel structures on the Cordelia #1 Tap 60 kV; • Replace 77 existing wood poles with steel structures on the Cordelia #2 Tap 60 kV; • Replace 2.33 miles of conductor from pole no. T001/006 to 006/107 on the Cordelia #1 Tap 60 kV; • Replace existing ceramic insulators on 26 structures with modern equivalent insulators; • Replace 5 existing switches with Supervisory Control and Data Acquisition (SCADA)-operable switches; • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-05-08 | 47 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 2.33 | NA | 60 | NA | NA | NA | NA | NA | NA | 5802895 | T.0005976 | Tulucay-Napa #1 | 4 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-11-02 | NA | 2022-11-06 | NA | NA | FALSE | NA | NA ¦ NA | 22.2534 | 22.2534 | 0 | 0 | 14.1736 | 6.9675 | 0.7524 | 0.3599 | 0 | 0 | 0 | 0 | 21.8935 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2375 | Cordelia #2 Structure Replacement |  |  | Fairfield, Solano ¦ Green Valley CDP, Napa ¦ Green Valley CDP, Solano ¦ Napa ¦ Solano | The project will increase system performance and reduce fire ignition risk in Napa County by performing the following work: • Replace 4 steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 8 steel structures on the Cordelia #2 Tap 60 kV; • Replace 126 existing wood poles with steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 19 existing wood poles with steel structures on the Cordelia #1 Tap 60 kV; • Replace 77 existing wood poles with steel structures on the Cordelia #2 Tap 60 kV; • Replace 2.33 miles of conductor from pole no. T001/006 to 006/107 on the Cordelia #1 Tap 60 kV; • Replace existing ceramic insulators on 26 structures with modern equivalent insulators; • Replace 5 existing switches with Supervisory Control and Data Acquisition (SCADA)-operable switches; • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-11-26 | 47 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 2.33 | NA | 60 | NA | NA | NA | NA | NA | NA | 5802896 | T.0005976 | Tulucay-Napa #1 | 4 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-11-02 | NA | 2022-11-06 | NA | NA | FALSE | NA | NA ¦ NA | 31.4282 | 31.4282 | 0 | 0 | 25.5354 | 1.9043 | 3.3903 | 0.5981 | 0 | 0 | 0 | 0 | 30.8301 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2376 | Tulucay-Napa #1-Repl Steel Poles |  |  | Green Valley CDP, Napa ¦ Green Valley CDP, Solano ¦ Napa ¦ Napa, Napa ¦ Solano | The project will increase system performance and reduce fire ignition risk in Napa County by performing the following work: • Replace 4 steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 8 steel structures on the Cordelia #2 Tap 60 kV; • Replace 126 existing wood poles with steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 19 existing wood poles with steel structures on the Cordelia #1 Tap 60 kV; • Replace 77 existing wood poles with steel structures on the Cordelia #2 Tap 60 kV; • Replace 2.33 miles of conductor from pole no. T001/006 to 006/107 on the Cordelia #1 Tap 60 kV; • Replace existing ceramic insulators on 26 structures with modern equivalent insulators; • Replace 5 existing switches with Supervisory Control and Data Acquisition (SCADA)-operable switches; • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring; and • Include all open maintenance tags within the project scope where applicable. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2025-03-27 | 75 | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 2.33 | NA | 60 | NA | 11313 | 1. Work that prevents fire ignition | 161 | 3.0011 | In-flight Future Scope | 5791021 | T.0005976 | Tulucay-Napa #1 | 4 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | On Hold | 4 | 2033-10-27 | NA | 2034-04-26 | NA | NA | FALSE | NA | NA ¦ NA | 859.814 | 29434.524 | 18.4024 | 348.4271 | 423.6989 | 39.8086 | 29.4769 | 53.6518 | 0 | 0 | 0 | 0 | 859.814 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2377 | Drum-Rio Oso 115kV Line Reinforcement |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | The project will increase system performance and reduce fire ignition risk in Nevada and Placer Counties by performing the following work: • Replace approximately 34.0 miles of conductor on the Drum – Rio Oso #1 and #2 115 kV Lines from structure no. 011/111 to Rio Oso Substation with 477 aluminum conductor steel supported (ACSS); • Upgrade substation terminal equipment to match new conductor rating, if needed; • Replace existing 408 structures with self-weathering tubular steel poles (TSPs) on the Drum – Rio Oso #1 and #2 115 kV Line; • Replace existing 40 structures with self-weathering steel poles on the Brunswick #1 and #2 Tap 115 kV; • Replace existing 4 structures with self-weathering steel poles on the Dutch Flat #2 Tap 115 kV; • Replace existing ceramic insulators on all structures with modern equivalent insulators on the Drum – Rio Oso #1 and #2 115 kV Lines, Brunswick #1 and #2 Tap 115 kV and Dutch Flat #2 Tap 115 kV; • Conduct field verification on the Dutch Flat #2 Tap 115 kV to determine if conductor replacement is needed; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-05-02 | 112 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 68 | NA | 115 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | 5791639 | T.0006067 | Drum-Rio Oso 115kV Line Reinforcement | 3 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2038-06-18 | NA | 2038-08-13 | NA | NA | FALSE | NA | NA ¦ NA | 396.3193 | 256947.0441 | 1.5607 | 242.4266 | 185.9406 | -62.3769 | 28.7684 | 24.2072 | 0 | 0 | 0 | 0 | 396.3193 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | 40.9% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2378 | Drum-Rio Oso 115kV- Dutch Flat #2 Tap |  |  | Nevada | The project will increase system performance and reduce fire ignition risk in Nevada and Placer Counties by performing the following work: • Replace approximately 34.0 miles of conductor on the Drum – Rio Oso #1 and #2 115 kV Lines from structure no. 011/111 to Rio Oso Substation with 477 aluminum conductor steel supported (ACSS); • Upgrade substation terminal equipment to match new conductor rating, if needed; • Replace existing 408 structures with self-weathering tubular steel poles (TSPs) on the Drum – Rio Oso #1 and #2 115 kV Line; • Replace existing 40 structures with self-weathering steel poles on the Brunswick #1 and #2 Tap 115 kV; • Replace existing 4 structures with self-weathering steel poles on the Dutch Flat #2 Tap 115 kV; • Replace existing ceramic insulators on all structures with modern equivalent insulators on the Drum – Rio Oso #1 and #2 115 kV Lines, Brunswick #1 and #2 Tap 115 kV and Dutch Flat #2 Tap 115 kV; • Conduct field verification on the Dutch Flat #2 Tap 115 kV to determine if conductor replacement is needed; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-03-19 | 35 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | 5796875 | T.0006067 | Drum-Rio Oso 115kV Line Reinforcement | 3 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2035-10-08 | NA | 2037-10-05 | NA | NA | FALSE | NA | NA ¦ NA | 28.9711 | 31899.8141 | 0 | 1.4176 | 23.0112 | 3.549 | 0.9932 | 1.7696 | 0 | 0 | 0 | 0 | 28.9711 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2379 | Drum-Rio Oso 115kV-Brunswick 1 & 2 Tap |  |  | Grass Valley, Nevada ¦ Nevada | The project will increase system performance and reduce fire ignition risk in Nevada and Placer Counties by performing the following work: • Replace approximately 34.0 miles of conductor on the Drum – Rio Oso #1 and #2 115 kV Lines from structure no. 011/111 to Rio Oso Substation with 477 aluminum conductor steel supported (ACSS); • Upgrade substation terminal equipment to match new conductor rating, if needed; • Replace existing 408 structures with self-weathering tubular steel poles (TSPs) on the Drum – Rio Oso #1 and #2 115 kV Line; • Replace existing 40 structures with self-weathering steel poles on the Brunswick #1 and #2 Tap 115 kV; • Replace existing 4 structures with self-weathering steel poles on the Dutch Flat #2 Tap 115 kV; • Replace existing ceramic insulators on all structures with modern equivalent insulators on the Drum – Rio Oso #1 and #2 115 kV Lines, Brunswick #1 and #2 Tap 115 kV and Dutch Flat #2 Tap 115 kV; • Conduct field verification on the Dutch Flat #2 Tap 115 kV to determine if conductor replacement is needed; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2024-04-03 | 50 | Lifecycle Replacement Analysis | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | 5796876 | T.0006067 | Drum-Rio Oso 115kV Line Reinforcement | 3 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2035-10-05 | NA | 2037-10-02 | NA | NA | FALSE | NA | NA ¦ NA | 11.0774 | 31869.3277 | 0 | 1.5751 | 5.7665 | 3.3561 | 0.3798 | 0.6766 | 0 | 0 | 0 | 0 | 11.0774 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2380 | Kerckhoff #1 PH Sub Site Retirement Plan |  |  | Fresno | Replace the Bank#4 (6.6/12kV Bank) with a new 16MVA (115/12kV) CEM stock bank. Add circuit switcher for the bank high side protection. | Transmission Line - Multiple | Relocate | NA | NA | Asset Condition | Age/Condition - Replace Conductor | NA | NA | 2023-06-08 | NA | Lifecycle Replacement Analysis | TBD | TBD | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | 5797625 | T.0007384 | KERCKHOFF1:REP TXFR BK 4 | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2024-10-01 | NA | 2024-12-17 | NA | NA | FALSE | NA | NA ¦ NA | 200.701 | 200.701 | 0 | 4.3119 | 18.0192 | 55.1883 | 118.1685 | 5.013 | 0 | 0 | 0 | 0 | 195.688 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 10.9024 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2381 | TLine USFS-SteelSpeciesProtection(North) |  |  | NA | Bucket for replacement for raptor protection involves reframing structures, replacement of insulators, conversion of insulator configurations and installation of guano shields in the US Forest Services Northern Area on steel towers. These capital related improvements have been identified during annual patrols as critical work needing to be corrected. Correction of these findings will assist in optimize the integrity of our transmission lines and to reduce the risk of unplanned outages. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Raptor Protection - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 180 | 1. Work that prevents fire ignition | 408 | 3.0011 | Future IGP Scope | 5510401 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 5051.8902 | 5051.8902 | 64.0078 | 54.8013 | -48.881 | 23.2185 | 58.478 | 9.7243 | 0 | 0 | 0 | 0 | 5042.1659 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 54.6403 | 0.91685 | 3.8322 | 1.6988 | 0.96564 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2382 | Switch Rplcmnts - Steel - Program |  |  | NA | Bucket for Switch Replacements on steel structures | Transmission Line - Switch | Replace | NA | NA | Asset Condition | Age/Condition - Switch Replacement - Steel | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | 1. Work that prevents fire ignition | 194 | NA | NA | 5507681 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2013 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2960.3412 | 2960.3412 | 0 | 0 | 8.7948 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 2960.3412 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 8.7948 | 0.3 | 3.3842 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2383 | Vineyard Transition Station- Switch 265 and 245 |  |  | Alameda ¦ Livermore, Alameda ¦ Pleasanton, Alameda | Switches 265 and 245 at Vineyard Transition Station have bottles with low SF6 gas and need to be replaced before failure. In last two years, we have had similar problem with Lone Tree – Cayetano switch 295, which resulted replacement of the switch by OH crew /contractor. | Transmission Line - Switch | Replace | NA | NA | Asset Condition | Age/Condition - Switch Replacement - Steel | NA | NA | 2025-04-04 | 22 | Lifecycle Replacement Analysis | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 4.01 | In-flight Future Scope | EX112189 | TBD | TBD | TBD | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-12-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 1200.0025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2384 | GO95 Steel N - Low Cond Proj |  |  | NA | Bucket for GO95 compliance on conductors | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 197 | 5. Compliance/Commitments With Strong Safety Link | NA | 5.101 | In-flight Future Scope | 5510404 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 12599.1786 | 12599.1786 | 2780.3889 | 27.4866 | -687.3718 | 296.7707 | 1114.0891 | 90.0861 | 0 | 0 | 0 | 0 | 12509.0925 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 2780.3889 | 27.4866 | -688.3251 | 244.7947 | 737.6671 | 101.0597 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2385 | GO95 Steel N - Low Cond Proj (Sac) |  |  | NA | Bucket for GO95 low conductor work on steel poles in Sacramento area. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | 5511321 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1098.2009 | 1098.2009 | 0 | 0 | 19.2812 | 4.7045 | 3.7341 | 0.039 | 0 | 0 | 0 | 0 | 1098.1619 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 27.7198 | 0.039 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2386 | 93T: GO-95 Mitigation |  |  | NA | Forecast placeholder for potential mitigation needed for GO-95 mitigation on HFTD Lines. This work will be developed after line assessments/LiDAR analysis. Represents mitigation on steel structure lines. | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.101 | Future IGP Scope | EX112095 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 75066.0704 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 6000 | 12000 | 9065.612 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2387 | Pit #3-Pit #1 Ph 2 Tower Replacement |  |  | Burney CDP, Shasta ¦ Johnson Park CDP, Shasta ¦ Shasta | Increase reliability by replacing insulators and hardware on 183 structures on Pit #3-Pit #1 230kV circuit | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2024-03-20 | 97 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | NA | 230 | NA | NA | NA | NA | NA | NA | 5796790 | T.0002405 | Pit#3-Pit#1 230 kV Insulators | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-05-27 | 2019-09-05 | 2021-07-01 | Material | NA | FALSE | 6300 | NA ¦ NA | 732.0892 | 732.0892 | 0 | 720.7728 | 11.3163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 732.0892 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 552.6621 | 8.6611 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2388 | Pit 1 - Cottonwood Insulator Ph 2 |  |  | Burney CDP, Shasta ¦ Cottonwood CDP, Shasta ¦ Johnson Park CDP, Shasta ¦ Millville CDP, Shasta ¦ Oak Run CDP, Shasta ¦ Round Mountain CDP, Shasta ¦ Shasta | Over the decades the insulators and steel members have been exposed to avian nesting, guano and streamers. There have been relatively few failures, however with this prolonged exposure and age consideration. The project is to increase reliability by replacing insulators and hardware on 530 structures on Pit #1-Cottonwood 230kV circuit. | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Steel | NA | NA | 2025-03-25 | 96 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat ¦ Weather |  | NA | NA | 230 | NA | NA | NA | NA | NA | NA | 5545597 | T.0002407 | Pit#1-Cottonwood 230kV Insulators | 2 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-05-10 | 2019-11-21 | 2021-06-01 | Prioritization | NA | FALSE | 8671 | NA ¦ NA | 339.9837 | 339.9837 | 0 | 335.0328 | 4.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339.9837 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 335.0328 | 4.951 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2389 | DEL MONTE - FORT ORD#1 |  |  | Del Rey Oaks, Monterey ¦ Monterey, Monterey ¦ Seaside, Monterey | The project will rebuild the 4.2- and 4.1-mile sections of the lines with 397.5 kcmil all-aluminum conductor (AAC) mounted on new LSP’s. Completion of the project will ensure reliable service to the existing 14,200 and future customers served from Fort Ord Substation. The expected in-service date is May 2020. The total project cost for the project is estimated at roughly $8.00M based on preliminary cost estimates (AACE Class 5). | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | 2024-12-05 | 90 | Lifecycle Replacement Analysis | Wires - System Configuration Alternative | $20 Mil - $30 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 8.3 | NA | 60 | NA | 380 | 1. Work that prevents fire ignition | 105 | 5.101 | In-flight Future Scope | 5781040 | T.0004114 | DEL MONTE - FORT ORD#1 | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | NOC | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-01-19 | 2025-02-07 | 2027-03-30 | Prioritization | NA | FALSE | 12698 | NA ¦ NA | 2913.3264 | 9635.1091 | 455.0065 | 550.1414 | 553.5948 | 450.2994 | 25.0808 | 211.3891 | 0 | 0 | 0 | 222.2582 | 2883.4511 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2390 | FAA Tower Marking, North Area |  |  | NA | Bucket for FAA Tower Marking, North Area | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 182 | NA | 295 | 4.011 | Non-IGP | 5511879 | NA | NA | NA | 93 | NA ¦ 5529049 ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 8051.1169 | 16997.0071 | 643.1422 | 1505.057 | 1482.2612 | 1249.2339 | 1107.9946 | 591.7371 | 0 | 1200 | 1200 | 1200 | 8005.27 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 613.6452 | 1489.9569 | 1517.0751 | 1249.2148 | 1107.9946 | 100.0438 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2391 | TO TLine (93P) - Insulator Replacements |  |  | NA | Bucket for insulator replacement on wood poles | Transmission Line - Other Equipment | Replace | NA | NA | Asset Condition | Age/Condition - Insulator Replacement - Wood | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | 10 | NA | NA | 5526200 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2426.2501 | 2426.2501 | 57.3504 | 9.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2426.2501 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 57.3504 | 4.4577 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2392 | Cathodic Protection Installs |  |  | NA | Bucket for cathodic protection improvements for overhead transmission circuits | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Future IGP Scope | 5547633 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 43257.2871 | 142677.1771 | 0 | 4245.4934 | 14580.7134 | 10446.4008 | 13251.2162 | 14161.2883 | 13460.7555 | 14133.794 | 14840.483 | 15582.507 | 42558.5518 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 2966.2691 | 15151.4411 | 7803.8465 | 16510.2995 | 376.0626 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2393 | Tower Coating Program Capital |  |  | NA | Bucket for capital tower coating work | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | NA | NA | NA | NA | NA | NA | 5.102 | Future IGP Scope | 5549743 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 57618.0182 | 140126.0813 | 4.107 | 2.0766 | 18293.9132 | 13756.8399 | 24466.7832 | 27555.2333 | 27928.9557 | 21611.5396 | 6506.5507 | 0 | 56523.7199 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 6.1836 | 17801.3851 | 14120.7676 | 22743.0961 | 1396.2262 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2394 | Arc Fault Mitigation Program |  |  | NA | Bucket for Arc Fault Mitigation Program | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 3.0011 | Non-IGP | 5546935 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 11533.0847 | 13347.4424 | 0 | 0 | 4441.7348 | 567.143 | 5568.2443 | 2036.7635 | 733.5567 | 0 | 0 | 0 | 10577.1222 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 0 | 0 | 4431.9466 | 556.3311 | 5450.4978 | 801.7541 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2395 | Early Fault Detectors - Transmission |  |  | NA | Forecast placeholder for Early Fault Detectors (EFD) for use in wildfire risk reduction(~$10.6k per unit) | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.2001 | Non-IGP | EX112096 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 500 | 500 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2396 | MWC 93: Coatings – Strategy |  |  | NA | Forecast placeholder for tower coating work | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.012 | Non-IGP | Ex112982 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 86540.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9135.04 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2397 | MWC 93: Coatings – Tags |  |  | NA | Forecast placeholder for Completion of priority E/F paint tags (within the 12mo-60 mo time frame) to mitigate asset conditions that may pose a safety or wildfire risk. Also includes backlogged tags. This backlog must be cleared in order to reach steady-state compliance with GO-95. | Transmission Line - Pole/Tower | Upgrade/Retrofit | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.012 | Future IGP Scope | Ex112983 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2023 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 141919.597 | 0 | 0 | 0 | 0 | 0 | 0 | 2675.198 | 35815.008 | 29037.923 | 26998.47 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2398 | Marker Balls |  |  | NA | Bucket for Marker Balls. TLAS has identified 3000+ T-Line spans that need FAA lighting and marking. Per FAA guideline, T-Line spans that are higher than 200 ft (above ground level) should to have catenary markings (aviation balls). Marker balls ensure power lines and guy wires are more visible to low-flying planes and helicopters. Marker Balls are typically used in airports and where power lines span long distances crossing canyons, lakes and rivers etc | Transmission Line - Other Equipment | New | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | NA | NA | Lifecycle Replacement Analysis | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 4.011 | Non-IGP | 5775030 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1249.0773 | 5029.0773 | 4.0491 | 120.1445 | 69.8555 | 107.1261 | 705.959 | 241.9431 | 540 | 540 | 540 | 540 | 1007.1342 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs. [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2399 | Beale AFB 60 kV line, Pole Replacement |  |  | Beale AFB CDP, Yuba ¦ East Nicolaus CDP, Sutter ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Smartsville CDP, Yuba ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ Wheatland, Yuba ¦ Yuba | This project proposes to reconductor 4.1 miles of the Smartville-Nicolaus #2 60 kV Line from pole 5/112 to 9/184. Completion of this project would increase transmission capacity and reliability for Pacific Gas and Electric Company’s (the Utility’s) customers served by the Smartville-Nicolaus #2 60 kV line. | Transmission Line - Conductor | Replace | NA | NA | Asset Condition | Age/Condition - Replace Other T-Line Equipment | NA | NA | 2024-03-27 | 64 | Lifecycle Replacement Analysis | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 4.1 | NA | 60 | NA | 197 | NA | NA | NA | NA | 5765441 | T.0001325 | SMARTVILLE-NICOLAUS#2 PH 1B-INSIDE BAFB | 1 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5174-E | 2017-11-03 | Approved | 2017 | Operational | 2 | 2018-04-23 | 2018-10-30 | 2018-10-01 | NA | NA | FALSE | 4720 | NA ¦ NA | 1972.8809 | 1972.8809 | -20.1965 | 0.0269 | 0.0292 | -0.4403 | 0 | 0 | 0 | 0 | 0 | 0 | 1972.8809 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | -19.0212 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Types of Analyses] For all Analyses listed, results of these analyses are include in the AAs & BCs.
| 2400 | Eagle Rock - Cloverdale 115kV Build Line |  |  | Cloverdale, Sonoma ¦ Sonoma | This planned project will convert Eagle Rock 115 kV bus to DBSB, decommission Geysers 3 & 4, and build 1.5 miles between Eagle Rock and Cloverdale Substations | Transmission Line - Multiple | New | NA | T.0005743 | Reliability | New T-Line | NA | NA | 2024-05-07 | NA | NA | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 1.5 | NA | 115 | NA | NA | NA | NA | 4.01 | In-flight Future Scope | 5800050 | T.0007732 | Eagle Rock: Convert 115 kV Bus | 3 | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2028-06-26 | NA | 2028-11-07 | NA | NA | FALSE | NA | NA ¦ NA | 5.6222 | 1199.167 | 0 | 0 | 5.6222 | 0 | 0 | 0 | 0 | 0 | 0 | 260.0394 | 5.6222 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2401 | WSIP - Steel Pole Reframe |  |  | NA | Bucket for steel pole reframes in HFTD | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | 18 | 5.201 | In-flight Future Scope | 5534699 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 13921.4429 | 13921.4429 | 907.4107 | 436.8283 | 12046.849 | 1.1763 | 417.2357 | 74.1338 | 0 | 0 | 0 | 0 | 13847.3091 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 840.8536 | 443.3849 | 196.956 | 11728.2241 | 318.6887 | 5.7821 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2402 | Steel Pole Reframe |  |  | NA | Bucket for steel pole reframing | Transmission Line - Pole/Tower | Replace | NA | NA | Asset Condition | Age/Condition - Wood Pole Reframe | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.201 | In-flight Future Scope | 5555068 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | TRUE | NA | NA ¦ NA | 3324.2478 | 3324.2478 | 776.2156 | 464.6175 | 427.9758 | 1139.5873 | 478.1625 | 7.8323 | 0 | 0 | 0 | 0 | 3316.4155 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 516.9552 | 458.9242 | 330.1176 | 1039.6465 | 353.8479 | 6.7655 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2403 | Lattice Steel Pole Guarding/Marking |  |  | NA | Bucket for installing 707 anti climb guards / mesh on Lattice Steel Poles on various 500, 230, 115 & 70KV T/Lines so that PG&E will be in compliance with GO95. This was performed on 31 different line names over 7 counties. | Transmission Line - Multiple | Replace | NA | NA | Asset Condition | GO95 Mitigation - Steel | Other [See Notes] | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | NA | NA | 380 | NA | NA | NA | NA | 5515925 | NA | NA | NA | 93 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 2656.2103 | 2656.2103 | 0 | 57.6231 | 67.1279 | 2.5494 | 0.5982 | 2.5616 | 0 | 0 | 0 | 0 | 2653.6487 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 47.1599 | 67.2305 | 2.5494 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [NERC/WECC/CAISO Standard/Requirement/Contingency] GO-95 [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2404 | 94A-Trans Line SCADA Switch Program |  |  | NA | Bucket for transmission line SCADA switch upgrades | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ TRUE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | 58 | NA | NA | NA | NA | 5507910 | NA | NA | NA | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 4599.0936 | 4599.0936 | -23.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4599.0936 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 1.2119 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2405 | NORTH BUNDLE N-15 |  |  | Humboldt ¦ Junction City CDP, Trinity ¦ Trinity ¦ Weaverville CDP, Trinity | Add SCADA capability to Motor Operated Air Switches (MOAS) Nos. 29, 19, 25, 37, 39, 137, 139, and 59 on the Essex Jct. – Arcata – Fairhaven 60 kV, Bridgeville – Garberville 60 kV, Ultra Power Tap 60 kV, Trinity – Maple Creek 60 kV, Humboldt – Trinity 115 kV, and Rio Dell Jct. – Bridgeville 60 kV Lines. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-13 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5735163 | T.0000033 | NORTH BUNDLE N-15 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-09-20 | 2018-12-03 | 2017-10-22 | NA | NA | FALSE | 5519 | NA ¦ NA | 3447.3198 | 3447.3198 | 1175.8254 | -2.1273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447.3198 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 1133.4782 | -2.0507 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2406 | NORTH BUNDLE N-11 |  |  | Butte Valley CDP, Butte | The following work scope is required to complete the North Bundle N-11 project:•Replace manually operated switch Nos. 77 and 79 on the Centerville – Table Mountain – Oroville 60 kV Line at Clark Road Substation with SCADA-operable switches •Install three new SCADA-operable switches on the Centerville – Table Mountain – Oroville 60 kV Line at Miocene Junction•Install new steel structures as required Engineering, procurement and construction will be performed by contract resources. Design oversight and construction safety and quality inspection activities for this project will be performed by PG&E internal resources. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-05 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.40715 | 60 | NA | 69 | 3. Emergency Preparedness | NA | NA | NA | 5738847 | T.0000035 | NORTH BUNDLE N-11 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-08 | 2019-05-03 | 2019-02-28 | NA | NA | FALSE | 1835 | NA ¦ NA | 2938.1894 | 2938.1894 | 1065.7934 | 76.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2938.1894 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 1027.409 | 73.3554 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2407 | Eel River:Instal2-60kV SCADA Sw.17/71 |  |  | Humboldt | Install new SCADA switches at Eel River Junction SW Nos. 17 and 71. Install TSP and Foundation At the completion of this project, the Humboldt Bay – Rio Dell Junction 60 kV Line will be able to be operated remotely. | Transmission Line - Switch | New | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-01 | NA | NA | Wires - New T-Line Alternative | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.55583 | 60 | NA | 180 | NA | NA | NA | NA | 5738828 | T.0000108 | EEL RIVER: INSTALL 2-60KV SCADA SW.17 & | 1 | 94 | NA ¦ 5767087 ¦ NA ¦ NA | TRUE | 2011 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 4858-E | 2016-06-17 | Approved | 2016 | Operational | 2 | 2017-06-05 | 2016-09-06 | 2017-07-03 | Construction Delays | NA | FALSE | 2400 | NA ¦ NA | 2336.3963 | 2336.3963 | 14.7335 | 171.5028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2336.3963 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 12.9017 | 150.1799 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2408 | Serramonte: Install 3-115kV SCADA Sws |  |  | Daly City, San Mateo ¦ San Mateo ¦ South San Francisco, San Mateo | This project proposes to replace manually operated Switches 165, 167 and 169 at the Serramonte 115 kV Tap Line connection into the Martin-Daly City No. 2 115 kV Line with SCADA-operable switches. The project will improve electric service reliability while reducing the potential environmental impacts to the San Bruno Parks mountain during an outage. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-05-18 | 34 | NA | Wires - New T-Line Alternative | $10 Mil -$15 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 58 | NA | NA | NA | NA | 5738840 | T.0000280 | Serramonte 115kV SCADA SWS | 1 | 94 | NA ¦ 5767601 ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5028-E | 2017-02-23 | Approved | 2017 | Operational | 2 | 2017-09-25 | 2016-12-01 | 2017-10-02 | Permitting | NA | FALSE | 1493.15 | NA ¦ NA | 2160.2323 | 2160.2323 | 2.3418 | 12.4466 | 0.6128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2160.2323 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 2.309 | 12.2721 | 0.60417 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2409 | Gold Hill Sub: Install 230kV Tline work |  |  | Folsom, Sacramento ¦ Granite Bay CDP, Placer ¦ Granite Bay CDP, Sacramento ¦ Orangevale CDP, Sacramento ¦ Roseville, Placer ¦ Sacramento | This project will replace 230kV circuit breakers 212, 222, 242, 252, 712 and associated equipment at Gold Hill Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NA | NA | 2021-11-18 | 58 | NA | Other - Deferral | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 230 | NA | 80 | NA | NA | NA | NA | 5790353 | T.0000466 | GOLD HILL: REPL CBS 252,212,222,242,712 | 4 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-10-15 | 2020-12-18 | 2022-03-30 | Prioritization | NA | FALSE | 10585 | NA ¦ NA | 1329.9296 | 1329.9296 | 820.5106 | 84.5325 | 424.8834 | 0.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 1329.9296 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2025 | 0 | 0 | 1329.9264 | 0.00312 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2410 | Kern PP 115kV Tline |  |  | Bakersfield, Kern ¦ East Niles CDP, Kern ¦ Fairfax CDP, Kern ¦ Fuller Acres CDP, Kern ¦ Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Transmission Line - Switch | Upgrade/Retrofit | NA | T.0000204 | Reliability | SCADA Switch Installation | NA | NA | 2025-04-03 | 34 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 37.7504 | 115 | NA | 705 | 9. Reliability (Low Safety Risk) | NA | 3.0011 | In-flight Future Scope | 5771732 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-03-08 | 2022-10-12 | 2025-03-03 | Prioritization | NA | TRUE | 77400 | NA ¦ NA | 10406.4186 | 12261.0217 | 1516.0921 | 1591.0401 | 2301.9607 | 808.563 | 1855.5636 | 3334.2159 | 0 | 0 | 0 | 0 | 8926.8057 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2411 | Kern PP 115kV Tline Reroute Phase 3 |  |  | Bakersfield, Kern ¦ Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000204 | Reliability | Line Termination | NA | NA | 2025-03-06 | 73 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | NA | 115 | NA | 705 | NA | NA | 3.0011 | In-flight Future Scope | 5788178 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-05-01 | 2022-10-12 | 2027-05-21 | Prioritization | NA | FALSE | 77400 | NA ¦ NA | 9.3765 | 9578.7318 | 0 | 2.1524 | 4.4873 | 0.4334 | 0.2217 | 1434.7037 | 8136.7331 | 0 | 0 | 0 | 7.2949 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2412 | Kern PP 115kV Tline Reroute Phase 4 |  |  | Bakersfield, Kern ¦ Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0000204 | Reliability | Line Termination | NA | NA | 2025-03-06 | 73 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | NA | 115 | NA | 705 | NA | NA | 3.0011 | In-flight Future Scope | 5788179 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-04-02 | 2022-10-12 | 2028-04-03 | Prioritization | NA | FALSE | 77400 | NA ¦ NA | 4.9008 | 16196.5343 | 0 | 3.3038 | 0.2028 | 0.223 | 1.1713 | 0.2983 | 14525.8815 | 1665.4537 | 0 | 0 | 4.9008 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2413 | SOUTH BUNDLE S-22 |  |  | Merced | Install two new 70 kV SCADA-operable switches at Wright Junction, on the Los Banos – Mercy Springs SW STA 70 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-07 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.92862 | 70 | NA | 58 | NA | NA | NA | NA | 5768809 | T.0001214 | South Bundle S-22 | 1 | 94 | NA ¦ 5738883 ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-01 | 2019-02-05 | 2019-04-12 | NA | NA | FALSE | 1345 | NA ¦ NA | 1247.862 | 1247.862 | 38.8548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.862 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 37.4554 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2414 | CENTRAL BUNDLE C-02 |  |  | Garden Acres CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel). Seven manually operated transmission line switches (SWITCH 17, SWITCH 19, SWITCH 67, SWITCH 37, SWITCH 65, SWITCH 39, SWITCH 37 with SCADA-operable switches on the Stockton ‘A’ – Weber No. 3, Weber – Mormon Junction, and the Lockeford No. 1 60 kV lines. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-12-20 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5764511 | T.0001521 | CENTRAL BUNDLE C-02 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-10-30 | 2019-11-12 | 2022-03-14 | Prioritization | NA | FALSE | 2727 | NA ¦ NA | 4624.2205 | 4624.2205 | 194.2171 | 172.7908 | 632.4922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4624.2205 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 187.2224 | 166.5677 | 609.713 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2415 | CENTRAL BUNDLE C-03 |  |  | Grayson CDP, Stanislaus ¦ Manteca, San Joaquin ¦ San Joaquin ¦ Stanislaus | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel), Switch Nos. 27 and 29 near Medlin Road Junction, Switch No 29 near Patterson Junction, Switch No. 71 near Banta Junction and Switch Nos. 47 and 49 near Westley Substation respectively. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-12-20 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | 60 | NA | 76 | NA | NA | NA | NA | 5764513 | T.0001522 | CENTRAL BUNDLE C-03 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-09-18 | 2018-11-02 | 2017-10-18 | NA | NA | FALSE | 2110.99 | NA ¦ NA | 3042.1127 | 3042.1127 | 27.8508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3042.1127 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 26.7595 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2416 | Midway: Upgrade 230KV Tline Phase 2 |  |  | Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NA | NA | 2023-11-02 | 58 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | NA | 230 | NA | 705 | NA | NA | 3.0011 | In-flight Future Scope | 5788381 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-08-05 | 2022-04-01 | 2026-09-08 | Prioritization | NA | TRUE | 105100 | NA ¦ NA | 3.7045 | 2276.1529 | 0 | 0.1791 | 0.8428 | 0.0755 | 0.5493 | 1306.2891 | 968.2171 | 0 | 0 | 0 | 1.6467 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2417 | Midway: Upgrade 230KV Tline Phase 4 |  |  | Bakersfield, Kern ¦ Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-06 | 58 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | 5788383 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-08-06 | 2022-04-01 | 2028-02-03 | Prioritization | NA | FALSE | 105100 | NA ¦ NA | 2.332 | 4117.074 | 0 | 0 | 0.2629 | 0.0194 | 0.0069 | 2.0606 | 0 | 0 | 0 | 0 | 0.2891 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2418 | MIDWAY SUB: T-LINE WORK WITHIN SUB |  |  | Bakersfield, Kern ¦ Buttonwillow CDP, Kern ¦ Greenacres CDP, Kern ¦ Kern ¦ Rosedale CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NA | NA | 2025-03-06 | 63 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | NA | 230 | NA | 705 | 9. Reliability (Low Safety Risk) | NA | 3.0011 | In-flight Future Scope | 5782605 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-07 | 2022-04-01 | 2023-05-29 | Prioritization | NA | TRUE | 105100 | NA ¦ NA | 9604.4584 | 11670.2473 | 642.4049 | 4893.3729 | 1054.2462 | 1715.9264 | 11.7631 | 2065.789 | 0 | 0 | 0 | 0 | 9604.4584 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 8729.2598 | 10.5543 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2419 | Midway: Upgrade 230KV Tline Phase 3 |  |  | Bakersfield, Kern ¦ Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-06 | 58 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | 5788382 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-05-19 | 2022-04-01 | 2026-10-15 | Prioritization | NA | TRUE | 105100 | NA ¦ NA | 0 | 9050.9234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2420 | Midway: Upgrade 230KV Tline Phase 5 |  |  | Bakersfield, Kern ¦ Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-06 | 58 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | NA | 230 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | 5788384 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2028-02-17 | 2022-04-01 | 2030-08-22 | Prioritization | NA | FALSE | 105100 | NA ¦ NA | 0 | 4587.1036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2421 | SOUTH BUNDLE S-23 |  |  | Chowchilla, Madera ¦ Fresno ¦ Madera | Add SCADA capability to Oakhurst Junction Motor Operated Air Switches (MOAS) Nos. 147 and 149 on the Chowchilla - Kerckhoff No. 2 115 kV Line, | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-06-17 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 76 | NA | NA | NA | NA | 5772325 | T.0002254 | SOUTH BUNDLE S-23 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-03-19 | 2020-06-19 | 2019-03-29 | NA | NA | FALSE | 1380 | NA ¦ NA | 1313.0147 | 1313.0147 | 106.2053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1313.0147 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 102.3803 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2422 | NORTH BUNDLE N-05 |  |  | Kennedy CDP, San Joaquin ¦ San Joaquin ¦ Stockton, San Joaquin | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel), Bangor Substation SWs 37 and 39 and SW 17 at Oregon House JCT on Colgate – Palermo 60 kV line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-08-30 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5772359 | T.0002265 | NORTH BUNDLE N-05 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-03-19 | 2019-11-15 | 2018-03-27 | NA | NA | FALSE | 891 | NA ¦ NA | 1517.1804 | 1517.1804 | 153.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1517.1804 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 148.1905 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2423 | NORTH BUNDLE N-08 |  |  | Anderson, Shasta ¦ Cottonwood CDP, Shasta ¦ Redding, Shasta ¦ Shasta | This project proposes to replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel): Anderson Substation SWs 17 and 19, Girvan Substation SWs 47 and 49, and Oregon Trail Substation SWs 147 and 149. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-11 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 ¦ 60 | NA | 76 | NA | NA | NA | NA | 5772360 | T.0002266 | NORTH BUNDLE N-08 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-12-06 | 2020-04-27 | 2019-04-07 | NA | NA | FALSE | 2127 | NA ¦ NA | 3015.911 | 3015.911 | 496.593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3015.911 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 478.7083 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2424 | NORTH BUNDLE N-13 |  |  | Canyondam CDP, Plumas ¦ Clear Creek CDP, Lassen ¦ East Shore CDP, Plumas ¦ Lassen ¦ Plumas ¦ Westwood CDP, Lassen | Replace manually operated switch Nos. 29, and 37 on the Hat Creek No. 1 – Westwood 60 kV Line, switch No. 27 on the Hat Creek No. 1 – Pit No. 1 60 kV Line and switch Nos. 37, 39, and 97 on the Caribou – Westwood 60 kV Line with SCADA-operable switches and Engineered Direct Embedded Pole (Steel), | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-06-01 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5772362 | T.0002268 | NORTH BUNDLE N-13 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-05-13 | 2020-04-24 | 2019-02-28 | NA | NA | FALSE | 1300 | NA ¦ NA | 2608.5979 | 2608.5979 | 1084.8833 | 308.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608.5979 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 1045.8115 | 297.1175 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2425 | NORTH BUNDLE N-16 |  |  | Bangor CDP, Butte ¦ Butte ¦ Nevada ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte ¦ Yuba | This project proposes to replace the following manually operated switches and its existing structures with a SCADA- operable switches and Engineered Direct Embedded Poles (Steel): Switch Nos. 15, 17 and 19 on the Spaulding – Summit 60 kV Line, at Cisco Grove Junction, Switch No. 19 on the Drum – Grass Valley – Weimar 60 kV Line, at Colfax Junction, and Switch Nos. 15 and 47 on the Drum – Grass Valley – Weimar 60 kV Line, at Shady Glen Substation. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-07-09 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | 76 | NA | NA | NA | NA | 5772363 | T.0002269 | NORTH BUNDLE N-16 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-30 | 2020-03-18 | 2019-02-28 | NA | NA | FALSE | 4198 | NA ¦ NA | 2574.5084 | 2574.5084 | -161.6699 | -0.8655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2574.5084 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | -155.8474 | -0.8343 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2426 | SOUTH BUNDLE S-01 |  |  | Greenfield, Monterey ¦ King City, Monterey ¦ Monterey ¦ Soledad, Monterey | The project is needed to improve electric transmission service reliability by reducing customer outage minutes for emergency conditions to customers served in Monterey County, California. The expected benefit of this program is a reduction of safety risks and improvement in reliability levels on transmission lines prone to outages. The remote control features of SCADA switches will eliminate the need to provide on-site, manual operation. This will reduce traveling safety risks during non-ideal weather conditions and to remote, off-road locations. Replace the following manually operated Switches and their existing structures with SCADA operable Switches and Engineered Direct Embedded Poles (Steel), Switch No. 39 on the King City – Coburn No. 1 Line, Switch No. 37 on the Soledad No. 4 Line, and Switch No. 39 on the King City – Coburn No. 2 Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-11-29 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5772480 | T.0002297 | SOUTH BUNDLE S-01 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-09-29 | 2020-03-05 | 2017-10-12 | NA | NA | FALSE | 1705.23 | NA ¦ NA | 1670.6626 | 1670.6626 | 98.9815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1670.6626 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 92.0997 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2427 | SOUTH BUNDLE S-06 |  |  | Boronda CDP, Monterey ¦ Carmel Valley Village CDP, Monterey ¦ Monterey ¦ Monterey, Monterey ¦ Salinas, Monterey | This project will reduce safety risk, improve service reliability and provide additional transmission capacity. In addition, this project will also reduce the duration of sustained outages for the customers served by Del Monte – Viejo, and Salinas – Laureles 60 kV Lines. Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel), Switch Nos. 19 & 17 on Del Monte – Viejo and Salinas – Laureles 60 kV Lines. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-04 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 76 | NA | NA | NA | NA | 5772491 | T.0002320 | SOUTH BUNDLE S-06 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-03-12 | 2019-09-12 | 2018-03-20 | NA | NA | FALSE | 1012 | NA ¦ NA | 1378.2725 | 1378.2725 | 54.8536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1378.2725 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 52.878 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2428 | Ashlan: Reroute 230kV T-Lines |  |  | Fresno, Fresno | This project will upgrade the existing 230kV bus from looped design to a ring bus design as well as install an MPAC building and upgrade protection at Ashlan, Herndon, Gregg, and Figarden substations. These upgrades will improve reliability, safety, and maintenance at Ashlan substation and the 230kV protection in the local area. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NA | NA | 2023-11-16 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 230 | NA | 270 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5776978 | T.0002362 | Ashlan Ave 230kV Bus Reliability | 7 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-01-22 | 2020-02-11 | 2020-03-24 | NA | NA | FALSE | 40900 | NA ¦ NA | 2124.8942 | 2124.8942 | 179.651 | 4.1697 | 0.5922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2124.8942 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 2087.514 | 4.0998 | 0.58231 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2429 | HERNDON-MANCHESTER 115KV OPGW |  |  | Fresno, Fresno ¦ Madera ¦ Old Fig Garden CDP, Fresno | This project will upgrade the existing 230kV bus from looped design to a ring bus design as well as install an MPAC building and upgrade protection at Ashlan, Herndon, Gregg, and Figarden substations. These upgrades will improve reliability, safety, and maintenance at Ashlan substation and the 230kV protection in the local area. | Transmission Line - Other Equipment | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-11-17 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 270 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5779821 | T.0002362 | Ashlan Ave 230kV Bus Reliability | 7 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5310-E | 2018-06-13 | Approved | 2018 | Operational | 2 | 2019-08-12 | 2020-02-11 | 2020-04-08 | NA | NA | FALSE | 40900 | NA ¦ NA | 7224.675 | 7224.675 | 887.3967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7224.675 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 7170.8974 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2430 | NORTH BUNDLE N-07 |  |  | Cottonwood CDP, Shasta | This project proposes to replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel): Coleman Hatchery SW 65, Hamilton JCT SWs 27 and 29, Loomis JCT SW 49 and 59 and Wintu JCT SWs 37 and 39. In addition this project proposes to add two SWs (approximately close to structure 0/18 and 1/21) on the Coleman-Cottonwood 60 kV line close to Coleman-Hatchery 60 kV tap line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-12 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 26.1945 | 60 | NA | 180 | 1. Work that prevents fire ignition | NA | NA | NA | 5772867 | T.0002402 | NORTH BUNDLE N-07 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-04-10 | 2019-12-09 | 2019-02-28 | NA | NA | FALSE | 2664 | NA ¦ NA | 3454.9414 | 3454.9414 | 867.5629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3454.9414 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 836.3178 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2431 | CENTRAL BUNDLE C-01 |  |  | Healdsburg, Sonoma | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel). There have been several outages on the Monte Rio-Fulton 60 kV line. One of the most recent outages affected over 14,000 customers for over eight hours with a SAIDI contribution of 0.27. Upgrading Wohler JCT SWs 67 and 69, Trenton JCT SW 59 to SCADA-operable switches will significantly reduce the outage duration for this line and customers affected. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-07-10 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5774082 | T.0002753 | CENTRAL BUNDLE C-01 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-01-08 | 2017-10-18 | 2019-02-28 | Project Design | NA | FALSE | 2940 | NA ¦ NA | 4073.6459 | 4073.6459 | 510.7282 | 342.7549 | 0.3221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4073.6459 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 492.3344 | 330.4106 | 0.31053 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2432 | Val Springs-Clay60kV, Pardee Tap 5 SCADA |  |  | Amador ¦ Buena Vista CDP, Amador ¦ Calaveras ¦ Ione, Amador | Phase 1 of this project will replace 6 manually operated switches with SCADA-operable switches on the Valley Springs-Martell No. 1, Valley Springs – Clay, and the Pardee No. 2 Tap 60kV lines. The associated wood poles will be replaced with 4 Tubular Steel Poles (TSP) and 2 Engineered Direct Embedded Poles (EDEP) as required. This project will improve customer electric service reliability by reducing outage durations and allowing greater operational flexibility. Phase 2 of this project will replace 4 manually operated switches with SCADA-operable switches on the Clay - Martell 60kV line. The associated wood poles will be replaced with 3 Fiberglass Poles and one Engineered Direct Embedded Poles (EDEP) as required. The manual switches will be replaced with either Cleveland/Price or SEECO switches. The project is being constructed in 2 phases due to testing required for the new fiberglass pole design. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-19 | 49 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 58 | NA | NA | NA | NA | 5792368 | T.0003024 | ValleySprings-Martell No.2 SCADA | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5801-E | 2020-04-03 | Approved | 2020 | Operational | 2 | 2021-12-06 | 2021-10-31 | 2021-12-15 | NA | NA | FALSE | 10500 | NA ¦ NA | 2329.8047 | 2329.8047 | 19.4643 | 2194.7393 | 134.2638 | -18.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 2329.8047 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 2054.9363 | 124.5199 | -17.3084 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ $50 Mil – $75 Mil
| 2433 | Clay Martell 60kV SCADA |  |  | Amador ¦ Amador City, Amador ¦ Drytown CDP, Amador ¦ Ione, Amador ¦ Martell CDP, Amador ¦ Plymouth, Amador ¦ Sutter Creek, Amador | Phase 1 of this project will replace 6 manually operated switches with SCADA-operable switches on the Valley Springs-Martell No. 1, Valley Springs – Clay, and the Pardee No. 2 Tap 60kV lines. The associated wood poles will be replaced with 4 Tubular Steel Poles (TSP) and 2 Engineered Direct Embedded Poles (EDEP) as required. This project will improve customer electric service reliability by reducing outage durations and allowing greater operational flexibility. Phase 2 of this project will replace 4 manually operated switches with SCADA-operable switches on the Clay - Martell 60kV line. The associated wood poles will be replaced with 3 Fiberglass Poles and one Engineered Direct Embedded Poles (EDEP) as required. The manual switches will be replaced with either Cleveland/Price or SEECO switches. The project is being constructed in 2 phases due to testing required for the new fiberglass pole design. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-07 | 51 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | 5798378 | T.0003024 | ValleySprings-Martell No.2 SCADA | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5801-E | 2020-04-03 | Approved | 2020 | Engineering more than 50% complete | 4 | 2027-06-28 | 2021-10-31 | 2027-08-19 | Prioritization | NA | FALSE | 10500 | NA ¦ NA | 463.6686 | 3094.7641 | 0 | 0 | 275.5444 | 142.6107 | 40.0231 | 33.586 | 0 | 0 | 0 | 2203 | 458.1781 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $10 Mil -$15 Mil ¦ $50 Mil – $75 Mil
| 2434 | NICOLAUS WILKINS SLOUGH SW REPLACEMENT |  |  | East Nicolaus CDP, Sutter ¦ Knights Landing CDP, Yolo ¦ Nicolaus CDP, Sutter ¦ Sutter ¦ Yolo | The purpose of this project is to improve the resistance of this line to failures caused by extreme wind speeds (in excess of 70mph) and to minimize future outages to Wilkins Slough Substation and 4 Reclamation District Substations. This project proposes to relocate/replace 274 wood transmission poles with light duty steel poles on the Nicolaus – Wilkins Slough 60kV Line, and Replace 2 manual switches on the District 1001 tap line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-08 | 75 | NA | Wires - Reconductor/Line Rebuild Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | 5784327 | T.0003076 | Nicolaus-Wilkins Slough 60kV line Pole | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2031-07-25 | 2022-10-11 | 2031-08-05 | Prioritization | NA | FALSE | 13482 | NA ¦ NA | 0 | 15577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12103 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2435 | North Bundle N-01 |  |  | Dixon, Solano ¦ Elmira CDP, Solano ¦ Fairfield, Solano ¦ Solano ¦ Vacaville, Solano | This project proposes to replace the following manually operated switches and its existing structures with SCADA- operable switches and Engineered Direct Embedded Poles (Steel): Switch Nos. 87 and 89 on the Dixon-Vaca No. 1 60 kV Line at Dixon Canning Junction, Switch No. 19 on the Dixon – Vaca No. 1 60 kV Line at Travis Junction, and Switch Nos. 37, 39, and 59 on the Dixon – Vaca No. 1 60 kV Line at Vaca Junction. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-27 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5526481 | T.0003142 | North Bundle N-01 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-16 | 2018-12-31 | 2020-02-04 | Prioritization | NA | FALSE | 2374 | NA ¦ NA | 2117.0602 | 2117.0602 | 806.6498 | -321.3684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2117.0602 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 777.5985 | -309.7944 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2436 | North Bundle N-02 |  |  | Dixon, Solano ¦ Elmira CDP, Solano ¦ Fairfield, Solano ¦ Solano ¦ Vacaville, Solano | This project proposes to replace the following manually operated switches and its existing structures with SCADA- operable switches and Engineered Direct Embedded Pole (Steel): Switch Nos. 27 and 29 on the Dixon – Vaca No. 2 60 kV Line at Dixon Substation, Switch No. 27, on the Dixon – Vaca No. 2 60 kV Line at Travis Junction, and Switch Nos. 47 and 49 on the Dixon – Vaca No. 2 60 kV Line at Vaca Junction. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-07 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5526482 | T.0003143 | North Bundle N-02 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-19 | 2018-12-31 | 2021-05-13 | Prioritization | NA | FALSE | 1895 | NA ¦ NA | 2185.3793 | 2185.3793 | 276.4124 | 4.1474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2185.3793 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 266.4574 | 3.998 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2437 | North Bundle N-03 |  |  | West Sacramento, Yolo | This project will increase reliability and operational flexibility for the customers of Colusa, Sutter, Yolo and Yuba counties by providing remote sectionalizing capability to the Smartville – Nicolaus No. 2, Almendra Junction – Nicolaus, Nicolaus – Wilkins Slough, Colusa Junction No. 1, Nicolaus – Marysville 60 kV lines and the Deepwater 115 kV Tap No. 1. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2020-09-11 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | NA | NA | NA | NA | 5526483 | T.0003144 | NORTH BUNDLE N-03 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-02-19 | 2017-12-31 | 2017-12-12 | NA | NA | FALSE | 2087 | NA ¦ NA | 2815.8561 | 2815.8561 | 541.9053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2815.8561 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 522.3887 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2438 | North Bundle N-04 |  |  | Arbuckle CDP, Colusa ¦ College City CDP, Colusa ¦ Colusa ¦ Yolo | This project proposes to replace six manually operated switches and their associated structures with SCADA-operable switches and Engineered Direct-Embedded Poles (Steel). Specifically, the switches that will be replaced are as follows: Switch No. 29, near Maxwell Junction, Switch No. 45, near Maxwell Substation, and Switch No. 57, near Wilson Ave, on the Cortina 60 kV Line No. 4. Switch No. 3, near Wilkins Slough, on the Cortina 60 kV Line No. 2. Switch No. 47, near Colusa Junction, on the Cortina 60 kV Line No. 3. Switch No. 69, near Encinal Substation, on the Peachton – Pease 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-03 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526484 | T.0003146 | North Bundle N-04 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-04-02 | 2017-12-31 | 2018-04-18 | NA | NA | FALSE | 2098 | NA ¦ NA | 2782.5481 | 2782.5481 | 579.7989 | 1.8284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2782.5481 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 558.9175 | 1.7626 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2439 | North Bundle N-06 |  |  | Butte ¦ Chico, Butte ¦ Durham CDP, Butte | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel): Durham JCT SWs 15, 17, 19, 45, 47 and 49 on Butte – Esquon 60 kV line as well as Tres Vias Substation SWs 27, and 29 on Table Mountain – Peachton 60 kV line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-10-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526485 | T.0003147 | North Bundle N-06 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-12-05 | 2017-12-31 | 2017-12-12 | NA | NA | FALSE | 2315 | NA ¦ NA | 3709.4507 | 3709.4507 | 613.7045 | 27.4439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709.4507 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 591.602 | 26.4555 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2440 | North Bundle N-09 |  |  | Butte ¦ Forbestown CDP, Butte ¦ Oroville East CDP, Butte ¦ Palermo CDP, Butte | Replace manually operated switch No. 47 on the Garberville – Laytonville 60 kV Line at Bell Springs with SCADA-operable switch and Engineered Direct Embedded Pole (Steel) and add SCADA to existing SCADA-ready switches Nos. 145, 147, and 149 on the Woodleaf – Palermo 115 kV Line at Kanaka Tap. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-06-13 | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | NA | NA | NA | NA | 5526486 | T.0003149 | NORTH BUNDLE N-09 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-10-02 | 2019-08-30 | 2019-11-25 | NA | NA | FALSE | 2020 | NA ¦ NA | 1764.7469 | 1764.7469 | 506.5279 | -0.3474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1764.7469 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 488.2854 | -0.33489 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2441 | North Bundle N-10 |  |  | Fairfield, Solano ¦ Green Valley CDP, Napa ¦ Green Valley CDP, Solano ¦ Napa ¦ Solano | This project proposes to replace the following manually operated switches and its existing structures with SCADA- operable switches and Engineered Direct Embedded Poles (Steel): Switch Nos. 135 and 137 on the Brighton – Davis 115 kV Line at Barker Slough Junction, Switch Nos. 155, 157 and 159 on the Cordelia No.2 115 kV Tap Line near the Cordelia Pumping Plant. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-11-26 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5526487 | T.0003152 | North Bundle N-10 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5455-E | 2018-12-26 | Approved | 2019 | Operational | 2 | 2020-03-03 | 2019-03-30 | 2021-03-23 | Prioritization | NA | FALSE | 3298 | NA ¦ NA | 3268.5921 | 3268.5921 | 1444.2062 | 759.9213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3268.5921 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 1392.1933 | 732.5527 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | NA
| 2442 | North Bundle N-12 |  |  | Keddie CDP, Plumas ¦ Paxton CDP, Plumas ¦ Plumas ¦ Quincy CDP, Plumas ¦ Twain CDP, Plumas | This project will reduce safety risk, improve service reliability and provide additional transmission capacity for the customers served by the Caribou Power House Substation by providing remote sectionalizing capability to the Caribou No. 2 60 kV Line. This project will also reduce the duration of momentary and sustained outages for the customers served by the Caribou No. 2 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-27 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526488 | T.0003153 | North Bundle N-12 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-27 | 2018-11-30 | 2019-11-27 | Prioritization | NA | FALSE | 1490 | NA ¦ NA | 1817.3352 | 1817.3352 | 393.0654 | -77.4108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1817.3352 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 378.9092 | -74.6228 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2443 | South Bundle S-07 |  |  | Monterey ¦ Salinas, Monterey | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel): Switch Nos. 27 & 29 on the Salinas – Firestone 60 kV No. 2 Line. And remove Switch No. 41 on the Soledad 60 kV No. 1 Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-09-21 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526490 | T.0003155 | SOUTH BUNDLE S-07 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-11-27 | 2017-12-31 | 2017-12-12 | NA | NA | FALSE | 1129.29 | NA ¦ NA | 1228.1934 | 1228.1934 | 85.5537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1228.1934 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 81.0136 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2444 | South Bundle S-10 |  |  | Monterey, Monterey | Replace manually operated Switch No. 17 on the Del Monte – Monterey 60 kV Line and Switch No. 37 on the Del Monte – Viejo 60 kV Line and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel). Also install a new SCADA operable Switch No. 19 on the Del Monte – Monterey Line at the Navy School tap connection. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-04-24 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5526491 | T.0003156 | South Bundle S-10 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-01-28 | 2018-05-01 | 2020-02-03 | Prioritization | NA | FALSE | 1620 | NA ¦ NA | 1405.064 | 1405.064 | 803.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1405.064 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 774.4525 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2445 | South Bundle S-11 |  |  | King City, Monterey ¦ Monterey ¦ San Lucas CDP, Monterey | Add SCADA capability to Switch Nos. 17 and 19 on the Coburn – Oil Fields No. 1 60 kV Line and Switch Nos. 27 and 29 on the Coburn – Oil Fields No. 2 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-12-13 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526492 | T.0003157 | South Bundle S-11 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-11-02 | 2018-09-30 | 2019-04-11 | Prioritization | NA | FALSE | 1499 | NA ¦ NA | 1850.6604 | 1850.6604 | 127.9186 | 0.536 | 0 | 56.3819 | 0 | 0 | 0 | 0 | 0 | 0 | 1850.6604 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2023 ¦ 2025 | 123.3116 | 0.5167 | 0 | 54.3513 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2446 | South Bundle S-12 |  |  | Monterey ¦ Salinas, Monterey | Add SCADA capability to Switch Nos. 67 and 69 on the Salinas – Firestone No. 1 60 kV Line and Switch Nos. 19, 25 and 49 on the Salinas – Firestone No. 2 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-09-21 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5526493 | T.0003158 | South Bundle S-12 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-23 | 2018-12-31 | 2021-01-28 | Prioritization | NA | FALSE | 2607 | NA ¦ NA | 3012.4946 | 3012.4946 | 1797.105 | 231.5874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3012.4946 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 1385.8568 | 178.591 | 580.8828 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2447 | South Bundle S-13 |  |  | Aromas CDP, Monterey ¦ Aromas CDP, San Benito ¦ Monterey ¦ Prunedale CDP, Monterey ¦ Prunedale CDP, San Benito ¦ Salinas, Monterey ¦ San Benito ¦ Santa Cruz ¦ Watsonville, Santa Cruz | Add SCADA capability to Switch Nos. 27, 37 and 39 on the Watsonville – Salinas 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-06-07 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526494 | T.0003159 | South Bundle S-13 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-05-01 | 2018-10-31 | 2019-06-05 | Workforce | NA | FALSE | 1630 | NA ¦ NA | 1639.8601 | 1639.8601 | 295.1107 | 4.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1639.8601 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 284.4823 | 3.9039 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2448 | South Bundle S-16 |  |  | Monterey ¦ Prunedale CDP, Monterey ¦ Salinas, Monterey ¦ Soledad, Monterey | Replace transmission line Switch Nos. 37 and 39 at Gabilan Substation on the Salinas – Lagunitas 60 kV Line and Switch Nos. 117 and 119 at Natividad Junction on the Crazy Horse Canyon – Salinas – Soledad 115 kV Lines with SCADA-operable switches and install new Switch Nos. 127, 129, 137 and 139 at Natividad Junction on the 115 kV lines. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-10-26 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 ¦ 60 | NA | 180 | NA | NA | NA | NA | 5526496 | T.0003161 | South Bundle S-16 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-17 | 2018-12-31 | 2019-06-05 | NA | NA | FALSE | 2663 | NA ¦ NA | 4072.5266 | 4072.5266 | 326.5163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4072.5266 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 314.7568 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2449 | South Bundle S-18 |  |  | San Luis Obispo | Replace manually operated switch Nos. 57 and 59 on the San Luis Obispo – Cayucos 70 kV Line at Mustang Junction and Switch Nos. 135 and 145 on the Goldtree 115 kV Tap Line at Goldtree Junction with SCADA-operable switches and new steel structures. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-03 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 ¦ 70 | NA | 180 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5526497 | T.0003162 | South Bundle S-18 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-14 | 2020-03-01 | 2020-06-03 | NA | NA | FALSE | 2120 | NA ¦ NA | 2452.5724 | 2452.5724 | 303.4495 | 3.5201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2452.5724 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 292.5209 | 3.3933 | -0.00018 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2450 | South Bundle S-24 |  |  | Lompoc, Santa Barbara ¦ Santa Barbara | Replace manually operated switch No. 169 on the City No. 2 Tap 115 kV Line at the Lompoc Junction, switch No. 115 on the Manville Tap 115 kV at the Manville Junction, switch No. 149 on the Cabrillo – Santa Ynez SW STA 115 kV at the Manville Junction, switch No. 135 on the Surf Tap 115 kV Line at the Surf Junction, and switch Nos. 137 and 139 on the Divide – Cabrillo No. 1 115 kV Line at the Surf Junction with SCADA-operable switches and Tubular Steel Poles (TSP). | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2021-07-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5526500 | T.0003165 | South Bundle S-24 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-02-14 | 2019-06-30 | 2020-01-27 | Workforce | NA | FALSE | 4140 | NA ¦ NA | 5201.6986 | 5201.6986 | 1893.9526 | 0.0053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5201.6986 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 1825.7422 | 0.00507 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2451 | South Bundle S-25 |  |  | Santa Barbara ¦ Sisquoc CDP, Santa Barbara | Replace manually operated switch Nos. 127 and 129 on the Sisquoc – Santa Ynez Sw Sta 115 kV Line at Palmer Substation with SCADA-operable switches and Tubular Steel Poles (TSP). | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-06-06 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 180 | NA | NA | NA | NA | 5526501 | T.0003166 | South Bundle S-25 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-11-08 | 2018-12-31 | 2019-11-19 | Prioritization | NA | FALSE | 1390 | NA ¦ NA | 1312.6 | 1312.6 | 5.9076 | 0.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.6 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 5.6948 | 0.5167 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2452 | South Bundle S-26 |  |  | Santa Barbara ¦ Sisquoc CDP, Santa Barbara | Replace manually operated switch Nos. 147 and 149 on the Sisquoc – Santa Ynez Sw Sta 115 kV Line at Zaca Substation and Switch No. 129 on the Santa Ynez 115 kV Tap at Santa Ynez Sw Sta with SCADA-operable switches and Tubular Steel Poles (TSP),. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-06-06 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 180 | NA | NA | NA | NA | 5526502 | T.0003167 | South Bundle S-26 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-08-22 | 2019-02-01 | 2018-10-04 | NA | NA | FALSE | 1135 | NA ¦ NA | 1520.5674 | 1520.5674 | 84.2843 | 4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1520.5674 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 81.2488 | 3.9041 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2453 | South Bundle S-27 |  |  | Fresno ¦ Hanford, Kings ¦ Kings | Add SCADA capability to Contadina Junction SWs 137 and 139 in the GWF – Kingsburg 115 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-10-30 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | NA | NA | NA | NA | 5526503 | T.0003168 | South Bundle S-27 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-03-03 | 2018-12-31 | 2019-04-01 | NA | NA | FALSE | 1560 | NA ¦ NA | 1369.5792 | 1369.5792 | 57.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1369.5792 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 55.1493 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2454 | Central Bundle C-04 |  |  | Alameda ¦ Brentwood, Contra Costa ¦ Byron CDP, Contra Costa ¦ Contra Costa ¦ San Joaquin | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel). Switch Nos. 5 and 7 on the Herdlyn – Balfour 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-10 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526504 | T.0003169 | Central Bundle C-04 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-12-01 | 2017-12-31 | 2017-12-12 | NA | NA | FALSE | 1347 | NA ¦ NA | 1232.0568 | 1232.0568 | 80.8894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1232.0568 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 75.2655 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2455 | Central Bundle C-05 |  |  | Alameda ¦ Livermore, Alameda ¦ Pleasanton, Alameda | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel): Switch Nos. 47 and 67 on the Radum – Vallecitos, and Radum – Livermore 60 kV Lines. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-08-18 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526505 | T.0003170 | Central Bundle C-05 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-01-19 | 2017-12-31 | 2017-12-12 | NA | NA | FALSE | 1288 | NA ¦ NA | 1175.9918 | 1175.9918 | 73.4128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1175.9918 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 68.6782 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2456 | Central Bundle C-06 |  |  | Clearlake Oaks CDP, Lake ¦ Clearlake, Lake ¦ Lake ¦ Lower Lake CDP, Lake ¦ Sonoma | Add SCADA capability to Motor Operated Air Switches (MOAS) Nos. 17, 139, 67, 19, and 67 on the Potter Valley – Willits 60 kV, Eagle Rock – Redbud 115 kV, Elk – Gualala 60 kV, Philo Jct. – Elk 60 kV, Laytonville – Willits 60 kV Lines. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-07 | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 ¦ 60 | NA | 180 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5526506 | T.0003171 | Central Bundle C-06 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-05 | 2018-12-31 | 2020-05-07 | Prioritization | NA | FALSE | 3010 | NA ¦ NA | 1524.5457 | 1524.5457 | 108.4797 | -263.9041 | 16.0109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1524.5457 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 104.5728 | -254.3996 | -127.8693 | -3e-05 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2457 | Central Bundle C-08 |  |  | Alameda ¦ Lathrop, San Joaquin ¦ Manteca, San Joaquin ¦ Ripon, San Joaquin ¦ San Joaquin ¦ Tracy, San Joaquin | Replace the following manually operated switches and their existing structures with SCADA operable switches and Engineered Direct Embedded Poles (Steel). Switch Nos. 119, 127 and 129 on the Tesla – Stockton Cogen Junction 115 kV Line.. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-23 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | NA | NA | NA | NA | 5526508 | T.0003173 | Central Bundle C-08 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-02-26 | 2017-12-31 | 2017-12-12 | NA | NA | FALSE | 1601 | NA ¦ NA | 1827.6154 | 1827.6154 | 110.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1827.6154 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 106.3004 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2458 | Central Bundle C-09 |  |  | Bay Point CDP, Contra Costa ¦ Contra Costa ¦ Martinez, Contra Costa | This project proposes to replace the following manually operated switch and its existing structures with a SCADA- operable switch and an Engineered Direct Embedded Pole (Steel): Switch No. 57 at Pole No. 06/09 on Christie – Willow Pass 60 kV Line at Stauffer Junction. The project is needed to improve electric transmission service reliability by reducing customer outage minutes for emergency conditions to customers served in Contra Costa County, California. The expected benefit of this program is a reduction of safety risks and improvement in reliability levels on transmission lines prone to outages. The remote control features of SCADA switches will eliminate the need to provide on-site, manual operation. This will reduce traveling safety risks during non-ideal weather conditions and to remote, off-road locations. In parallel, SCADA enables faster fault isolation and restoration possibilities as well as improved clearance planning | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-27 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5526509 | T.0003174 | Central Bundle C-09 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-10-05 | 2019-06-30 | 2020-10-12 | Project Design | NA | FALSE | 790 | NA ¦ NA | 1066.906 | 1066.906 | 639.9171 | 13.4537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1066.906 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 616.8705 | 12.9692 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2459 | Central Bundle C-10 |  |  | Larkfield-Wikiup CDP, Sonoma ¦ Napa ¦ Saint Helena, Napa ¦ Santa Rosa, Sonoma ¦ Sonoma ¦ Yolo | This project proposes to replace the following manually operated switch and its existing structures with a SCADA- operable switch and an Engineered Direct Embedded Pole (Steel): Switch Nos. 27, 37, and 47 at Pole Nos. 33/14, 20/00, and 16/03 on Fulton – Calistoga 60 kV Line at St. Helena Junction. The project is needed to improve electric transmission service reliability by reducing customer outage minutes for emergency conditions to customers served in Napa and Sonoma Counties, California. The expected benefit of this program is a reduction of safety risks and improvement in reliability levels on transmission lines prone to outages. The remote control features of SCADA switches will eliminate the need to provide on-site, manual operation. This will reduce traveling safety risks during non-ideal weather conditions and to remote, off-road locations. In parallel, SCADA enables faster fault isolation and restoration possibilities as well as improved clearance planning | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-06 | NA | NA | Other - Status Quo | NA | Zone 1 - HHZ ¦ Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | 70 | NA | NA | 5526510 | T.0003175 | Central Bundle C-10 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6291-E | 2021-08-10 | Approved | 2021 | Operational | 2 | 2021-11-29 | 2019-12-31 | 2021-12-10 | Prioritization | NA | FALSE | 2240 | NA ¦ NA | 2758.7166 | 2758.7166 | 382.8894 | 1827.945 | 75.2232 | 4.4951 | 0 | 0 | 0 | 0 | 0 | 0 | 2758.7166 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 369.0996 | 1762.1118 | 72.5139 | 4.3332 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | NA
| 2460 | Central Bundle C-15 |  |  | Alameda ¦ Fremont, Alameda ¦ Livermore, Alameda ¦ Sunol CDP, Alameda | Add SCADA capability to Switch Nos. 67, 69, and 57 on Newark – Vallecitos, and Newark – Livermore 60 kV Lines at Sunol and San Ramon Junctions. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-12 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | 249 | NA | NA | 5526512 | T.0003177 | Central Bundle C-15 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-10 | 2019-05-30 | 2021-05-12 | Prioritization | NA | FALSE | 1422 | NA ¦ NA | 1878.2055 | 1878.2055 | 591.0623 | 332.7495 | 0.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1878.2055 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 569.7753 | 320.7656 | 0.08758 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2461 | Central Bundle C-17 |  |  | Fulton CDP, Sonoma ¦ Santa Rosa, Sonoma ¦ Sonoma | Replace the Switch Nos. 67 and 69 on Fulton – Molino – Cotati 60 kV Line at Laguna Junction transmission line switch with SCADA-operable switch. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-01-23 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 9. Reliability (Low Safety Risk) | 9 | NA | NA | 5526514 | T.0003179 | Central Bundle C-17 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-04-27 | 2018-12-31 | 2021-05-03 | Prioritization | NA | FALSE | 1660 | NA ¦ NA | 1622.0476 | 1622.0476 | 59.0405 | 707.5077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1622.0476 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 56.9142 | 682.027 | -0.00017 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2462 | Central Bundle C-18 |  |  | Clearlake Oaks CDP, Lake ¦ Colusa ¦ Lake ¦ Lucerne CDP, Lake ¦ Mendocino ¦ Nice CDP, Lake | This project proposes to replace the following manually operated switch and its existing structures with a SCADA- operable switch and an Engineered Direct Embedded Pole (Steel): Switch No. 117 at Pole No. 26/125 on Cortina – Mendocino # 1 115 kV Line at Redbud Junction. The project is needed to improve electric transmission service reliability by reducing customer outage minutes for emergency conditions to customers served in Lake County, California. The expected benefit of this program is a reduction of safety risks and improvement in reliability levels on transmission lines prone to outages. The remote control features of SCADA switches will eliminate the need to provide on-site, manual operation. This will reduce traveling safety risks during non-ideal weather conditions and to remote, off-road locations. In parallel, SCADA enables faster fault isolation and restoration possibilities as well as improved clearance planning. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-07-19 | NA | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5526515 | T.0003180 | Central Bundle C-18 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-05-16 | 2018-12-31 | 2022-05-19 | Prioritization | NA | FALSE | 1030 | NA ¦ NA | 1109.8106 | 1109.8106 | 298.3279 | 219.1148 | 381.5897 | -21.1045 | 14.7157 | 0 | 0 | 0 | 0 | 0 | 1109.8106 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 287.5838 | 211.2234 | 367.8468 | -20.3444 | 14.1857 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2463 | Central Bundle C-19 |  |  | Burlingame, San Mateo ¦ Millbrae, San Mateo ¦ San Mateo ¦ San Mateo, San Mateo ¦ South San Francisco, San Mateo | This project proposes to replace the following manually operated switches and existing structures with SCADA- operable switches and Engineered Direct Embedded Poles (Steel): Switch Nos. 137 & 139 on the East Grand – San Mateo 115 kV Line, Switch No. 147 at Millbrae Junction on the on Millbrae – San Mateo No. 1 115 kV Line and Switch No. 69 on the San Mateo – Bair 60 kV Line. The project is needed to improve electric transmission service reliability by reducing customer outage minutes for emergency conditions to customers served in San Mateo County, California. The expected benefit of this program is a reduction of safety risks and improvement in reliability levels on transmission lines prone to outages. The remote control features of SCADA switches will eliminate the need to provide on-site, manual operation. This will reduce traveling safety risks during non-ideal weather conditions and to remote, off-road locations. In parallel, SCADA enables faster fault isolation and restoration possibilities as well as improved clearance planning | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2020-10-06 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 ¦ 60 | NA | 180 | 9. Reliability (Low Safety Risk) | NA | 4.0211 | Future IGP Scope | 5526516 | T.0003181 | Central Bundle C-19 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 3 | 2024-01-04 | 2019-10-31 | 2026-12-31 | Prioritization | NA | FALSE | 3970 | NA ¦ NA | 1286.0128 | 1286.0128 | 508.5492 | 10.2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1286.0128 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2026 | 490.2339 | 9.911 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2464 | Central Bundle C-22 |  |  | San Joaquin ¦ Stanislaus ¦ Valley Home CDP, Stanislaus | This project proposes to replace the following manually operated switches and its existing structures with SCADA- operable switches and an Engineered Direct Embedded Poles (Steel): Switch No. 113, at Stockton Junction, on the Tesla – Tracy 115 kV Line, Switch Nos. 117 and 119, at the Stockton Co-gen Junction, on the Stockton ‘A’ – Lockeford – Bellota No. 1 115 kV Line, and Switch No. 169, at Melones Junction, on the Stanislaus – Melones Sw Sta – Riverbank Junction Sw Sta 115 kV Line, and Switch No. 179, at Riverbank Junction, on the Bellota – Riverbank 115 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-11-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 9. Reliability (Low Safety Risk) | 611 | 4.0211 | Future IGP Scope | 5526519 | T.0003184 | Central Bundle C-22 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2021-11-15 | 2019-06-30 | 2028-02-14 | Prioritization | NA | TRUE | 2386 | NA ¦ NA | 3091.365 | 4999.4526 | 708.4316 | 679.7869 | 114.4838 | 56.3819 | 10.6288 | 897.8456 | 0 | 0 | 0 | 1010.242 | 3091.365 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2028 | 682.9175 | 655.3044 | 110.3607 | 54.3513 | 10.246 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2465 | Central Bundle C-23 |  |  | Alameda ¦ Lathrop, San Joaquin ¦ Manteca, San Joaquin ¦ Ripon, San Joaquin ¦ San Joaquin ¦ Tracy, San Joaquin | The project proposes to replace three manually operated switches and their associated structures, on the Tesla – Stockton Cogen Junction 115 kV Line with SCADA-operable switches and Engineered Direct Embedded Poles (Steel). | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-23 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | NA | NA | NA | NA | 5526520 | T.0003185 | Central Bundle C-23 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-05-22 | 2019-06-30 | 2019-12-13 | NA | NA | FALSE | 2000 | NA ¦ NA | 1726.342 | 1726.342 | 122.105 | 0.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1726.342 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 117.7073 | 0.1834 | -2e-05 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2466 | South Bundle S-04 |  |  | Greenfield, Monterey ¦ King City, Monterey ¦ Monterey ¦ Soledad, Monterey | Replace the following manually operated switches and their existing structures with SCADA-operable switches and Engineered Direct Embedded Poles (Steel), at a cost not to exceed $2.7 million: Switch Nos. 27 and 29 on King City – Coburn No. 1 60 kV Line and Switch No. 27 on King City – Coburn No. 2 60 kV Line. And remove Switch 57 on the King City – Coburn No. 1 Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-11-29 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526764 | T.0003239 | South Bundle S-04 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-10-11 | 2017-12-31 | 2017-10-24 | NA | NA | FALSE | 1988.28 | NA ¦ NA | 2118.4159 | 2118.4159 | 78.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2118.4159 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 75.0484 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2467 | South Bundle S-15 |  |  | Chualar CDP, Monterey ¦ Gonzales, Monterey ¦ Monterey ¦ Soledad, Monterey | Remove Switch No. 55 on the Gonzales No. 1 Tap Line and add SCADA capability to Switch Nos. 51 and 53 on the Soledad No. 1 Line, Switch No. 29 on the Soledad No. 2 Line, Switch Nos. 67 and 87 on the Gonzales No. 1 Tap Line and Switch No. 25 on the Gonzales No. 2 Tap Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-03-20 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526765 | T.0003240 | SOUTH BUNDLE S-15 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-24 | 2019-05-30 | 2019-12-13 | Clearances | NA | FALSE | 3239 | NA ¦ NA | 3371.8706 | 3371.8706 | 254.1345 | -0.0143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3371.8706 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 244.9819 | -0.01374 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2468 | North Bundle N-14 |  |  | Gerber CDP, Tehama ¦ Los Molinos CDP, Tehama ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama ¦ Tehama, Tehama | Add SCADA capability to Motor Operated Air Switches (MOAS) Nos. 39, 51, 57, 59, 227, 229, 37, and 17 on the Coleman – Red Bluff 60 kV, Bridgeville – Cottonwood 115 kV, Cottonwood #1 60 kV, and Kilarc – Cedar Creek 60 kV Lines. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-04 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5526767 | T.0003242 | North Bundle N-14 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-03 | 2019-05-30 | 2019-12-23 | Prioritization | NA | FALSE | 1871 | NA ¦ NA | 4503.9747 | 4503.9747 | 832.4064 | -0.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4503.9747 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 802.4273 | -0.92598 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2469 | North Bundle N-17 |  |  | Greenfield, Monterey ¦ King City, Monterey ¦ Monterey ¦ Soledad, Monterey | Add SCADA capability to Motor Operated Air Switches (MOAS) Nos. 39, 47, and 49 on the Kilarc – Deschutes 60 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-11-29 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | NA | NA | NA | NA | 5527390 | T.0003394 | North Bundle N-17 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-23 | 2019-07-30 | 2019-10-08 | NA | NA | FALSE | 4570 | NA ¦ NA | 1763.9572 | 1763.9572 | 401.4693 | -0.9549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1763.9572 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 387.0104 | -0.92051 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2470 | Central Bundle C-24 |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Manteca, San Joaquin ¦ Murphys CDP, Calaveras ¦ San Joaquin ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | This project proposes to replace a total of seven manually-operated switches with SCADA-operable switches, install one new SCADA-operable switch and replace associated existing structures with Engineered Direct Embedded Poles (Steels). The switches include: Ignacio-Bolinas 60 kV Line Number (No.) 2 Switches (SWs) 25, 27, 29, 57, 59 (SW 25 is new), Valley Springs 60 kV Line No. 1 SW 17, Valley Springs-Martell 60 kV Line No. 1 SW 75 and Valley Springs 60 kV Line No. 2 SW 19. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-07-08 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5530439 | T.0004062 | Central Bundle C-24 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-04-15 | 2020-10-31 | 2020-10-26 | NA | NA | FALSE | 5190 | NA ¦ NA | 4430.5256 | 4430.5256 | 4296.4034 | 43.4024 | 0.2809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4430.5256 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 4177.6573 | 42.2276 | 0.27332 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2471 | Central Bundle C-25 |  |  | Calaveras ¦ Linden CDP, San Joaquin ¦ Rancho Calaveras CDP, Calaveras ¦ San Joaquin ¦ Valley Springs CDP, Calaveras | This project proposes to replace the following manually operated switches and existing structures with SCADA- operable switches and Engineered Direct Embedded Poles (Steel): Fort Ross-Gualala 60kV Line Switch Nos. 47 and 49, and Mendocino-Hartley 60kV Line Switch Nos. 17 and 19. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-24 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5530440 | T.0004063 | Central Bundle C-25 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-11 | 2020-10-31 | 2020-05-28 | NA | NA | FALSE | 3005 | NA ¦ NA | 2298.3071 | 2298.3071 | 2200.6497 | 57.7483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2298.3071 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 2140.001 | 56.1852 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2472 | Central Bundle C-26 |  |  | San Joaquin ¦ Stockton, San Joaquin | This project proposes to replace the following manually operated switches and the existing structures with SCADA- operable switches mounted on Engineered Direct Embedded Poles (Steel): Ignacio-Alto-Sausalito No. 1 60 kV Line Switch Nos. 67 and 69, Ignacio-Bolinas No. 1 60 kV Line Switch Nos. 47 and 49, and Christie-Willow Pass 60 kV Line Switch Nos. 47 and 59. The project will also install two, new SCADA-operable switches mount on Steel poles: Ignacio-Alto-Sausalito No. 2 60 kV Line Switch Nos. 84 and 85. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-10 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530441 | T.0004064 | Central Bundle C-26 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6186-E | 2021-05-04 | Approved | 2022 | Operational | 2 | 2020-10-06 | 2020-12-31 | 2022-08-12 | Prioritization | NA | TRUE | 5650 | NA ¦ NA | 14093.1696 | 14204.6547 | 2234.6679 | 1557.5436 | 7014.2463 | 3070.2906 | 101.5868 | 157.8411 | 0 | 0 | 0 | 0 | 14046.8136 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 2172.3243 | 1515.3825 | 6824.3788 | 2987.1812 | 98.837 | 45.1012 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2473 | Central Bundle C-27 |  |  | French Camp CDP, San Joaquin ¦ Lathrop, San Joaquin ¦ Manteca, San Joaquin ¦ San Joaquin | This project proposes to retrofit the following manually operated switches to be SCADA-operable switches: Santa Rosa-Corona 115 kV Line Switch Nos.127, 129, 147, and 149 and add two (2) new SCADA-operable switches on the Cortina-Mendocino No. l 115 kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-11-24 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530442 | T.0004065 | Central Bundle C-27 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2020-10-29 | 2020-12-31 | 2028-10-12 | Prioritization | NA | TRUE | 4670 | NA ¦ NA | 4900.9616 | 5938.8616 | 2546.3342 | 1213.0014 | 1061.8977 | 14.1841 | 10.4627 | 491.366 | 0 | 0 | 0 | 546.534 | 4900.9616 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2028 | 2499.3894 | 1191.1117 | 1042.7348 | 13.9281 | 10.2739 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2474 | Central Bundle C-28 |  |  | Dogtown CDP, San Joaquin ¦ Lockeford CDP, San Joaquin ¦ Lodi, San Joaquin ¦ San Joaquin ¦ Thornton CDP, San Joaquin ¦ Woodbridge CDP, San Joaquin | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: SILVERADO-FULTON JCT 115 kV (SW 165, 187, & 189) FULTON-PUEBLO 115 kV (SW 117, 137, 155, & 179) EAGLE ROCK-FULTON-SILVERADO 115 kV (SW 129) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-07 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530443 | T.0004066 | Central Bundle C-28 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-11-12 | 2023-01-27 | 2027-11-30 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 1919.4891 | 4887.7753 | -9.8454 | 370.317 | 1351.1885 | 78.3205 | 41.9435 | 1896.9278 | 0 | 0 | 0 | 0 | 1919.4891 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | -9.8454 | 370.317 | 1351.1885 | 78.3205 | 41.9435 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2475 | Central Bundle C-29 |  |  | Fremont, Alameda ¦ Milpitas, Santa Clara ¦ San Jose, Santa Clara | Wave 3 Transmission Line SCADA Switch Program: Replace SWs 199, 137, & 139 with SCADA SWs on SAN JOSE B-STONE-EVERGREEN 115 kV line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2020-08-07 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 | NA | 180 | 9. Reliability (Low Safety Risk) | NA | 4.0211 | Future IGP Scope | 5530444 | T.0004068 | CENTRAL BUNDLE C-29 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2029-03-08 | 2023-04-19 | 2029-03-26 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 581.508 | 5117.7127 | 30.2411 | 310.3838 | 107.2813 | 22.9129 | 10.7206 | 729.0717 | 0 | 0 | 0 | 279.151 | 581.508 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2029 | 30.2411 | 310.3838 | 107.2813 | 22.9129 | 10.7206 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2476 | CENTRAL BUNDLE C-30 |  |  | Alameda ¦ Contra Costa | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: MONTA VISTA-BURNS 60 kV (SW 27) PERMANENTE #2 TAP 60 kV (SW 39) PERMANENTE #1 TAP 60 kV (SW 47) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-09-28 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530445 | T.0004069 | Central Bundle C-30 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-11-17 | 2023-02-16 | 2027-12-02 | Prioritization | NA | FALSE | 154700 | NA ¦ NA | 393.6065 | 2811.4412 | -9.3679 | 57.2326 | 254.2546 | 38.0217 | 10.4627 | 0.399 | 0 | 0 | 0 | 0 | 393.6065 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | -9.3679 | 57.2326 | 254.2546 | 38.0217 | 10.4627 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2477 | CENTRAL BUNDLE C-31 |  |  | Contra Costa ¦ El Cerrito, Contra Costa ¦ El Sobrante CDP, Contra Costa ¦ Hercules, Contra Costa ¦ Pinole, Contra Costa ¦ Richmond, Contra Costa ¦ Rodeo CDP, Contra Costa | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: Pine Grove Tap 60 kV (SW 25) Beardsley Tap 115 kV (SW 139) Donnells-MiWuk 115 kV (SW 137) Melones-Curtis 115 kV (SWs 147, 149, & 137) Fulton-Molino-Cotati 60 kV (SW 15 & 2 new SWs) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-28 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather ¦ Heat Wave |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530499 | T.0004070 | Central Bundle C-31 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2028-01-12 | 2023-04-11 | 2028-02-08 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 986.204 | 11340.3041 | 0.6028 | 382.325 | 621.1282 | -166.286 | 137.5124 | 4753.9499 | 0 | 0 | 0 | 5497.058 | 986.0021 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2028 | 0.60279 | 382.325 | 621.1282 | -166.286 | 137.5124 | 0.20192 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2478 | CENTRAL BUNDLE C-32 |  |  | Mendocino ¦ Sea Ranch CDP, Mendocino ¦ Sea Ranch CDP, Sonoma ¦ Sonoma ¦ Timber Cove CDP, Sonoma | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: ELK-GUALALA 60 kV (SW 69) FULTON-HOPLAND 60 kV (SW 47, 55, 57, & 89) WINDSOR-FITCH MOUNTAIN 60 kV (SW 67, 69, 77, & 87) GEYSERS #3-CLOVERDALE 115 kV (SWs 157 & 159) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-02 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530501 | T.0004071 | Central Bundle C-32 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2022-07-07 | 2023-04-28 | 2026-11-20 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 1971.3109 | 4185.368 | 4.0572 | 248.6214 | 1604.9242 | -51.5113 | 128.6753 | 2.3608 | 0 | 0 | 0 | 4185.368 | 1968.9501 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 4.0572 | 248.6214 | 1604.9242 | -51.5113 | 128.6753 | 2.3608 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2479 | CENTRAL BUNDLE C-35 |  |  | Lake ¦ Mendocino | Wave 3 Transmission Line SCADA Switch Program: • Retrofit existing structure 006/128 SW 17 on Cordelia Tap #2 60 kV line to be SCADA operable. • Replace existing structure 006/015 SW 19 on Tulucay-Napa #1 60 kV line with a SCADA operable switch structure. • Retrofit existing structure 001/011C 3-Way SW 155, 157, & 159 on Mission Power Tap 115kV and Geyers #3-Cloverdale 115kV lines to be SCADA operable. • Replace existing structure 004/097 SW 39 on Palermo-Oroville #1 60 kV line with a SCADA operable switch structure. • Replace existing structure 005/126 SW 27 on Kilarc-Cedar Creek 60 kV line with a SCADA operable switch structure. • 004/036 SW 327 (New) on the Trinity-Cottonwood 115 kV line • 004/038 SW 329 (New) on the Trinity-Cottonwood 115 kV line • 003/093 SW 39 on the Colgate-Allegany 60kV line • 003/089 SW 47 on the Colgate-Grass Valley 60 kV line • 008/212 SW 47 on the Drum-Spaulding 60 kV line • 008/214 SW 49 on the Drum-Spaulding 60 kV line | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-07 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5530503 | T.0004074 | Central Bundle C-35 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-06-01 | 2021-11-15 | 2021-11-15 | NA | NA | FALSE | 154700 | NA ¦ NA | 6784.8662 | 6784.8662 | -2.7361 | 6716.3922 | 38.0746 | -0.0005 | 0 | 0 | 0 | 0 | 0 | 0 | 6784.8662 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | -2.7361 | 6533.7653 | 37.044 | -0.00049 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2480 | North Bundle N-18 |  |  | Palermo CDP, Butte ¦ Plumas | This project proposes to replace the following four manually operated switches and the associated existing structures with SCADA-operable switches and Engineered Direct Embedded Poles (Steel): • Coleman-Red Bluff 60 kV Line Switch #67 and #69 • Cottonwood #2 60 kV Line Switch #57 and #69 The project will also install four, new SCADA-operable switches mounted on Steel poles: • Cottonwood #2 60 kV Line Switch #59 • Red Bank 60 kV Tap Switch #67 • Bridgeville-Cottonwood 115 kV Line Switch #239 • Cascade-Cottonwood 115 kV Line Switch #137 | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-06-28 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5530505 | T.0004076 | North Bundle N-18 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-04-19 | 2020-12-31 | 2021-01-16 | NA | NA | FALSE | 6600 | NA ¦ NA | 4411.0674 | 4411.0674 | 4041.7954 | 255.1438 | 5.1239 | 49.3054 | 0 | 0 | 0 | 0 | 0 | 0 | 4411.0674 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 3958.5288 | 249.9641 | 5.0199 | 48.3044 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2481 | North Bundle N-19 |  |  | East Quincy CDP, Plumas ¦ Plumas ¦ Quincy CDP, Plumas ¦ Twain CDP, Plumas | This project proposes to replace a total of five manually operated switches with SCADA-operable switches and replace associated existing structures with Engineered Direct Embedded Poles (Steels). The switches include: • Smartville-Marysville 60 kV Line Switch #37 and 39 • Caribou-Plumas Jct 60 kV Line Switch #15, #25, and #95 | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-01-27 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5530506 | T.0004077 | North Bundle N-19 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-04-19 | 2020-12-31 | 2021-02-04 | NA | NA | FALSE | 4240 | NA ¦ NA | 3308.2161 | 3308.2161 | 2924.1054 | 335.2428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3308.2161 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 2843.6298 | 326.168 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2482 | CENTRAL BUNDLE C-37 |  |  | Colusa ¦ Glenn ¦ Orland, Glenn ¦ Willows, Glenn | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: Pittsburg-Martinez #1 115 kV (SW 139) Pittsburg-Martinez #2 115 kV (SW 167, 169, 187, & 189) Oleum-Martinez 115 kV (SW 127 & 129) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-10-11 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530507 | T.0004078 | Central Bundle C-37 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2028-09-11 | 2024-12-15 | 2028-09-25 | Prioritization | NA | TRUE | 149600 | NA ¦ NA | 68.1722 | 6542.3296 | 19.718 | 16.2448 | 2.6558 | 0 | 10.4627 | 754.4671 | 0 | 0 | 0 | 0 | 68.1722 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2024 ¦ 2028 | 19.718 | 16.2448 | 2.6558 | 0 | 10.4627 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2483 | CENTRAL BUNDLE C-38 |  |  | Arcata, Humboldt ¦ Humboldt ¦ Indianola CDP, Humboldt ¦ Manila CDP, Humboldt ¦ Samoa CDP, Humboldt | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: Christie-Franklin #1 60 kV (SW 57 & 59) OLEUM-G #1 115 kV (SW 117 & 119) OLEUM-G #2 115 kV (SW 127 & 129) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-11-21 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530508 | T.0004079 | Central Bundle C-38 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2028-09-12 | 2024-12-15 | 2028-09-25 | Prioritization | NA | TRUE | 149600 | NA ¦ NA | 83.9328 | 3291.8965 | 48.0825 | 7.6406 | 7.7383 | 0 | 0 | 942.0916 | 0 | 0 | 0 | 0 | 83.9328 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2028 | 48.0825 | 7.6406 | 7.7383 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2484 | CENTRAL BUNDLE C-39 |  |  | Meridian CDP, Sutter ¦ Sutter ¦ Sutter CDP, Sutter ¦ Yuba City, Sutter | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: BELLOTA-RIVERBANK-MELONES SW STA 115 kV (SW 157 & 159) STANISLAUS-MELONES SW STA-MANTECA #1 115 kV (SW 147 & 149) STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA 115 kV (SW 165) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-05-09 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530509 | T.0004080 | Central Bundle C-39 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-07-02 | 2024-12-15 | 2027-07-02 | Prioritization | NA | TRUE | 149600 | NA ¦ NA | 47.0345 | 2695.468 | 5.4897 | 7.3547 | 2.6558 | 0 | 0 | 577.4236 | 0 | 0 | 0 | 0 | 47.0345 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2027 | 5.4897 | 7.3547 | 2.6558 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2485 | NORTH BUNDLE N-20 |  |  | Cameron Park CDP, El Dorado ¦ Diamond Springs CDP, El Dorado ¦ El Dorado ¦ El Dorado Hills CDP, El Dorado ¦ Folsom, Sacramento ¦ Shingle Springs CDP, El Dorado | This project proposes to replace the following two manually operated switches and the associated existing structures with SCADA-operable switches mounted on Engineered Direct Embedded Poles (Steel): • Maple Creek-Hoopa 60 kV Line Switch #17 • Kilarc-Cedar Creek 60 kV Line Switch #29 The project will also install five, new SCADA-operable switches mounted on Steel poles: • Hat Creek #1-Westwood 60 kV Line Switch #17, #19, #27 and #39 • Garberville-Laytonville 60 kV Line Switch north of Kekawaka Tap | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-10 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5530510 | T.0004082 | North Bundle N-20 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-02-06 | 2020-11-30 | 2021-04-21 | NA | NA | FALSE | 5590 | NA ¦ NA | 4034.2098 | 4034.2098 | 3882.4391 | 130.7238 | 1.6166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4034.2098 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 3847.2331 | 129.5444 | 1.6021 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2486 | CENTRAL BUNDLE C-40 |  |  | East Nicolaus CDP, Sutter ¦ Madison CDP, Yolo ¦ Nicolaus CDP, Sutter ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ Woodland, Yolo ¦ Yolo | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: SOBRANTE-G #1 115 kV (SW 119) SOBRANTE-GRIZZLY-CLAREMONT #1 115 kV (SW 159 & 1 New SW) SOBRANTE-GRIZZLY-CLAREMONT #2 115 kV (SW 149 & 165) SOBRANTE-R #1 115 kV (SW 137) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-12-08 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530511 | T.0004084 | Central Bundle C-40 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-08-27 | 2024-12-15 | 2027-08-27 | Prioritization | NA | TRUE | 149600 | NA ¦ NA | 45.4495 | 4275.1489 | 12.9437 | 10.9501 | 2.6558 | 0 | 0 | 191.2893 | 0 | 0 | 0 | 0 | 45.4495 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2027 ¦ 2028 | 12.9437 | 10.9501 | 2.6558 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2487 | NORTH BUNDLE N-21 |  |  | Marysville, Yuba ¦ Smartsville CDP, Yuba ¦ Yuba | Replace three manually-operated switches on the Cottonwood #1 and Palermo-Oroville #1 60 kV lines with SCADA-operable switches and install four new SCADA-operable switches on the Cottonwood #2 60 kV Line, with the associated structures replaced with Engineered Direct Embedded Poles (Steel). | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-03 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5530512 | T.0004085 | North Bundle N-21 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-11-16 | 2020-12-31 | 2020-12-21 | NA | NA | FALSE | 5170 | NA ¦ NA | 4255.809 | 4255.809 | 3948.8488 | 292.3135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4255.809 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 3948.8488 | 292.3135 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2488 | NORTH BUNDLE N-22 |  |  | Allendale CDP, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Yolo | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: BRUNSWICK #1 TAP 115 kV (SW 315) BRUNSWICK #2 TAP 115 kV (SW 325) COLGATE-ALLEGHANY 60 kV (SW 75) DRUM-GRASS VALLEY-WEIMAR 115 kV (SW 27 & 29) DRUM-HIGGINS 115 kV (SW 127) DRUM-RIO OSO #1 115 kV (SW 317 & 319) DRUM-RIO OSO #2 115 kV (SW 327 & 329) DRUM-SPAULDING 60 kV (SW 47 & 49) DUTCH FLAT #2 TAP 115 kV (SW 129) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-03-14 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530513 | T.0004086 | North Bundle N-22 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2021-07-26 | 2023-04-11 | 2026-09-18 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 3570.6981 | 4923.411 | 27.6842 | 1904.648 | 1257.5346 | 294.7781 | 69.373 | 2.3608 | 0 | 0 | 0 | 4923.411 | 3568.3373 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 27.6842 | 1710.9579 | 1132.4111 | 265.448 | 62.4704 | 2.1259 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2489 | NORTH BUNDLE N-23 |  |  | Arbuckle CDP, Colusa ¦ Colusa ¦ Yolo | The project objective is to replace and install the following structures with new SCADA operable switch structure: • 004/030 SW 317 & SW 327 on the El Dorado-Missouri Flat 1&2 115kV line. • 004/032 SW 319 & SW 329 on the El Dorado-Missouri Flat 1&2 115kV Line. • 010/092A SW 337 & SW 347 on the El Dorado-Missouri Flat 1&2 115kV Line. • 010/095A SW 339 & SW 349 on the El Dorado-Missouri Flat 1&2 115kV Line. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-10-01 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530514 | T.0004087 | North Bundle N-23 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-08-18 | 2024-12-15 | 2027-09-02 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 1874.4914 | 3757.886 | 11.8153 | 356.1187 | 1414.8231 | 51.9034 | 23.305 | 0 | 0 | 0 | 0 | 3757.886 | 1874.4914 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 11.8153 | 356.1187 | 1414.8231 | 51.9034 | 23.305 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2490 | NORTH BUNDLE N-25 |  |  | Shasta | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: PALERMO-OROVILLE #2 60 kV (SW 47 & 65) PALERMO-OROVILLE #1 60 kV (SW 39) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-06-09 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530516 | T.0004089 | North Bundle N-25 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-12-22 | 2022-05-31 | 2026-12-31 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 1326.4918 | 2377.1598 | 39.6276 | 178.7571 | 1028.001 | 50.7055 | 10.8514 | 285.202 | 0 | 0 | 0 | 765.466 | 1326.4918 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 39.6276 | 178.7571 | 1028.001 | 50.7055 | 10.8514 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2491 | NORTH BUNDLE N-26 |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: CLOVER CREEK TAP 115 kV (SW 25) KILARC-CEDAR CREEK 115 kV (SW 27) Trinity-Cottonwood 115 kV (2 New SWs) VOLTA-DESCHUTES 60 kV (SW 51, 57, & 59) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-05-02 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530517 | T.0004090 | North Bundle N-26 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-01-21 | 2022-03-21 | 2026-01-21 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 3078.1031 | 3078.1031 | 20.5594 | 1781.9137 | 1426.0494 | 6.6786 | -176.4684 | 2.4954 | 0 | 0 | 0 | 1287.1 | 3075.6077 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 20.5594 | 1781.9137 | 1426.0494 | 6.6786 | -176.4684 | 2.4954 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2492 | NORTH BUNDLE N-27 |  |  | Auburn, Placer ¦ North Auburn CDP, Placer ¦ Placer | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: CORDELIA #2 TAP 60 kV (SW 17) TULUCAY-NAPA #1 115 kV (SW 19) VACA-SUISUN 115 kV (177 & 179) VACA-SUISUN-JAMESON 115 kV (SW 167 & 169) VACA-VACAVILLE-CORDELIA 115 kV (SW 137 & 139) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-14 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 ¦ 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530518 | T.0004091 | North Bundle N-27 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-01-21 | 2022-08-08 | 2026-01-21 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 1307.25 | 2408.981 | 5.7582 | 93.9775 | 1055.7685 | 62.619 | 65.0556 | 2.3608 | 0 | 0 | 0 | 1312.431 | 1304.8892 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2026 | 5.7582 | 93.9775 | 1055.7685 | 62.619 | 65.0556 | 2.3608 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2493 | South Bundle S-28 |  |  | Corcoran, Kings ¦ Kings | Retrofit seven manually operated switches on the Balch-Sanger, Kings River-Sanger-Reedley, Cascade-Cottonwood, and Eagle Rock-Cortina 115kV lines, to be SCADA-operable switches | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-01 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5530369 | T.0004092 | South Bundle S-28 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-03-18 | 2020-05-31 | 2020-05-06 | NA | NA | FALSE | 3830 | NA ¦ NA | 2341.1204 | 2341.1204 | 2288.299 | 30.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2341.1204 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 2225.747 | 29.4672 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2494 | CENTRAL BUNDLE C-41 |  |  | Kern ¦ South Taft CDP, Kern ¦ Taft, Kern | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: STOCKTON "A" #1 60 kV (SW 27 & 47) NEW HOGAN TAP 60 kV (SW 35) TESLA-SALADO-MANTECA 115 kV (SW 179) VALLEY SPRINGS #2 60 kV (SW 87) VALLEY SPRINGS-CALAVERAS CEMENT 60 kV (SW 67, 69, & 1 New SW) WEST POINT-VALLEY SPRINGS 60 kV (SW 29) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-05-23 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530370 | T.0004093 | Central Bundle C-41 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2019-11-05 | 2024-12-15 | 2029-10-09 | Prioritization | NA | TRUE | 149600 | NA ¦ NA | 976.8606 | 6524.7085 | 35.4896 | 835.0477 | 66.6196 | 9.2692 | 10.4627 | 973.5119 | 0 | 0 | 0 | 152.92 | 976.8606 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2029 | 35.4896 | 835.0477 | 66.6196 | 9.2692 | 10.4627 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2495 | CENTRAL BUNDLE C-44 |  |  | Firebaugh, Fresno ¦ Fresno ¦ Madera | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: BRIONES TAP 60 kV (SW 35) PITTSBURG-COLUMBIA STEEL 115 kV (SW 197) PITTSBURG-KIRKER-COLUMBIA STEEL 115 kV (SW 109, `49, 187, & 1 New SW) Pittsburg-Clayton #3 115 kV (1 New SW) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-27 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530373 | T.0004096 | Central Bundle C-44 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-08-09 | 2024-12-15 | 2027-08-09 | Prioritization | NA | TRUE | 149600 | NA ¦ NA | 92.5095 | 1230.7898 | 30.7046 | 15.5806 | 2.6558 | 0 | 0 | 223.5942 | 0 | 0 | 0 | 0 | 92.5095 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2027 | 30.7046 | 15.5806 | 2.6558 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2496 | SOUTH BUNDLE S-29 |  |  | Fresno ¦ Sanger, Fresno | This project proposes to replace the following three manually operated switches and the associated existing structures with SCADA-operable switches mounted on Engineered Direct Embedded Poles (Steel): • Balch-Sanger 115 kV Line Switch #127, #129, and #147 The project will also install the following four new SCADA-operable switches mounted on Steel poles: • Divide-Cabrillo #2 115 kV Line Switch #127 and #129 • One new switch on the Kings River-Sanger-Reedley 115 kV Line at Piedra Junction • One new switch on the Exchequer-Yosemite 70 kV Line near Saxon Creek Tap | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-03-15 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | NA | NA | NA | 5530374 | T.0004097 | South Bundle S-29 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-05-20 | 2020-12-31 | 2021-07-19 | Prioritization | NA | FALSE | 5370 | NA ¦ NA | 4176.1264 | 4176.1264 | 3445.0504 | 711.0113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4176.1264 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 3378.0527 | 697.264 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2497 | CENTRAL BUNDLE C-45 |  |  | Fresno ¦ Sanger, Fresno | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: FULTON-PUEBLO 115 kV (SW 135, 145, & 177) EAGLE ROCK-FULTON-SILVERADO 115 kV (SW 157, 167, & 177) IONE TAP 60 kV (SW 29) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-03-15 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530375 | T.0004098 | Central Bundle C-45 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-11-16 | 2022-09-08 | 2027-12-02 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 1204.0661 | 5128.152 | 10.3562 | 343.2171 | 645.294 | 167.605 | 23.1738 | 0 | 0 | 0 | 0 | 2180.424 | 1204.0661 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 10.3562 | 343.2171 | 645.294 | 167.605 | 23.1738 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2498 | CENTRAL BUNDLE C-47 |  |  | Fresno ¦ Fresno, Fresno ¦ Madera ¦ Madera Ranchos CDP, Madera ¦ Rolling Hills CDP, Madera | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: Lakewood-Meadow Lane-Clayton 115 kV (2 New SWs) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-02-11 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530377 | T.0004100 | Central Bundle C-47 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2030-03-25 | 2024-12-15 | 2030-04-08 | Prioritization | NA | FALSE | 149600 | NA ¦ NA | 53.9506 | 1104.9725 | 23.61 | 9.4388 | 2.6558 | 0 | 0 | 10.4973 | 0 | 0 | 0 | 0 | 53.9506 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2030 | 23.61 | 9.4388 | 2.6558 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2499 | SOUTH BUNDLE S-30 |  |  | Kern ¦ South Taft CDP, Kern ¦ Taft, Kern | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: WISHON-SAN JOAQUIN #3 70 kV (SW 27 & 29) OAKHURST TAP 115 kV (SW 159) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-05-23 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 ¦ 70 | NA | 180 | 3. Emergency Preparedness | NA | 4.0211 | Future IGP Scope | 5530378 | T.0004101 | South Bundle S-30 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2028-10-10 | 2024-12-15 | 2029-04-09 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 1038.8822 | 1567.4694 | 12.1851 | 137.9343 | 952.0396 | -93.2128 | 13.1046 | 71.4342 | 0 | 0 | 0 | 331.641 | 1038.8822 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2029 | 12.1851 | 137.9343 | 952.0396 | -120.9808 | 12.7498 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2500 | Line Fuses: Remove Wood Pole at Arbuckle |  |  | Arbuckle CDP, Colusa ¦ Colusa ¦ Yolo | In conjunction with the emergency projects to transfer the Drake and Harrington 2.4 kV services from transmission to distribution and to install the mobile transformer at Dunnigan Substation, this project proposes to increase capacity at Dunnigan Substation from 8.6 MVA to 30 MVA as follows: • Expand the yard to the east property line to accommodate the new arrangement. • Modify the 60 kV transmission line ingress to match the new alignment of equipment. • Install one 60 kV circuit breaker. • Replace the control building. • Install a new 60/12 kV, 30 MVA load-tap-changing (LTC) transformer to replace Dunnigan Bank 1. • Install one 12 kV bus-tie breaker and three 12 kV feeder breakers in an open-air 12 kV double bus. • Install two new distribution feeders outside of the substation including the installation of 19,400 circuit feet of new distribution line and 35,000 circuit feet of reconductored distribution line. • Transfer the existing Dunnigan 1101 feeder from the old Transformer Bank 1 to the new Bank 1. • Remove the old 60/12 kV Bank 1, 1101 feeder breaker, 1101 voltage regulator, and the old 12 kV bus and support structures. | Transmission Line - Pole/Tower | Removal | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-10-01 | NA | NA | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | 5810075 | T.0005790 | Dunnigan: Repl 60/12kV Bank 1 | 2 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2025-02-01 | 2023-03-31 | 2025-03-06 | Scope Change | NA | FALSE | 43500 | NA ¦ NA | 98.5382 | 98.8338 | 0 | 0 | 0 | 0 | 23.2145 | 75.6192 | 0 | 0 | 0 | 0 | 23.2146 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2501 | North Bundle N-30 |  |  | Allendale CDP, Solano ¦ Hartley CDP, Solano ¦ Solano ¦ Vacaville, Solano ¦ Yolo | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: MADISON-VACA 115 kV (SW 159) Fulton JCT-Vaca 115 kV (SW 137 & 139) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2021-08-25 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541983 | T.0006522 | North Bundle N-30 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-05-26 | 2024-12-15 | 2026-12-31 | Prioritization | NA | TRUE | 149600 | NA ¦ NA | 14.3906 | 2653.8006 | 0.2193 | 11.5155 | 2.6558 | 0 | 0 | 246.3043 | 0 | 0 | 0 | 0 | 14.3906 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2026 ¦ 2027 | 0 | 11.7348 | 2.6558 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2502 | North Bundle N-31 |  |  | Humboldt ¦ Junction City CDP, Trinity ¦ Trinity ¦ Weaverville CDP, Trinity | Wave 3 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: JANES CREEK TAP 60 kV (SW 71) BRIDGEVILLE-COTTONWOOD 115 kV (SW 237) TRINITY-MAPLE CREEK 60 kV (SW 67 & 69) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-06-10 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 115 ¦ 60 | NA | 180 | NA | NA | 4.0211 | Future IGP Scope | 5541984 | T.0006523 | North Bundle N-31 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2022-04-19 | 2022-03-18 | 2026-12-31 | Prioritization | NA | FALSE | 154700 | NA ¦ NA | 2252.6528 | 2252.6528 | 13.1642 | 283.5755 | 1888.4175 | 65.3758 | 2.1198 | 0 | 0 | 0 | 0 | 808.49 | 2252.6528 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2026 | 0 | 296.7397 | 1888.4175 | 65.3758 | 2.1198 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2503 | North Bundle N-33 |  |  | Auburn, Placer ¦ Folsom, Sacramento ¦ Granite Bay CDP, Placer ¦ Placer | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: FLINT TAP 115 kV (SW 115 & 125) HALSEY-PLACER 60 kV (SW 49) PLACER-GOLD HILL #1 115 kV (SW 117, 119, 337, & 339) PLACER-GOLD HILL #2 115 kV (127, 129, 347, & 349) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-01-22 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 115 ¦ 60 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541986 | T.0006525 | North Bundle N-33 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-04-01 | 2024-12-15 | 2027-04-01 | Prioritization | NA | TRUE | 149600 | NA ¦ NA | 14.9138 | 6817.2326 | 0.4385 | 9.4754 | 4.9999 | 0 | 0 | 3634.2036 | 0 | 0 | 0 | 0 | 14.9138 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2027 | 0 | 9.9139 | 4.9999 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2504 | North Bundle N-34 |  |  | Corning, Tehama ¦ Cottonwood CDP, Shasta ¦ Gerber CDP, Tehama ¦ Las Flores CDP, Tehama ¦ Proberta CDP, Tehama ¦ Red Bluff, Tehama ¦ Shasta ¦ Tehama | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: COLEMAN-RED BLUFF 60 kV (SW 69) COTTONWOOD #1 60 kV (SW 3, 15, & 59) ORO FINO TAP 60 kV (SW 25) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-07 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541987 | T.0006526 | North Bundle N-34 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-01-25 | 2024-12-15 | 2027-01-25 | Prioritization | NA | FALSE | 149600 | NA ¦ NA | 410.1534 | 2509.138 | 0.4385 | 108.9524 | 293.7463 | 7.0161 | 0 | 0 | 0 | 0 | 0 | 0 | 410.1534 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2027 | 0 | 109.391 | 293.7463 | 7.0161 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2505 | North Bundle N-35 |  |  | Chester CDP, Plumas | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: HAMILTON BRANCH-CHESTER 60 kV (SW 99) COLLINS PINE TAP 60 kV (SW 25 | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-08-17 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541988 | T.0006527 | North Bundle N-35 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-04-02 | 2024-12-15 | 2027-04-02 | Prioritization | NA | FALSE | 149600 | NA ¦ NA | 10.7086 | 1004.0201 | 0 | 8.0528 | 2.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7086 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2027 | 0 | 8.0528 | 2.6558 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2506 | North Bundle N-36 |  |  | East Quincy CDP, Plumas ¦ Plumas ¦ Quincy CDP, Plumas ¦ Twain CDP, Plumas | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: CARIBOU-PLUMAS JCT 60 kV (SW 65, 69, 79, & 91) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-01-27 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541989 | T.0006528 | North Bundle N-36 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-04-02 | 2024-12-15 | 2027-04-02 | Prioritization | NA | FALSE | 149600 | NA ¦ NA | 13.0367 | 2182.2463 | 0 | 10.3809 | 2.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0367 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2027 | 0 | 10.3809 | 2.6558 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2507 | North Bundle N-38 |  |  | Beale AFB CDP, Yuba ¦ East Nicolaus CDP, Sutter ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Smartsville CDP, Yuba ¦ Sutter ¦ Trowbridge CDP, Sutter ¦ Wheatland, Yuba ¦ Yuba | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: SMARTVILLE TAP 60 kV (SW 97) SMARTVILLE-CAMP FAR WEST 60 kV (SW 99) SMARTVILLE-NICOLAUS #1 60 kV (SW 59) SMARTVILLE-NICOLAUS #2 60 kV (SW 67 & 71) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-03-27 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541991 | T.0006530 | North Bundle N-38 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2027-04-01 | 2024-12-15 | 2027-04-01 | Prioritization | NA | TRUE | 149600 | NA ¦ NA | 182.6629 | 3853.6656 | 0 | 180.0071 | 2.6558 | 0 | 0 | 246.5517 | 0 | 0 | 0 | 0 | 182.6629 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2027 | 0 | 180.0071 | 2.6558 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2508 | North Bundle N-39 |  |  | Colusa ¦ Colusa, Colusa ¦ Princeton CDP, Colusa ¦ Williams, Colusa | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: CORTINA #4 60 kV (SW 19 & 27) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-11 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541992 | T.0006533 | North Bundle N-39 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-04-15 | 2024-12-15 | 2027-04-30 | Prioritization | NA | FALSE | 149600 | NA ¦ NA | 14.1366 | 1007.4482 | 0 | 7.7807 | 6.3559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.1366 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2027 | 0 | 7.7807 | 6.3559 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2509 | North Bundle N-41 |  |  | Cassel CDP, Shasta ¦ Shasta | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: HAT CREEK #1-PIT #1 60 kV (SW 69) PIT #3-PIT #1 230 kV (SW 217 & 219) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-06-21 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 230 ¦ 60 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541994 | T.0006535 | North Bundle N-41 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-02-16 | 2024-12-15 | 2027-02-16 | Prioritization | NA | TRUE | 149600 | NA ¦ NA | 12.3635 | 2616.1122 | 0 | 7.7057 | 4.6578 | 0 | 0 | 1537.2945 | 0 | 0 | 0 | 0 | 12.3635 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2027 | 0 | 7.7057 | 4.6578 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2510 | North Bundle N-42 |  |  | Manton CDP, Tehama ¦ Shasta ¦ Tehama | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: MTN GATE JCT-CASCADE 60 kV (SW 39) COLEMAN-SOUTH 60 kV (SW 15 & 45) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-06-05 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | NA | 60 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541995 | T.0006536 | North Bundle N-42 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-02-16 | 2024-12-15 | 2027-02-16 | Prioritization | NA | FALSE | 149600 | NA ¦ NA | 11.7505 | 1541.6728 | 0 | 9.0947 | 2.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7505 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2027 | 0 | 9.0947 | 2.6558 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2511 | South Bundle S-31 |  |  | Clovis, Fresno ¦ Fresno | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: KERCKHOFF-CLOVIS-SANGER #1 115 kV (SW 137, 139, 155, 157, 159, & 335) KERCKHOFF-CLOVIS-SANGER #2 115 kV (SW 147, 149, & 345) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-10-31 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541996 | T.0006537 | South Bundle S-31 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-06-01 | 2024-12-15 | 2027-06-01 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 61.3915 | 5899.806 | 18.4474 | 27.6671 | 15.277 | 0 | 0 | 477.9636 | 0 | 0 | 0 | 0 | 61.3915 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2027 | 0 | 46.1145 | 15.277 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2512 | South Bundle S-33 |  |  | Kern ¦ Lebec CDP, Kern | Wave 3 Transmission Line SCADA Switch Program: Replace SWs 47 & 69 with SCADA SWs on TEJON-LEBEC 70 kV Line | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-12-04 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541998 | T.0006539 | South Bundle S-33 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-08-19 | 2024-12-15 | 2027-12-31 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 433.0586 | 1245.4948 | 0.6378 | 72.8251 | 318.7319 | 40.6086 | 0.255 | 596.0831 | 0 | 0 | 0 | 0 | 433.0586 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2027 | 0 | 71.4744 | 310.1042 | 39.5094 | 0.24811 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2513 | South Bundle S-34 |  |  | Kern ¦ San Luis Obispo | Wave 4 Transmission Line SCADA Switch Program: Replace switches with SCADA switches on the following lines: ARCO-CHOLAME 70 kV (SW 65 & New Switch on 003/041) ARCO-POLONIO PASS PP 70 kV (SW 85) | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-06-15 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 70 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5541999 | T.0006540 | South Bundle S-34 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2030-10-06 | 2024-12-15 | 2030-11-19 | Prioritization | NA | FALSE | 154700 | NA ¦ NA | 363.9707 | 3039.8142 | 8.0656 | 56.9055 | 295.4161 | 4 | 0 | 8.2594 | 0 | 0 | 0 | 119.8671 | 363.9707 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2030 | 0 | 64.9711 | 295.4161 | 3.5834 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2514 | South Bundle S-36 |  |  | Fresno ¦ Sanger, Fresno | Wave 3 Transmission Line SCADA Switch Program: Replace SWs 135 & 145 with SCADA SWs on ARVIN EDISON TAP 115 kV Line | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-03-15 | NA | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | 4.0211 | Future IGP Scope | 5542001 | T.0006542 | South Bundle S-36 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2026-02-06 | 2024-12-15 | 2026-02-24 | Prioritization | NA | TRUE | 154700 | NA ¦ NA | 686 | 1700 | 0 | 31.9222 | 504.6422 | 137.2145 | 12 | 0 | 0 | 0 | 0 | 1014.3597 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 | 0 | 0 | 522.0401 | 133.5002 | 12.367 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2515 | Merced #1 El Nido Customer Switch Installation |  |  | Fresno ¦ Madera ¦ Merced | Install two new switches along the Merced #1 70 kV line to improve the reliability and cost of service to El Nido Customer. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-03-08 | 95 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 70 | NA | NA | NA | NA | 4.01 | In-flight Future Scope | EX112701 | TBD | TBD | TBD | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-06-01 | NA | 2030-03-04 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 28234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4988 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2516 | Husted Jct SW 47 and 49 Switch Capability Upgrades |  |  | Colusa ¦ Colusa, Colusa ¦ Williams, Colusa | Replace switch 47 and 49 with SCADA operable upgrades that have loop breaking and line dropping capabilities on Cortina #2 60kV. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-04-07 | 71 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | NA | NA | NA | 4.01 | In-flight Future Scope | EX112702 | TBD | TBD | TBD | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-06-01 | NA | 2030-02-28 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 3360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2517 | Re-locate and Replace Ripon Switch 339 and 337 |  |  | Ripon, San Joaquin ¦ San Joaquin ¦ Stanislaus | Relocate switch 337 and 339 to a more accessible location for safe and reliable operation. Replace both switches with SCADA operable upgrades. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2025-03-28 | 89 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | 115 | NA | NA | NA | NA | 3.0011 | In-flight Future Scope | EX112703 | TBD | TBD | TBD | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-06-01 | NA | 2031-02-28 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 6219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2073 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2518 | Ignacio-Alto 60KV ET Line CB |  |  | Novato, Marin | This project proposes to install one 60 kV circuit breaker with bypass switches to the Ignacio 60 kV Bus, in order to sectionalize the Ignacio-Alto 60 kV Line. This work will reduce the impact of transmission line outages to the customers fed from both Greenbrae and Novato Substations. The amount requested will cover the cost for advanced engineering and design and developing final project cost. It will also cover the cost of purchasing equipment with long lead times including CCVTs, disconnect switches, and steel, switch, and bus support structures. | Transmission Line - Switch | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-03-11 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 11.9486 | NA | 60 kV | 428 | NA | NA | NA | NA | 5737079 | P.04893 | IGNACIO/ ALTO- 60 KV LINE W/ CB | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2011 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2012-04-01 | 2015-12-15 | 2012-05-31 | NA | NA | FALSE | 1316.88 | NA ¦ NA | 3873.0331 | 3873.0331 | 13.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3873.0331 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 289.6522 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2519 | Red Bluff Sub - Cottonwd-Red Bluff |  |  | Red Bluff, Tehama | Rebuild the 16.5 miles-long Cottonwood-Red Bluff 60 kV Line and release the project to operations, The proposed project would rebuild the 16.5 mile Cottonwood-Red Bluff 60 kV line with new transmission poles and new conductor. The project scope of work includes the following:•Replace 304 transmission poles with 240 light duty steel poles (LDSPs), 7 tubular steel poles (TSPs), and 57 higher-class wood poles as identified by design.•Reconductor the Cottonwood-Red Bluff 60 kV line (16.5 miles) with 715 kcmil aluminum conductor.•Reroute a 3-pole section of the line to a new location and alignment. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NA | NA | 2025-02-14 | 81 | NA | Wires - Replacement Alternative | $40 Mil - $50 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.71356 | NA | 60 kV | 270 | NA | NA | NA | NA | 5781042 | T.0000456 | Cottonwood-Red Bluff Reconductor | 4 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2020-06-02 | 2019-12-27 | 2020-06-15 | NA | NA | FALSE | 47000 | NA ¦ NA | 61.3871 | 61.3871 | 44.5371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.3871 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 61.3871 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2520 | BELLVUE: Install 2-115 KV CB |  |  | Sonoma | This project proposes to install two new SCADA-operable 115 kV circuit breakers at Bellevue Substation. This project is needed to improve electric service reliability by reducing customer outage time and frequency at Bellevue, Penngrove and Stony Point substations. | Substation - Circuit Breaker | New | NA | EX113679 | Reliability | Substation Reliability | NA | NA | 2025-03-03 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.6531 | NA | 115 kV | 168 | 9. Reliability (Low Safety Risk) | 9 | 4.011 | In-flight Future Scope | 5743009 | T.0000555 | BELLEVUE SUB: INSTALL: 115KV CB | 4 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2030-10-10 | NA | 2031-01-15 | NA | NA | FALSE | NA | NA ¦ NA | 173.9785 | 3592.6614 | 73.4518 | 23.9617 | 10.6864 | 11.6599 | 5.9645 | 10.6642 | 0 | 0 | 0 | 0 | 173.9785 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2521 | BELLEVUE: Install CBs - CORONA END |  |  | Petaluma, Sonoma | This project proposes to install two new SCADA-operable 115 kV circuit breakers at Bellevue Substation. This project is needed to improve electric service reliability by reducing customer outage time and frequency at Bellevue, Penngrove and Stony Point substations. | Substation - Circuit Breaker | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-02-18 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.57982 | NA | 115 kV | NA | NA | NA | 4.011 | In-flight Future Scope | 5793878 | T.0000555 | BELLEVUE SUB: INSTALL: 115KV CB | 4 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 5 | 2031-07-30 | NA | 2031-09-24 | NA | NA | FALSE | NA | NA ¦ NA | 2.0762 | 155.8073 | 0.7742 | 0.9651 | 0.1265 | 0.1391 | 0.0712 | 0.1273 | 0 | 0 | 0 | 0 | 2.0762 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2522 | BELLEVUE: Install 2 115 kV CBs - CB 162 |  |  | Sonoma | This project proposes to install two new SCADA-operable 115 kV circuit breakers at Bellevue Substation. This project is needed to improve electric service reliability by reducing customer outage time and frequency at Bellevue, Penngrove and Stony Point substations. | Substation - Circuit Breaker | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-03-03 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.6531 | NA | 115 kV | NA | NA | NA | 4.011 | In-flight Future Scope | 5793876 | T.0000555 | BELLEVUE SUB: INSTALL: 115KV CB | 4 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 5 | 2031-03-19 | NA | 2031-09-12 | NA | NA | FALSE | NA | NA ¦ NA | 7.7063 | 768.3851 | 2.0845 | 4.3716 | 0.4696 | 0.5165 | 0.2642 | 0.4724 | 0 | 0 | 0 | 0 | 7.7063 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2523 | BELLEVUE: Install CBs - SANTA ROSA END |  |  | Santa Rosa, Sonoma | This project proposes to install two new SCADA-operable 115 kV circuit breakers at Bellevue Substation. This project is needed to improve electric service reliability by reducing customer outage time and frequency at Bellevue, Penngrove and Stony Point substations. | Substation - Circuit Breaker | New | NA | T.0009626 ¦ T.0002317 | Reliability | Substation Reliability | NA | NA | 2025-03-11 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.91804 | NA | 115 kV | NA | NA | NA | 4.011 | In-flight Future Scope | 5793877 | T.0000555 | BELLEVUE SUB: INSTALL: 115KV CB | 4 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 5 | 2031-06-25 | NA | 2031-06-25 | NA | NA | FALSE | NA | NA ¦ NA | 3.8336 | 2467.6517 | 1.7802 | 1.4314 | 0.2336 | 0.257 | 0.1314 | 0.235 | 0 | 0 | 0 | 0 | 3.8336 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2524 | WUK: Convert Ring Bus |  |  | Twain Harte CDP, Tuolumne | This project proposes to install two 115 kV circuit breakers at Mi-Wuk Substation and reconfigure the 115 kV bus in to a ring bus arrangement. In addition, this project will install three SCADA-operable switches at Spring Gap Junction. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-02-06 | NA | NA | Wires - Bus Upgrade Alternative | $10 Mil -$15 Mil | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.7875 | NA | 115 kV | 598 | NA | NA | NA | NA | 5767768 | T.0000587 | MI-WUK SUB: BREAKER INSTALLATION | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-03-12 | 2018-05-08 | 2018-12-17 | Project Design | NA | FALSE | 9240 | NA ¦ NA | 8507.8738 | 8507.8738 | 45.8427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8507.8738 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 44.9344 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2525 | COLUMBUS: Install 2-115 KV CBs |  |  | Bakersfield, Kern | Install two 115 kV circuit breakers with SCADA at Columbus Substation. | Substation - Circuit Breaker | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-04-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.3875 | NA | 115 kV | 247 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5768808 | T.0001209 | COLUMBUS SUB: INSTALL 2-115KV CIRCUIT | 3 | 94 | NA ¦ 5738859 ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-01 | 2019-02-05 | 2019-03-19 | NA | NA | FALSE | 8660 | NA ¦ NA | 5196.0527 | 5196.0527 | 336.3658 | 34.4701 | 0.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5196.0527 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 455.983 | 33.6026 | 0.33632 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2526 | COLUMBUS: INSTALL CB 122 |  |  | Bakersfield, Kern | Install two 115 kV circuit breakers with SCADA at Columbus Substation. | Substation - Circuit Breaker | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-04-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.3875 | NA | 115 kV | 247 | NA | NA | NA | NA | 5787178 | T.0001209 | COLUMBUS SUB: INSTALL 2-115KV CIRCUIT | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-10-01 | 2020-02-01 | 2020-04-21 | NA | NA | FALSE | 8660 | NA ¦ NA | 1556.9533 | 1556.9533 | 1183.0167 | -7.2533 | -0.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1556.9533 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 1412.2051 | -6.5409 | -0.06329 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2527 | COLUMBUS 115KV CB- SHOOFLY |  |  | Bakersfield, Kern | Install two 115 kV circuit breakers with SCADA at Columbus Substation. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-04-04 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 2.3875 | 115 | NA | 247 | NA | NA | NA | NA | 5775604 | T.0001209 | COLUMBUS SUB: INSTALL 2-115KV CIRCUIT | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-03-01 | 2020-02-01 | 2018-04-23 | NA | NA | FALSE | 8660 | NA ¦ NA | 419.6204 | 419.6204 | 24.9873 | 3.1923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419.6204 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 22.3418 | 2.8543 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2528 | OROVILLE: Inst Sectionalizing CBs Bus |  |  | Oroville, Butte | This project will install bus sectionalizing circuit breakers on the Oroville Substation 60kV loop bus that serves the 60/12kV Banks 1, 2 and 3. The breakers will replace bus-tie switches 89 and 97. The control building cannot accommodate the additional panels required for the new breakers; therefore, it will need to be replaced (likely as part of an in-flight D-SCADA project). | Substation - Circuit Breaker | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-02-07 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 0.75208 | NA | 60 kV | 598 | 9. Reliability (Low Safety Risk) | 10 | 4.011 | In-flight Future Scope | 5769942 | T.0001569 | Oroville:Inst Sectionalizg CBs on60kVBus | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2031-08-08 | NA | 2032-06-10 | NA | NA | FALSE | NA | NA ¦ NA | 313.5817 | 6464.7397 | 197.9642 | 30.9798 | 19.1486 | 21.016 | 10.7505 | 19.2213 | 0 | 0 | 0 | 0 | 313.5817 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2529 | PERRY SUB BANK 1- T-LINE SUPPORT |  |  | San Luis Obispo | This planned project is needed to maintain safe and reliable power to the customers served from Cambria Sub, and will provide the following benefits: • Removes seven oil filled tanks (4 transformers tanks, 3 regulator tanks), and replace them with one oil filled equipment (one 3-phase 70/12 kV, 16 MVA, with LTC). • Increase the existing distribution transformer capacity from 4.5 MVA to 16 MVA and allow accommodation for future load growth. • Provide a firm station at Perry (per request of Distribution Planning and Energy Solutions – two banks are required) • Improve employee safety by eliminating a possible catastrophic transformer failure due to equipment condition. • By eliminating Cambria Sub, this project also decreases the annual recurring maintenance costs by replacing the existing transformer and switches in a new location with newer equipment. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-04-04 | NA | NA | Wires - Replacement Alternative | $10 Mil -$15 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.85615 | NA | 70 kV | NA | NA | NA | NA | NA | 5798593 | T.0001652 | Perry Sub: Install New Bank 1 & Convert | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2023-05-01 | 2022-06-15 | 2023-05-01 | Prioritization | NA | FALSE | 7410 | NA ¦ NA | 220.8087 | 220.8087 | 0 | 7.6513 | 18.8123 | 193.625 | 0.72 | 0 | 0 | 0 | 0 | 0 | 220.8087 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 211.8284 | 0.69274 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2530 | Valley Springs: 60kV BAAH |  |  | Calaveras | This project will Install a Distribution Bank 3 60/12 kV, a 60 kV Breaker and a half (BAAH) Bay 5, a 12 kV Double Bus Single Breaker (DBSB) at Valley Springs Substation so to decommission North Branch Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-04-04 | 50 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 8.8736 | NA | 60 kV | 362 | 9. Reliability (Low Safety Risk) | 9 | NA | NA | 5788199 | T.0002197 | Valley Springs: Install New Bank | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-08-31 | 2021-11-01 | 2023-01-26 | Prioritization | NA | TRUE | 10000 | NA ¦ NA | 4622.1269 | 4622.1269 | 348.144 | 2278.0371 | 1714.0302 | 156.486 | 125.4297 | 0 | 0 | 0 | 0 | 0 | 4622.1269 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 4463.6238 | 124.4218 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $5 Mil - $10 Mil ¦ NA [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2531 | PURISIMA: Install 115 KV SCADA SW |  |  | Santa Barbara | It is recommended that the existing Purisima Switch Nos. 125 and 115 be replaced with SCADA-operable Motor Operated Air Switch (MOAS) switches. The installation of 115kV MOAS switches is needed to improve service reliability to customers served by Purisima and is expected to reduce sustained customer outage minutes by 214,383 annually. | Substation - Switch | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-02-04 | NA | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 0.86746 | NA | 115 kV | 107 | 9. Reliability (Low Safety Risk) | 12 | 4.011 | In-flight Future Scope | 5772327 | T.0002252 | Purisima 115 kV SCADA Switch Project | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2031-09-12 | NA | 2032-01-22 | NA | NA | FALSE | NA | NA ¦ NA | 16.1981 | 2106.026 | 0.9255 | 1.2417 | 0.9871 | 1.0856 | 0.5553 | 0.9929 | 0 | 0 | 0 | 0 | 16.1981 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2532 | VACA DIXON: Add Aux Breaker |  |  | Solano | Upgrade the existing 60kV Main and Auxiliary Bus configuration at Vaca-Dixon Sub by installing two new bays. The project plans to relocate the Vaca-Dixon #2 Line, CB 42 position to make space for a new Sectionalizing breaker. In addition a new 60kV bus parallel breaker will be installed to support the bus sectionalizing upgrade. The addition of the two new 60kV bays will be installed within PG&E property and should not require any fence relocation. | Substation - Circuit Breaker | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-03-05 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 42.1076 | NA | 60 kV | 270 | 9. Reliability (Low Safety Risk) | 4 | 4.011 | In-flight Future Scope | 5777339 | T.0003461 | Vaca Dixon 60 kV- Add Aux Breaker | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-04-06 | NA | 2034-02-09 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 12679.5269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2533 | WEST SACRAMENTO: Add CB or Sectionalizer |  |  | West Sacramento, Yolo | This project plans to replace SW 347 and Circuit Switcher 349 with 115kV circuit breakers, associated structures and disconnect switches. This project is part of Substation Asset Strategy’s Transmission Bus Reliability Improvement Program. It proposes to improve the 115kV bus reliability at West Sacramento Substation by December 2026. West Sacramento Substation is a Distribution Substation that serves over 12,000 customers. The 115kV bus is arranged as an eight (8) element single bus configuration. The 115kV bus is comprised of three (3) distribution banks, three (3) 115kV transmission lines, and two (2) capacitors banks. During normal operation the distribution banks are separated by SW 347 and Circuit Switcher 349 keeping two banks connected to one bus section. That means any bank fault or faults in the bus could trip two banks, causing the sustained outage to about 7,000 customers. This arrangement does not provide protection for individual distribution transformer and makes it very difficult to get clearances. | Substation - Circuit Breaker | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-02-12 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.303 | NA | 115 kV | 171 | 9. Reliability (Low Safety Risk) | 16 | 4.011 | In-flight Future Scope | 5777340 | T.0003462 | W Sac. 115 kV- Add CB or Sectionalizer | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2032-01-05 | NA | 2033-10-27 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 8498.2097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2534 | Chester Substation |  |  | East Shore CDP, Plumas | The purpose of the project is to improve the reliability performance of the Hamilton Branch-Chester 60kV transmission line. The scope of the project is to rebuild 12 miles of the Hamilton Branch-Chester 60kV line with a combination of direct embedded engineered steel poles (EDEP) and tubular steel poles (TSP) with galvanize finish for the majority of the route. Five locations where a distribution service is attached will require a fiber glass pole. The project will install new 397ACSR conductor for the transmission circuit and replace all existing distribution underbuild with 1/0ACSR tree wire. In addition, a new OPGW will be installed between structures 000/002 and 012/250. A new ADSS cable will be installed between structures 000/002 and 000/001 as well as between 012/250 and 012/251. The ADSS will then be routed to the control building at Hamilton Branch and Chester substations via a riser at structure 000/001 and 012/251 respectively. Also included in the scope is the external generation of Chester Substation during the 6-8 month construction schedule. This generation is necessary due to the 60kv circuit being the only feed to Chester Substation and providing Distribution service. The generator’s location will be at Collins Pine Lumber Company property and the Collins Pine 60kV Tap will act as a Distribution shoofly back to the Chester Substation main Distribution Feeder. The project will include upgrading or replacing 30 poles on this tap to upgrade the 60kv circuit to 397 in-lieu of the existing 2-6/1 ACSR. Scope: replace or upgrade poles 000/001 to 000/029. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-02-04 | 68 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 1.1317 | NA | 60 kV | NA | NA | NA | 4.011 | In-flight Future Scope | 5792884 | T.0003637 | Hamilton Branch - Chester Conductor Repl | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2026-01-06 | NA | 2034-02-06 | NA | NA | FALSE | NA | NA ¦ NA | 33.4659 | 1355.6804 | 0 | 12.0383 | 21.4276 | 0 | 0 | 2.0759 | 0 | 0 | 0 | 0 | 33.4659 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2535 | Hamilton Branch Substation |  |  | East Shore CDP, Plumas | The purpose of the project is to improve the reliability performance of the Hamilton Branch-Chester 60kV transmission line. The scope of the project is to rebuild 12 miles of the Hamilton Branch-Chester 60kV line with a combination of direct embedded engineered steel poles (EDEP) and tubular steel poles (TSP) with galvanize finish for the majority of the route. Five locations where a distribution service is attached will require a fiber glass pole. The project will install new 397ACSR conductor for the transmission circuit and replace all existing distribution underbuild with 1/0ACSR tree wire. In addition, a new OPGW will be installed between structures 000/002 and 012/250. A new ADSS cable will be installed between structures 000/002 and 000/001 as well as between 012/250 and 012/251. The ADSS will then be routed to the control building at Hamilton Branch and Chester substations via a riser at structure 000/001 and 012/251 respectively. Also included in the scope is the external generation of Chester Substation during the 6-8 month construction schedule. This generation is necessary due to the 60kv circuit being the only feed to Chester Substation and providing Distribution service. The generator’s location will be at Collins Pine Lumber Company property and the Collins Pine 60kV Tap will act as a Distribution shoofly back to the Chester Substation main Distribution Feeder. The project will include upgrading or replacing 30 poles on this tap to upgrade the 60kv circuit to 397 in-lieu of the existing 2-6/1 ACSR. Scope: replace or upgrade poles 000/001 to 000/029. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-02-04 | 68 | NA | TBD | TBD | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 1.13 | NA | 60 kV | NA | NA | NA | 4.011 | In-flight Future Scope | 5792883 | T.0003637 | Hamilton Branch - Chester Conductor Repl | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 5 | 2026-01-06 | NA | 2032-07-07 | NA | NA | FALSE | NA | NA ¦ NA | 107.5535 | 848.4014 | 0 | 14.9524 | 92.6011 | 0 | 0 | 6.6717 | 0 | 0 | 0 | 0 | 107.5535 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2536 | Redbud: Install Bus Sect CB |  |  | Clearlake Oaks CDP, Lake | These projects will replace the fused disconnect switches on Banks 1 & 3 with a sectionalizing breaker and upgrade the relays and controls at Redbud Substation to enable rapid shut-off and restoration of customers triggered by a PSPS event. This project is needed to maintain safe and reliable power to electric customers served from Redbud Substation and provides the following benefits: • Mitigates impacts to customers during a PSPS event by increasing operating flexibility and by facilitating more rapid shut off and restoration of electric substation equipment • Improve employee safety by enhancing visibility, control, and coordination of devices in the electric transmission system • Help achieve goals of the Wildfire Safety Program; namely reduce the risk and customer impacts of wildfires | Substation - Circuit Breaker | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-02-10 | NA | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 3.1825 | NA | 115 kV | NA | NA | NA | 4.011 | In-flight Future Scope | 5801329 | T.0005771 | Redbud - Replace Bank 3 Fuse PSPS Relay | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-06-05 | 2022-12-03 | 2025-12-31 | Prioritization | NA | TRUE | 5530 | NA ¦ NA | 20.7216 | 2575.7921 | 0 | 0 | 11.6018 | 7.7701 | 0.6483 | 2355.772 | 195.4925 | 0 | 0 | 0 | 20.0201 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2537 | Paradise Term Upg - Wyn Reconfig |  |  | Paradise, Butte | This project proposes to complete the removal of the Caribou-Palermo 115kV Line by removing abandoned lattice steel tower structures and assessing the remaining towers supporting other transmission lines and replacing or strengthening these towers if needed. To mitigate the risk of Wyandotte being single sourced, this project proposes to reconfigure Wyandotte Substation to utilize the Paradise-Table Mountain 115kV circuit as a backup source. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-04-07 | 21 | NA | Other - Deferral | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.79098 | NA | 115 kV | NA | NA | NA | NA | NA | 5796196 | T.0006251 | Caribou-Palermo 10391 Remove Structures | 5 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-02-01 | 2021-12-31 | 2022-05-27 | NA | NA | FALSE | 20700 | NA ¦ NA | 2356.1999 | 2356.1999 | 0 | 292.1829 | 1573.6231 | 480.6199 | 9.774 | 0 | 0 | 0 | 0 | 0 | 2356.1999 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 1762.5868 | 453.7975 | 9.2286 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2538 | Table Mtn Term Upg - Wyn Reconfig |  |  | Butte | This project proposes to complete the removal of the Caribou-Palermo 115kV Line by removing abandoned lattice steel tower structures and assessing the remaining towers supporting other transmission lines and replacing or strengthening these towers if needed. To mitigate the risk of Wyandotte being single sourced, this project proposes to reconfigure Wyandotte Substation to utilize the Paradise-Table Mountain 115kV circuit as a backup source. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-03-13 | 20 | NA | Other - Deferral | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 47.516 | NA | 115 kV | NA | NA | NA | NA | NA | 5796197 | T.0006251 | Caribou-Palermo 10391 Remove Structures | 5 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-03-15 | 2021-12-31 | 2022-05-27 | NA | NA | FALSE | 20700 | NA ¦ NA | 876.4766 | 876.4766 | 0 | 247.7217 | 614.2931 | 13.1837 | 1.2781 | 0 | 0 | 0 | 0 | 0 | 876.4766 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 778.5563 | 11.8877 | 1.1524 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2539 | WyandotteTerm Upg - Wyn Reconfig |  |  | South Oroville CDP, Butte | This project proposes to complete the removal of the Caribou-Palermo 115kV Line by removing abandoned lattice steel tower structures and assessing the remaining towers supporting other transmission lines and replacing or strengthening these towers if needed. To mitigate the risk of Wyandotte being single sourced, this project proposes to reconfigure Wyandotte Substation to utilize the Paradise-Table Mountain 115kV circuit as a backup source. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-04-04 | 14 | NA | Other - Deferral | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 2.2226 | NA | 115 kV | NA | NA | NA | NA | NA | 5796195 | T.0006251 | Caribou-Palermo 10391 Remove Structures | 5 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-12-06 | 2021-12-31 | 2022-05-27 | NA | NA | FALSE | 20700 | NA ¦ NA | 1146.8025 | 1146.8025 | 0 | 509.1436 | 635.3481 | 2.3108 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.8025 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2025 | 0 | 0 | 1066.5583 | 2.15 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2540 | PALERMO SUB: INSTALL 115KV AUX CB |  |  | Palermo CDP, Butte | The project scope of work includes following: • Install 115kV a Bus Tie Breaker and associated structure and switches • Install 115kV Breaker and associated structure and switches • Install new foundations • Install controls and protection equipment • Upgrade ground grid as required • Extending 115kV Bus • Extend Fence | Substation - Circuit Breaker | New | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-03-19 | NA | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 8.0464 | NA | 115 kV | NA | NA | NA | NA | NA | 5799371 | T.0006252 | Palermo Sub: Install 115KV Aux CB | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-07-11 | 2023-05-31 | 2022-11-17 | NA | NA | FALSE | 7170 | NA ¦ NA | 3919.7465 | 3919.7465 | 11.1327 | 373.0903 | 3163.363 | 372.1604 | 0 | 0 | 0 | 0 | 0 | 0 | 3919.7465 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 384.223 | 2968.731 | 351.7425 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2541 | Humb Sub:Instl 115kV section CB& 2nd CB |  |  | Humboldt | The project scope of work includes following: Install 115 kV Bus Sectionalizing circuit breaker and associated equipment as required. Install second Aux circuit breaker and associated equipment as required. | Substation - Circuit Breaker | New | NA | T.0009597 ¦ EX111032 | Reliability | Substation Reliability | NA | NA | 2025-04-02 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 4.569 | NA | 115 kV | NA | NA | NA | 4.011 | In-flight Future Scope | 5796758 | T.0006372 | Humboldt - Install 115kv Sec & AUX CB | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-12-01 | NA | 2027-04-16 | NA | NA | FALSE | NA | NA ¦ NA | 1165.668 | 7393.6672 | 0 | 428.2879 | 498.345 | 59.3518 | 148.3121 | 245.773 | 500 | 0 | 0 | 0 | 1134.2968 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 ¦ 2027 | 0 | 428.2879 | 498.345 | 59.3518 | 148.3121 | 31.3712 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2542 | PAUL SWEET: EM INS SHOO-FLY 115KV |  |  | Live Oak CDP, Santa Cruz | Switch 157 failed to completely open during switching, and is currently left in the open position. A shoo-fly is planned for this work as well. This emergency project is to replace the switch with a new circuit switcher 376 and Vee switches 375, 395. | Transmission Line - Conductor | Relocate | NA | NA | Reliability | Substation Reliability | NA | NA | 2025-02-13 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.5678 | NA | 115 kV | NA | NA | NA | 4.011 | NA | 5548619 | T.0007845 | PAUL SWEET: EM REP MOAS 157 | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-02-25 | NA | 2024-06-22 | NA | NA | FALSE | NA | NA ¦ NA | 148.2524 | 148.2524 | 0 | 0 | 127.1946 | 6.7834 | 14.2745 | 0 | 0 | 0 | 0 | 0 | 148.2524 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 84.8252 | 4.5237 | 9.5195 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2543 | SYSPLN - MAT 94D |  |  | NA | Forecast placeholder for BAAH bus upgrades | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | NA | NA | NA | Other - Status Quo | NA | NA | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | NA | NA | NA | NA | NA | NA | 5.2 | Future IGP Scope | 5531484 | NA | NA | NA | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | NA | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 0 | 4592.5729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429.3343 | 163.2386 | 4000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2544 | COTTONWOOD: Improve 60 KV Bus |  |  | Cottonwood CDP, Shasta | This project proposes to convert the existing Cottonwood 60 kV Main-Auxiliary Buses into Double-Bus-Single-Breaker (DBSB). This project is needed to improve the electric transmission service to customers served from Cottonwood Substation, and will and will eliminate a single point of failure for the 2 transformers that serve the 60 kV bus. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-12 | 58 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | NA | 26.1945 | NA | 60 kV | 270 | 9. Reliability (Low Safety Risk) | NA | 5.2 | In-flight Future Scope | 5744979 | T.0000519 | COTTONWOOD SUB - 60KV BUS IMPROVEMENT | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2029-02-02 | NA | 2030-02-08 | NA | NA | FALSE | NA | NA ¦ NA | 167.7843 | 10534.6448 | 59.3062 | 12.1165 | 14.8913 | 11.2448 | 5.7521 | 10.2845 | 0 | 0 | 0 | 0 | 167.7843 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2545 | Land Purchase for Potrero |  |  | San Francisco, San Francisco | Replacement of 115/12kV, 45MVA Bank 2 with a 75MVA Bank and convert 115 KV Bus to GIS BAAH at Potrero Substation. This bank will be replaced as a part of the Potrero Substation rebuild project. The entire substation is recommended to be moved to north of Humboldt Street. | Other | Upgrade/Retrofit | NA | T.0002438 | Reliability | Bus Upgrade | NA | NA | 2025-03-12 | NA | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 5.647 | NA | NA | NA | NA | NA | 5.1001 | In-flight Future Scope | 5558807 | T.0000557 | POTRERO: CONVERT 115KV BUS TO GIS BAAH | 2 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Programmatic Work | NA | NA | NA | OAI | NA | NA | FALSE | NA | NA ¦ NA | 1533.1891 | 1533.1891 | 0 | 0 | 0 | 0 | 1533.1891 | 0 | 0 | 0 | 0 | 0 | 1533.1891 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 1533.1891 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | NA
| 2546 | POTRERO: CONVERT 115 KV BUS TO GIS BAAH |  |  | San Francisco, San Francisco | Replacement of 115/12kV, 45MVA Bank 2 with a 75MVA Bank and convert 115 KV Bus to GIS BAAH at Potrero Substation. This bank will be replaced as a part of the Potrero Substation rebuild project. The entire substation is recommended to be moved to north of Humboldt Street. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0002438 | Reliability | Bus Upgrade | NA | NA | 2025-03-12 | 34 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 5.647 | NA | 115 kV | 564 | 5a.Mitigates System Wide Failure Risk | 5 | 5.1001 | In-flight Future Scope | 5760988 | T.0000557 | POTRERO: CONVERT 115KV BUS TO GIS BAAH | 2 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2029-07-11 | NA | 2031-09-08 | NA | NA | FALSE | NA | NA ¦ NA | 2024.5163 | 173024.3956 | 109.1514 | 30.7987 | 656.4403 | 181.7928 | 143.5923 | 147.3405 | 0 | 0 | 0 | 0 | 2000.396 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | NA
| 2547 | HUNTERS POINT: Repl 115 KV GIS BAAH |  |  | San Francisco, San Francisco | This proposed project will rebuild the entire Hunters Point Substation about 2,000 feet from its current location but is still within the existing PG&E parcel. Rebuilding at a new site has many benefits based on lessons learned from other substation rebuild projects. Specific scope of work includes: • A new 115 kV bus using gas-insulated switchgear (GIS) in a breaker-and-a-half (BAAH) configuration, • 115 kV modular protection, automation, and control (MPAC) panels, • New 12 kV switchgear in a double-bus-double-breaker configuration, • Two new 115/12 kV substation transformers, • Spill prevention control and countermeasure (SPCC) facilities, and • Relocation and potentially undergrounding of the 115 kV transmission and 12 kV outlets. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0008764 | Reliability | Bus Upgrade | NA | NA | 2025-03-05 | 29 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 2.9037 | NA | 115 kV | 181 | 5a.Mitigates System Wide Failure Risk | 9 | 5.1 | In-flight Future Scope | 5752496 | T.0000590 | Hunters Point Substation | 4 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2015 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5483-E | 2019-02-13 | Approved | 2019 | Engineering more than 50% complete | 4 | 2030-01-10 | 2017-12-15 | 2032-07-16 | Prioritization | NA | FALSE | 190398 | NA ¦ NA | 42694.6248 | 276683.9619 | 5071.6679 | 5134.577 | 11801.7712 | 6997.0969 | 6044.3039 | -7050.1537 | 0 | 0 | 0 | 0 | 42152.45 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $200 Mil - $250 Mil
| 2548 | SANGER: Replace 115 KV Bus |  |  | Fresno | Install a new seven bay 115 kV BAAH bus, two MPAC buildings, and relocate all associated 115 kV lines at Sanger Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-02-07 | 20 | NA | Wires - Bus Upgrade Alternative | $50 Mil – $75 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 11.0513 | NA | 115 kV | 225 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5741360 | T.0000601 | Sanger Substation 115kV Bus Replacement | 4 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | Final Certified | 2017-07-13 | IS/MND | NA | CPUC | NA | PTC: A.15-09-012 | 2015-09-30 | Approved | 2017 | Operational | 2 | 2019-04-25 | 2019-12-31 | 2020-11-02 | Prioritization | NA | FALSE | 55300 | NA ¦ NA | 38198.2485 | 38198.2485 | 9830.3857 | 5330.994 | 78.7486 | 0.3371 | 0 | 0 | 0 | 0 | 0 | 0 | 38198.2485 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 30598.2789 | 4940.8772 | 72.986 | 0.3124 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2549 | RIO OSO: Repl 230 KV BAAH/GIS |  |  | Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-14 | 64 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.3219 | NA | 230 kV | 462 | 9. Reliability (Low Safety Risk) | NA | 5.2 | In-flight Future Scope | 5732785 | T.0000614 | Rio Oso Substation Upgrade | 11 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-08-25 | 2019-12-02 | 2024-12-29 | Prioritization | NA | TRUE | 264900 | NA ¦ NA | 109474.1505 | 120893.8135 | 5569.8569 | 19870.4131 | 30232.6822 | 17532.998 | 22135.651 | 8750.0226 | 3363.0744 | 1.888 | 0 | 0 | 108581.1405 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 106491.544 | 871.7541 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2550 | RIO OSO: Install 115 KV BAAH/GIS |  |  | Sutter | This project will resolve current configuration issues, address reliability and capacity concerns, and alleviate high- voltage issues at Rio Oso Substation. The upgrades to Rio Oso will also position the substation for future system reinforcement projects, enhanced automation, and additional controls of PG&E’s transmission system. This proposed project will rebuild Rio Oso Substation within the existing substation fence line. The project will include a 115kV and 230kV gas-insulated switchgear (GIS) in a breaker and a half (BAAH) configuration, and replacement of the two 230/115kV transformers with larger capacity units. This proposal will allow the project team to perform most of the work without interfering with the existing equipment. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-14 | 64 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 9.3219 | NA | 115 kV | 462 | 9. Reliability (Low Safety Risk) | NA | 5.2 | In-flight Future Scope | 5740958 | T.0000614 | Rio Oso Substation Upgrade | 11 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-10-28 | 2019-12-02 | 2024-12-29 | Prioritization | NA | TRUE | 264900 | NA ¦ NA | 74762.8901 | 81218.4399 | 3975.2109 | 13734.9676 | 15509.0442 | 14265.1842 | 15036.9839 | 5999.1594 | 1219.4014 | 4.052 | 0 | 0 | 73797.5025 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 ¦ 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 72255.1154 | 939.9123 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Minimum Required Scope (spot repair) Alternative ¦ Wires - Bus Upgrade Alternative ¦ Wires - Location/Route Alternative [Alternative Solutions and Costs - Costs] $200 Mil - $250 Mil ¦ $250 Mil – $300 Mil ¦ $250 Mil – $300 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2551 | El Cerrito - Fencing/Grading |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Substation - Structure | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-06 | NA | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 8.2538 | NA | 115 kV | NA | NA | NA | 5.1001 | In-flight Future Scope | 5799974 | T.0000636 | El Cerrito G Substation Rebuild | 7 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2024-10-30 | 2021-02-18 | 2025-03-24 | Prioritization | NA | FALSE | 94600 | NA ¦ NA | 124.7369 | 124.8826 | 0 | 0 | 29.3095 | 45.1669 | 50.2605 | 0.1457 | 0 | 0 | 0 | 0 | 124.7369 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2552 | EL CERRITO G: Upgrade 115 KV Bus Phase 1 |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-06 | NA | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 8.2538 | NA | 115 kV | 270 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5767958 | T.0000636 | El Cerrito G Substation Rebuild | 7 | 94 | NA ¦ 5746713 ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-04-25 | 2021-02-18 | 2020-01-27 | NA | NA | FALSE | 94600 | NA ¦ NA | 26411.1108 | 26411.1108 | 788.9472 | 107.2289 | 0.0581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26411.1108 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 25750.3622 | -26.9981 | 0.05629 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2553 | EL CERRITO G: Upgrade PACI RAS at VGCC |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-06 | NA | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 8.2538 | NA | 115 kV | 276 | 5a.Mitigates System Wide Failure Risk | 4 | NA | NA | 5768679 | T.0000636 | El Cerrito G Substation Rebuild | 7 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-02-09 | 2021-02-18 | 2021-02-18 | NA | NA | FALSE | 94600 | NA ¦ NA | 247.488 | 247.488 | 33.9908 | 102.1955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247.488 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2025 | 0 | 247.4881 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2554 | EL CERRITO G: Upgrade PACI RAS at SFCC |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Other - Remedial Action Scheme/Special Protection Scheme | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-06 | NA | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 8.2538 | NA | 115 kV | 276 | 5a.Mitigates System Wide Failure Risk | 4 | NA | NA | 5768778 | T.0000636 | El Cerrito G Substation Rebuild | 7 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-02-02 | 2021-02-18 | 2021-02-18 | NA | NA | FALSE | 94600 | NA ¦ NA | 283.3985 | 283.3985 | 50.3684 | 89.5034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283.3985 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2025 | 0 | 283.3986 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2555 | EL CERRITO G: Upgrade 115 KV Bus Phase 2 |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-06 | 63 | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 8.2538 | NA | 115 kV | 276 | 5a.Mitigates System Wide Failure Risk | 4 | NA | NA | 5767959 | T.0000636 | El Cerrito G Substation Rebuild | 7 | 94 | NA ¦ 5746713 ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-11 | 2021-02-18 | 2022-01-23 | Prioritization | NA | FALSE | 94600 | NA ¦ NA | 21408.0713 | 21408.0713 | 7482.4677 | 6079.2606 | 3677.5325 | 563.8597 | 40.8532 | 0 | 0 | 0 | 0 | 0 | 21408.0713 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 18626.8158 | 499.2134 | 36.1694 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2556 | EL CERRITO G: Upgrade 115 KV Bus |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-06 | 63 | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 8.2538 | NA | 115 kV | 276 | 5a.Mitigates System Wide Failure Risk | 4 | NA | NA | 5767962 | T.0000636 | El Cerrito G Substation Rebuild | 7 | 94 | NA ¦ 5746713 ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2016-12-06 | 2021-02-18 | 2022-01-23 | Prioritization | NA | FALSE | 94600 | NA ¦ NA | 2176.8706 | 2176.8706 | 158.2029 | 461.4965 | 6.7038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2176.8706 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2025 | 0 | 0 | 1923.6228 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2557 | El Cerrito G: 115kV BAAH Bay 4 |  |  | El Cerrito, Contra Costa | This project will rebuild the entire substation excluding the 34.5kV facilities serving BART. This project will replace three 115/12kV transformers with higher capacity units and upgrade the 115kV bus to a breaker-and-a-half (BAAH) configuration and the 12kV bus to a double-bus-double-breaker (DBDB) switchgear. The two transformers serving BART are lightly loaded and are in good working condition | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-06 | 73 | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Subsidence |  | NA | 8.2538 | NA | 115 kV | 276 | NA | NA | 5.1001 | In-flight Future Scope | 5795286 | T.0000636 | El Cerrito G Substation Rebuild | 7 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2024-01-12 | 2021-02-18 | 2024-12-18 | Prioritization | NA | TRUE | 94600 | NA ¦ NA | 17559.0175 | 19056.3214 | 0 | 147.8961 | 2345.6849 | 1261.0173 | 12149.4303 | 3152.2928 | 0 | 0 | 0 | 0 | 15904.0286 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2024 ¦ 2025 | 0 | 0 | 0 | 0 | 14850.897 | 1538.7079 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2558 | SOBRANTE: Add & Repl 14-115 KV Breakers |  |  | Orinda, Contra Costa | Install 115 kV automation equipment and rebuild the 115 kV facilities (buses, breakers, switches, and structure foundations) at Sobrante Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-04-03 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather ¦ Corrosion |  | NA | 11.0767 | NA | 115 kV | 127 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5770140 | T.0000654 | Sobrante Substation 115kV Upgrade | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2012 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2016-03-01 | 2018-05-07 | 2019-04-05 | Workforce | NA | FALSE | 34500 | NA ¦ NA | 16804.3475 | 16804.3475 | 338.7295 | 8.0778 | 33.1757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16804.3475 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 308.9492 | 7.3343 | 30.1223 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2559 | LERDO: Improve 115 KV Bus Reliability |  |  | Kern | The scope of work for this project is to replace the 115 kV breakers and bus with a new ring bus, and protection relays at Lerdo Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-04-04 | 61 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 1.3576 | NA | 115 kV | 110 | NA | NA | NA | NA | 5767822 | T.0000867 | LERDO 115KVB BUS REL. - T-LINE | 1 | 94 | NA ¦ 5747741 ¦ NA ¦ NA | TRUE | 2014 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2016-05-23 | 2017-04-10 | 2017-04-24 | NA | NA | FALSE | 9542.81 | NA ¦ NA | 10483.2889 | 10483.2889 | 52.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10483.2889 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | 50.1036 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2560 | LARKIN: Upgd 115 KV Reliability |  |  | San Francisco, San Francisco | Replacement of the existing 115 kV single bus to a five (5) bay Breaker-and-A-Half (BAAH) 115 kV Gas Insulated Switchgear ( GIS) configuration at Larkin Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0000603 | Reliability | Bus Upgrade | NA | NA | 2025-02-10 | 27 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 1.0478 | NA | 115 kV | 705 | 5a.Mitigates System Wide Failure Risk | 5 | 5.1001 | In-flight Future Scope | 5768170 | T.0000934 | LARKIN: 115KV RELIABILITY | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2032-07-16 | NA | 2034-10-23 | NA | NA | FALSE | NA | NA ¦ NA | 244.9102 | 91670.7416 | 60.403 | 28.7264 | 16.3149 | 16.4137 | 8.3962 | 15.2822 | 0 | 6410.5492 | 20000 | 35000 | 244.9102 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2561 | KERN PP: Convert 115 KV Bus to BAAH - Ph. 1 |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0000204 | Reliability | Bus Upgrade | NA | NA | 2025-04-03 | 72 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 37.7504 | NA | 115 kV | 705 | 5a.Mitigates System Wide Failure Risk | 10 | 5.1001 | In-flight Future Scope | 5770678 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA ¦ 5762085 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-10-01 | 2022-10-12 | 2025-01-09 | Prioritization | NA | TRUE | 77400 | NA ¦ NA | 40242.7257 | 42153.7905 | 6357.9332 | 9588.7026 | 10170.0783 | 2280.4259 | 5901.8651 | 2963.733 | 0 | 0 | 0 | 0 | 39190.0575 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 | 0 | 0 | 0 | 0 | 0 | 38505.3211 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2562 | KERN PP: CONV. 115kV BUS TO BAAH – Ph. 2 |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0000204 | Reliability | Bus Upgrade | NA | NA | 2025-04-03 | 73 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 37.7504 | NA | 115 kV | 705 | 5a. Mitigates System Wide Failure Risk | 10 | 5.1001 | In-flight Future Scope | 5787960 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2025-05-01 | 2022-10-12 | 2025-12-05 | Prioritization | NA | TRUE | 77400 | NA ¦ NA | 0 | 11757.0073 | 0 | 0 | 0 | 0 | 0 | 8270.7718 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2563 | KERN PP: CONV. 115kV BUS TO BAAH - Ph. 3 |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0000204 | Reliability | Bus Upgrade | NA | NA | 2025-04-03 | 73 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 37.7504 | NA | 115 kV | NA | 5a. Mitigates System Wide Failure Risk | 10 | 5.1 | In-flight Future Scope | 5787961 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-01-08 | 2022-10-12 | 2026-12-04 | Prioritization | NA | TRUE | 77400 | NA ¦ NA | 0 | 19953.9607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1610.1209 | 10406.6983 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2564 | KERN PP: CONV. 115kV BUS TO BAAH - Ph. 4 |  |  | Bakersfield, Kern | Upgrade the existing Kern PP Substation 115kV bus to a breaker-and-a-half (BAAH) configuration | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0000204 | Reliability | Bus Upgrade | NA | NA | 2025-04-03 | 73 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Extreme Heat |  | NA | 37.7504 | NA | 115 kV | NA | 5a. Mitigates System Wide Failure Risk | 10 | 5.1 | In-flight Future Scope | 5787962 | T.0000980 | KERN PP 115kV BAAH & MPAC | 11 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-11-01 | 2022-10-12 | 2027-12-13 | Prioritization | NA | FALSE | 77400 | NA ¦ NA | 0 | 20778.5421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17941.7808 | 2836.7613 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Wires - Bus Upgrade Alternative ¦ Wires - Minimum Required Scope (spot repair) Alternative ¦ Other - Deferral [Alternative Solutions and Costs - Costs] $150 Mil - $175 Mil ¦ $20 Mil - $30 Mil ¦ $125 Mil - $150 Mil [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2565 | MOUNT EDEN: Check 115 KV Bus Reliability |  |  | Hayward, Alameda | System Protection recommends that the backup relays at both ends be replaced with new SEL line differential relays with separate communication channel from the primary relay. Eastshore-Mt Eden #1 and #2 lines are short line slightly longer than 1.00 mile. For such a short line, one set of line differential relay plus another set of overcurrent relay configuration does not meet current PG&E protection standard and results in significant coordination problems when line differential protection is not available for any reason (e.g., relay or communication channel maintenance or failure). | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-10 | 65 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 1.6074 | NA | 115 kV | 270 | 9. Reliability (Low Safety Risk) | NA | 5.2 | In-flight Future Scope | 5757753 | T.0001212 | MT. EDEN 115 KV BUS RELIABILITY | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-02-13 | NA | 2032-06-29 | NA | NA | FALSE | NA | NA ¦ NA | 112.0224 | 4158.6604 | 17.4092 | 16.9159 | 42.6206 | 6.6329 | 15.1197 | 7.5021 | 0 | 0 | 0 | 0 | 110.6959 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2566 | MOSS LANDING: Convert 115 KV Bus to BAAH |  |  | Monterey | This project will replace the existing DBSB 115 kV bus with seven bays of BAAH configuration. The new 115kV BAAH bus will be located at the foot print of the old 230kV double bus single breaker site. The protection and controls of the new equipment will be moved to new MPAC buildings. | Substation - Multiple | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-04-07 | 35 | NA | Wires - Bus Upgrade Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 41.3213 | NA | 115 kV | 764 | NA | NA | NA | In-flight Future Scope | 5769268 | T.0001406 | Moss Landing 115kV BAAH | 2 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2017-02-02 | 2018-12-05 | 2018-07-27 | NA | NA | FALSE | 69500 | NA ¦ NA | 40385.725 | 40435.725 | 870.3856 | 73.4202 | 943.2072 | 44.8017 | 10.4627 | 50 | 0 | 0 | 0 | 0 | 40385.725 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 786.6067 | 66.3532 | 852.4189 | 40.4898 | 9.4556 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2567 | HICKS: Improve 230 KV Bus Reliability |  |  | San Jose, Santa Clara | To reduce customer interruptions at Hicks Substation, it is recommended to re-connect existing T-Line and distribution bank connections and install four new 230kV circuit breakers to build a six-breaker ring bus in conjunction with a new MPAC building. This will reduce System Average Interruption Duration Index (SAIDI) impacts affecting these 44,000 customers. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-02-06 | 46 | NA | Wires - Bus Upgrade Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.8635 | NA | 230 kV | 247 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5739142 | T.0001600 | HICKS SUB: 230 KV BUS REL IMPROV | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-09-17 | 2017-08-29 | 2021-11-04 | Prioritization | NA | FALSE | 21300 | NA ¦ NA | 15898.2897 | 15898.2897 | 4324.0054 | 4688.6254 | 564.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15898.2897 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 13990.2491 | 507.6014 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2568 | CALIENTE: Upgd Relay-Midway 230kV Remote |  |  | San Luis Obispo | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Line Termination | NA | NA | 2023-11-02 | 58 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | NA | NA | 230 kV | NA | 5a. Mitigates System Wide Failure Risk | 23 | 5.2 | In-flight Future Scope | 5537608 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (25%-50%) | 3 | 2021-04-08 | 2022-04-01 | 2028-05-24 | Prioritization | NA | FALSE | 105100 | NA ¦ NA | 304.8154 | 1564.6098 | 291.7344 | 12.0246 | 0.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304.8154 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2028 | 292.2657 | 12.0246 | 0.525 | -12.6486 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2569 | MIDWAY: UPGRADE 230 KV BUS SECT D PH 2 |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-04-07 | 48 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 230 kV | 705 | 5a.Mitigates System Wide Failure Risk | 9 | NA | NA | 5787769 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-11-10 | 2022-04-01 | 2021-11-10 | NA | NA | FALSE | 105100 | NA ¦ NA | 2163.4719 | 2163.4719 | 0.1364 | 2084.0326 | 72.2453 | 5.1745 | 0 | 0 | 0 | 0 | 0 | 0 | 2163.4719 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 1987.3353 | 67.1413 | 4.9226 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2570 | MIDWAY: UPGRADE 230 KV BUS SECT D PH 3 |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-04-07 | 49 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 230 kV | 705 | 5a.Mitigates System Wide Failure Risk | 9 | NA | In-flight Future Scope | 5787770 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2022-10-11 | 2022-04-01 | 2023-04-24 | Prioritization | NA | TRUE | 105100 | NA ¦ NA | 8096.3294 | 8152.3534 | 19.9223 | 3968.6785 | 1545.6632 | 2214.6159 | 326.3132 | 66.8671 | 0 | 0 | 0 | 0 | 8085.4863 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 7155.9371 | 298.8429 | 9.9303 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2571 | MIDWAY: Upgrade 230 KV Bus Section D |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-04-07 | 56 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 230 kV | 705 | 5a.Mitigates System Wide Failure Risk | 9 | 5.2 | In-flight Future Scope | 5768786 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Construction (50%-75%) | 3 | 2021-07-08 | 2022-04-01 | 2025-10-24 | Prioritization | NA | TRUE | 105100 | NA ¦ NA | 58855.6343 | 69118.2959 | 4339.9589 | 24534.8253 | 14799.3581 | 909.5321 | 6621.8974 | 10952.4682 | 911.9738 | 0 | 0 | 0 | 57253.8539 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2572 | MIDWAY: UPGRADE 230 KV BUS SECT D PH 4 |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-04-07 | 50 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 230 kV | 705 | 5a. Mitigates System Wide Failure Risk | 9 | 5.2 | In-flight Future Scope | 5787771 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2026-01-23 | 2022-04-01 | 2026-02-19 | Prioritization | NA | TRUE | 105100 | NA ¦ NA | 545.3294 | 10100.9843 | 0 | 91.9827 | 10.0103 | 9.6601 | 420.7332 | 46.134 | 2407.6515 | 3725.104 | 0 | 0 | 532.3863 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2026 ¦ 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2573 | MIDWAY: UPGRADE 230 KV BUS SECT D PH 5 |  |  | Buttonwillow CDP, Kern | Install seven bays (four full and three partial) of 230kV systems (new Bus Section D) and its connection to the existing 230kV bus at Midway Substation. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-04-07 | 50 | NA | Wires - Bus Upgrade Alternative | $125 Mil - $150 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence ¦ Heat Wave |  | NA | 94.5324 | NA | 230 kV | 705 | 5a. Mitigates System Wide Failure Risk | 9 | 5.2 | In-flight Future Scope | 5787772 | T.0001650 | Midway 230kV Bus Upgrade Section D | 12 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Engineering more than 50% complete | 4 | 2027-05-13 | 2022-04-01 | 2028-02-18 | Prioritization | NA | FALSE | 105100 | NA ¦ NA | 35.2632 | 22493.5015 | 0 | 26.026 | 1.8932 | 4.2426 | 1.0937 | 4.0387 | 309.738 | 7423.692 | 6295.02 | 5058.235 | 33.2557 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2574 | ASHLAN: Convert to 230 KV Ring Bus |  |  | Fresno, Fresno | This project will upgrade the existing 230kV bus from looped design to a ring bus design as well as install an MPAC building and upgrade protection at Ashlan, Herndon, Gregg, and Figarden substations. These upgrades will improve reliability, safety, and maintenance at Ashlan substation and the 230kV protection in the local area. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-07 | NA | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.6505 | NA | 230 kV | 270 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5772494 | T.0002362 | Ashlan Ave 230kV Bus Reliability | 7 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-04-09 | 2020-02-11 | 2020-02-20 | NA | NA | FALSE | 40900 | NA ¦ NA | 15814.8639 | 15814.8639 | 3181.2482 | 33.4246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15814.8639 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 15077.0839 | 31.8651 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2575 | ORO LOMA: Upgrade 70 KV Bus |  |  | Fresno | This project is part of Substation Asset Strategy’s Bus Reliability Improvement Program. It proposes to replace the 70kV single-bus with a ring-bus. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0000563 ¦ T.0000891 ¦ T.0001473 | Reliability | Bus Upgrade | NA | NA | 2025-04-04 | NA | NA | Wires - Bus Upgrade Alternative | $20 Mil - $30 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.8637 | NA | 70 kV | 705 | 9. Reliability (Low Safety Risk) | NA | NA | NA | 5776078 | T.0003408 | UPGRADE ORO LOMA 70KV BUS | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2019-11-19 | 2020-07-01 | 2020-04-05 | NA | NA | FALSE | 5669 | NA ¦ NA | 7069.8241 | 7069.8241 | 3627.4005 | 211.2978 | 3.5127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7069.8241 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 6224.6676 | 191.1469 | 3.1777 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2576 | Milpitas 115kV: Bus Reliability Improve. |  |  | Milpitas, Santa Clara | Replace circuit switchers 177 and 187 with circuit breakers in Milpitas. Install associated equipment as required. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-02-07 | 37 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave |  | NA | 3.3452 | NA | 115 kV | 171 | 9. Reliability (Low Safety Risk) | NA | 5.1001 | In-flight Future Scope | 5777265 | T.0003451 | Milpitas 115kV: Bus Reliability Improve. | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-10-11 | NA | 2032-11-30 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 2438.4621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2577 | Butte: Convert 115kV Bus to BAAH |  |  | Chico, Butte | Upgrade the exisiting double-bus single-breaker set-up at Butte Substaton to a breaker-and-a-half (BAAH) layout. The new 115kV bus will include circuit breakers, disconnect switches, voltage transformers, current transformers, buses, bushings, structures, and connections of the equipment. A moudular control building (MPAC) will also be required. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-02-04 | 11 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 3.1949 | NA | 115 kV | 270 | 9. Reliability (Low Safety Risk) | 3 | 5.1001 | In-flight Future Scope | 5777333 | T.0003457 | Butte 115kV Sec MA BAAH DBSB | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Planning | 5 | 2032-03-30 | NA | 2034-03-03 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 22298.5971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2578 | EMBARCADERO: Cutover GIS BK 5 |  |  | San Francisco, San Francisco | Replace and upgrade the Embarcadero 230 kV bus. The new transmission bus will improve electric reliability in downtown San Francisco and reduce clearance restrictions for equipment maintenance, thereby eliminating abnormal conditions and instances where electric service to downtown San Francisco and the Financial District are at risk. The new bus will also be designed to accommodate future expansion. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-12 | NA | NA | Wires - Replacement Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.55624 | NA | 230 kV | 598 | 5a.Mitigates System Wide Failure Risk | NA | NA | NA | 5778322 | T.0003671 | SAN FRAN Z 230kV CONV\BAAH\REBUILD | 2 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2012 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-12-28 | 2018-12-28 | 2019-12-08 | Project Design | NA | FALSE | 94500 | NA ¦ NA | 1656.8186 | 1656.8186 | 382.4117 | 67.1788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1656.8186 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | 370.6854 | 92.9334 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2579 | Embarcadero 230 kV Bus Conv. Rel. Prj |  |  | San Francisco, San Francisco | Replace and upgrade the Embarcadero 230 kV bus. The new transmission bus will improve electric reliability in downtown San Francisco and reduce clearance restrictions for equipment maintenance, thereby eliminating abnormal conditions and instances where electric service to downtown San Francisco and the Financial District are at risk. The new bus will also be designed to accommodate future expansion. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-03-12 | 49 | NA | Wires - Replacement Alternative | $75 Mil – $100 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Subsidence |  | NA | 0.55624 | NA | 230 kV | 598 | NA | NA | NA | NA | 5731442 | T.0003671 | SAN FRAN Z 230kV CONV\BAAH\REBUILD | 2 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2012 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2014-09-01 | 2018-12-28 | 2017-07-31 | NA | NA | FALSE | 94500 | NA ¦ NA | 81219.4223 | 81219.4223 | -50.5346 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81219.4223 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2025 | -50.5346 | -928.2753 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 100% | 0% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2580 | Placer: Convert 60kV Bus Sec ""D"" |  |  | Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-02-04 | 65 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 kV | NA | NA | NA | 5.1 | In-flight Future Scope | 5801702 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2029-08-27 | 2024-12-30 | 2030-02-07 | Prioritization | NA | FALSE | 17200 | NA ¦ NA | 205.2962 | 5225.4853 | 0 | 0 | 27.7064 | 166.7087 | 10.8811 | 0 | 0 | 0 | 0 | 0 | 205.2962 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2025 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2581 | Placer: 60kV T-Line Work |  |  | Auburn, Placer ¦ Loomis, Placer ¦ Newcastle CDP, Placer ¦ Penryn CDP, Placer ¦ Placer ¦ Rocklin, Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2024-04-02 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | 60 kV | NA | NA | NA | 5.1 | In-flight Future Scope | 5801601 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2027-02-17 | 2024-12-30 | 2027-04-05 | Prioritization | NA | FALSE | 17200 | NA ¦ NA | 169.4983 | 3876.2257 | 0 | 0 | 24.56 | 134.8232 | 10.1151 | 0 | 0 | 0 | 0 | 0 | 169.4983 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 ¦ 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2582 | Placer: Convert 115kV Bus Sec ""E"" |  |  | Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-02-04 | 65 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 kV | NA | NA | NA | 5.1 | In-flight Future Scope | 5801700 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2028-07-19 | 2024-12-30 | 2029-08-01 | Prioritization | NA | FALSE | 17200 | NA ¦ NA | 446.776 | 7641.784 | 0 | 0 | 37.6157 | 390.5471 | 18.6133 | 0 | 0 | 0 | 0 | 0 | 446.776 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2583 | PLACER: CONVERT 60KV BUS SEC ""E"" |  |  | Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-02-04 | 62 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 60 kV | NA | NA | NA | 5.1 | In-flight Future Scope | 5796180 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA ¦ 5792685 ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2029-04-23 | 2024-12-30 | 2029-10-09 | Prioritization | NA | FALSE | 17200 | NA ¦ NA | 451.884 | 7291.2722 | 0 | 113.3854 | 93.4396 | 223.9046 | 21.1545 | 0 | 0 | 0 | 0 | 0 | 451.884 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2029 ¦ 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2584 | Placer: 115kV T-Line Work |  |  | Auburn, Placer ¦ Folsom, Sacramento ¦ Granite Bay CDP, Placer ¦ Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Line Termination | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-01-22 | NA | NA | Other - Status Quo | NA | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | NA | NA | 115 kV | NA | NA | NA | 5.1 | In-flight Future Scope | 5801600 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2029-01-02 | 2024-12-30 | 2030-09-26 | Prioritization | NA | FALSE | 17200 | NA ¦ NA | 304.302 | 3657.5842 | 0 | 0 | 30.2039 | 250.5653 | 23.5329 | 0 | 0 | 0 | 0 | 0 | 304.302 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2585 | Placer: Convert 115kV Bus Sec ""D"" |  |  | Placer | The existing 115 kV and 60 kV busses are of legacy designs that do not provide adequate emergency restoration and clearance support for a transmission substation, as well as having future expansion limitations. In 2016, Placer Sub experienced an animal related outage that impacted 14,654 Customers for 448,412 Customer-Minutes. Multiple deteriorated infrastructure replacement projects at Placer Sub, including replacement of OB insulators and bus relays, supported an economic decision to upgrade both busses at this time to improve system operation as well as to support Wildfire and PSPS events. The Placer 115 kV bus is arranged in a Single-Bus-Single-Breaker (SBSB) configuration which is targeted for elimination from the PG&E system. This bus Ranks #3 out of 941 in the Bus Reliability Program Ranking. The project scope of work includes following: • Convert 3 elements of 60 kV Main & Aux bus to Double-Bus-Single-Breaker (DBSB) • Replace Ohio Brass (OB) insulators on the 60 kV bus | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-02-04 | 65 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 2.9734 | NA | 115 kV | NA | NA | NA | 5.1 | In-flight Future Scope | 5801701 | T.0005697 | Placer: Rebuild Substation | 9 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2022 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | On Hold | 4 | 2029-08-27 | 2024-12-30 | 2030-04-19 | Prioritization | NA | FALSE | 17200 | NA ¦ NA | 291.9786 | 6440.8796 | 0 | 0 | 33.1651 | 244.5069 | 14.3065 | 0 | 0 | 0 | 0 | 0 | 291.9786 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2586 | HENRIETTA: Upgrade 230 KV Bus |  |  | Kings | The BAAH work scope under MWC 94 includes installation of three bays of 230 kV systems and its connection to the existing 230 kV bus at Henrietta Substation. The new 230 kV bus bus will include circuit breakers, disconnect switches, voltage transformers, current transformers, buses, bushings, structures, and connections of the equipment. Three bays with eight breakers will be installed to connect two lines and three transformer banks. T‐line re‐arrangement will be a required, but line relocation will depend on ultimate plan completion. | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-04-03 | 50 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Weather |  | NA | 7.0079 | NA | 230 kV | 171 | NA | NA | 5.1 | In-flight Future Scope | 5777343 | T.0007174 | Henrietta 230kV Bus Upgrade | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2031-12-18 | NA | 2032-11-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 15923.4527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 100% | 0% | NA
| 2587 | Eagle Rock: Convert 115 kV Bus |  |  | Sonoma | This planned project will convert Eagle Rock 115 kV bus to DBSB, decommission Geysers 3 & 4, and build 1.5 miles between Eagle Rock and Cloverdale Substations | Substation - Bus Arrangement | Upgrade/Retrofit | NA | T.0005743 | Reliability | Bus Upgrade | NA | NA | 2025-04-01 | NA | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ FALSE ¦ FALSE | FALSE | Corrosion |  | NA | 2.8266 | NA | 115 kV | NA | NA | NA | 5.1001 | In-flight Future Scope | 5799300 | T.0007732 | Eagle Rock: Convert 115 kV Bus | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2028-06-12 | NA | 2028-10-25 | NA | NA | FALSE | NA | NA ¦ NA | 1081.9556 | 3045.072 | 0 | 0 | 1081.9556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081.9556 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2028 ¦ 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2588 | Exchequer: Rebuild Substation |  |  | Mariposa | Rebuild Exchequer PG&E owned substation | Substation - Bus Arrangement | Upgrade/Retrofit | NA | NA | Reliability | Bus Upgrade | NA | NA | 2025-02-07 | 99 | NA | TBD | TBD | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | NA | 0.92717 | NA | 115 ¦ 70 kV | NA | NA | NA | 5.1 | In-flight Future Scope | EX113780 | TBD | TBD | TBD | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2028-06-01 | NA | 2029-12-01 | NA | NA | FALSE | NA | NA ¦ NA | 0 | 56000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 20000 | 20000 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2589 | Cortina #3 Improve Trans Line Reliab |  |  | Colusa ¦ Colusa, Colusa ¦ Williams, Colusa | The purpose of this project is to improve the reliability of the Cortina #3-60kV Line. The Cortina #3-60kV Line was placed on the list of worst performing circuits. This line is approximately 25 miles long and has a total of 471 structures. This project proposes to replace 105 poles and reframe structures, install vibration dampers install 2-guy-shunt splices, install jumper support I-strings, lube and adjust switches, secure or replace static ground wires and remove links to shorten jumpers and increase clearances on 271 structures. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2025-04-07 | 74 | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Extreme Heat |  | 25 | NA | 60 | NA | NA | NA | 573 | NA | NA | 5746614 | P.04885 | Cortina #3 Impr.Trans Line Reliab. Proj. | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2013 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | NA | 2014-12-31 | OAI | NA | NA | FALSE | 4805 | NA ¦ NA | 3408.2318 | 3408.2318 | -12.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3408.2318 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | -12.142 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2590 | Drum-Rio Oso 115 kV Re-Build (Phase 1) |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | The project proposes to abandon and rebuild the first 11 miles of the 45-mile long Drum-Rio Oso #1 and #2 circuits. Specifically, 241 lattice steel structures and conductors in the current 11 mile tower line (dual tower configuration) will be replaced with a double-circuit 115kV tower line (single tower configuration) using fire resistant, self-weathering steel poles and components, conductors in the centerline of the existing ROW.The project will also widen the existing ROW, where required, as the current ROW is only 70 feet wide. By replacing the existing dual tower configuration with a single, double-circuit tower line and siting them in the existing ROW centerline, the project will eliminate the need for a more rigorous permitting process, avoid costlier ROW land acquisition costs, and provide the new tower line greater clearance distances from the edges of the ROW. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2024-05-02 | 109 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 11 | NA | 115 | NA | 2032 | 1. Work that prevents fire ignition | 83 | 4.0111 | In-flight Future Scope | 5747900 | T.0000036 | Drum-Rio Oso 115kV Reliability | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6073-E | 2021-01-29 | Approved | 2021 | Operational | 2 | 2021-11-01 | 2022-02-09 | 2022-03-14 | NA | NA | TRUE | 54700 | NA ¦ NA | 19819.7581 | 20025.5791 | 802.6707 | 13798.9415 | 3862.5146 | 198.5989 | 94.8873 | 210.4758 | 0 | 0 | 0 | 0 | 19815.1032 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 18741.3367 | 190.3411 | 90.9418 | 4.4614 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $50 Mil – $75 Mil
| 2591 | Drum-Rio Oso 115 kV Re-Build (Phase 2) |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | The project proposes to abandon and rebuild the first 11 miles of the 45-mile long Drum-Rio Oso #1 and #2 circuits. Specifically, 241 lattice steel structures and conductors in the current 11 mile tower line (dual tower configuration) will be replaced with a double-circuit 115kV tower line (single tower configuration) using fire resistant, self-weathering steel poles and components, conductors in the centerline of the existing ROW.The project will also widen the existing ROW, where required, as the current ROW is only 70 feet wide. By replacing the existing dual tower configuration with a single, double-circuit tower line and siting them in the existing ROW centerline, the project will eliminate the need for a more rigorous permitting process, avoid costlier ROW land acquisition costs, and provide the new tower line greater clearance distances from the edges of the ROW. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | SCADA Switch Installation | NA | NA | 2023-07-07 | 109 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 11 | NA | 115 | NA | 534 | 1. Work that prevents fire ignition | NA | NA | NA | 5784525 | T.0000036 | Drum-Rio Oso 115kV Reliability | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6073-E | 2021-01-29 | Approved | 2021 | Operational | 2 | 2022-04-01 | 2022-02-09 | 2022-05-23 | NA | NA | FALSE | 54700 | NA ¦ NA | 4919.9874 | 4919.9874 | 29.919 | 326.9828 | 4332.809 | 27.3854 | 21.0365 | 0 | 0 | 0 | 0 | 0 | 4919.9874 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 4029.8861 | 22.5681 | 17.336 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $50 Mil – $75 Mil
| 2592 | Drum-Rio Oso 115 kV Re-Build (Phase 3) |  |  | Alta Sierra CDP, Nevada ¦ Nevada ¦ Placer ¦ Sheridan CDP, Placer ¦ Sheridan CDP, Sutter ¦ Sutter | The project proposes to abandon and rebuild the first 11 miles of the 45-mile long Drum-Rio Oso #1 and #2 circuits. Specifically, 241 lattice steel structures and conductors in the current 11 mile tower line (dual tower configuration) will be replaced with a double-circuit 115kV tower line (single tower configuration) using fire resistant, self-weathering steel poles and components, conductors in the centerline of the existing ROW.The project will also widen the existing ROW, where required, as the current ROW is only 70 feet wide. By replacing the existing dual tower configuration with a single, double-circuit tower line and siting them in the existing ROW centerline, the project will eliminate the need for a more rigorous permitting process, avoid costlier ROW land acquisition costs, and provide the new tower line greater clearance distances from the edges of the ROW. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2023-07-07 | 110 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | TRUE | Heat Wave ¦ Weather |  | 22 | NA | 115 | NA | 2032 | NA | NA | 4.0111 | In-flight Future Scope | 5788868 | T.0000036 | Drum-Rio Oso 115kV Reliability | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2019 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6073-E | 2021-01-29 | Approved | 2021 | Operational | 2 | 2022-10-03 | 2022-02-09 | 2023-10-23 | Prioritization | NA | TRUE | 54700 | NA ¦ NA | 28989.1547 | 28989.1547 | 0 | 15.5678 | 17297.3409 | 11500.4379 | 174.956 | 0.8522 | 0 | 0 | 0 | 0 | 28988.3025 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 0 | 24879.368 | 145.0629 | 0.72941 | 0% | NA ¦ NA | 230% ¦ Electric Operations Risk Management | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $40 Mil - $50 Mil ¦ $50 Mil – $75 Mil
| 2593 | Bridgeville-Garberville Imprv Tline Reli |  |  | Garberville CDP, Humboldt ¦ Humboldt | The purpose of this project is to determine the scope of improving reliability on the Bridgeville-Garberville 60kV Line. The Bridgeville-Garberville 60kV Line was placed on the list of worst performing circuits. This line is approximately 36 miles long and has a total of 490 structures. This project proposes to do any of the following items that are deemed appropriate by a thorough patrol and inspection: tree trimming, replace insulators, replace bond connectors with AMPACT connectors, bridge all distribution cross arms, reframe structures, secure or replace static ground wires, remove links to shorten jumpers and increase clearance, repair/replace structures, replace quadrant clams, replace vibration dampers, and adjust or replace switches. | Transmission Line - Switch | Upgrade/Retrofit | NA | T.0009603 | Reliability | SCADA Switch Installation | NA | NA | 2025-04-07 | 66 | NA | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 36 | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 115 | 4.0111 | In-flight Future Scope | 5747823 | T.0000044 | Bridgeville-Garberville 60kV Reliability | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2029-06-29 | NA | 2030-04-02 | NA | NA | FALSE | NA | NA ¦ NA | 61.4656 | 5228.4879 | 3.2674 | 2.685 | 4.2847 | 3.3005 | 13.1799 | 402.4151 | 0 | 0 | 0 | 0 | 60.7378 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2594 | Konocti Area Improve Trans Line Reliab |  |  | Hidden Valley Lake CDP, Lake ¦ Lake ¦ Lower Lake CDP, Lake ¦ Middletown CDP, Lake | This project proposes to increase reliability along the Clearlake-Konocti, Eagle Rock-Konocti, and Konocti-Middletown 60 kV lines by tree trimming, replace poles, replace insulators, reframe, install non-ceramic horizontal post jumper supports, bridging, install guy links, install raptor mitigation, install/replace vibration dampners, replace bolted connectors with fired wedge connectors and adjust/replace switches | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2024-06-20 | 23 | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 60 | NA | 430 | NA | NA | NA | NA | 5767140 | T.0000110 | Clearlake - Konocti Reliability | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2022 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-09-04 | 2019-02-15 | 2018-11-05 | NA | NA | FALSE | 6300 | NA ¦ NA | 855.6391 | 855.6391 | 0 | 0 | 37.1704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855.6391 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2025 | 0 | 0 | 32.9978 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: T-line maintenance or minor alteration activity, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2595 | Colgate-Challenge 60kV Imprv TLine Relia |  |  | Challenge-Brownsville CDP, Yuba ¦ Yuba | The project proposes to upgrade approximately 13 miles of the Colgate-Challenge 60kV line. Reliability upgrades include rotten pole replacements, reframes, replacement or installation of damaged and missing hardware, and raptor mitigation on 183 Structures between the Colgate and Challenge Substations. A four mile transmission reconductor with #2 ACSR will also be completed from structure 8/151 to the Challenge Substation. KPF Switch #19, Located at structure 5/99, will be replaced with a Triangular SEECO 70kV SCADA Switch with Special Motor Operator and Vacuum Interrupter. Wood poles will be replaced with light duty steel poles (LDSP’s). Note: Some field drilling will be required for LDSP installation. Helicopter and crane set procedures will be used for 103 pole structures and 43 anchors. Electric Transmission General Construction will perform their own pre-drilled holes at the pole and anchor set locations. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2023-05-04 | 21 | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 3 - Extreme ¦ Tier 2 - Elevated | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 4 | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 153 | NA | NA | 5747898 | T.0000112 | COLGATE-CHALLENGE RELIABILITY PROJEC | 1 | 94 | NA ¦ 5767640 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5114-E | 2017-07-14 | Approved | 2017 | Operational | 2 | 2018-09-17 | 2018-10-02 | 2021-06-30 | Weather | NA | FALSE | 9971 | NA ¦ NA | 13283.8988 | 13283.8988 | 1485.8532 | 1914.9444 | 35.5614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13283.8988 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 11765.7416 | 30.9094 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2596 | Monta Vista-Big Basin Sw 19 to Big Basin |  |  | Bonny Doon CDP, Santa Cruz ¦ Cupertino, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Address 15 miles of aging infrastructure on the Monta Vista – Burns 60 kV Line located in Tier 2 and 3 fire risk zones in Santa Clara and Santa Cruz Counties between Monta Vista and Big Basin Substations. The work includes the installation, replacement and reframing of poles, vibration dampers and insulators. The project will also address any line maintenance tags that are to be completed at that time, as well as completing the right-of-way (ROW) expansion tree trimming project for the line. During this timeframe the project scope was reduced to the 15-mile section from Monta Vista to Big Basin in order to better address risk mitigation and gain execution efficiencies. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2023-06-23 | 61 | NA | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 5.9 | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 78 | 4.0111 | Future IGP Scope | 5767513 | T.0000262 | MONTA VISTA-BIG BASIN SW 67 TO SW 19 | 3 | 94 | NA ¦ 5747825 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2034-07-27 | NA | 2035-01-15 | NA | NA | FALSE | NA | NA ¦ NA | 475.2117 | 18461.7513 | 37.0443 | 33.526 | 13.2144 | 0 | 18.6221 | 5.6272 | 0 | 0 | 0 | 0 | 469.5845 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2597 | Monta Vista-Big Basin M.V. Sub to Sw 67 |  |  | Bonny Doon CDP, Santa Cruz ¦ Cupertino, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Address 15 miles of aging infrastructure on the Monta Vista – Burns 60 kV Line located in Tier 2 and 3 fire risk zones in Santa Clara and Santa Cruz Counties between Monta Vista and Big Basin Substations. The work includes the installation, replacement and reframing of poles, vibration dampers and insulators. The project will also address any line maintenance tags that are to be completed at that time, as well as completing the right-of-way (ROW) expansion tree trimming project for the line. During this timeframe the project scope was reduced to the 15-mile section from Monta Vista to Big Basin in order to better address risk mitigation and gain execution efficiencies. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2023-06-23 | 61 | NA | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 5.5 | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 78 | 4.0111 | Future IGP Scope | 5767514 | T.0000262 | MONTA VISTA-BIG BASIN SW 67 TO SW 19 | 3 | 94 | NA ¦ 5747825 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2034-06-30 | NA | 2035-01-31 | NA | NA | FALSE | NA | NA ¦ NA | 500.3969 | 18457.3099 | 39.6316 | 35.5333 | 14.0595 | 0 | 19.0561 | 5.9254 | 0 | 0 | 0 | 0 | 494.4715 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2598 | Monta Vista-Big Basin Sw 67 to Sw 19 |  |  | Bonny Doon CDP, Santa Cruz ¦ Cupertino, Santa Clara ¦ Santa Clara ¦ Santa Cruz | Address 15 miles of aging infrastructure on the Monta Vista – Burns 60 kV Line located in Tier 2 and 3 fire risk zones in Santa Clara and Santa Cruz Counties between Monta Vista and Big Basin Substations. The work includes the installation, replacement and reframing of poles, vibration dampers and insulators. The project will also address any line maintenance tags that are to be completed at that time, as well as completing the right-of-way (ROW) expansion tree trimming project for the line. During this timeframe the project scope was reduced to the 15-mile section from Monta Vista to Big Basin in order to better address risk mitigation and gain execution efficiencies. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2023-06-23 | 61 | NA | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 3.7 | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 78 | 4.0111 | Future IGP Scope | 5767318 | T.0000262 | MONTA VISTA-BIG BASIN SW 67 TO SW 19 | 3 | 94 | NA ¦ 5747825 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | On Hold | 4 | 2032-09-24 | NA | 2034-01-10 | NA | NA | FALSE | NA | NA ¦ NA | 841.1969 | 18624.5806 | 63.4792 | 60.2489 | 25.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841.1969 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2599 | MERCED FALLS-EXCHEQUER 70KV RELIABILITY |  |  | Mariposa ¦ Merced | This project will replace existing Lattice Steel Poles/Steel Towers with new Lattice Steel Poles, replace insulators, and reconductor identified portions of the Merced Falls-Exchequer transmission line (~6 miles) | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2024-05-07 | 91 | NA | Other - Deferral | $5 Mil - $10 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 5.9 | NA | 70 | NA | 290 | 1. Work that prevents fire ignition | 342 | NA | NA | 5767308 | T.0000270 | MERCED FALLS-EXCHEQUER REL PROJECT | 1 | 94 | NA ¦ 5743840 ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5294-E | 2018-05-03 | Approved | 2018 | Operational | 2 | 2020-09-08 | 2020-10-04 | 2020-12-07 | NA | NA | FALSE | 12300 | NA ¦ NA | 7801.9408 | 7801.9408 | 6344.9774 | 526.9145 | 4.331 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 7801.9408 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 6529.6096 | 470.6393 | 3.8676 | 0.11077 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2600 | EXCHEQUER-YOSEMITE 70KV RELIABILITY - BEAR VALLEY SUB TO BRICEBURG SW |  |  | Mariposa | Replace/raise towers, install new lattice steel interset poles, replace insulators, add bird spikes, and re-tension and re-conductor identified portions of the Exchequer-Yosemite 70kV transmission line (~40 miles) to address California Public Utilities Commission (CPUC) General Order 95 (GO-95)1 infractions. Achieve Our Mission to safely and reliably deliver affordable and clean energy to our customers by striving to be the safest gas and electric company in the country and running an operationally excellent, resilient system: The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2025-04-07 | 119 | NA | Other - Status Quo | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 3.8 | NA | 70 | NA | 534 | 1. Work that prevents fire ignition | NA | NA | NA | 5774210 | T.0000322 | EXCHEQUER-YOSEMITE 70KV RELIABILITY | 5 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5486-E | 2019-02-28 | Approved | 2019 | Operational | 2 | 2019-09-16 | 2019-06-28 | 2019-12-23 | NA | NA | FALSE | 24800 | NA ¦ NA | 10787.2648 | 10787.2648 | -1280.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10787.2648 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2025 | -1016.6002 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2601 | EXCHEQUER-YOSEMITE 70KV RELIABILITY - BRICEBURG SW TO TOWER 024/99 |  |  | Mariposa | Replace/raise towers, install new lattice steel interset poles, replace insulators, add bird spikes, and re-tension and re-conductor identified portions of the Exchequer-Yosemite 70kV transmission line (~40 miles) to address California Public Utilities Commission (CPUC) General Order 95 (GO-95)1 infractions. Achieve Our Mission to safely and reliably deliver affordable and clean energy to our customers by striving to be the safest gas and electric company in the country and running an operationally excellent, resilient system: The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2025-04-07 | 71 | NA | Other - Deferral | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 3.1 | NA | 70 | NA | 534 | 1. Work that prevents fire ignition | 75 | NA | NA | 5774211 | T.0000322 | EXCHEQUER-YOSEMITE 70KV RELIABILITY | 5 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6085-E | 2021-02-11 | Approved | 2021 | Operational | 2 | 2021-06-08 | 2018-06-29 | 2021-09-27 | Scope Change | NA | FALSE | 24800 | NA ¦ NA | 10427.1255 | 10427.1255 | 149.1691 | 10267.1481 | -2.9577 | 1.2913 | 0 | 0 | 0 | 0 | 0 | 0 | 10427.1255 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 9480.0672 | -2.6853 | 1.1724 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2602 | EXCHEQUER-YOSEMITE 70KV RELIABILITY - TOWER 024/99 TO INDIAN FLAT SUB 35/203 |  |  | Mariposa | Replace/raise towers, install new lattice steel interset poles, replace insulators, add bird spikes, and re-tension and re-conductor identified portions of the Exchequer-Yosemite 70kV transmission line (~40 miles) to address California Public Utilities Commission (CPUC) General Order 95 (GO-95)1 infractions. Achieve Our Mission to safely and reliably deliver affordable and clean energy to our customers by striving to be the safest gas and electric company in the country and running an operationally excellent, resilient system: The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2025-04-07 | 71 | NA | Other - Deferral | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 11.4 | NA | 70 | NA | 534 | 1. Work that prevents fire ignition | 75 | NA | NA | 5774212 | T.0000322 | EXCHEQUER-YOSEMITE 70KV RELIABILITY | 5 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6085-E | 2021-02-11 | Approved | 2021 | Operational | 2 | 2021-07-07 | 2018-06-29 | 2021-09-27 | Scope Change | NA | FALSE | 24800 | NA ¦ NA | 20422.0252 | 20422.0252 | 43.231 | 20567.8386 | -192.7324 | 1.2913 | 0 | 0 | 0 | 0 | 0 | 0 | 20422.0252 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 18734.6324 | -175.0337 | 1.1727 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2603 | EXCHEQUER-YOSEMITE 70KV RELIABILITY - INDIAN FLAT SUB 35/203 TO 40/243 (EOL) |  |  | Mariposa | Replace/raise towers, install new lattice steel interset poles, replace insulators, add bird spikes, and re-tension and re-conductor identified portions of the Exchequer-Yosemite 70kV transmission line (~40 miles) to address California Public Utilities Commission (CPUC) General Order 95 (GO-95)1 infractions. Achieve Our Mission to safely and reliably deliver affordable and clean energy to our customers by striving to be the safest gas and electric company in the country and running an operationally excellent, resilient system: The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2025-04-07 | 73 | NA | Other - Deferral | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 5.1 | NA | 70 | NA | 534 | 1. Work that prevents fire ignition | 75 | NA | NA | 5774213 | T.0000322 | EXCHEQUER-YOSEMITE 70KV RELIABILITY | 5 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6085-E | 2021-02-11 | Approved | 2021 | Operational | 2 | 2021-08-02 | 2018-06-29 | 2021-11-08 | Scope Change | NA | FALSE | 24800 | NA ¦ NA | 10556.5712 | 10556.5712 | 32.9962 | 10290.3673 | 149.3124 | 8.3975 | 0 | 0 | 0 | 0 | 0 | 0 | 10556.5712 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 9373.014 | 134.3816 | 7.5578 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2604 | EXCHEQUER-YOSEMITE 70KV RELIABILITY - EXCHEQUER SUB TO BEAR VALLEY SUB |  |  | Mariposa | Replace/raise towers, install new lattice steel interset poles, replace insulators, add bird spikes, and re-tension and re-conductor identified portions of the Exchequer-Yosemite 70kV transmission line (~40 miles) to address California Public Utilities Commission (CPUC) General Order 95 (GO-95)1 infractions. Achieve Our Mission to safely and reliably deliver affordable and clean energy to our customers by striving to be the safest gas and electric company in the country and running an operationally excellent, resilient system: The project expects to improve service reliability in core operations and will improve system performance and reliability, which will reduce outages. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2025-04-07 | 71 | NA | Other - Deferral | NA | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 6.5 | NA | 70 | NA | 534 | 1. Work that prevents fire ignition | 75 | NA | NA | 5767391 | T.0000322 | EXCHEQUER-YOSEMITE 70KV RELIABILITY | 5 | 94 | NA ¦ 5745129 ¦ NA ¦ NA | TRUE | 2017 | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5766-E | 2020-02-20 | Approved | 2020 | Operational | 2 | 2020-11-03 | 2018-06-29 | 2021-01-13 | Bundling Dependencies | NA | FALSE | 24800 | NA ¦ NA | 10201.73 | 10201.73 | 6286.6648 | 275.2319 | -8.4123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10201.73 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 9343.732 | -7.6264 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | NA
| 2605 | Maple Creek#Willow Creek 60 kV Reliabili |  |  | Hoopa CDP, Humboldt ¦ Humboldt ¦ Willow Creek CDP, Humboldt | Increase reliability along the Maple Creek-Hoopa 60kV line by rebuilding a 20-mile section with new transmission poles and other reliability work. | Transmission Line - Switch | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2024-07-20 | 73 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | NA | NA | 60 | NA | 534 | 1. Work that prevents fire ignition | 84 | NA | NA | 5747824 | T.0000609 | MAPLE CREEK-WILLOW CK 60KV RELIABILITY | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2014 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5121-E | 2017-08-08 | Approved | 2017 | Operational | 2 | 2020-07-06 | 2018-01-29 | 2020-09-29 | Construction Delays | NA | FALSE | 15900 | NA ¦ NA | 10919.4919 | 10919.4919 | 7133.4455 | 534.1956 | -55.5298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10919.4919 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 9989.7945 | 509.658 | -52.9791 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $20 Mil - $30 Mil ¦ $50 Mil – $75 Mil
| 2606 | Ph 2-Maple Ck- Willow Ck REL |  |  | Hoopa CDP, Humboldt ¦ Humboldt ¦ Willow Creek CDP, Humboldt | Increase reliability along the Maple Creek-Hoopa 60kV line by rebuilding a 20-mile section with new transmission poles and other reliability work. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2024-07-20 | 64 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 10 | NA | 60 | NA | 534 | NA | NA | NA | NA | 5791525 | T.0000609 | MAPLE CREEK-WILLOW CK 60KV RELIABILITY | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6161-E | 2021-04-16 | Approved | 2021 | Operational | 2 | 2021-07-23 | 2020-06-30 | 2021-10-05 | Permitting | NA | FALSE | 15900 | NA ¦ NA | 16285.8328 | 16285.8328 | 73.7602 | 16446.2068 | -245.7801 | 11.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 16285.8328 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2023 ¦ 2025 | 0 | 12841.0551 | -190.7161 | 9.0367 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $20 Mil - $30 Mil ¦ $50 Mil – $75 Mil
| 2607 | Ph 3-Maple Ck- Willow Ck REL |  |  | Hoopa CDP, Humboldt ¦ Humboldt ¦ Willow Creek CDP, Humboldt | Increase reliability along the Maple Creek-Hoopa 60kV line by rebuilding a 20-mile section with new transmission poles and other reliability work. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2024-07-20 | 66 | NA | Multiple Options [See Notes] | Multiple Options [See Notes] | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Corrosion |  | 10.5 | NA | 60 | NA | 534 | NA | NA | NA | NA | 5791526 | T.0000609 | MAPLE CREEK-WILLOW CK 60KV RELIABILITY | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2018 | Project Management Governance Standard | 2020 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 6161-E | 2021-04-16 | Approved | 2021 | Operational | 2 | 2022-07-01 | 2020-06-30 | 2022-11-07 | Permitting | NA | FALSE | 15900 | NA ¦ NA | 36277.8838 | 36277.8838 | 15.3634 | 485.1761 | 27920.8998 | 7856.3519 | 0.0926 | 0 | 0 | 0 | 0 | 0 | 36277.8838 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2022 ¦ 2023 ¦ 2024 ¦ 2025 | 0 | 0 | 23255.3304 | 6412.05 | 0.0756 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [Alternative Solutions and Costs - Solutions] Other - Deferral ¦ Wires - Reconductor/Line Rebuild Alternative [Alternative Solutions and Costs - Costs] $20 Mil - $30 Mil ¦ $50 Mil – $75 Mil
| 2608 | Kilarc-Cedar Creek 60 kV Reliability |  |  | Round Mountain CDP, Shasta ¦ Shasta | This project proposes to Evaluate the line and complete targeted reliability improvements as recommended on the Kilarc – Cedar Creek 60kV Line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2023-12-20 | 68 | NA | TBD | TBD | Tier 3 - Extreme | FALSE ¦ TRUE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 13 | NA | 60 | NA | 412 | 1. Work that prevents fire ignition | 192 | 4.0111 | In-flight Future Scope | 5772894 | T.0002386 | Kilarc-Cedar Creek 60 kV Reliability | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2018 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2029-09-21 | NA | 2030-03-19 | NA | NA | FALSE | NA | NA ¦ NA | 893.8049 | 34704.3629 | 1.9631 | 4.2489 | 206.6536 | 592.0733 | 69.8633 | 63.3696 | 0 | 0 | 0 | 0 | 884.0024 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2609 | Nicolaus-Wilkens Slough 60kV line Pole |  |  | East Nicolaus CDP, Sutter ¦ Knights Landing CDP, Yolo ¦ Nicolaus CDP, Sutter ¦ Sutter ¦ Yolo | The purpose of this project is to improve the resistance of this line to failures caused by extreme wind speeds (in excess of 70mph) and to minimize future outages to Wilkins Slough Substation and 4 Reclamation District Substations. This project proposes to relocate/replace 274 wood transmission poles with light duty steel poles on the Nicolaus – Wilkins Slough 60kV Line, and Replace 2 manual switches on the District 1001 tap line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2025-03-08 | 75 | NA | Wires - Reconductor/Line Rebuild Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 43 | NA | 60 | NA | 240 | 2. Overhead With Strong Safety Link | 630 | 4.0111 | In-flight Future Scope | 5775319 | T.0003076 | Nicolaus-Wilkins Slough 60kV line Pole | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5459-E | 2018-12-28 | Approved | 2018 | On Hold | 4 | 2029-06-27 | 2022-10-11 | 2030-12-05 | Prioritization | NA | FALSE | 13482 | NA ¦ NA | 2281.4807 | 11057.05 | 173.1446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2281.4807 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2610 | Nicolaus-Wilkens Slough 60kV line Pole#2 |  |  | East Nicolaus CDP, Sutter ¦ Knights Landing CDP, Yolo ¦ Nicolaus CDP, Sutter ¦ Sutter ¦ Yolo | The purpose of this project is to improve the resistance of this line to failures caused by extreme wind speeds (in excess of 70mph) and to minimize future outages to Wilkins Slough Substation and 4 Reclamation District Substations. This project proposes to relocate/replace 274 wood transmission poles with light duty steel poles on the Nicolaus – Wilkins Slough 60kV Line, and Replace 2 manual switches on the District 1001 tap line. | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2025-03-08 | 75 | NA | Wires - Reconductor/Line Rebuild Alternative | $15 Mil - $20 Mil | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | Heat Wave ¦ Weather |  | 43 | NA | 60 | NA | 240 | 2. Overhead With Strong Safety Link | 630 | 4.0111 | In-flight Future Scope | 5782846 | T.0003076 | Nicolaus-Wilkins Slough 60kV line Pole | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2020 | Project Management Governance Standard | 2019 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NOC: AL 5459-E | 2018-12-28 | Approved | 2018 | On Hold | 5 | 2030-05-20 | 2022-10-11 | 2031-10-27 | Prioritization | NA | FALSE | 13482 | NA ¦ NA | 58.3617 | 1076.9495 | 1.9176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.3617 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | [Project Status] Project is On Hold due to prioritization and is not accuring AFUDC due to the automated AFUDC process
| 2611 | ELECTRA-VLY SPNGS REL./RECOND |  |  | Amador ¦ Calaveras ¦ Mokelumne Hill CDP, Calaveras ¦ Pine Grove CDP, Amador ¦ Pioneer CDP, Amador ¦ Red Corral CDP, Amador | This project proposes to reconductor the West Point-Valley Springs 60kV Line between Electra Substation and Valley Springs Substation to provide additional system capability to the area that serves electric customers in Calaveras County. The project scope of work includes the following: • Replace 181 wood poles with Light Duty Steel Poles (LDSP) and composite poles • Reconductor 10.9 miles line section with 715 All Aluminum Conductor (AAC) • Raise existing Tower 7/58 by 10 feet on the Tiger Creek-Valley Springs/Electra-Bellota 230kV • Install one SCADA Line Switch | Transmission Line - Conductor | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2024-12-09 | 60 | NA | TBD | TBD | Tier 3 - Extreme ¦ Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 10.9 | NA | 60 | NA | 564 | 1. Work that prevents fire ignition | 1 | 4.0111 | In-flight Future Scope | 5767631 | T.0003726 | ELECTRA TO WEST PT SCADA SWT. | 1 | 94 | NA ¦ 5743838 ¦ NA ¦ NA | TRUE | TBD | Project Management Governance Standard | 2017 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Engineering more than 50% complete | 4 | 2027-09-03 | NA | 2027-12-16 | NA | NA | FALSE | NA | NA ¦ NA | 2116.634 | 5979.8766 | 94.4834 | 172.5491 | 358.1085 | 255.985 | 150.2823 | 151.1795 | 0 | 0 | 0 | 0 | 2093.4736 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2027 ¦ 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 34.79% | 65.21% | NA
| 2612 | Palermo-Wyandotte: Reconfigure Wyandotte |  |  | Palermo CDP, Butte ¦ South Oroville CDP, Butte | This project proposes to complete the removal of the Caribou-Palermo 115kV Line by removing abandoned lattice steel tower structures and assessing the remaining towers supporting other transmission lines and replacing or strengthening these towers if needed. To mitigate the risk of Wyandotte being single sourced, this project proposes to reconfigure Wyandotte Substation to utilize the Paradise-Table Mountain 115kV circuit as a backup source. | Transmission Line - Multiple | Upgrade/Retrofit | NA | NA | Reliability | Targeted Line Reliability | NA | NA | 2024-03-05 | 45 | NA | Other - Deferral | $20 Mil - $30 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | NA | NA | 115 | NA | NA | NA | NA | NA | NA | 5795388 | T.0006251 | Caribou-Palermo 10391 Remove Structures | 5 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2021 | Project Management Governance Standard | 2021 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2021-07-16 | 2021-12-31 | 2021-07-29 | NA | NA | FALSE | 20700 | NA ¦ NA | 391.5892 | 391.5892 | 0 | 389.7281 | 1.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391.5892 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2021 ¦ 2022 ¦ 2025 | 0 | 374.1996 | 1.7867 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements
| 2613 | Stanislaus Manteca 2 035/212-233 Recond |  |  | Angels, Calaveras ¦ Calaveras ¦ Copperopolis CDP, Calaveras ¦ Manteca, San Joaquin ¦ San Joaquin ¦ Stanislaus ¦ Tuolumne ¦ Vallecito CDP, Calaveras | This project will increase operating flexibility, load serving capability, customer reliability, eliminate contingency overloads, and harden the transmission system by performing the following scope: • Reconductor 1.3 circuit miles between Riverbank Jct. SW STA and Structure 035/212 of the Stanislaus – Melones SW STA – Riverbank Jct. SW STA 115 kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating. • Reconductor 1.8 circuit miles between Riverbank SW STA and Valley Home Tap (038/233) of the Riverbank SW STA – Ripon 115 kV Line with 715 AAC conductor, or equivalent, to achieve at least 742 Amps of summer interior emergency rating. • Include all open maintenance tags within the project scope where applicable. • Replace structures, all insulators and insulator hardware to accommodate the increase in conductor size. | Transmission Line - Conductor | Upgrade/Retrofit | NA | T.0004301 ¦ T.0007979 ¦ T.0004515 | Reliability | Targeted Line Reliability | NA | NA | 2024-08-16 | 99 | NA | Other - Deferral | $15 Mil - $20 Mil | Tier 2 - Elevated ¦ Tier 1 | FALSE ¦ TRUE ¦ FALSE | FALSE | Extreme Heat |  | 1.3 | NA | 115 | NA | NA | NA | NA | 4.0111 | In-flight Future Scope | 5813401 | T.0008743 | Riverbank-Ripon - Line Reconductor | 3 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2025 | Project Management Governance Standard | 2024 | NA | FALSE | NA | NA | NA | FALSE | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | 5 | 2029-06-08 | 2027-12-31 | 2030-04-17 | Project Design | NA | FALSE | 23450 | NA ¦ NA | 0.1143 | 415.6376 | 0 | 0 | 0 | 0 | 0 | 0.1213 | 0 | 0 | 0 | 0 | 0 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | NA ¦ NA | TBD ¦ TBD | NA | 0% | 100% | NA
| 2614 | KERN OIL-WITCO BB: Replace Relay |  |  | Oildale CDP, Kern | Replace protection relays for CB 152 & 122 at Kern Oil Substation, Discovery and at Witco Sw Sta and associated equipment. System Protection recommends replacement of the whole panel, since remaining relays are at or beyond their life length expectancy on both the Kern Oil CB 122 & 152, Discovery and Witco Sw Sta. Also, it is necessary for fiber optic with two independent channels be installed for the current differential protection. | Substation - Protection Relay | Replace | NA | NA | Reliability | Age/Condition - Targeted Relay Replacement | NA | NA | 2025-04-04 | 49 | NA | Other - Status Quo | NA | Tier 1 | FALSE ¦ FALSE ¦ FALSE | FALSE | NA |  | NA | 4.2122 | NA | 115 kV | 437 | NA | NA | NA | NA | 5777183 | T.0003325 | BB:KERN OIL - WITCO RELAY REPLACEMENT | 1 | 94 | NA ¦ NA ¦ NA ¦ NA | TRUE | 2016 | Project Management Governance Standard | 2016 | NA | FALSE | NA | NA | NA | FALSE | NA | NA | NA | NA | NA | NA | NA | NA | NA [See Notes] | NA | Operational | 2 | 2018-08-02 | 2019-02-28 | 2018-12-19 | NA | NA | FALSE | 1486 | NA ¦ NA | 1582.5647 | 1582.5647 | 32.8273 | 107.4808 | 44.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1582.5647 | Accrued Overheard included in Data Field #57 | Accrued AFUDC included in Data Field #57 | 2020 ¦ 2021 ¦ 2022 ¦ 2025 | 32.0213 | 104.8413 | 43.4301 | 0 | 0 | 0 | 0% | NA ¦ NA | NA ¦ NA | NA | 0% | 100% | [CPUC Status] CPUC Permit Status Exempt: Substation modifications, not subject to GO 131-E NOC, PTC or CPCN requirements

## Data Field Descriptions
Line | Transmission Project Data Field | Format | Example | Input Terms and Descriptions | Notes
1 | Row/Line No. | Number (whole number) | 4 | Row/line number in spreadsheet. Include separate project lines, as described and required in data fields 26-28, for all subparts, i.e., ID #1 of all FERC-jurisdictional electric transmission projects, including generator interconnection-related network upgrades: 1. the total cost of which At Unique ID #2 will at any point equal or exceed $1 million. In the event that there is no ID#2 to provide, the million-dollar threshold applies to ID #1. and 2. for which there were capital expenditures in the last five years OR for which any capital expenditures are anticipated in the current or next four years, regardless of the actual or anticipated operative date. Each project should have at least one Row/Line No. in this spreadsheet, as subparts of projects will require additional project lines.
Project Description
2 | Project Name | Text String, separated by " ¦ " as necessary | Manzanita Substation | Include Project Name at date of report filing. Identify all prior names of the project and other names currently used in different venues, including the name as approved and included in the CAISO's TPP. | Please refer to Unique Utility ID#2 for the CAISO TPP Project Name
3a | Latitude | Number (decimal), separated by " ¦ " for multiple locations; NA if no geolocation | 20.234 ¦ 19.983 | Positive number indicates north of equator. Subject to redaction in the public data. | The lat/long provided for t-line projects is the end points for corresponding t-line.
3b | Longitude | Number (decimal), separated by " ¦ " for multiple locations; NA if no geolocation | -132.018 ¦ -132.231 | Negative number indicates west of Prime Meridian. Subject to redaction in the public data. | The lat/long provided for t-line projects is the end points for corresponding t-line.
4 | Location 2 | Text String, with comma separator between City and County. Multiple entries separated by " ¦ ". Order of values to be consistent with latitude and longitude values * City1, County1 ¦ City2, County2 | Berkeley, Alameda ¦ Concord, Contra Costa | All Cities and Counties included in the scope of the project. | Please note some assets have locations in a given county that does not have a a city. This is the case where only one location is provided. "CDP" refers to Census Designated Place.
5 | Project Description | Text String | This project will repair the transmission line connecting 4th and Townsend to the East Northfork station which failed as consequence of the 2019 San Clemente Hedge Fire. Assets to be replaced include... at ....kV. | General project overview: what, where, and why. Discuss all assets to be installed and include all capacities (MVA) and voltages (kV).
6 | Project Description - What | Select text from drop-down menu | Substation - Circuit Breaker | Transmission line (new, reconductor, relocation), substation (breaker, transformer relay protection), etc.
7 | Project Description - Action Taken | Select text from drop-down menu(s) | Upgrade/Retrofit | See drop-down menu for options. If more than two options are required, select "Multiple Options" in second column and provide remaining responses, pipe-delimited, in "Notes" data field. If the primary or secondary purpose relates to complying with a NERC, WECC, or CAISO requirement, list the specific standard(s), requirement(s), and/or any contingencies that are being addressed.
8 | Project Dependencies | Number (whole) indicating required project or projects' Unique ID #(s), separated by " ¦ " as necessary | 235435 ¦ 432787 | Identify all other projects (Unique ID #1) in the spreadsheet that this project depends on and/or whose construction will be bundled with this project. | For a given PO, Project Dependencies are identified as T.Dots if part of a different T.Dot. While POs can be populated and would require including many POs in this field, the T.Dot is the most complete option as it captures the entire project. POs are populated where there is not T.Dot. Projects within the same T.Dot are inherently dependent and therefore N/A is populated.
9 | Primary Purpose | Select text from drop-down menu | Reliability | May include, but not limited to: CAISO Transmission Planning Standards (NERC Compliance and contingency code, WECC Requirement (and the specific requirement)), Reliability, Load Growth, Local Capacity Requirement, Address Results of Power Flow Analysis, Address Results of Protection Studies, Physical Security, Policy, Economic, Generator Interconnection, Work Requested by Others, Age/End of Life, Wildfire Mitigation, Field Test Results, Emergency Event, Location, Environmental Conditions, Safety, Asset Condition, or Other. In the "Notes" data field, please explain a purpose identified as "Other" or provide additional details on the purpose identified.
10 | Secondary Purpose | Select text from drop-down menu | Age/Condition - Anti Climb Guards | May include, but not limited to: 3rd Party Damage, Age/Condition, Age/Condition - 230/115/70/60 kV Relay Replacement, Age/Condition - 500 kV Relay Replacement, Age/Condition - Anti Climb Guards, Age/Condition - Insulator Replacement - Steel, Age/Condition - Insulator Replacement - Wood, Age/Condition - Raptor Protection - Steel, Age/Condition - Replace 230/115/70/60 kV Breakers, Age/Condition - Replace 230/115/70/60 kV Transformers, Age/Condition - Replace 500 kV Breakers, Age/Condition - Replace 500 kV Transformers, Age/Condition - Replace Boardwalks, Age/Condition - Replace Breakers, Age/Condition - Replace Civil Structures, Age/Condition - Replace Conductor, Age/Condition - Replace Insulators, Age/Condition - Replace Other Substation Equipment, Age/Condition - Replace Other T-Line Equipment, Age/Condition - Replace Reactors, Age/Condition - Replace Relays, Age/Condition - Replace Relays, Age/Condition - Replace SCADA/RTU, Age/Condition - Replace Steel Poles, Age/Condition - Replace Switches, Age/Condition - Replace Transformers, Age/Condition - Replace Underground System, Age/Condition - Replace Wood Poles, Age/Condition - Switch Replacement - Steel, Age/Condition - Switch Replacement - Wood, Age/Condition - Targeted Relay Replacement, Age/Condition - Wood Pole Reframe, Animal Abatement, Automation, Bus Upgrade, Compliance - Remove Idle Facilities, Construct Roads/Gates/Culverts, Emergency Response - Fire Related, Emergency Response - Storm Related, Environmental, Facility Relocation, Fire Protection, Generation Interconnection, GO95 Mitigation - Steel, Install SCADA/RTU, Line Reconductoring, Line Termination, Load Interconnection, Modular Protection and Automation Control, NERC CIP Compliance, NERC Compliance - GO 95, New Substation, New T-Line, Priority 1 Steel Structure Replacement, Priority 1 Wood Structure Replacement, Protection NERC Compliance, Relay Upgrades, Replace Breakers, Replace Other Substation Equipment, Replace Transformers, Safety - Line Right of Way Access, SCADA Emergency Replacement, SCADA Switch Installation, Security Upgrades, Seismic Upgrade - Replace Conductor, Special Protection Scheme, Substation Capacity, Substation Reliability, System Design Upgrade, System Operations, Targeted Line Reliability, T-Line Capacity, T-Line Emergency, T-Line Reliability, Tools, Transformer Addition/Replacement, Underground Emergency, Voltage Conversion, Voltage Support. If the secondary purpose is to comply with a NERC, WECC, or CAISO requirement, list the standard, requirement, and/or any contingencies that are being addressed in the "Notes" data field.
11 | NERC/WECC/CAISO Standard/Requirement/Contingency | Select text from drop-down menu(s) | CIP-006 | See drop-down menu for options. If more than two options are required, select "Multiple Options" in second column and provide remaining responses, pipe-delimited, in "Notes" data field. If the primary or secondary purpose relates to complying with a NERC, WECC, or CAISO requirement, list the specific standard(s), requirement(s), and/or any contingencies that are being addressed in the "Notes" data field.
12 | Last Inspection | Date, formatted YYYY-MM-DD if text; NA if not yet inspected | 2019-12-10 | Specific date when the last inspection of the asset being repaired, replaced, or upgraded occurred. | The latest inspection date for overhead transmission lines is based on detailed ground and/or aerial inspections. These are done every 3 years for HFTD lines and 5 years for non-HFTD lines (3 years if 500 kV). Please note that transmission lines can be inspected via climbing as triggered, inspected by infrared (annually if Tier 3, 3 years if Tier 2 or Zone 1, and 5 years if non -HFTD), and are patrolled annually. “N/A” is noted for projects that do not impact assets that require inspections (e.g. technology or operational upgrades), or are programs that cover multiple assets in various locations (e.g. pole replacement). "TBD" is noted for projects that involve new assets that have yet to be installed.
13 | Age of Asset | Number (whole number) | 12 | Age in years from original in-service date of the asset being repaired, replaced, or upgraded. | The age of asset is a calculated value based on installation data of the asset at the functional location. For transmission lines, the assets on each line are not typically all the same age. Therefore, the age reflects an approximation of the oldest asset on the line for replacement projects. “N/A” is noted where there is no functional location for the project, programmatic work, or if the project is installing a new asset (e.g. new transmission line).
14 | Types of Analyses | Select text from drop-down menu | Load Flow | Types of analyses that have been performed on the asset being repaired, replaced, or upgraded (e.g., load flow, short circuit, corrosion). List all field test and results that indicated the need for the project, and include inspector ID, when available in the "Notes" data field.
15a | Alternative Solutions and Costs - Solutions | Select text from drop-down menu(s) | Dynamic System Analysis | See drop-down menu for options. If more than two options are required, select "Multiple Options" in second column and provide remaining responses, pipe-delimited, in "Notes" data field. Include all alternative solutions to the project that were considered and the costs of all alternatives considered. | Where "TBD" is indicated, that refers to planning and/or where the Project does not have utility approval yet.
15b | Alternative Solutions and Costs - Costs | Select text from drop-down menu(s) | $5 Mil - $10 Mil | See drop-down menu for options. If more than two options are required, select "Multiple Options" in second column and provide remaining responses, pipe-delimited, in "Notes" data field. If multiple responses as included for the Sulutions and Costs fields, please provide costs in the same order as solutions.
16 | CPUC Fire Threat Zone/Rating | Text String, separated by " ¦ " as necessary, or NA | HFTD Tier 2 | Indicate whether the project is located in Tier1, Tier 2, or Tier 3 of CPUC's High Fire-Threat Districts (HFTD) or Zone 1 in CalFire/USFS High Hazard Zone (HHZ). | If a project footprint spans multiple Tiers/Zone, all are listed. Tier 1 is any location that is not Tiers 2 & 3 and Zone 1. Programmatic Work is assigned Tier 1 unless the program is work specifically related to Tiers 2 & 3.
17 | Wildfire Related | Boolean, TRUE or FALSE, divided by " ¦ " | TRUE ¦ TRUE ¦ FALSE | Indicate whether the project is 1. related to repairing wildfire damage, 2. a measure identified in the Wildfire Mitigation Plan, or 3. is related to wildfire in some other way. If #3, please explain in the "Notes" data field. | Replacement and/or upgrades of transmission line assets for Projects in programs as defined in PG&E’s Wildfire Mitigation Plan (MWC 60, 70, 71, 82, 92, 93, & 94) with an in-service date of 2019 or later and assets with Fire Threat Tiers 2 or 3 or Zone 1 were designated as Wildfire Mitigation Plan. A small subset of MWC 2F and 65 Projects were designated as Wildfire Other on a project basis. In addition, PG&E has identified wildfire-related repair work, which is generally in category MWC 92, but may include other specific projects as well.
18 | RAMP | Boolean, TRUE or FALSE | TRUE | Indicate whether the project is a proposed mitigation measure in the utility's Risk Assessment & Mitigation Phase (RAMP).
19 | Other Environmental Factors | Text String, or NA | Project exists in CA Building Climate Zone 3 which presents a high risk of accelerated oxidation or steel structures due to coastal humidity and salt exposure. | Environmental factors in the project's location that may affect the length of the asset's service life.
20 | Project Manager | Text String: Last, First | Doe, John | Person in charge of the implementation of this project for the Utility.
21 | Transmission Project Size (length in miles) | Number (decimal), or NA | 42.66 | Miles of transmission power lines included in the project.
22 | Substation Project Footprint (acres) | Number (decimal), or NA | 12.25 | Acres of substation footprint included in the project.
23 | Transmission Voltage Level (kV) | Number (whole), separated by " ¦ " as necessary, or NA | 230 | Use kV for transmission power lines ratings.
24 | Substation or Transformer Capacity (MVA and/or kV) | Text String, separated by " ¦ " as necessary, or NA if unrelated | 115kV | Use MVA and/or kV for substations.
25 | Utility Prioritization Ranking | Number (whole), in reference to ranking system identified in field name | 1 | Using the Utility's prioritization ranking. If multiple metrics are used to prioritize projects, please include a separate data subfield for each. (Sub-columns can be created to accommodate multiple or tiered ranking methodologies.) | Loading Order was implemented in 2019 and applied to 2019 and beyond in the portfolio. Loading Order prioritization evaluates and prioritizes the work portfolio for Electric Operations in alignment with the reduction of both wildfire ignition and safety risk. RIBA scoring inputs (e.g. Safety, Environmental and Reliability) and Classifications (e.g. Required work flags) are used to aid in the assignment of Loading Order. Loading Order comprises of a scale from 1 to 9, with 1 being the highest priority and 9 being the lowest priority. "N/A" is listed for Projects before PG&E's usage of Loading Order or programmatic projects. Circuit Based Plan was implemented in 2020 and applied to 2020 and beyond in the portfolio. The CBP ranks each transmission circuit and substation 1-N, based on varying weighted risk values from a PSPS, safety, wildfire, reliability, and commitment/capacity driven perspective. CBP is used to identify critical circuits lines and substations, and also aid bundling of work occurring on the same line. "N/A" is listed for Projects before PG&E's usage of CBP. RBPPF was implemented in 2023 and applied to 2024 and beyond in the portfolio. Below is a description of the RBPPF Funding Tiers. o IGP: Electric distribution circuit, substation and transmission line capital investments that have been bundled and prioritized using PG&E’s Integrated Grid Planning approach. o Tier 5: Proposed non-IGP investment with the highest risk-reduction/compliance/capacity/reliability/other TNS objectives impact and highest urgency. Financial and/or opportunity losses due to inability to fund Tier 5 investments cannot be recovered in future periods. o Tier 4: Proposed non-IGP investment with high risk-reduction/compliance/capacity/reliability/other TNS objectives impact or high urgency. Financial and/or opportunity losses due to inability to fund Tier 4 investments are at high risk for non-recovery in future periods. o Tier 3: Proposed non-IGP investment with medium risk-reduction/compliance/capacity/reliability/other TNS objectives impact or medium urgency; financial and/or opportunity losses due to inability to fund Tier 3 investments are at medium risk for non-recovery in future periods. o Tier 2: Proposed non-IGP investment with low risk-reduction/compliance/capacity/reliability/other TNS objectives impact or low urgency; financial and/or opportunity losses due to inability to fund Tier 2 investments are recoverable in future periods. o Tier 1: Proposed non-IGP investment with no risk-reduction/compliance/capacity/reliability/other TNS objectives impact and no urgency; Financial and/or opportunity losses due to inability to fund Tier 1 investments are recoverable in future periods. o N/A: listed for Projects before PG&E’s usage of RBPPF To increase the information content of Value Category scoring an aggregate Value Category score reflecting how the proposed investment scored across all Value Categories will be created using the format described in order: Funding Tier Assignment, Count of Value Categories with a Score of 5, Count of Value Categories with a Score of 4, Count of Value Categories with a Score of 3, Count of Value Categories with a Score of 2, Count of Value Categories with a Score of 1.
26 | Utility Unique ID #1 | Text String | 78493 | Most specific (PG&E = Planning Order, SCE = SCE ID, SDG&E = Project ID)
27 | Utility Unique ID #2 | Text String | 432 | Less specific (PG&E = T.dot, SCE = Capital Work Breakdown Structure, SDG&E = Budget Code)
28 | Utility Unique ID #3 | Text String | 92 | Least specific (PG&E = Major Work Category, SCE = Project Identification Number , SDG&E = NA)
29 | Changes in Unique IDs | Date, formatted YYYY-MM-DD, and former identifiers: YYYY-MM-DD ¦ UID1 ¦ UID2 ¦ UID 3 If any components remain unchanged, use NA for those UIDs | 2022-05-05 ¦ NA ¦ NA ¦ 78322 | If any of the Unique IDs above changed at any time, please note the date of change and the former ID, using the presecribed format. | PG&E does not have a computerized method for tracking changes in unique IDs. However, PG&E took manual steps to provide the requested information for a portion of the Projects. PG&E is unable to provide the date of the change as well.
Utility/CAISO Approval and FERC Rate Cases
30 | Utility Approval | Boolean: TRUE or FALSE | TRUE | "TRUE" if the Utility self-approved the project; "FALSE" if not.
Year of AA
AA Collected
31 | Year of Internal Utility Approval | Date, formatted YYYY-MM-DD, or NA | 2022-01-02 | If utility has approved the project, insert first year of internal approval. If not insert "NA." | PG&E is treating this field as the Year of the first approved Business Case. Where "TBD" is indicated that means the Project has not yet advanced to the point at which the first business case is presented to PG&E management for approval. Where "N/A" is indicated, a Business Case is not applicable.
BC Collected
32 | Process(es) for Utility Approval | Text String, or NA | Annual Capital Operating Plan Process | If utility has approved the project, insert utility approval process for which a description has been provided to the CPUC and Stakeholders.
33 | Long term Transmission Investment Plan Inclusion | Year, formatted YYYY | 2022 | The year in which the project was first included in the utility's long-term transmission investment plan.
34 | CAISO Year | Year, formatted YYYY, or NA | 2019 | Insert the year when approved by CAISO. If not a CAISO-approved project, insert "NA".
35 | Transmission Planning Process ("TPP") Phase 3 | Boolean: TRUE or FALSE | FALSE | Please indicate with "TRUE" if any part of this project was subject to the competitive solicitation process in the TPP. In the "Notes" section briefly describe any portion of the project awarded to another developer and how it relates to the project in this Spreadsheet. | Please refer to the Project Description field for the description of the portion of the project awarded to another developer and how it relates to the project in this Spreadsheet.
36 | Year(s) when considered in CAISO TPP | Years, formatted YYYY and separated by " ¦ ", or NA | 2020 ¦ 2021 | Indicate years in which the project was considered in the TPP. If considered in year(s) prior to CAISO approval, please indicate all years.
37 | Year when expected to be considered in CAISO TPP | Years, formatted YYYY and separated by " ¦ ", or NA | 2025 | If not yet considered in the CAISO TPP, indicate the year when it is expected to be considered in the CAISO TPP.
38 | Link to TPP where project has been considered, approved, and/or expected to be considered | URL | http://www.caiso.com/Documents/BoardApproved-2017-2018_Transmission_Plan.pdf | Insert active hyperlink to any TPP where project was considered, including years in which the project was not approved. | CAISO does not archive Transmission Plans prior to 2013. CAISO Transmission Plans prior to 2013 are available on request.
39 | Generator Interconnection and Deliverability Allocation Procedures (GIDAP) Related | Boolean: TRUE or FALSE | TRUE | Please indicate with TRUE or FALSE whether this transmission project is a transmission network upgrade related to generator interconnection(s).
CPUC Permit Status
40a | CEQA Status | Select text from drop-down menu | Final Certified | See drop-down menu for options. Include one of the following: Expected PEA Completion, PEA Deemed Complete, CEQA Draft Published, CEQA Final Published, Final Certified, TBD, Other [See Notes], or NA.
40b | CEQA Status - Date | Date, formatted YYYY-MM-DD, or NA | 2020-03-29 | Include the date that corresponds with the CEQA status.
41a | CEQA Document Type | Select text from drop-down menu | EIR | Examples include: IS/ND, IS/MND, EIR, Exempted, Other, or NA (If "Other," include explanation in the "Notes" data field.).
41b | NEPA Document Type | Select text from drop-down menu | EIS | Examples include: EIS, EA, Categorical Exclusion, Other, or NA (If "Other," include explanation in the "Notes" data field.).
42a | CEQA Lead Agency | Text String, separated by " ¦ " as necessary, or NA | CPUC | Examples include: CPUC, SWRCB, CSLC, NA etc. If more than two options are required, enter each, pipe-delimited.
42b | NEPA Lead Agency | Text String, separated by " ¦ " as necessary, or NA | USFS | Examples include: USFS, NA etc. If more than two options are required, enter each, pipe-delimited.
43 | CPUC Filing Type | Text String, or NA | PG&E AL 2355-E | NOC Advice Letter (AL), Application for 851, PTC, CPCN, or NA. If an AL, include the number. If an Application, include number.
44 | CPUC Date Filed | Date, formatted YYYY-MM-DD, or NA | 2022-04-08 | The year filed at the CPUC or insert "Not yet filed" with the expected filing date.
45 | CPUC Status | Select text from drop-down menu | Approved | Indicate "Approved", "Rejected", "To be Filed", "Filed and Under Review," "Other," or "NA" (If "Other" or "NA", include explanation in the "Notes" data field.).
46 | CPUC Status - Year | Year, formatted YYYY, or NA | 2019 | Insert the year this CPUC Status was determined.
Project Status
47 | Project Status | Select text from drop-down menu | Construction (10%-25%) | See drop-down menu for options. Examples include: Planning, Engineering less than 50% complete, Engineering more than 50% complete, Permitting, Construction (include percentage of construction completed at the time this data spreadsheet is provided (i.e., less than 10%, 10%-25%, 25%-50%, 50%-75%, greater than 75%), Operational, On Hold, Canceled, or Abandoned (if On Hold, Canceled, or Abandoned, include explanation in the "Notes" data field.). | PG&E is using the Project Status of Programmatic Work for buckets and Planning for forecast placeholders. PG&E’s current systems have no way to track engineering & construction percentages. The % provided for Engineering and Construction Project Statuses are a function of the day the data was pulled from PG&E systems and milestone start and end dates or both Engineering and Construction.
48 | AACE Class | Select text from drop-down menu | 3 | The current Estimate Class in AACE International's Cost Estimate Classification System at the time this data spreadsheet is provided.
49 | Construction Start Date | Date, formatted YYYY-MM-DD, or NA | 2025-06-01 | The date on which construction began or is expected to begin.
50 | Original Planned In-Service Date | Date, formatted YYYY-MM-DD, or NA* | 2025-06-01 | What was the expected in-service date when the project was first approved by the CAISO? If not a CAISO-approved project, provide the expected in-service date when the project was approved internally by the Utility.
51 | Current Projected or Actual In-Service Date | Date, formatted YYYY-MM-DD, followed by OAI indicator if applicable (or NA) | 2021-01-01 ¦ NA 2021-01-01 ¦ OAI | At the time the data was extracted from the Utility’s Database(s) as provided in Section 2.1.5 of the Transmission Project Review Process Description. Projects without identified in-service dates that are "Operative as Installed" should be identified as "OAI".
52 | Reason for Change in In-Service Date | Select text from drop-down menu(s) | Customer Action | See drop-down menu for options. If the current projected or actual in-service date varies more than six months from the original in-service date, please select all reasons for this change. If more than two options are required, select "Multiple Options" in second column and provide remaining responses, pipe-delimited, in "Notes" data field.
53 | In-Flight Projects | Boolean: TRUE or FALSE | TRUE | For projects with costs expected to go into rate base in the current rate year or in the following rate year at FERC, please indicate with "TRUE." If there will be no additions to rate base in either year, indicate with "FALSE."
Costs
54 | Original Projected Cost or Cost Range ($000) | Dollar value, or dollar value range, separated by " ¦ " | 2100 ¦ 2500 | Forecast cost or forecast cost range for Utility Unique ID #2, i.e., the totality of the project, at the earliest of CAISO, CPUC, or utility internal approval.
55 | Cost Cap ($000) | Dollar value and Text String, separated by " ¦ ", or NA | 2500 ¦ CAISO TPP | Insert Cost Cap on project if available, as well as the authority imposing the cost cap. This shall include any maximum cost determined to be reasonable and prudent in a CPUC proceeding or a cost cap set for a competitively bid project in the CAISO's Transmission Planning Process.
56 | Current Projected Total or Actual Final Cost ($000) | Dollar value | 78 | Updated projected fully-loaded total or actual fully loaded final cost of project. Projected total should be the anticipated sum of all capital expenditures, overhead,and AFUDC. Actual cost should be the total expenditures, overhead and AFUDC in the addition to rate base. Operational projects and all data must remain in this report for at least five (5) years after the last of the project's expenditures and capital additions.
57 | Actual Capital Expenditures ($000) | Dollar value | 12 | Please include separate columns for each of the previous five (5) years and one for actual expenditures for the current year as of the date the data was extracted. If these expenditures do not include overheads and AFUDC, please provide those year-by-year.
58 | Projected Capital Expenditures ($000) | Dollar value | 4650 | For the current year and four (4) future years, provide the year-by-year fully-loaded forecast capital expenditures for the project. Please include separate columns for each year. If these expenditures do not include overheads and AFUDC, please provide those year-by-year.
59 | Construction Work in Progress Expenditures ($000) | Dollar value | 2350 | Total amount of money that has been spent so far for the project through the last calendar year.
60 | Accrued Overhead ($000) | Dollar value | 12 | If the capital expenditures provided in Data Field #57 do not include Overhead, please provide the accrued Overhead through the last calendar year.
61 | Accrued AFUDC ($000) | Dollar value | 0 | If the capital expenditures provided in Data Field #57 do not include AFUDC, please provide the accrued AFUDC through the last calendar year.
62 | FERC: Year(s) | Years, separated by " ¦ ", or NA | 2023 ¦ 2024 ¦ 2025 ¦ 2026 ¦ 2027 | Insert ALL rate years when any costs of this project went - or are forecast to go - into FERC jurisdictional transmission rate base.
63 | Dollars Put into FERC Rate Base ($000) | Dollar Value, per year column e.g., FERC_dollars_in_rate_base_2022 | 500000 | Insert the year(s) and actual dollars added to FERC jursidictional transmission rate base on the project for each of the four prior years and the present year. This should include additional costs added to rate base in years after operation first occurred.
64 | Percentage of Bid | Percentage to two decimals, and Text String, separated by " ¦ " | 33.33% ¦ "SuperPower LLC is developing a third of the project as part of its "TransValley Electrification" project. See http://.... | Percentage (or actual cost) of project implemented by outside developer, as opposed to the incumbent utility. If there is a project being developed by a non-incumbent utility that relates to this project, please indicate the name of the project as approved in the CAISO TPP. | 0% of the projects included in the TPR data spreadsheet are not being implemented by an outside developer. However, there are projects being developed by a non-incumbent utility that relates to some of these projects. Please refer to Unique Utility ID #2 for the name of the project as approved in the CAISO TPP.
65 | Percentage and Value ($000) of Work Requested by Others Passed onto Ratepayers | Percentage to two decimals and/or dollar value. If both, separate by " ¦ ". If either is not provided, please enter NA. | 25.00% ¦ 2300 35% ¦ NA NA ¦ 50000 | If the project is work requested by others or customer-driven, what percentage of the projects costs has been - or is expected to be - passed onto ratepayers? If the dollar amount being passed onto ratepayers is fixed, then this number can be expressed as a dollar amount. Please provide the values in order, using an NA placeholder if either is not provided.
66 | Cost-Benefit Analysis | Percentage to two decimals, and ranking system identifier, separated by " ¦ " | 25.00% ¦ EnergyRank | The Cost-to-Benefit ratio. If the Utility's Cost-Benefit analysis related to its Risk-Based Decision-Making Framework (RDF) has not already been included in the "Utility Prioritization Ranking" data field above, please include it here. | N/A is populated for Operational projects. TBD is provided for in-flight projects that do not have a project specific CBR score yet.
67 | FERC Incentives | Test Strings, separated by " ¦ ", or NA | Abandoned Plant ¦ CWIP | List any project-specific transmission incentives granted under any FERC Orders.
68 | Percentage of Cost in High Voltage TAC | Percentage to two decimals | 23.05% | Insert % of project cost recovered in the high-voltage TAC. | If in Data Field 65 (Percentage and Value ($000) of WRO Passed onto Ratepayers) the percentage is 0%, then PG&E has updated Data Field 68 (Percent Cost in High Voltage TAC) as well.
69 | Percentage of Cost in Low Voltage TAC | Percentage to two decimals | 0% | Insert % of project cost recovered in the low-voltage TAC. | If in Data Field 65 (Percentage and Value ($000) of WRO Passed onto Ratepayers) the percentage is 0%, then PG&E has updated Data Field 69 (Percent Cost in Low Voltage TAC) to 0% as well.
Notes
70 | Notes | Strings, inclusive of field identifiers in brackets, separated by 3 linebreaks ("\n\n\n"), or NA [ID1] String1 [ID2] String2 | [CEQA/NEPA Document Type] Form STD762 [CPUC Status] Approved in part following bifurcation. Details indeterminate as of 5/6/2024. Expected update and clarification by 8/1/2024. | Any additionally requested information or other needed details about the project that were not otherwise covered.

## Options Lists
06. Project Description - What | 07. Project Description - Action taken | 09. Primary Purpose | 10. Secondary Purpose | 11. NERC/WECC/CAISO Standard/Requirement/Contingency | 14. Types of Analyses | 15a. Alternative Solutions and Costs - Solutions | 15b. Alternative Solutions and Costs - Costs | 40. CEQA Status | 41a. CEQA Document Type | 41b. NEPA Document Type | 45. CPUC Status | 47. Project Status | 48. AACE Class | 52. Reason for Change in In-Service Date
Multiple Options [See Notes] | NA | Address Results of Power Flow Analysis | 3rd Party Damage | CAISO Requirement | Dynamic System Analysis | NA | $0 Mil – $1 Mil | TBD | EIR | Categorical Exclusion | Administratively Complete and Under Technical Review | Abandoned | NA | Bundling Dependencies
Other | Multiple Options [See Notes] | Address Results of Protection Studies | Age/Condition | Multiple Options [See Notes] | Interconnection System Impact/Facilities Studies | Non-Wires - Large Scale Energy Alternative | $1 Mil - $2 Mil | CEQA Draft Published | Exempted | EA | Advice Letter Filed and In-Process | Canceled | 1 | Clearances
Other - Civil | New | Age/End of Life | Age/Condition - 230/115/70/60 kV Relay Replacement | NA | Lifecycle Replacement Analysis | Non-Wires - System DER Alternative | $10 Mil -$15 Mil | CEQA Final Published | IS/MND | EIS | Approved | Construction (10%-25%) | 2 | Completed Early
Other - Cybersecurity | Relocate | Asset Condition | Age/Condition - 500 kV Relay Replacement | NERC BAL Compliance | Multiple Options [See Notes] | Other - Deferral | $100 Mil – $125 Mil | Expected PEA Completion | IS/ND | NA | Filed and Under Administrative Review | Construction (25%-50%) | 3 | Construction Delays
Other - Environmental | Removal | CAISO Transmission Planning Standards [See Notes for NERC Compliance and contingency code, WECC Requirement (and the specific requirement)] | Age/Condition - Anti Climb Guards | NERC CIP Compliance | NA | Other - Status Quo | $125 Mil - $150 Mil | Final Certified | NA | Other [See Notes] | NA [See Notes] | Construction (50%-75%) | 4 | Customer Action
Other - IT | Replace | Economic | Age/Condition - Insulator Replacement - Steel | NERC FAC Compliance | Other [See Notes] | TBD | $15 Mil - $20 Mil | NA | Other [See Notes] |  | Other [See Notes] | Construction (over 75%) | 5 | Input Error
Other - Operations Tech | Upgrade/Retrofit | Emergency Event | Age/Condition - Insulator Replacement - Wood | NERC PRC Compliance | Protection Studies | Wires - Bus Upgrade Alternative | $150 Mil - $175 Mil | Other [See Notes] |  |  | Rejected | Construction (under 10%) |  | ISO Action
Other - Physical Security |  | Field Test Results | Age/Condition - Raptor Protection - Steel | NERC TPL Standards | Short Circuit Duty Analysis | Wires - Location/Route Alternative | $175 Mil - $200 Mil | PEA Deemed Complete |  |  | To be Filed | Engineering less than 50% complete |  | Land Rights
Other - Remedial Action Scheme/Special Protection Scheme |  | Generator Interconnection | Age/Condition - Replace 230/115/70/60 kV Breakers | Other [See Notes] | Steady State Power Flow System Analysis | Wires - Minimum Required Scope (spot repair) Alternative | $2 Mil - $3 Mil |  |  |  |  | Engineering more than 50% complete |  | Material
Substation - Bus Arrangement |  | Load Growth | Age/Condition - Replace 230/115/70/60 kV Transformers | WECC Audit Findings |  | Wires - New Substation Alternative | $20 Mil - $30 Mil |  |  |  |  | On Hold |  | Multiple Options [See Notes]
Substation - Circuit Breaker |  | Local Capacity Requirement | Age/Condition - Replace 500 kV Breakers |  |  | Wires - New T-Line Alternative | $200 Mil - $250 Mil |  |  |  |  | Operational |  | NA
Substation - Line Termination |  | Location, Environmental Conditions | Age/Condition - Replace 500 kV Transformers |  |  | Wires - Reconductor/Line Rebuild Alternative | $250 Mil – $300 Mil |  |  |  |  | Permitting |  | Other [See Notes]
Substation - Modular Protection and Automation Control Building |  | Other [See Notes] | Age/Condition - Replace Boardwalks |  |  | Wires - Replacement Alternative | $3 Mil -$5 Mil |  |  |  |  | Planning |  | Outage
Substation - Multiple |  | Physical Security | Age/Condition - Replace Breakers |  |  | Wires - System Configuration Alternative | $30 Mil - $40 Mil | [6 empty] | Permitting
Substation - Other Equipment |  | Policy | Age/Condition - Replace Civil Structures |  |  | Wires - Voltage Support/Reactive Support Alternative | $300 Mil - $350 Mil | [6 empty] | Prioritization
Substation - Protection Relay |  | Reliability | Age/Condition - Replace Conductor |  |  |  | $350 Mil – $400 Mil | [6 empty] | Project Design
Substation - Reactive Equipment |  | Safety | Age/Condition - Replace Insulators |  |  |  | $40 Mil - $50 Mil | [6 empty] | Scope Change
Substation - Structure |  | Wildfire Mitigation | Age/Condition - Replace Other Substation Equipment |  |  |  | $400 Mil - $500 Mil | [6 empty] | Vendor Quality/Delays
Substation - Switch |  | Work Requested by Others | Age/Condition - Replace Other T-Line Equipment |  |  |  | $5 Mil - $10 Mil | [6 empty] | Weather
Substation - Transformer |  |  | Age/Condition - Replace Reactors |  |  |  | $50 Mil – $75 Mil | [6 empty] | Workforce
Substation - Voltage Support Equipment |  |  | Age/Condition - Replace Relays |  |  |  | $75 Mil – $100 Mil
Transmission Line - Conductor |  |  | Age/Condition - Replace Relays |  |  |  | Multiple Options [See Notes]
Transmission Line - Multiple |  |  | Age/Condition - Replace SCADA/RTU |  |  |  | NA
Transmission Line - Other Equipment |  |  | Age/Condition - Replace Steel Poles |  |  |  | Over $500 Mil
Transmission Line - Pole/Tower |  |  | Age/Condition - Replace Switches
Transmission Line - Right of Way |  |  | Age/Condition - Replace Transformers
Transmission Line - Switch |  |  | Age/Condition - Replace Underground System
Transmission Line - Underground |  |  | Age/Condition - Replace Wood Poles
Transmission Line/Substation |  |  | Age/Condition - Switch Replacement - Steel
Age/Condition - Switch Replacement - Wood
Age/Condition - Targeted Relay Replacement
Age/Condition - Wood Pole Reframe
Animal Abatement
Automation
Bus Upgrade
Compliance - Remove Idle Facilities
Construct Roads/Gates/Culverts
Emergency Response - Fire Related
Emergency Response - Storm Related
Environmental
Facility Relocation
Fire Protection
Generation Interconnection
GO95 Mitigation - Steel
Install SCADA/RTU
Line Reconductoring
Line Termination
Load Interconnection
Modular Protection and Automation Control
NERC CIP Compliance
NERC Compliance - GO 95
New Substation
New T-Line
Priority 1 Steel Structure Replacement
Priority 1 Wood Structure Replacement
Protection NERC Compliance
Relay Upgrades
Replace Breakers
Replace Other Substation Equipment
Replace Transformer
Safety - Line Right of Way Access
SCADA Emergency Replacement
SCADA Switch Installation
Security Upgrades
Seismic Upgrade - Replace Conductor
Special Protection Scheme
Substation Capacity
Substation Reliability
System Design Upgrade
System Operations
Targeted Line Reliability
T-Line Capacity
T-Line Emergency
T-Line Reliability
Tools
Transformer Addition/Replacement
Underground Emergency
Voltage Conversion
Voltage Support