## Annual Report
Pursuant to California Public Utilities Commission (Commission or CPUC) Decision 14-12-015, this is a draft of Pacific Power's Fire Incident Data Collection Plan annual report. The attached information is preliminary and subject to change. The information is provided to facilitate review and comment by the recipient parties. Fire incidents from 2020 where the cause of the ignition is under investigation have been excluded from this report.
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations |  |  |  |  | Notes (Optional):
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size (small assumed to be no more than .25 acres) | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Notes (Optional):
PacifiCorp | 2020-04-24 17:20 | 19:11 | 41.4184 | -122.4031 | Vegetation | Rural | <0.25 | Fire Agency | Cal-Fire, Hammond Ranch Fire, Weed Fire and Lake | 06241005.0108700 | none | 12,470 | Lightning arrestor | Overhead | Yes | 2020-04-24 | 19:11 | Contamination |  |  |  | Contamination
PacifiCorp | 2020-05-06 02:00 | 0:12 | 41.833 | -123.1743 | Vegetation | Highly Rural | <0.25 | Fire Agency | Klamath National Forest and Seiad Fire Dept. | D 06246011.0180660 T 2/23 | none | 12,740 / 69,000 | Conductor - Primary | Overhead | Yes | 2020-05-06 | 00:12 | Object contact |  | Vegetation Contact | Electric facility | Weather
PacifiCorp | 2020-05-28 | 22:53 | 41.5049 | -122.8561 | Vegetation | Highly Rural | <3 meters of linear travel | Fire Agency | Cal Fire | 06242009.0110400 | none | 12,470 | Conductor - Primary | Overhead | Yes | 2020-05-28 | 22:53 | Object contact |  | Vegetation Contact | Electric facility | Weather
PacifiCorp | 2020-07-16 17:20 | 17:20 | 41.491 | -120.5615 | grass and shed | Rural | 0.26-9.99 | Fire Agency | Alturas Fire | 06142012.0111203 | none | 12,470 | Conductor - Secondary | Overhead | No |  |  | Object contact |  | Vegetation Contact | Electric facility | External Force
PacifiCorp | 2020-07-23 14:40 | 17:50 | 41.1593 | -122.3054 | Vegetation | Highly Rural | <0.25 | Fire Agency | Dunsmuir Fire Dept | 11/60 | na | 69,000 | Insulator | Overhead | Yes | 2020-07-23 | 14:40 | Contamination |  |  | Electric facility | Contamination
PacifiCorp | 2020-08-04 16:10 | 5:18 | 41.5318 | -122.8581 | Structure | Highly Rural | Structure Only | Fire Agency | CAL fire, Etna and FT. Jones emergancy personel | 06242009.0112400 | none | 12,470 | Crossarm | Overhead | Yes | 2020-08-04 | 05:18 | Object contact |  | Animal contact | Electric facility | Bird nest
PacifiCorp | 2020-08-10 17:45 | 17:31 | 41.617 | -122.9704 | Vegetation | Highly Rural | <0.25 | Fire Agency | Local Fire Department | 06244010.0352201 | none | 12,470 | Connector device | Overhead | Yes | 2020-08-10 | 17:31 | Equipment failure | Connector device |  | Electric facility | Unknown
PacifiCorp | 2020-08-15 13:55 | 13:55 | 41.5753 | -122.8365 | Vegetation | Rural | <3 meters of linear travel | Unknown | Unknown | 06243009.0131300 | none | 12,470 | Fuse | Overhead | Yes | 2020-08-15 | 13:54 | Equipment failure | Fuse |  | Electric facility | old equipment
PacifiCorp | 2020-09-03 01:15 | 13:17 | 41.5185 | -122.5204 | Vegetation | Rural | <3 meters of linear travel | Unknown | Unknown | 06242006.0037601 | AT&T CALIFORNIA Telco | 12,470 | Connector device | Overhead | Yes | 2020-09-03 | 13:17 | Equipment failure | Connector device |  |  | Unknown
PacifiCorp | 2020-09-06 00:15 | 0:16 | 41.6086 | -122.7871 | Vegetation | Rural | <0.25 | Fire Agency | Cal Fire | 06243008.0056900 | none | 12,470 | Lightning arrestor | Overhead | no |  |  | Equipment failure | Lightning arrestor |  |  | Unknown
PacifiCorp | 2020-09-17 15:25 | 15:25 | 41.4999 | -122.8732 | Vegetation | Highly Rural | <0.25 | Fire Agency | Local Fire Department | 06242009.0102101 | none | 12,470 | Conductor - Primary | Overhead | Yes | 2020-09-17 | 15:25 | Object contact |  | Vegetation Contact | Electric facility | External Force
PacifiCorp | 2020-09-18 | 12:21 | 41.5623 | -122.9308 | Vegetation | Highly Rural | 0.26-9.99 | Fire Agency | Cal Fire | 06243009.0192400 | none | 12,470 | Sectionalizer | Overhead | Yes | 2020-09-18 | 12:21 | Object contact |  | Vegetation Contact | Electric facility | External Force
PacifiCorp | 2020-10-21 17:00 | 16:30 | 41.7725 | -122.525 | Vegetation | Rural | <0.25 | Fire Agency | Cal Fire | 06245006.0035001 | HUNTER COMMUNICATIONS (CA)(Fiber) | 12,470 | Support structure (pole or tower) | Overhead | Yes | 2020-10-21 | 16:30 | Object contact |  | Vehicle contact - car pole | Pole | External Force
PacifiCorp | 2020-11-01 | 13:33 | 41.4311 | -122.3748 | Structure | Rural | < 1 meter | Fire Agency | Local emergancy personnel | 06241005.0013641 | none | 12,470 | Insulator and bushing | Overhead | Yes | 2020-11-01 | 13:33 | Equipment failure | Insulator and bushing |  | Electric facility | Unknown
PacifiCorp | 2020-11-07 17:25 | 17:25 | 41.2629 | -122.2742 | vegetation and structure | Rural | 0.26-9.99 | Fire Agency | Cal Fire | 06240004.0357000 | none | 12,470 | Lightning arrestor | Overhead | Yes | 2020-11-07 | 5:30 | Equipment failure | Lightning arrestor |  |  | Unknown